05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CUNNINHAM__3__QUAHADA____3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO QUAHADA 3 115.0 KV 528394 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CUSTERMTN__3__PONDEROSA__3 | 3 Phase fault on CUSTERMTN 3 (528239) 115 kV Bus a. Apply fault at the CUSTERMTN 3 (528239) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTERMTN 3 115.0 KV 528239 TO PONDEROSA 3 115.0 KV 528240 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CUSTERMTN__3__WHITTEN____3 | 3 Phase fault on CUSTERMTN 3 (528239) 115 kV Bus a. Apply fault at the CUSTERMTN 3 (528239) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTERMTN 3 115.0 KV 528239 TO WHITTEN 3 115.0 KV 528540 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | DCP_ZIA_TP_3__DCP_ZIA____3 | 3 Phase fault on DCP_ZIA TP 3 (528422) 115 kV Bus a. Apply fault at the DCP_ZIA TP 3 (528422) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DCP_ZIA TP 3 115.0 KV 528422 TO DCP_ZIA 3 115.0 KV 528423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | DCP_ZIA_TP_3__MALJMAR1&2_3 | 3 Phase fault on DCP_ZIA TP 3 (528422) 115 kV Bus a. Apply fault at the DCP_ZIA TP 3 (528422) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ZIA 3 115.0 KV 528420 TO DCP_ZIA TP 3 115.0 KV 528422 CKT 1 b.2. MALJMAR1&2 3 115.0 KV 528406 TO ZIA 3 115.0 KV 528420 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | DRINKARD_TP3__DRINKARD___3 | 3 Phase fault on DRINKARD_TP3 (528533) 115 kV Bus a. Apply fault at the DRINKARD_TP3 (528533) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRINKARD_TP3 115.0 KV 528533 TO DRINKARD 3 115.0 KV 528589 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | DRINKARD___3__NA_ENRICH__3 | 3 Phase fault on DRINKARD 3 (528589) 115 kV Bus a. Apply fault at the DRINKARD 3 (528589) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRINKARD 3 115.0 KV 528589 TO NA_ENRICH 3 115.0 KV 528603 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | DUNCAN_4__DUNCHERTP4 | 3 Phase fault on DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138.0 KV 511453 TO DUNCHERTP4 138.0 KV 511552 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | DUNCAN_4__OMDUNCN4 | 3 Phase fault on DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138.0 KV 511453 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | EAGLE_CREEK3__EDDY_NTH___3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO EDDY_NTH 3 115.0 KV 527798 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | EDDY_CNTY__7__KIOWA______7 | 3 Phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 345.0 KV 527802 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | EDDY_NORTH_6__7_RIVERS___6 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 230.0 KV 527799 TO 7-RIVERS 6 230.0 KV 528095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | EDDY_NORTH_6__CUNNIGHM_N_6 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 230.0 KV 527799 TO CUNNIGHM_N 6 230.0 KV 527865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | EDDY_NTH___3__CV_8_MILE__3 | 3 Phase fault on EDDY_NTH 3 (527798) 115 kV Bus a. Apply fault at the EDDY_NTH 3 (527798) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NTH 3 115.0 KV 527798 TO CV-8_MILE 3 115.0 KV 527809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | EDDY_STH___3__CV_DAYTON_+3 | 3 Phase fault on EDDY_STH 3 (527793) 115 kV Bus a. Apply fault at the EDDY_STH 3 (527793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_STH 3 115.0 KV 527793 TO CV-DAYTON +3 115.0 KV 527821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | EDDY_STH___3__PECOS______3 | 3 Phase fault on EDDY_STH 3 (527793) 115 kV Bus a. Apply fault at the EDDY_STH 3 (527793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_STH 3 115.0 KV 527793 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | ELGINJT4__ELSWORTH___4 | 3 Phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT4 138.0 KV 511486 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | ENRON_TP___3__ENRON______3 | 3 Phase fault on ENRON_TP 3 (528317) 115 kV Bus a. Apply fault at the ENRON_TP 3 (528317) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENRON_TP 3 115.0 KV 528317 TO ENRON 3 115.0 KV 528318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | ENRON_TP___3__LEA_NATIONL3 | 3 Phase fault on ENRON_TP 3 (528317) 115 kV Bus a. Apply fault at the ENRON_TP 3 (528317) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENRON_TP 3 115.0 KV 528317 TO LEA_NATIONL3 115.0 KV 528399 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | EUNICE_____3__CARDINAL___3 | 3 Phase fault on EUNICE 3 (528512) 115 kV Bus a. Apply fault at the EUNICE 3 (528512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUNICE 3 115.0 KV 528512 TO CARDINAL 3 115.0 KV 528596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | EUNICE_____3__DRINKARD_TP3 | 3 Phase fault on EUNICE 3 (528512) 115 kV Bus a. Apply fault at the EUNICE 3 (528512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUNICE 3 115.0 KV 528512 TO DRINKARD_TP3 115.0 KV 528533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | FIESTA_____3__CARLSBAD___3 | 3 Phase fault on FIESTA 3 (528151) 115 kV Bus a. Apply fault at the FIESTA 3 (528151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIESTA 3 115.0 KV 528151 TO CARLSBAD 3 115.0 KV 528160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | FLETCHR4__FLE_TAP4 | 3 Phase fault on FLETCHR4 (511422) 138 kV Bus a. Apply fault at the FLETCHR4 (511422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR4 138.0 KV 511422 TO FLE TAP4 138.0 KV 511423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | FLE_TAP4__G16_097_TAP | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | FLE_TAP4__L_E_S__4 | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | FLOYD_CNTY_3__BLANCO_____3 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 115.0 KV 525780 TO BLANCO 3 115.0 KV 525803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | FLOYD_CNTY_3__TUCO_INT___3 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 115.0 KV 525780 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | G16_091_TAP__GEN_2016_095 | 3 Phase fault on G16-091-TAP (587744) 345 kV Bus a. Apply fault at the G16-091-TAP (587744) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-091-TAP 345.0 KV 587744 TO GEN-2016-095 345.0 KV 587770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | G17_151TAP__G18_015_TAP | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | G17_151TAP__GEN_2017_151 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO GEN-2017-151 345.0 KV 762217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | G17_171_TAP__GEN_2017_171 | 3 Phase fault on G17-171-TAP (760938) 345 kV Bus a. Apply fault at the G17-171-TAP (760938) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-171-TAP 345.0 KV 760938 TO GEN-2017-171 345.0 KV 760939 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | GEN_2016_091__G16_091_TAP | 3 Phase fault on GEN-2016-091 (587740) 345 kV Bus a. Apply fault at the GEN-2016-091 (587740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2016-091 345.0 KV 587740 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | GEN_2018_004__G18_004_TAP | 3 Phase fault on GEN-2018-004 (762438) 115 kV Bus a. Apply fault at the GEN-2018-004 (762438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-004 115.0 KV 762438 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | GEN_2018_015__G18_015_TAP | 3 Phase fault on GEN-2018-015 (762460) 345 kV Bus a. Apply fault at the GEN-2018-015 (762460) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-015 345.0 KV 762460 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | GRACMNT4__ANADARK4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | GRACMNT4__WASHITA4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO WASHITA4 138.0 KV 521089 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | GRACMNT7__G16_037_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | GRACMNT7__G16_091_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | GRACMNT7__GEN_2015_093 | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO GEN-2015-093 345.0 KV 563269 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | GRASSLAND__6__CIRRUS_WND_6 | 3 Phase fault on GRASSLAND 6 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6 (526677) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 6 230.0 KV 526677 TO CIRRUS_WND 6 230.0 KV 526679 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | HALECENTER_2__TUCO_INT___2 | 3 Phase fault on HALECENTER 2 (525738) 69 kV Bus a. Apply fault at the HALECENTER 2 (525738) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALECENTER 2 69.0 KV 525738 TO TUCO_INT 2 69.0 KV 525826 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | HALE_CNTY__3__PLANT_X____3 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 115.0 KV 525454 TO PLANT_X 3 115.0 KV 525480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | HALE_CNTY__3__TUCO_INT___3 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 115.0 KV 525454 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | HIGGEAST___3__HIGG_______3 | 3 Phase fault on HIGGEAST 3 (527286) 115 kV Bus a. Apply fault at the HIGGEAST 3 (527286) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGGEAST 3 115.0 KV 527286 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | HOBBS_INT__3__HIGG_______3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO BENSING 3 115.0 KV 528433 CKT 1 b.2. LOAD 1 528433 b.3. LOAD 1* 528433 b.4. HIGG 3 115.0 KV 527363 TO BENSING 3 115.0 KV 528433 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | HOBBS_INT__3__LE_WEST_SUB3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO LE-WEST_SUB3 115.0 KV 528333 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | HOBBS_INT__3__MADDOX_____3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO MADDOX 3 115.0 KV 528355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | HOBBS_INT__3__MILLEN_TPW_3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO MILLEN_TPW 3 115.0 KV 528434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | HOBBS_INT__6__ANDREWS____6 | 3 Phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 230.0 KV 527894 TO ANDREWS 6 230.0 KV 528604 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | HOBBS_INT__7__KIOWA______7 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | IMC__1_TP__3__IMC__1_____3 | 3 Phase fault on IMC_#1_TP 3 (528035) 115 kV Bus a. Apply fault at the IMC_#1_TP 3 (528035) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMC_#1_TP 3 115.0 KV 528035 TO IMC_#1 3 115.0 KV 528037 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | IMC__1_TP__3__XTO_DI9_TP_3 | 3 Phase fault on IMC_#1_TP 3 (528035) 115 kV Bus a. Apply fault at the IMC_#1_TP 3 (528035) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMC_#1_TP 3 115.0 KV 528035 TO XTO_DI9_TP 3 115.0 KV 528064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | INK_BASIN__6__HOBBS_INT__6 | 3 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 230.0 KV 527028 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | INTREPDW_TP3__IMC__1_TP__3 | 3 Phase fault on INTREPDW_TP3 (527999) 115 kV Bus a. Apply fault at the INTREPDW_TP3 (527999) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INTREPDW_TP3 115.0 KV 527999 TO IMC_#1_TP 3 115.0 KV 528035 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | INTREPDW_TP3__INTREPIDWST3 | 3 Phase fault on INTREPDW_TP3 (527999) 115 kV Bus a. Apply fault at the INTREPDW_TP3 (527999) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INTREPDW_TP3 115.0 KV 527999 TO INTREPIDWST3 115.0 KV 528000 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | JOHNCO_7__SUNNYSD7 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | JOHNSON_DRW3__HIGG_______3 | 3 Phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNSON_DRW3 115.0 KV 527362 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | JOHNSON_DRW3__TAYLOR_____3 | 3 Phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNSON_DRW3 115.0 KV 527362 TO TAYLOR 3 115.0 KV 528413 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | JONES______6__GRASSLAND__6 | 3 Phase fault on JONES 6 (526337) 230 kV Bus a. Apply fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES 6 230.0 KV 526337 TO GRASSLAND 6 230.0 KV 526677 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | KIOWA______7__N_LOVING___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO N_LOVING 7 345.0 KV 528185 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | KIOWA______7__RDRUNNER___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | KRESS_INT__3__HALE_CNTY__3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | KRESS_INT__3__SWISHER____3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO SWISHER 3 115.0 KV 525212 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LAMTON_____3__HALE_CNTY__3 | 3 Phase fault on LAMTON 3 (525414) 115 kV Bus a. Apply fault at the LAMTON 3 (525414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMTON 3 115.0 KV 525414 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LEA_NATIONL3__SUMMIT_3 | 3 Phase fault on LEA_NATIONL3 (528399) 115 kV Bus a. Apply fault at the LEA_NATIONL3 (528399) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEA_NATIONL3 115.0 KV 528399 TO SUMMIT_3 115.0 KV 528404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LEA_ROAD___3__OIL_CENTER_3 | 3 Phase fault on LEA_ROAD 3 (528505) 115 kV Bus a. Apply fault at the LEA_ROAD 3 (528505) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEA_ROAD 3 115.0 KV 528505 TO OIL_CENTER 3 115.0 KV 528552 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LE_SANANDRS2__LE_BUCKEYE_2 | 3 Phase fault on LE-SANANDRS2 (528622) 69 kV Bus a. Apply fault at the LE-SANANDRS2 (528622) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-SANANDRS2 69.0 KV 528622 TO LE-BUCKEYE 2 69.0 KV 528630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LE_SANANDRS2__LE_LEE_____2 | 3 Phase fault on LE-SANANDRS2 (528622) 69 kV Bus a. Apply fault at the LE-SANANDRS2 (528622) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-SANANDRS2 69.0 KV 528622 TO LE-LEE 2 69.0 KV 528634 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LE_SANANDRS2__LE_MHOON___2 | 3 Phase fault on LE-SANANDRS2 (528622) 69 kV Bus a. Apply fault at the LE-SANANDRS2 (528622) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-SANANDRS2 69.0 KV 528622 TO LE-MHOON 2 69.0 KV 528667 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LE_SANANDRS2__LE_VACUUM__2 | 3 Phase fault on LE-SANANDRS2 (528622) 69 kV Bus a. Apply fault at the LE-SANANDRS2 (528622) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-SANANDRS2 69.0 KV 528622 TO LE-VACUUM 2 69.0 KV 528642 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LE_SANANDRS3__LE_TXACO_TP3 | 3 Phase fault on LE-SANANDRS3 (528341) 115 kV Bus a. Apply fault at the LE-SANANDRS3 (528341) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-SANANDRS3 115.0 KV 528341 TO LE-TXACO_TP3 115.0 KV 528627 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LE_TXACO_TP3__LE_TEXACO__3 | 3 Phase fault on LE-TXACO_TP3 (528627) 115 kV Bus a. Apply fault at the LE-TXACO_TP3 (528627) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-TXACO_TP3 115.0 KV 528627 TO LE-TEXACO 3 115.0 KV 528792 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LE_WEST_SUB3__LE_NRTH_INT3 | 3 Phase fault on LE-WEST_SUB3 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3 (528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3 115.0 KV 528333 TO LE-NRTH_INT3 115.0 KV 528334 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LIVSTNRIDGE3__CARDINAL___3 | 3 Phase fault on LIVSTNRIDGE3 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 115.0 KV 527953 TO MEDANOS 3 115.0 KV 527954 CKT 1 b.2. LOAD 1 527954 b.3. MEDANOS 3 115.0 KV 527954 TO SAGE_BRUSH 3 115.0 KV 527955 CKT 1 b.4. LOAD 1 527955 b.5. LOAD 1* 527955 b.6. SAGE_BRUSH 3 115.0 KV 527955 TO CARDINAL 3 115.0 KV 528596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LIVSTNRIDGE3__WIPP_______3 | 3 Phase fault on LIVSTNRIDGE3 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 115.0 KV 527953 TO WIPP 3 115.0 KV 528009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LIVSTNRIDGE3__XTO_DI9_TP_3 | 3 Phase fault on LIVSTNRIDGE3 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 115.0 KV 527953 TO XTO_DI9_TP 3 115.0 KV 528064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LUBBCK_EST_6__JONES______6 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 230.0 KV 526299 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LUBBCK_STH_3__LUBBCK_EST_3 | 3 Phase fault on LUBBCK_STH 3 (526268) 115 kV Bus a. Apply fault at the LUBBCK_STH 3 (526268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 3 115.0 KV 526268 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LUBBCK_STH_6__JONES______6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO JONES 6 230.0 KV 526337 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LUBBCK_STH_6__WOLFFORTH__6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LWSTAP_4__L_E_S__4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LWSTAP_4__RPPAPER4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LWS___S4__LWSTAP_4 | 3 Phase fault on LWS S4 (511431) 138 kV Bus a. Apply fault at the LWS S4 (511431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS S4 138.0 KV 511431 TO LWSTAP 4 138.0 KV 511439 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | L_E_S__2__LGORE_N2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-N2 69.0 KV 511469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | L_E_S__2__LGORE_S2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-S2 69.0 KV 511470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | L_E_S__4__ARTVLTP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 b.2. LOAD 1 511474 b.3. SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | L_E_S__4__COMMTAP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | L_E_S__4__ELGINJT4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | L_E_S__7__G16_091_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | L_E_S__7__G17_171_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | MADDOX_____3__ENRON_TP___3 | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO PEARLE 3 115.0 KV 528392 CKT 1 b.2. LOAD 1 528392 b.3. LOAD 1* 528392 b.4. ENRON_TP 3 115.0 KV 528317 TO PEARLE 3 115.0 KV 528392 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | MADDOX_____3__G18_004_TAP | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | MADDOX_____3__MONUMENT___3 | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO MONUMENT 3 115.0 KV 528491 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection. High voltage issue at G18-004-TAP. | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800. Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | MAPCO______3__JOHNSON_DRW3 | 3 Phase fault on MAPCO 3 (527360) 115 kV Bus a. Apply fault at the MAPCO 3 (527360) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAPCO 3 115.0 KV 527360 TO JOHNSON_DRW3 115.0 KV 527362 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | MILLEN_TPW_3__MILLEN_TPE_3 | 3 Phase fault on MILLEN_TPW 3 (528434) 115 kV Bus a. Apply fault at the MILLEN_TPW 3 (528434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPW 3 115.0 KV 528434 TO MILLEN_TPE 3 115.0 KV 528436 CKT *1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | MILLEN_TPW_3__MILLEN_____3 | 3 Phase fault on MILLEN_TPW 3 (528434) 115 kV Bus a. Apply fault at the MILLEN_TPW 3 (528434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPW 3 115.0 KV 528434 TO MILLEN 3 115.0 KV 528435 CKT *1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | MILLEN_____3__MILLEN_TPE_3 | 3 Phase fault on MILLEN 3 (528435) 115 kV Bus a. Apply fault at the MILLEN 3 (528435) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN 3 115.0 KV 528435 TO MILLEN_TPE 3 115.0 KV 528436 CKT *1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | MINCO__7__CIMARON7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | MINCO__7__GEN_2017_233 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GEN-2017-233 345.0 KV 761250 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8 or reduce to 0.2.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | MINCO__7__GRACMNT7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | MINCO__7__MCNOWND7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MCNOWND7 345.0 KV 515444 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | MINCO__7__MNCWND37 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MNCWND37 345.0 KV 515549 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | MINCO__7__NORMHLL7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | MONUMENT___3__MONUMNT_TP_3 | 3 Phase fault on MONUMENT 3 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3 115.0 KV 528491 TO MONUMNT_TP 3 115.0 KV 528568 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | MONUMENT___3__W_HOBBS____3 | 3 Phase fault on MONUMENT 3 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3 115.0 KV 528491 TO W_HOBBS 3 115.0 KV 528498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | MONUMNT_TP_3__BYRD_TP____3 | 3 Phase fault on MONUMNT_TP 3 (528568) 115 kV Bus a. Apply fault at the MONUMNT_TP 3 (528568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMNT_TP 3 115.0 KV 528568 TO BYRD_TP 3 115.0 KV 528581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | MUSTANG____6__SEMINOLE___6 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6 (527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 230.0 KV 527149 TO SEMINOLE 6 230.0 KV 527276 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | NEEDMORE___6__YOAKUM_____6 | 3 Phase fault on NEEDMORE 6 (525586) 230 kV Bus a. Apply fault at the NEEDMORE 6 (525586) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEEDMORE 6 230.0 KV 525586 TO YOAKUM 6 230.0 KV 526935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | NEWHART____6__PLANT_X____6 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 230.0 KV 525461 TO PLANT_X 6 230.0 KV 525481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | NICHOLS____6__AMA_SOUTH__6 | 3 Phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 230.0 KV 524044 TO AMA_SOUTH 6 230.0 KV 524415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | NORTH_LOVNG3__AGAVE_PDURO3 | 3 Phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 115.0 KV 528182 TO AGAVE_PDURO3 115.0 KV 528195 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | NORTH_LOVNG3__BLACKRIVER_3 | 3 Phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 115.0 KV 528182 TO BLACKRIVER 3 115.0 KV 528193 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | NORTH_LOVNG3__HOPI_SUB___3 | 3 Phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 115.0 KV 528182 TO HOPI_SUB 3 115.0 KV 528226 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | NORTH_LOVNG3__SOUTH_LOVNG3 | 3 Phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 115.0 KV 528182 TO SOUTH_LOVNG3 115.0 KV 528192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | N_LOVING___7__CHINA_DRAW_7 | 3 Phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 345.0 KV 528185 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | OASIS______6__ROOSEVELT__6 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 230.0 KV 524875 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | OKLEHV24__OKLEHV14 | 3 Phase fault on OKLEHV24 (590001) 138 kV Bus a. Apply fault at the OKLEHV24 (590001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKLEHV24 138.0 KV 590001 TO OKLEHV14 138.0 KV 590003 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | OXY_WSEM_TP3__JOHNSON_DRW3 | 3 Phase fault on OXY_WSEM_TP3 (527325) 115 kV Bus a. Apply fault at the OXY_WSEM_TP3 (527325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OXY_WSEM_TP3 115.0 KV 527325 TO JOHNSON_DRW3 115.0 KV 527362 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | O_K_U__7__G17_151TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | O_K_U__7__G18_015_TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | O_K_U__7__GEN_2017_033 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO GEN-2017-033 345.0 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | O_K_U__7__L_E_S__7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO L.E.S.-7 345.0 KV 511468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | O_K_U__7__OKLAUN_HVDC7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO OKLAUN HVDC7 345.0 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | PCA________3__CARLSBAD___3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO CARLSBAD 3 115.0 KV 528160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | PCA________3__CV_LUSK_TP_3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO CV-LUSK_TP 3 115.0 KV 527948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | PCA________3__POTASH_JCT_3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO POTASH_JCT 3 115.0 KV 527962 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | PCA________3__XTO_BIGEDDY3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO XTO_BIGEDDY3 115.0 KV 528396 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | PHANTOM____3__SOUTH_LOVNG3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO MALAGABEND 3 115.0 KV 528194 CKT 1 b.2. LOAD 1 528194 b.3. SOUTH_LOVNG3 115.0 KV 528192 TO MALAGABEND 3 115.0 KV 528194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | PHANTOM____3__WOLFCAMP_TP3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO BOPCO_PKRLK3 115.0 KV 528020 CKT 1 b.2. LOAD 1 528020 b.3. BOPCO_PKRLK3 115.0 KV 528020 TO WOLFCAMP_TP3 115.0 KV 528235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | PHANTOM____3__WOOD_DRAW__3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO WOOD_DRAW 3 115.0 KV 528228 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | PHANTOM____7__CHINA_DRAW_7 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 345.0 KV 528015 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | PHANTOM____7__RDRUNNER___7 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 345.0 KV 528015 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | PLAINS_INT_3__YOAKUM_____3 | 3 Phase fault on PLAINS_INT 3 (526928) 115 kV Bus a. Apply fault at the PLAINS_INT 3 (526928) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINS_INT 3 115.0 KV 526928 TO YOAKUM 3 115.0 KV 526934 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | PLANT_X____6__G17_146_TAP | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO G17-146-TAP 230.0 KV 760498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | PLANT_X____6__SUNDOWN____6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO SUNDOWN 6 230.0 KV 526435 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | PLANT_X____6__TOLK_______6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | PLSNT_HILL_6__ROOSEVELT__6 | 3 Phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 230.0 KV 524770 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | POTASH_JCT_2__DUVAL__1___2 | 3 Phase fault on POTASH_JCT 2 (527961) 69 kV Bus a. Apply fault at the POTASH_JCT 2 (527961) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 2 69.0 KV 527961 TO DUVAL_#1 2 69.0 KV 527980 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | POTASH_JCT_2__KERMAC_____2 | 3 Phase fault on POTASH_JCT 2 (527961) 69 kV Bus a. Apply fault at the POTASH_JCT 2 (527961) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 2 69.0 KV 527961 TO KERMAC 2 69.0 KV 527996 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | POTASH_JCT_2__MISSCHEM_2_2 | 3 Phase fault on POTASH_JCT 2 (527961) 69 kV Bus a. Apply fault at the POTASH_JCT 2 (527961) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 2 69.0 KV 527961 TO MISSCHEM#2 2 69.0 KV 528022 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | POTASH_JCT_2__NATPOT_TP__2 | 3 Phase fault on POTASH_JCT 2 (527961) 69 kV Bus a. Apply fault at the POTASH_JCT 2 (527961) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 2 69.0 KV 527961 TO NATPOT_TP 2 69.0 KV 528145 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | POTASH_JCT_3__CARLSBAD___3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO CARLSBAD 3 115.0 KV 528160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | POTASH_JCT_3__INTREPDW_TP3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO INTREPDW_TP3 115.0 KV 527999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | POTASH_JCT_3__KIOWA______3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO KIOWA 3 115.0 KV 527966 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | POTASH_JCT_6__PECOS______6 | 3 Phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6 230.0 KV 527963 TO PECOS 6 230.0 KV 528179 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | POTTER_CO__6__NEWHART____6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | PRENTICE___3__YOAKUM_____3 | 3 Phase fault on PRENTICE 3 (526792) 115 kV Bus a. Apply fault at the PRENTICE 3 (526792) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRENTICE 3 115.0 KV 526792 TO YOAKUM 3 115.0 KV 526934 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | QUAHADA____3__DCP_ZIA_TP_3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO DCP_ZIA TP 3 115.0 KV 528422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | QUAHADA____3__LEA_NATIONL3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO LEA_NATIONL3 115.0 KV 528399 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | QUAHADA____3__PCA________3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO XTO_BIGEDDY3 115.0 KV 528396 CKT 1 b.2. LOAD 1 528396 b.3. PCA 3 115.0 KV 527930 TO XTO_BIGEDDY3 115.0 KV 528396 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | RANDALL____6__AMA_SOUTH__6 | 3 Phase fault on RANDALL 6 (524365) 230 kV Bus a. Apply fault at the RANDALL 6 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 230.0 KV 524365 TO AMA_SOUTH 6 230.0 KV 524415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | RDRUNNER___3__AGAVE_RHIL23 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHIL23 115.0 KV 528231 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | RDRUNNER___3__BATTLE_AXE_3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO BATTLE_AXE 3 115.0 KV 528040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | RDRUNNER___3__CUSTERMTN__3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO CUSTERMTN 3 115.0 KV 528239 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | RDRUNNER___3__GEN_2016_121 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO GEN-2016-121 115.0 KV 587990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | RDRUNNER___3__GEN_2018_052 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO GEN-2018-052 115.0 KV 762866 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | RDRUNNER___3__OCHOA______3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHILL3 115.0 KV 528230 CKT 1 b.2. LOAD 1 528230 b.3. AGAVE_RHILL3 115.0 KV 528230 TO OCHOA 3 115.0 KV 528232 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | RED_BLUFF__3__RDRUNNER___3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 115.0 KV 528018 TO RDRUNNER 3 115.0 KV 528025 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | RED_BLUFF__3__WIPP_______3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAND_DUNES 3 115.0 KV 528016 TO RED_BLUFF 3 115.0 KV 528018 CKT 1 b.2. WIPP 3 115.0 KV 528009 TO SAND_DUNES 3 115.0 KV 528016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | RED_BLUFF__3__WOLFCAMP_TP3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 115.0 KV 528018 TO WOLFCAMP_TP3 115.0 KV 528235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | ROOSEVELT__6__TOLK_______6 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 230.0 KV 524909 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | RR_SVC_HV__3__RDRUNNER___3 | 3 Phase fault on RR_SVC_HV 3 (528024) 115 kV Bus a. Apply fault at the RR_SVC_HV 3 (528024) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RR_SVC_HV 3 115.0 KV 528024 TO RDRUNNER 3 115.0 KV 528025 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8. Reclosing was removed.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | RSVLT_CC_E_7__CROSSROADS_7 | 3 Phase fault on RSVLT_CC_E 7 (527655) 345 kV Bus a. Apply fault at the RSVLT_CC_E 7 (527655) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_E 7 345.0 KV 527655 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | RUSHSPR7__GEN_2018_055 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345.0 KV 511571 TO GEN-2018-055 345.0 KV 762900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | RUSSELL____3__HIGG_______3 | 3 Phase fault on RUSSELL 3 (527284) 115 kV Bus a. Apply fault at the RUSSELL 3 (527284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL 3 115.0 KV 527284 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | SAGA_SCOL__7__CROSSROADS_7 | 3 Phase fault on SAGA_SCOL 7 (527610) 345 kV Bus a. Apply fault at the SAGA_SCOL 7 (527610) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAGA_SCOL 7 345.0 KV 527610 TO CROSSROADS 7 345.0 KV 527656 CKT 1 | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | SANGER_SW__3__G18_004_TAP | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | SANGER_SW__3__SW_4J44____3 | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO SW_4J44 3 115.0 KV 528484 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | SANGER_SW__3__W_BENDER___3 | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO OXYPERMIAN 3 115.0 KV 528575 CKT 1 b.2. LOAD 1 528575 b.3. LOAD 2 528575 b.4. OXY_NHU_RCF3 115.0 KV 528574 TO OXYPERMIAN 3 115.0 KV 528575 CKT 1 b.5. LOAD 1 528575 b.6. LOAD 2 528575 b.7. W_BENDER 3 115.0 KV 528449 TO OXY_NHU_RCF3 115.0 KV 528574 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | SN_JUAN_TAP6__CHAVES_CNTY6 | 3 Phase fault on SN_JUAN_TAP6 (524885) 230 kV Bus a. Apply fault at the SN_JUAN_TAP6 (524885) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SN_JUAN_TAP6 230.0 KV 524885 TO CHAVES_CNTY6 230.0 KV 527483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | SP_ABERNTHY2__TUCO_INT2__2 | 3 Phase fault on SP-ABERNTHY2 (525731) 69 kV Bus a. Apply fault at the SP-ABERNTHY2 (525731) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ABERNTHY2 69.0 KV 525731 TO TUCO_INT2 2 69.0 KV 525816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | SUNDOWN____6__WOLFFORTH__6 | 3 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 230.0 KV 526435 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | SUNNYSD7__G17_075_TAP | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G17-075-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | SUNNYSD7__GEN_2017_167 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO GEN-2017-167 345.0 KV 761859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | SWISHER____6__NEWHART____6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | SWISHER____6__TUCO_INT___6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | SW_4J44____3__TAYLOR_____3 | 3 Phase fault on SW_4J44 3 (528484) 115 kV Bus a. Apply fault at the SW_4J44 3 (528484) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OXY_S_HOBBS3 115.0 KV 528480 TO SW_4J44 3 115.0 KV 528484 CKT 1 b.2. S_HOBBS 3 115.0 KV 528477 TO OXY_S_HOBBS3 115.0 KV 528480 CKT 1 b.3. LOAD 1 528480 b.4. LOAD 2 528480 b.5. LOAD 3 528480 b.6. E_SANGER 3 115.0 KV 528470 TO S_HOBBS 3 115.0 KV 528477 CKT 1 b.7. LOAD 1 528477 b.8. LOAD 2 528477 b.9. TAYLOR 3 115.0 KV 528413 TO E_SANGER 3 115.0 KV 528470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | SW_4J44____3__W_HOBBS____3 | 3 Phase fault on SW_4J44 3 (528484) 115 kV Bus a. Apply fault at the SW_4J44 3 (528484) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW_4J44 3 115.0 KV 528484 TO W_HOBBS 3 115.0 KV 528498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | S_JAL______3__DOLLARHIDE_3 | 3 Phase fault on S_JAL 3 (528547) 115 kV Bus a. Apply fault at the S_JAL 3 (528547) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S_JAL 3 115.0 KV 528547 TO DOLLARHIDE 3 115.0 KV 528561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TAYLOR_____3__MILLEN_TPE_3 | 3 Phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 3 115.0 KV 528413 TO NE_HOBBS 3 115.0 KV 528442 CKT 1 b.2. LOAD 1 528442 b.3. MILLEN_TPE 3 115.0 KV 528436 TO NE_HOBBS 3 115.0 KV 528442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TAYLOR_____3__W_BENDER___3 | 3 Phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 3 115.0 KV 528413 TO W_BENDER 3 115.0 KV 528449 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TEAGUE_____3__CARDINAL___3 | 3 Phase fault on TEAGUE 3 (528526) 115 kV Bus a. Apply fault at the TEAGUE 3 (528526) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEAGUE 3 115.0 KV 528526 TO CARDINAL 3 115.0 KV 528596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TEAGUE_____3__S_JAL______3 | 3 Phase fault on TEAGUE 3 (528526) 115 kV Bus a. Apply fault at the TEAGUE 3 (528526) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEAGUE 3 115.0 KV 528526 TO S_JAL 3 115.0 KV 528547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TERRYRD7__G17_171_TAP | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TERRYRD7__RSHSPR1_MPT1 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RSHSPR1_MPT1 345.0 KV 511979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TERRYRD7__RUSHSPR7 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TERRYRD7__SUNNYSD7 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TOLK_______6__GEN_2017_158 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO GEN-2017-158 230.0 KV 762132 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TOLK_______6__LAMB_CNTY__6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO LAMB_CNTY 6 230.0 KV 525637 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TOLK_______6__NEEDMORE___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO NEEDMORE 6 230.0 KV 525586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TOLK_______6__TUCO_INT___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TOLK_______7__CROSSROADS_7 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TUCO_INT___2__LH_WIL&ELN+2 | 3 Phase fault on TUCO_INT 2 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 2 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 69.0 KV 525826 TO LH-WIL&ELN+2 69.0 KV 525853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TUCO_INT___2__SP_NEWDEAL_2 | 3 Phase fault on TUCO_INT 2 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 2 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 69.0 KV 525826 TO SP-NEWDEAL 2 69.0 KV 525885 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TUCO_INT___3__CARLISLE___3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO STANTON_W 3 115.0 KV 526076 CKT 1 b.2. LOAD 1 526076 b.3. STANTON_W 3 115.0 KV 526076 TO INDIANA 3 115.0 KV 526146 CKT 1 b.4. LOAD 1 526146 b.5. LOAD 2 526146 b.6. SP-ERSKINE 3 115.0 KV 526109 TO INDIANA 3 115.0 KV 526146 CKT 1 b.7. LOAD 1 526146 b.8. LOAD 2 526146 b.9. SP-ERSKINE 3 115.0 KV 526109 TO CARLISLE 3 115.0 KV 526160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TUCO_INT___3__LUBBCK_EST_3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TUCO_INT___6__ANTELOPE_1_6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO ANTELOPE_1 6 230.0 KV 525840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TUCO_INT___6__CARLISLE___6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO CARLISLE 6 230.0 KV 526161 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TUCO_INT___6__HALE_WNDCL16 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO HALE_WNDCL16 230.0 KV 525957 CKT 1 | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TUCO_INT___6__JONES______6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TUCO_INT___7__ELK_CT1 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO ELK_CT1 345.0 KV 525850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TUCO_INT___7__G17_151TAP | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TUCO_INT___7__YOAKUM_345 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO YOAKUM_345 345.0 KV 526936 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TWEEDY_____3__EDDY_NTH___3 | 3 Phase fault on TWEEDY 3 (527597) 115 kV Bus a. Apply fault at the TWEEDY 3 (527597) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWEEDY 3 115.0 KV 527597 TO EDDY_NTH 3 115.0 KV 527798 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | WHITTEN____3__LEA_ROAD___3 | 3 Phase fault on WHITTEN 3 (528540) 115 kV Bus a. Apply fault at the WHITTEN 3 (528540) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 3 115.0 KV 528519 TO WHITTEN 3 115.0 KV 528540 CKT 1 b.2. LOAD 1 528540 b.3. LEA_ROAD 3 115.0 KV 528505 TO WARD 3 115.0 KV 528519 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | WHITTEN____3__S_JAL______3 | 3 Phase fault on WHITTEN 3 (528540) 115 kV Bus a. Apply fault at the WHITTEN 3 (528540) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITTEN 3 115.0 KV 528540 TO S_JAL 3 115.0 KV 528547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | WOLFCAMP_TP3__WOLFCAMP___3 | 3 Phase fault on WOLFCAMP_TP3 (528235) 115 kV Bus a. Apply fault at the WOLFCAMP_TP3 (528235) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCAMP_TP3 115.0 KV 528235 TO WOLFCAMP 3 115.0 KV 528236 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | WWRDEHV7__BECKHAM7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | WWRDEHV7__DGRASSE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | WWRDEHV7__G07621119_20 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G07621119-20 345.0 KV 515599 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | WWRDEHV7__G16_003_TAP | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G16-003-TAP 345.0 KV 560071 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | WWRDEHV7__GUTHRIE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GUTHRIE7 345.0 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | WWRDEHV7__TATONGA7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | W_BENDER___3__N_HOBBS____3 | 3 Phase fault on W_BENDER 3 (528449) 115 kV Bus a. Apply fault at the W_BENDER 3 (528449) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_BENDER 3 115.0 KV 528449 TO N_HOBBS 3 115.0 KV 528456 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | W_HOBBS____3__DRINKARD_TP3 | 3 Phase fault on W_HOBBS 3 (528498) 115 kV Bus a. Apply fault at the W_HOBBS 3 (528498) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_HOBBS 3 115.0 KV 528498 TO DRINKARD_TP3 115.0 KV 528533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | XTO_DI9_TP_3__XTO_DI9____3 | 3 Phase fault on XTO_DI9_TP 3 (528064) 115 kV Bus a. Apply fault at the XTO_DI9_TP 3 (528064) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XTO_DI9_TP 3 115.0 KV 528064 TO XTO_DI9 3 115.0 KV 528066 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | XTO_MAHONEY6__GEN_2017_239 | 3 Phase fault on XTO_MAHONEY6 (527011) 230 kV Bus a. Apply fault at the XTO_MAHONEY6 (527011) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XTO_MAHONEY6 230.0 KV 527011 TO GEN-2017-239 230.0 KV 761355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | YOAKUM_345__HOBBS_INT__7 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | YOAKUM_____3__ARCO_TP____3 | 3 Phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 115.0 KV 526934 TO ARCO_TP 3 115.0 KV 527041 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | YOAKUM_____3__LG_PLSHILL_3 | 3 Phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 115.0 KV 526934 TO LG-PLSHILL 3 115.0 KV 527194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | YOAKUM_____6__BRU_SUB____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | YOAKUM_____6__INK_BASIN__6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO INK_BASIN 6 230.0 KV 527028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | YOAKUM_____6__MUSTANG____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO MUSTANG 6 230.0 KV 527149 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | YOAKUM_____6__SUNDOWN____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 b.2. SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | 53CACHE4__ARTVLTP4 | 3 Phase fault on 53CACHE4 (511509) 138 kV Bus a. Apply fault at the 53CACHE4 (511509) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53CACHE4 138.0 KV 511509 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | 7_RIVERS___6__PECOS______6 | 3 Phase fault on 7-RIVERS 6 (528095) 230 kV Bus a. Apply fault at the 7-RIVERS 6 (528095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 7-RIVERS 6 230.0 KV 528095 TO PECOS 6 230.0 KV 528179 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | AMA_SOUTH__6__SWISHER____6 | 3 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 230.0 KV 524415 TO SWISHER 6 230.0 KV 525213 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | AMOCOWASSON6__MUSTANG____6 | 3 Phase fault on AMOCOWASSON6 (526784) 230 kV Bus a. Apply fault at the AMOCOWASSON6 (526784) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCOWASSON6 230.0 KV 526784 TO MUSTANG 6 230.0 KV 527149 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | AMOCOWASSON6__XTO_MAHONEY6 | 3 Phase fault on AMOCOWASSON6 (526784) 230 kV Bus a. Apply fault at the AMOCOWASSON6 (526784) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCOWASSON6 230.0 KV 526784 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | ARTVLTP4__ARTVILL4 | 3 Phase fault on ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTVLTP4 138.0 KV 511537 TO ARTVILL4 138.0 KV 511538 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | BLCKRVR_DST3__CHINA_DRAW_3 | 3 Phase fault on BLCKRVR_DST3 (528206) 115 kV Bus a. Apply fault at the BLCKRVR_DST3 (528206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLCKRVR_DST3 115.0 KV 528206 TO CHINA_DRAW 3 115.0 KV 528222 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | BLUECLDPOI_6__NEEDMORE___6 | 3 Phase fault on BLUECLDPOI 6 (525585) 230 kV Bus a. Apply fault at the BLUECLDPOI 6 (525585) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUECLDPOI 6 230.0 KV 525585 TO NEEDMORE 6 230.0 KV 525586 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Reduce acceleration factor to 0.2.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | BORDER_____7__BECKHAM7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | BORDER_____7__TUCO_INT___7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO TUCO_INT 7 345.0 KV 525832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | BRU_SUB____6__OXYBRU_____6 | 3 Phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRU_SUB 6 230.0 KV 527009 TO OXYBRU 6 230.0 KV 527010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | BRU_SUB____6__XTO_MAHONEY6 | 3 Phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRU_SUB 6 230.0 KV 527009 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | BUCKEYE_TP_3__BUCKEYE____3 | 3 Phase fault on BUCKEYE_TP 3 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3 115.0 KV 528348 TO BUCKEYE 3 115.0 KV 528385 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | BUCKEYE_TP_3__LE_TXACO_TP3 | 3 Phase fault on BUCKEYE_TP 3 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3 115.0 KV 528348 TO LE-TXACO_TP3 115.0 KV 528627 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | BYRD_TP____3__BYRD_______3 | 3 Phase fault on BYRD_TP 3 (528581) 115 kV Bus a. Apply fault at the BYRD_TP 3 (528581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BYRD_TP 3 115.0 KV 528581 TO BYRD 3 115.0 KV 528582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CALLAHAN___3__FLOYD_CNTY_3 | 3 Phase fault on CALLAHAN 3 (525763) 115 kV Bus a. Apply fault at the CALLAHAN 3 (525763) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALLAHAN 3 115.0 KV 525763 TO FLOYD_CNTY 3 115.0 KV 525780 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CARDINAL___3__TARGA______3 | 3 Phase fault on CARDINAL 3 (528596) 115 kV Bus a. Apply fault at the CARDINAL 3 (528596) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARDINAL 3 115.0 KV 528596 TO TARGA 3 115.0 KV 528605 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CARLISLE___3__LP_DOUD_TP_3 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 115.0 KV 526160 TO LP-DOUD_TP 3 115.0 KV 526162 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CARLISLE___3__MURPHY_____3 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 115.0 KV 526160 TO MURPHY 3 115.0 KV 526192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CARLISLE___6__WOLFFORTH__6 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 230.0 KV 526161 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CARLSBAD___3__PECOS______3 | 3 Phase fault on CARLSBAD 3 (528160) 115 kV Bus a. Apply fault at the CARLSBAD 3 (528160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLSBAD 3 115.0 KV 528160 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CHAVES_CNTY6__EDDY_NORTH_6 | 3 Phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY6 230.0 KV 527483 TO EDDY_NORTH 6 230.0 KV 527799 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CHINA_DRAW_3__CD_SVC_HV__3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO CD_SVC_HV 3 115.0 KV 528225 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CHINA_DRAW_3__CHVRN_EDDYS3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO CHVRN_EDDYS3 115.0 KV 528252 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CHINA_DRAW_3__WOOD_DRAW__3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO WOOD_DRAW 3 115.0 KV 528228 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CHISHOLM7__BECKHAM7 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CHISHOLM7__G16_037_TAP | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | COMANC_2__L_E_S__2 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L.E.S.-2 69.0 KV 511466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | COMANC_4__112GORE4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | COMANC_4__COMMTAP4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | COMANC_4__L_E_S__4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | COMMTAP4__OMDUNCN4 | 3 Phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMMTAP4 138.0 KV 511494 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | COOPER_RNCH3__BYRD_TP____3 | 3 Phase fault on COOPER_RNCH3 (528554) 115 kV Bus a. Apply fault at the COOPER_RNCH3 (528554) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_RNCH3 115.0 KV 528554 TO BYRD_TP 3 115.0 KV 528581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | COX________3__HALE_CNTY__3 | 3 Phase fault on COX 3 (525326) 115 kV Bus a. Apply fault at the COX 3 (525326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 115.0 KV 525326 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CROSBY_____3__LUBBCK_EST_3 | 3 Phase fault on CROSBY 3 (525926) 115 kV Bus a. Apply fault at the CROSBY 3 (525926) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSBY 3 115.0 KV 525926 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CROSSROADS_7__EDDY_CNTY__7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 345.0 KV 527656 TO EDDY_CNTY 7 345.0 KV 527802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CUNNIGHM_N_6__POTASH_JCT_6 | 3 Phase fault on CUNNIGHM_N 6 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6 (527865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_N 6 230.0 KV 527865 TO POTASH_JCT 6 230.0 KV 527963 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CUNNIGHM_S_6__HOBBS_INT__6 | 3 Phase fault on CUNNIGHM_S 6 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 230.0 KV 527867 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CUNNINHAM__3__BUCKEYE_TP_3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO BUCKEYE_TP 3 115.0 KV 528348 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CUNNINHAM__3__HOBBS_INT__3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO HOBBS_INT 3 115.0 KV 527891 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CUNNINHAM__3__MADDOX_____3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO MADDOX 3 115.0 KV 528355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CUNNINHAM__3__MONUMNT_TP_3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO MONUMNT_TP 3 115.0 KV 528568 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CUNNINHAM__3__QUAHADA____3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO QUAHADA 3 115.0 KV 528394 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CUSTERMTN__3__PONDEROSA__3 | 3 Phase fault on CUSTERMTN 3 (528239) 115 kV Bus a. Apply fault at the CUSTERMTN 3 (528239) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTERMTN 3 115.0 KV 528239 TO PONDEROSA 3 115.0 KV 528240 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CUSTERMTN__3__WHITTEN____3 | 3 Phase fault on CUSTERMTN 3 (528239) 115 kV Bus a. Apply fault at the CUSTERMTN 3 (528239) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTERMTN 3 115.0 KV 528239 TO WHITTEN 3 115.0 KV 528540 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | DCP_ZIA_TP_3__DCP_ZIA____3 | 3 Phase fault on DCP_ZIA TP 3 (528422) 115 kV Bus a. Apply fault at the DCP_ZIA TP 3 (528422) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DCP_ZIA TP 3 115.0 KV 528422 TO DCP_ZIA 3 115.0 KV 528423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | DCP_ZIA_TP_3__MALJMAR1&2_3 | 3 Phase fault on DCP_ZIA TP 3 (528422) 115 kV Bus a. Apply fault at the DCP_ZIA TP 3 (528422) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ZIA 3 115.0 KV 528420 TO DCP_ZIA TP 3 115.0 KV 528422 CKT 1 b.2. MALJMAR1&2 3 115.0 KV 528406 TO ZIA 3 115.0 KV 528420 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | DRINKARD_TP3__DRINKARD___3 | 3 Phase fault on DRINKARD_TP3 (528533) 115 kV Bus a. Apply fault at the DRINKARD_TP3 (528533) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRINKARD_TP3 115.0 KV 528533 TO DRINKARD 3 115.0 KV 528589 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | DRINKARD___3__NA_ENRICH__3 | 3 Phase fault on DRINKARD 3 (528589) 115 kV Bus a. Apply fault at the DRINKARD 3 (528589) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRINKARD 3 115.0 KV 528589 TO NA_ENRICH 3 115.0 KV 528603 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | DUNCAN_4__DUNCHERTP4 | 3 Phase fault on DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138.0 KV 511453 TO DUNCHERTP4 138.0 KV 511552 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | DUNCAN_4__OMDUNCN4 | 3 Phase fault on DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138.0 KV 511453 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | EAGLE_CREEK3__EDDY_NTH___3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO EDDY_NTH 3 115.0 KV 527798 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | EDDY_CNTY__7__KIOWA______7 | 3 Phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 345.0 KV 527802 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | EDDY_NORTH_6__7_RIVERS___6 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 230.0 KV 527799 TO 7-RIVERS 6 230.0 KV 528095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | EDDY_NORTH_6__CUNNIGHM_N_6 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 230.0 KV 527799 TO CUNNIGHM_N 6 230.0 KV 527865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | EDDY_NTH___3__CV_8_MILE__3 | 3 Phase fault on EDDY_NTH 3 (527798) 115 kV Bus a. Apply fault at the EDDY_NTH 3 (527798) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NTH 3 115.0 KV 527798 TO CV-8_MILE 3 115.0 KV 527809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | EDDY_STH___3__CV_DAYTON_+3 | 3 Phase fault on EDDY_STH 3 (527793) 115 kV Bus a. Apply fault at the EDDY_STH 3 (527793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_STH 3 115.0 KV 527793 TO CV-DAYTON +3 115.0 KV 527821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | EDDY_STH___3__PECOS______3 | 3 Phase fault on EDDY_STH 3 (527793) 115 kV Bus a. Apply fault at the EDDY_STH 3 (527793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_STH 3 115.0 KV 527793 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | ELGINJT4__ELSWORTH___4 | 3 Phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT4 138.0 KV 511486 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | ENRON_TP___3__ENRON______3 | 3 Phase fault on ENRON_TP 3 (528317) 115 kV Bus a. Apply fault at the ENRON_TP 3 (528317) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENRON_TP 3 115.0 KV 528317 TO ENRON 3 115.0 KV 528318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | ENRON_TP___3__LEA_NATIONL3 | 3 Phase fault on ENRON_TP 3 (528317) 115 kV Bus a. Apply fault at the ENRON_TP 3 (528317) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENRON_TP 3 115.0 KV 528317 TO LEA_NATIONL3 115.0 KV 528399 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | EUNICE_____3__CARDINAL___3 | 3 Phase fault on EUNICE 3 (528512) 115 kV Bus a. Apply fault at the EUNICE 3 (528512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUNICE 3 115.0 KV 528512 TO CARDINAL 3 115.0 KV 528596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | EUNICE_____3__DRINKARD_TP3 | 3 Phase fault on EUNICE 3 (528512) 115 kV Bus a. Apply fault at the EUNICE 3 (528512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUNICE 3 115.0 KV 528512 TO DRINKARD_TP3 115.0 KV 528533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | FIESTA_____3__CARLSBAD___3 | 3 Phase fault on FIESTA 3 (528151) 115 kV Bus a. Apply fault at the FIESTA 3 (528151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIESTA 3 115.0 KV 528151 TO CARLSBAD 3 115.0 KV 528160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | FLETCHR4__FLE_TAP4 | 3 Phase fault on FLETCHR4 (511422) 138 kV Bus a. Apply fault at the FLETCHR4 (511422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR4 138.0 KV 511422 TO FLE TAP4 138.0 KV 511423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | FLE_TAP4__G16_097_TAP | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | FLE_TAP4__L_E_S__4 | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | FLOYD_CNTY_3__BLANCO_____3 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 115.0 KV 525780 TO BLANCO 3 115.0 KV 525803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | FLOYD_CNTY_3__TUCO_INT___3 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 115.0 KV 525780 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | G16_091_TAP__GEN_2016_095 | 3 Phase fault on G16-091-TAP (587744) 345 kV Bus a. Apply fault at the G16-091-TAP (587744) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-091-TAP 345.0 KV 587744 TO GEN-2016-095 345.0 KV 587770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | G17_151TAP__G18_015_TAP | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | G17_151TAP__GEN_2017_151 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO GEN-2017-151 345.0 KV 762217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | G17_171_TAP__GEN_2017_171 | 3 Phase fault on G17-171-TAP (760938) 345 kV Bus a. Apply fault at the G17-171-TAP (760938) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-171-TAP 345.0 KV 760938 TO GEN-2017-171 345.0 KV 760939 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | GEN_2016_091__G16_091_TAP | 3 Phase fault on GEN-2016-091 (587740) 345 kV Bus a. Apply fault at the GEN-2016-091 (587740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2016-091 345.0 KV 587740 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | GEN_2018_004__G18_004_TAP | 3 Phase fault on GEN-2018-004 (762438) 115 kV Bus a. Apply fault at the GEN-2018-004 (762438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-004 115.0 KV 762438 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | GEN_2018_015__G18_015_TAP | 3 Phase fault on GEN-2018-015 (762460) 345 kV Bus a. Apply fault at the GEN-2018-015 (762460) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-015 345.0 KV 762460 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | GRACMNT4__ANADARK4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | GRACMNT4__WASHITA4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO WASHITA4 138.0 KV 521089 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | GRACMNT7__G16_037_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | GRACMNT7__G16_091_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | GRACMNT7__GEN_2015_093 | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO GEN-2015-093 345.0 KV 563269 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | GRASSLAND__6__CIRRUS_WND_6 | 3 Phase fault on GRASSLAND 6 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6 (526677) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 6 230.0 KV 526677 TO CIRRUS_WND 6 230.0 KV 526679 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | HALECENTER_2__TUCO_INT___2 | 3 Phase fault on HALECENTER 2 (525738) 69 kV Bus a. Apply fault at the HALECENTER 2 (525738) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALECENTER 2 69.0 KV 525738 TO TUCO_INT 2 69.0 KV 525826 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | HALE_CNTY__3__PLANT_X____3 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 115.0 KV 525454 TO PLANT_X 3 115.0 KV 525480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | HALE_CNTY__3__TUCO_INT___3 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 115.0 KV 525454 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | HIGGEAST___3__HIGG_______3 | 3 Phase fault on HIGGEAST 3 (527286) 115 kV Bus a. Apply fault at the HIGGEAST 3 (527286) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGGEAST 3 115.0 KV 527286 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | HOBBS_INT__3__HIGG_______3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO BENSING 3 115.0 KV 528433 CKT 1 b.2. LOAD 1 528433 b.3. LOAD 1* 528433 b.4. HIGG 3 115.0 KV 527363 TO BENSING 3 115.0 KV 528433 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | HOBBS_INT__3__LE_WEST_SUB3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO LE-WEST_SUB3 115.0 KV 528333 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | HOBBS_INT__3__MADDOX_____3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO MADDOX 3 115.0 KV 528355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | HOBBS_INT__3__MILLEN_TPW_3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO MILLEN_TPW 3 115.0 KV 528434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | HOBBS_INT__6__ANDREWS____6 | 3 Phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 230.0 KV 527894 TO ANDREWS 6 230.0 KV 528604 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | HOBBS_INT__7__KIOWA______7 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | IMC__1_TP__3__IMC__1_____3 | 3 Phase fault on IMC_#1_TP 3 (528035) 115 kV Bus a. Apply fault at the IMC_#1_TP 3 (528035) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMC_#1_TP 3 115.0 KV 528035 TO IMC_#1 3 115.0 KV 528037 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | IMC__1_TP__3__XTO_DI9_TP_3 | 3 Phase fault on IMC_#1_TP 3 (528035) 115 kV Bus a. Apply fault at the IMC_#1_TP 3 (528035) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMC_#1_TP 3 115.0 KV 528035 TO XTO_DI9_TP 3 115.0 KV 528064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | INK_BASIN__6__HOBBS_INT__6 | 3 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 230.0 KV 527028 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | INTREPDW_TP3__IMC__1_TP__3 | 3 Phase fault on INTREPDW_TP3 (527999) 115 kV Bus a. Apply fault at the INTREPDW_TP3 (527999) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INTREPDW_TP3 115.0 KV 527999 TO IMC_#1_TP 3 115.0 KV 528035 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | INTREPDW_TP3__INTREPIDWST3 | 3 Phase fault on INTREPDW_TP3 (527999) 115 kV Bus a. Apply fault at the INTREPDW_TP3 (527999) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INTREPDW_TP3 115.0 KV 527999 TO INTREPIDWST3 115.0 KV 528000 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | JOHNCO_7__SUNNYSD7 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | JOHNSON_DRW3__HIGG_______3 | 3 Phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNSON_DRW3 115.0 KV 527362 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | JOHNSON_DRW3__TAYLOR_____3 | 3 Phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNSON_DRW3 115.0 KV 527362 TO TAYLOR 3 115.0 KV 528413 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | JONES______6__GRASSLAND__6 | 3 Phase fault on JONES 6 (526337) 230 kV Bus a. Apply fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES 6 230.0 KV 526337 TO GRASSLAND 6 230.0 KV 526677 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | KIOWA______7__N_LOVING___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO N_LOVING 7 345.0 KV 528185 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | KIOWA______7__RDRUNNER___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | KRESS_INT__3__HALE_CNTY__3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | KRESS_INT__3__SWISHER____3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO SWISHER 3 115.0 KV 525212 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LAMTON_____3__HALE_CNTY__3 | 3 Phase fault on LAMTON 3 (525414) 115 kV Bus a. Apply fault at the LAMTON 3 (525414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMTON 3 115.0 KV 525414 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LEA_NATIONL3__SUMMIT_3 | 3 Phase fault on LEA_NATIONL3 (528399) 115 kV Bus a. Apply fault at the LEA_NATIONL3 (528399) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEA_NATIONL3 115.0 KV 528399 TO SUMMIT_3 115.0 KV 528404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LEA_ROAD___3__OIL_CENTER_3 | 3 Phase fault on LEA_ROAD 3 (528505) 115 kV Bus a. Apply fault at the LEA_ROAD 3 (528505) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEA_ROAD 3 115.0 KV 528505 TO OIL_CENTER 3 115.0 KV 528552 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LE_SANANDRS2__LE_BUCKEYE_2 | 3 Phase fault on LE-SANANDRS2 (528622) 69 kV Bus a. Apply fault at the LE-SANANDRS2 (528622) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-SANANDRS2 69.0 KV 528622 TO LE-BUCKEYE 2 69.0 KV 528630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LE_SANANDRS2__LE_LEE_____2 | 3 Phase fault on LE-SANANDRS2 (528622) 69 kV Bus a. Apply fault at the LE-SANANDRS2 (528622) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-SANANDRS2 69.0 KV 528622 TO LE-LEE 2 69.0 KV 528634 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LE_SANANDRS2__LE_MHOON___2 | 3 Phase fault on LE-SANANDRS2 (528622) 69 kV Bus a. Apply fault at the LE-SANANDRS2 (528622) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-SANANDRS2 69.0 KV 528622 TO LE-MHOON 2 69.0 KV 528667 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LE_SANANDRS2__LE_VACUUM__2 | 3 Phase fault on LE-SANANDRS2 (528622) 69 kV Bus a. Apply fault at the LE-SANANDRS2 (528622) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-SANANDRS2 69.0 KV 528622 TO LE-VACUUM 2 69.0 KV 528642 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LE_SANANDRS3__LE_TXACO_TP3 | 3 Phase fault on LE-SANANDRS3 (528341) 115 kV Bus a. Apply fault at the LE-SANANDRS3 (528341) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-SANANDRS3 115.0 KV 528341 TO LE-TXACO_TP3 115.0 KV 528627 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LE_TXACO_TP3__LE_TEXACO__3 | 3 Phase fault on LE-TXACO_TP3 (528627) 115 kV Bus a. Apply fault at the LE-TXACO_TP3 (528627) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-TXACO_TP3 115.0 KV 528627 TO LE-TEXACO 3 115.0 KV 528792 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LE_WEST_SUB3__LE_NRTH_INT3 | 3 Phase fault on LE-WEST_SUB3 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3 (528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3 115.0 KV 528333 TO LE-NRTH_INT3 115.0 KV 528334 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LIVSTNRIDGE3__CARDINAL___3 | 3 Phase fault on LIVSTNRIDGE3 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 115.0 KV 527953 TO MEDANOS 3 115.0 KV 527954 CKT 1 b.2. LOAD 1 527954 b.3. MEDANOS 3 115.0 KV 527954 TO SAGE_BRUSH 3 115.0 KV 527955 CKT 1 b.4. LOAD 1 527955 b.5. LOAD 1* 527955 b.6. SAGE_BRUSH 3 115.0 KV 527955 TO CARDINAL 3 115.0 KV 528596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LIVSTNRIDGE3__WIPP_______3 | 3 Phase fault on LIVSTNRIDGE3 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 115.0 KV 527953 TO WIPP 3 115.0 KV 528009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LIVSTNRIDGE3__XTO_DI9_TP_3 | 3 Phase fault on LIVSTNRIDGE3 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 115.0 KV 527953 TO XTO_DI9_TP 3 115.0 KV 528064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LUBBCK_EST_6__JONES______6 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 230.0 KV 526299 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LUBBCK_STH_3__LUBBCK_EST_3 | 3 Phase fault on LUBBCK_STH 3 (526268) 115 kV Bus a. Apply fault at the LUBBCK_STH 3 (526268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 3 115.0 KV 526268 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LUBBCK_STH_6__JONES______6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO JONES 6 230.0 KV 526337 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LUBBCK_STH_6__WOLFFORTH__6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LWSTAP_4__L_E_S__4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LWSTAP_4__RPPAPER4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LWS___S4__LWSTAP_4 | 3 Phase fault on LWS S4 (511431) 138 kV Bus a. Apply fault at the LWS S4 (511431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS S4 138.0 KV 511431 TO LWSTAP 4 138.0 KV 511439 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | L_E_S__2__LGORE_N2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-N2 69.0 KV 511469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | L_E_S__2__LGORE_S2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-S2 69.0 KV 511470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | L_E_S__4__ARTVLTP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 b.2. LOAD 1 511474 b.3. SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | L_E_S__4__COMMTAP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | L_E_S__4__ELGINJT4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | L_E_S__7__G16_091_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | L_E_S__7__G17_171_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | MADDOX_____3__ENRON_TP___3 | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO PEARLE 3 115.0 KV 528392 CKT 1 b.2. LOAD 1 528392 b.3. LOAD 1* 528392 b.4. ENRON_TP 3 115.0 KV 528317 TO PEARLE 3 115.0 KV 528392 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | MADDOX_____3__G18_004_TAP | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | MADDOX_____3__MONUMENT___3 | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO MONUMENT 3 115.0 KV 528491 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | MAPCO______3__JOHNSON_DRW3 | 3 Phase fault on MAPCO 3 (527360) 115 kV Bus a. Apply fault at the MAPCO 3 (527360) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAPCO 3 115.0 KV 527360 TO JOHNSON_DRW3 115.0 KV 527362 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | MILLEN_TPW_3__MILLEN_TPE_3 | 3 Phase fault on MILLEN_TPW 3 (528434) 115 kV Bus a. Apply fault at the MILLEN_TPW 3 (528434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPW 3 115.0 KV 528434 TO MILLEN_TPE 3 115.0 KV 528436 CKT *1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | MILLEN_TPW_3__MILLEN_____3 | 3 Phase fault on MILLEN_TPW 3 (528434) 115 kV Bus a. Apply fault at the MILLEN_TPW 3 (528434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPW 3 115.0 KV 528434 TO MILLEN 3 115.0 KV 528435 CKT *1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | MILLEN_____3__MILLEN_TPE_3 | 3 Phase fault on MILLEN 3 (528435) 115 kV Bus a. Apply fault at the MILLEN 3 (528435) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN 3 115.0 KV 528435 TO MILLEN_TPE 3 115.0 KV 528436 CKT *1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | MINCO__7__CIMARON7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | MINCO__7__GEN_2017_233 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GEN-2017-233 345.0 KV 761250 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | MINCO__7__GRACMNT7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | MINCO__7__MCNOWND7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MCNOWND7 345.0 KV 515444 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | MINCO__7__MNCWND37 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MNCWND37 345.0 KV 515549 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | MINCO__7__NORMHLL7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | MONUMENT___3__MONUMNT_TP_3 | 3 Phase fault on MONUMENT 3 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3 115.0 KV 528491 TO MONUMNT_TP 3 115.0 KV 528568 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | MONUMENT___3__W_HOBBS____3 | 3 Phase fault on MONUMENT 3 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3 115.0 KV 528491 TO W_HOBBS 3 115.0 KV 528498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | MONUMNT_TP_3__BYRD_TP____3 | 3 Phase fault on MONUMNT_TP 3 (528568) 115 kV Bus a. Apply fault at the MONUMNT_TP 3 (528568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMNT_TP 3 115.0 KV 528568 TO BYRD_TP 3 115.0 KV 528581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | MUSTANG____6__SEMINOLE___6 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6 (527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 230.0 KV 527149 TO SEMINOLE 6 230.0 KV 527276 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | NEEDMORE___6__YOAKUM_____6 | 3 Phase fault on NEEDMORE 6 (525586) 230 kV Bus a. Apply fault at the NEEDMORE 6 (525586) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEEDMORE 6 230.0 KV 525586 TO YOAKUM 6 230.0 KV 526935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | NEWHART____6__PLANT_X____6 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 230.0 KV 525461 TO PLANT_X 6 230.0 KV 525481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | NICHOLS____6__AMA_SOUTH__6 | 3 Phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 230.0 KV 524044 TO AMA_SOUTH 6 230.0 KV 524415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8 or reduce to 0.2.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | NORTH_LOVNG3__AGAVE_PDURO3 | 3 Phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 115.0 KV 528182 TO AGAVE_PDURO3 115.0 KV 528195 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | NORTH_LOVNG3__BLACKRIVER_3 | 3 Phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 115.0 KV 528182 TO BLACKRIVER 3 115.0 KV 528193 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | NORTH_LOVNG3__HOPI_SUB___3 | 3 Phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 115.0 KV 528182 TO HOPI_SUB 3 115.0 KV 528226 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | NORTH_LOVNG3__SOUTH_LOVNG3 | 3 Phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 115.0 KV 528182 TO SOUTH_LOVNG3 115.0 KV 528192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | N_LOVING___7__CHINA_DRAW_7 | 3 Phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 345.0 KV 528185 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | OASIS______6__ROOSEVELT__6 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 230.0 KV 524875 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | OKLEHV24__OKLEHV14 | 3 Phase fault on OKLEHV24 (590001) 138 kV Bus a. Apply fault at the OKLEHV24 (590001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKLEHV24 138.0 KV 590001 TO OKLEHV14 138.0 KV 590003 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | OXY_WSEM_TP3__JOHNSON_DRW3 | 3 Phase fault on OXY_WSEM_TP3 (527325) 115 kV Bus a. Apply fault at the OXY_WSEM_TP3 (527325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OXY_WSEM_TP3 115.0 KV 527325 TO JOHNSON_DRW3 115.0 KV 527362 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | O_K_U__7__G17_151TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | O_K_U__7__G18_015_TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | O_K_U__7__GEN_2017_033 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO GEN-2017-033 345.0 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | O_K_U__7__L_E_S__7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO L.E.S.-7 345.0 KV 511468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | O_K_U__7__OKLAUN_HVDC7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO OKLAUN HVDC7 345.0 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | PCA________3__CARLSBAD___3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO CARLSBAD 3 115.0 KV 528160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | PCA________3__CV_LUSK_TP_3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO CV-LUSK_TP 3 115.0 KV 527948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | PCA________3__POTASH_JCT_3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO POTASH_JCT 3 115.0 KV 527962 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | PCA________3__XTO_BIGEDDY3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO XTO_BIGEDDY3 115.0 KV 528396 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | PHANTOM____3__SOUTH_LOVNG3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO MALAGABEND 3 115.0 KV 528194 CKT 1 b.2. LOAD 1 528194 b.3. SOUTH_LOVNG3 115.0 KV 528192 TO MALAGABEND 3 115.0 KV 528194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | PHANTOM____3__WOLFCAMP_TP3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO BOPCO_PKRLK3 115.0 KV 528020 CKT 1 b.2. LOAD 1 528020 b.3. BOPCO_PKRLK3 115.0 KV 528020 TO WOLFCAMP_TP3 115.0 KV 528235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | PHANTOM____3__WOOD_DRAW__3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO WOOD_DRAW 3 115.0 KV 528228 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | PHANTOM____7__CHINA_DRAW_7 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 345.0 KV 528015 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | PHANTOM____7__RDRUNNER___7 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 345.0 KV 528015 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | PLAINS_INT_3__YOAKUM_____3 | 3 Phase fault on PLAINS_INT 3 (526928) 115 kV Bus a. Apply fault at the PLAINS_INT 3 (526928) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINS_INT 3 115.0 KV 526928 TO YOAKUM 3 115.0 KV 526934 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | PLANT_X____6__G17_146_TAP | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO G17-146-TAP 230.0 KV 760498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | PLANT_X____6__SUNDOWN____6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO SUNDOWN 6 230.0 KV 526435 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | PLANT_X____6__TOLK_______6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | PLSNT_HILL_6__ROOSEVELT__6 | 3 Phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 230.0 KV 524770 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | POTASH_JCT_2__DUVAL__1___2 | 3 Phase fault on POTASH_JCT 2 (527961) 69 kV Bus a. Apply fault at the POTASH_JCT 2 (527961) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 2 69.0 KV 527961 TO DUVAL_#1 2 69.0 KV 527980 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | POTASH_JCT_2__KERMAC_____2 | 3 Phase fault on POTASH_JCT 2 (527961) 69 kV Bus a. Apply fault at the POTASH_JCT 2 (527961) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 2 69.0 KV 527961 TO KERMAC 2 69.0 KV 527996 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | POTASH_JCT_2__MISSCHEM_2_2 | 3 Phase fault on POTASH_JCT 2 (527961) 69 kV Bus a. Apply fault at the POTASH_JCT 2 (527961) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 2 69.0 KV 527961 TO MISSCHEM#2 2 69.0 KV 528022 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | POTASH_JCT_2__NATPOT_TP__2 | 3 Phase fault on POTASH_JCT 2 (527961) 69 kV Bus a. Apply fault at the POTASH_JCT 2 (527961) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 2 69.0 KV 527961 TO NATPOT_TP 2 69.0 KV 528145 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | POTASH_JCT_3__CARLSBAD___3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO CARLSBAD 3 115.0 KV 528160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | POTASH_JCT_3__INTREPDW_TP3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO INTREPDW_TP3 115.0 KV 527999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | POTASH_JCT_3__KIOWA______3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO KIOWA 3 115.0 KV 527966 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | POTASH_JCT_6__PECOS______6 | 3 Phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6 230.0 KV 527963 TO PECOS 6 230.0 KV 528179 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | POTTER_CO__6__NEWHART____6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | PRENTICE___3__YOAKUM_____3 | 3 Phase fault on PRENTICE 3 (526792) 115 kV Bus a. Apply fault at the PRENTICE 3 (526792) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRENTICE 3 115.0 KV 526792 TO YOAKUM 3 115.0 KV 526934 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | QUAHADA____3__DCP_ZIA_TP_3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO DCP_ZIA TP 3 115.0 KV 528422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | QUAHADA____3__LEA_NATIONL3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO LEA_NATIONL3 115.0 KV 528399 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | QUAHADA____3__PCA________3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO XTO_BIGEDDY3 115.0 KV 528396 CKT 1 b.2. LOAD 1 528396 b.3. PCA 3 115.0 KV 527930 TO XTO_BIGEDDY3 115.0 KV 528396 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | RANDALL____6__AMA_SOUTH__6 | 3 Phase fault on RANDALL 6 (524365) 230 kV Bus a. Apply fault at the RANDALL 6 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 230.0 KV 524365 TO AMA_SOUTH 6 230.0 KV 524415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | RDRUNNER___3__AGAVE_RHIL23 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHIL23 115.0 KV 528231 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | RDRUNNER___3__BATTLE_AXE_3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO BATTLE_AXE 3 115.0 KV 528040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | RDRUNNER___3__CUSTERMTN__3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO CUSTERMTN 3 115.0 KV 528239 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | RDRUNNER___3__GEN_2016_121 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO GEN-2016-121 115.0 KV 587990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | RDRUNNER___3__GEN_2018_052 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO GEN-2018-052 115.0 KV 762866 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | RDRUNNER___3__OCHOA______3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHILL3 115.0 KV 528230 CKT 1 b.2. LOAD 1 528230 b.3. AGAVE_RHILL3 115.0 KV 528230 TO OCHOA 3 115.0 KV 528232 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | RED_BLUFF__3__RDRUNNER___3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 115.0 KV 528018 TO RDRUNNER 3 115.0 KV 528025 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | RED_BLUFF__3__WIPP_______3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAND_DUNES 3 115.0 KV 528016 TO RED_BLUFF 3 115.0 KV 528018 CKT 1 b.2. WIPP 3 115.0 KV 528009 TO SAND_DUNES 3 115.0 KV 528016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | RED_BLUFF__3__WOLFCAMP_TP3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 115.0 KV 528018 TO WOLFCAMP_TP3 115.0 KV 528235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | ROOSEVELT__6__TOLK_______6 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 230.0 KV 524909 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | RR_SVC_HV__3__RDRUNNER___3 | 3 Phase fault on RR_SVC_HV 3 (528024) 115 kV Bus a. Apply fault at the RR_SVC_HV 3 (528024) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RR_SVC_HV 3 115.0 KV 528024 TO RDRUNNER 3 115.0 KV 528025 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8. Reclosing was removed.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | RSVLT_CC_E_7__CROSSROADS_7 | 3 Phase fault on RSVLT_CC_E 7 (527655) 345 kV Bus a. Apply fault at the RSVLT_CC_E 7 (527655) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_E 7 345.0 KV 527655 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | RUSHSPR7__GEN_2018_055 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345.0 KV 511571 TO GEN-2018-055 345.0 KV 762900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | RUSSELL____3__HIGG_______3 | 3 Phase fault on RUSSELL 3 (527284) 115 kV Bus a. Apply fault at the RUSSELL 3 (527284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL 3 115.0 KV 527284 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | SAGA_SCOL__7__CROSSROADS_7 | 3 Phase fault on SAGA_SCOL 7 (527610) 345 kV Bus a. Apply fault at the SAGA_SCOL 7 (527610) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAGA_SCOL 7 345.0 KV 527610 TO CROSSROADS 7 345.0 KV 527656 CKT 1 | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8 or reduce to 0.2.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | SANGER_SW__3__G18_004_TAP | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | SANGER_SW__3__SW_4J44____3 | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO SW_4J44 3 115.0 KV 528484 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | SANGER_SW__3__W_BENDER___3 | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO OXYPERMIAN 3 115.0 KV 528575 CKT 1 b.2. LOAD 1 528575 b.3. LOAD 2 528575 b.4. OXY_NHU_RCF3 115.0 KV 528574 TO OXYPERMIAN 3 115.0 KV 528575 CKT 1 b.5. LOAD 1 528575 b.6. LOAD 2 528575 b.7. W_BENDER 3 115.0 KV 528449 TO OXY_NHU_RCF3 115.0 KV 528574 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | SN_JUAN_TAP6__CHAVES_CNTY6 | 3 Phase fault on SN_JUAN_TAP6 (524885) 230 kV Bus a. Apply fault at the SN_JUAN_TAP6 (524885) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SN_JUAN_TAP6 230.0 KV 524885 TO CHAVES_CNTY6 230.0 KV 527483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | SP_ABERNTHY2__TUCO_INT2__2 | 3 Phase fault on SP-ABERNTHY2 (525731) 69 kV Bus a. Apply fault at the SP-ABERNTHY2 (525731) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ABERNTHY2 69.0 KV 525731 TO TUCO_INT2 2 69.0 KV 525816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | SUNDOWN____6__WOLFFORTH__6 | 3 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 230.0 KV 526435 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | SUNNYSD7__G17_075_TAP | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G17-075-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | SUNNYSD7__GEN_2017_167 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO GEN-2017-167 345.0 KV 761859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | SWISHER____6__NEWHART____6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | SWISHER____6__TUCO_INT___6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | SW_4J44____3__TAYLOR_____3 | 3 Phase fault on SW_4J44 3 (528484) 115 kV Bus a. Apply fault at the SW_4J44 3 (528484) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OXY_S_HOBBS3 115.0 KV 528480 TO SW_4J44 3 115.0 KV 528484 CKT 1 b.2. S_HOBBS 3 115.0 KV 528477 TO OXY_S_HOBBS3 115.0 KV 528480 CKT 1 b.3. LOAD 1 528480 b.4. LOAD 2 528480 b.5. LOAD 3 528480 b.6. E_SANGER 3 115.0 KV 528470 TO S_HOBBS 3 115.0 KV 528477 CKT 1 b.7. LOAD 1 528477 b.8. LOAD 2 528477 b.9. TAYLOR 3 115.0 KV 528413 TO E_SANGER 3 115.0 KV 528470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | SW_4J44____3__W_HOBBS____3 | 3 Phase fault on SW_4J44 3 (528484) 115 kV Bus a. Apply fault at the SW_4J44 3 (528484) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW_4J44 3 115.0 KV 528484 TO W_HOBBS 3 115.0 KV 528498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | S_JAL______3__DOLLARHIDE_3 | 3 Phase fault on S_JAL 3 (528547) 115 kV Bus a. Apply fault at the S_JAL 3 (528547) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S_JAL 3 115.0 KV 528547 TO DOLLARHIDE 3 115.0 KV 528561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TAYLOR_____3__MILLEN_TPE_3 | 3 Phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 3 115.0 KV 528413 TO NE_HOBBS 3 115.0 KV 528442 CKT 1 b.2. LOAD 1 528442 b.3. MILLEN_TPE 3 115.0 KV 528436 TO NE_HOBBS 3 115.0 KV 528442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TAYLOR_____3__W_BENDER___3 | 3 Phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 3 115.0 KV 528413 TO W_BENDER 3 115.0 KV 528449 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TEAGUE_____3__CARDINAL___3 | 3 Phase fault on TEAGUE 3 (528526) 115 kV Bus a. Apply fault at the TEAGUE 3 (528526) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEAGUE 3 115.0 KV 528526 TO CARDINAL 3 115.0 KV 528596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TEAGUE_____3__S_JAL______3 | 3 Phase fault on TEAGUE 3 (528526) 115 kV Bus a. Apply fault at the TEAGUE 3 (528526) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEAGUE 3 115.0 KV 528526 TO S_JAL 3 115.0 KV 528547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TERRYRD7__G17_171_TAP | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TERRYRD7__RSHSPR1_MPT1 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RSHSPR1_MPT1 345.0 KV 511979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8 or reduce to 0.2.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TERRYRD7__RUSHSPR7 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TERRYRD7__SUNNYSD7 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TOLK_______6__GEN_2017_158 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO GEN-2017-158 230.0 KV 762132 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8 or reduce to 0.2.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TOLK_______6__LAMB_CNTY__6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO LAMB_CNTY 6 230.0 KV 525637 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TOLK_______6__NEEDMORE___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO NEEDMORE 6 230.0 KV 525586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TOLK_______6__TUCO_INT___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TOLK_______7__CROSSROADS_7 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TUCO_INT___2__LH_WIL&ELN+2 | 3 Phase fault on TUCO_INT 2 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 2 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 69.0 KV 525826 TO LH-WIL&ELN+2 69.0 KV 525853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TUCO_INT___2__SP_NEWDEAL_2 | 3 Phase fault on TUCO_INT 2 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 2 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 69.0 KV 525826 TO SP-NEWDEAL 2 69.0 KV 525885 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TUCO_INT___3__CARLISLE___3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO STANTON_W 3 115.0 KV 526076 CKT 1 b.2. LOAD 1 526076 b.3. STANTON_W 3 115.0 KV 526076 TO INDIANA 3 115.0 KV 526146 CKT 1 b.4. LOAD 1 526146 b.5. LOAD 2 526146 b.6. SP-ERSKINE 3 115.0 KV 526109 TO INDIANA 3 115.0 KV 526146 CKT 1 b.7. LOAD 1 526146 b.8. LOAD 2 526146 b.9. SP-ERSKINE 3 115.0 KV 526109 TO CARLISLE 3 115.0 KV 526160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TUCO_INT___3__LUBBCK_EST_3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TUCO_INT___6__ANTELOPE_1_6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO ANTELOPE_1 6 230.0 KV 525840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TUCO_INT___6__CARLISLE___6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO CARLISLE 6 230.0 KV 526161 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TUCO_INT___6__HALE_WNDCL16 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO HALE_WNDCL16 230.0 KV 525957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TUCO_INT___6__JONES______6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TUCO_INT___7__ELK_CT1 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO ELK_CT1 345.0 KV 525850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TUCO_INT___7__G17_151TAP | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TUCO_INT___7__YOAKUM_345 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO YOAKUM_345 345.0 KV 526936 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TWEEDY_____3__EDDY_NTH___3 | 3 Phase fault on TWEEDY 3 (527597) 115 kV Bus a. Apply fault at the TWEEDY 3 (527597) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWEEDY 3 115.0 KV 527597 TO EDDY_NTH 3 115.0 KV 527798 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | WHITTEN____3__LEA_ROAD___3 | 3 Phase fault on WHITTEN 3 (528540) 115 kV Bus a. Apply fault at the WHITTEN 3 (528540) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 3 115.0 KV 528519 TO WHITTEN 3 115.0 KV 528540 CKT 1 b.2. LOAD 1 528540 b.3. LEA_ROAD 3 115.0 KV 528505 TO WARD 3 115.0 KV 528519 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | WHITTEN____3__S_JAL______3 | 3 Phase fault on WHITTEN 3 (528540) 115 kV Bus a. Apply fault at the WHITTEN 3 (528540) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITTEN 3 115.0 KV 528540 TO S_JAL 3 115.0 KV 528547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | WOLFCAMP_TP3__WOLFCAMP___3 | 3 Phase fault on WOLFCAMP_TP3 (528235) 115 kV Bus a. Apply fault at the WOLFCAMP_TP3 (528235) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCAMP_TP3 115.0 KV 528235 TO WOLFCAMP 3 115.0 KV 528236 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | WWRDEHV7__BECKHAM7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | WWRDEHV7__DGRASSE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | WWRDEHV7__G07621119_20 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G07621119-20 345.0 KV 515599 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | WWRDEHV7__G16_003_TAP | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G16-003-TAP 345.0 KV 560071 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | WWRDEHV7__GUTHRIE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GUTHRIE7 345.0 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | WWRDEHV7__TATONGA7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | W_BENDER___3__N_HOBBS____3 | 3 Phase fault on W_BENDER 3 (528449) 115 kV Bus a. Apply fault at the W_BENDER 3 (528449) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_BENDER 3 115.0 KV 528449 TO N_HOBBS 3 115.0 KV 528456 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | W_HOBBS____3__DRINKARD_TP3 | 3 Phase fault on W_HOBBS 3 (528498) 115 kV Bus a. Apply fault at the W_HOBBS 3 (528498) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_HOBBS 3 115.0 KV 528498 TO DRINKARD_TP3 115.0 KV 528533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | XTO_DI9_TP_3__XTO_DI9____3 | 3 Phase fault on XTO_DI9_TP 3 (528064) 115 kV Bus a. Apply fault at the XTO_DI9_TP 3 (528064) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XTO_DI9_TP 3 115.0 KV 528064 TO XTO_DI9 3 115.0 KV 528066 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | XTO_MAHONEY6__GEN_2017_239 | 3 Phase fault on XTO_MAHONEY6 (527011) 230 kV Bus a. Apply fault at the XTO_MAHONEY6 (527011) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XTO_MAHONEY6 230.0 KV 527011 TO GEN-2017-239 230.0 KV 761355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | YOAKUM_345__HOBBS_INT__7 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | YOAKUM_____3__ARCO_TP____3 | 3 Phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 115.0 KV 526934 TO ARCO_TP 3 115.0 KV 527041 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | YOAKUM_____3__LG_PLSHILL_3 | 3 Phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 115.0 KV 526934 TO LG-PLSHILL 3 115.0 KV 527194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | YOAKUM_____6__BRU_SUB____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | YOAKUM_____6__INK_BASIN__6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO INK_BASIN 6 230.0 KV 527028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | YOAKUM_____6__MUSTANG____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO MUSTANG 6 230.0 KV 527149 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | YOAKUM_____6__SUNDOWN____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 b.2. SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | 7_RIVERS___6__528094_0 | 3 Phase fault on 7-RIVERS 6 (528095) 230 kV Bus a. Apply fault at the 7-RIVERS 6( 528095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 7-RIVERS 6 528095 TO 7-RIVERS 3 528094 TO 7-RIVER_TR11 528090 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | AMA_SOUTH__6__524414_0 | 4 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6( 524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 524415 TO AMA_SOUTH 3 524414 TO AMA_SO_TR1 1 524410 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CARLISLE___3__526159_0 | 5 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3( 526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 526160 TO CARLISLE 2 526159 TO CRLSLE_TR2 1 526158 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CARLISLE___6__526160_0 | 6 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6( 526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 526161 TO CARLISLE 3 526160 TO CRLSLE_TR1 1 526157 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CARLSBAD___3__528159_0 | 7 Phase fault on CARLSBAD 3 (528160) 115 kV Bus a. Apply fault at the CARLSBAD 3( 528160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLSBAD 3 528160 TO CARLSBAD 2 528159 TO CRLSBAD_TR21 528158 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CHAVES_CNTY6__527482_0 | 8 Phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6( 527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY6 527483 TO CHAVES_CNTY3 527482 TO CHAVES_TR2 1 527479 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CHINA_DRAW_7__528222_0 | 9 Phase fault on CHINA_DRAW 7 (528223) 345 kV Bus a. Apply fault at the CHINA_DRAW 7( 528223) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHINA_DRAW 7 528223 TO CHINA_DRAW 3 528222 TO CHINA_DRAW 1 528219 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CHISHOLM6__511553_0 | 10 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6( 511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CUNNIGHM_S_6__527864_0 | 11 Phase fault on CUNNIGHM_S 6 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6( 527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 527867 TO CUNNINHAM 3 527864 TO CUNNHM_TR1 1 527863 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | DUNCAN_2__511453_0 | 12 Phase fault on DUNCAN-2 (511452) 69 kV Bus a. Apply fault at the DUNCAN-2( 511452) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-2 511452 TO DUNCAN-4 511453 TO DUNC2-1 511410 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | EDDY_CNTY__7__527799_0 | 13 Phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7( 527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 527802 TO EDDY_NORTH 6 527799 TO EDDY_TR 1 527796 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | EDDY_NORTH_6__527793_0 | 14 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6( 527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 527799 TO EDDY_STH 3 527793 TO EDDY_TR3 1 527795 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | EDDY_NORTH_6__527798_0 | 15 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6( 527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 527799 TO EDDY_NTH 3 527798 TO EDDY_TR2 1 527797 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | ELGINJT2__511486_0 | 16 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2( 511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | FLOYD_CNTY_3__525779_0 | 17 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3( 525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 525780 TO FLOYD_CNTY 2 525779 TO FLOYD_TR2 1 525778 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | GRACMNT4__515800_0 | 18 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4( 515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | GRASSLAND__6__526676_0 | 19 Phase fault on GRASSLAND 6 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6( 526677) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 6 526677 TO GRASSLAND 3 526676 TO GRASLND_TR11 526674 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | HALE_CNTY__3__525453_0 | 20 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3( 525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 525454 TO HALE_CNTY 2 525453 TO HALE_TR2 1 525452 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | HALE_WNDCL16__525931_0 | 21 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16( 525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL11 525931 TO HALE_WD_TR11 525930 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | HALE_WNDCL16__525981_0 | 22 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16( 525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL21 525981 TO HALE_WD_TR21 525980 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | HALE_WNDCL16__525990_0 | 23 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16( 525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL31 525990 TO HALE_WD_TR31 525989 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | HOBBS_INT__6__527891_0 | 24 Phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6( 527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 527894 TO HOBBS_INT 3 527891 TO HOBBS_TR1 1 527890 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | HOBBS_INT__7__527894_0 | 25 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7( 527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 527896 TO HOBBS_INT 6 527894 TO HOBBS_TR3 1 527895 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | INK_BASIN__6__527027_0 | 26 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6( 527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 527028 TO INK_BASIN 3 527027 TO INKBASN_TR 1 527026 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | KIOWA______7__527966_0 | 27 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7( 527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 527965 TO KIOWA 3 527966 TO KIOWA_TR1 1 527964 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LAMB_CNTY__6__525636_0 | 28 Phase fault on LAMB_CNTY 6 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6( 525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 6 525637 TO LAMB_CNTY 3 525636 TO LAMB_TR3 1 525633 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LE_WEST_SUB3__528337_0 | 29 Phase fault on LE-WEST_SUB3 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3( 528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3 528333 TO WC_SEC 1 528337 TO WC_TER 1 528336 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LUBBCK_EST_3__526297_0 | 30 Phase fault on LUBBCK_EST 3 (526298) 115 kV Bus a. Apply fault at the LUBBCK_EST 3( 526298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 3 526298 TO LUBBCK_EST 2 526297 TO LBB_EST TR31 526296 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LUBBCK_EST_6__526298_0 | 31 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6( 526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 526299 TO LUBBCK_EST 3 526298 TO LBB_EST TR11 526294 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LUBBCK_STH_6__526268_0 | 32 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6( 526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 526269 TO LUBBCK_STH 3 526268 TO LBB_STH TR11 526265 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | L_E_S__2__511467_0 | 33 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2( 511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | L_E_S__4__511468_0 | 34 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4( 511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | MUSTANG____6__527146_0 | 35 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6( 527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 527149 TO MUSTANG 3 527146 TO MUSTANG_TR11 527143 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | NEWHART____6__525460_0 | 36 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6( 525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 525461 TO NEWHART 3 525460 TO NEWHART_TR11 525459 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | N_LOVING___7__528182_0 | 37 Phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7( 528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 528185 TO NORTH_LOVNG3 528182 TO N_LOVING TR1 528186 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | OKLAUN_7__590003_0 | 38 Phase fault on OKLAUN 7 (599891) 345 kV Bus a. Apply fault at the OKLAUN 7( 599891) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OKLAUN 7 599891 TO OKLEHV14 590003 TO OK1TERT 590004 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | PCA________3__527929_0 | 39 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3( 527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 527930 TO PCA 2 527929 TO PCA_TR1 1 527928 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | PECOS______6__528178_0 | 40 Phase fault on PECOS 6 (528179) 230 kV Bus a. Apply fault at the PECOS 6( 528179) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECOS 6 528179 TO PECOS 3 528178 TO PECOS_TR1 1 528176 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | PHANTOM____7__528013_0 | 41 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7( 528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 528015 TO PHANTOM 3 528013 TO PHANTOM TR21 528012 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | PLANT_X____6__525480_0 | 42 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6( 525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 525481 TO PLANT_X 3 525480 TO PLANTX_TR1 1 525479 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | No | Yes | Yes | High voltage issue. | Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | POTASH_JCT_3__527961_0 | 43 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3( 527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 527962 TO POTASH_JCT 2 527961 TO POTASH_TR3 1 527960 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | POTASH_JCT_6__527962_0 | 44 Phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6( 527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6 527963 TO POTASH_JCT 3 527962 TO POTASH_TR1 1 527958 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | RDRUNNER___7__528025_0 | 45 Phase fault on RDRUNNER 7 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7( 528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7 528027 TO RDRUNNER 3 528025 TO RDRNNER_TR11 528023 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | ROOSEVELT__6__524908_0 | 46 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6( 524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 524909 TO ROOSEVELT 3 524908 TO ROSEVLT_TR11 524907 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | RSHSPR1_COL1__511979_0 | 47 Phase fault on RSHSPR1_COL1 (511978) 34.5 kV Bus a. Apply fault at the RSHSPR1_COL1( 511978) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSHSPR1_COL1 511978 TO RSHSPR1_MPT1 511979 TO RSHSPR1_TER1 511583 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | RUSHSPR7__511965_0 | 48 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7( 511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 511571 TO RUSHSPRW1-1 511965 TO RUSHSPR1-1 511572 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | SUNDOWN____6__526434_0 | 49 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6( 526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 526435 TO SUNDOWN 3 526434 TO SUNDOWN_TR11 526432 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | SUNNYSD4__515136_0 | 50 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4( 515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | SUNNYSD7__515135_0 | 51 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7( 515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | SWISHER____6__525212_0 | 52 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6( 525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 525213 TO SWISHER 3 525212 TO SWISHER_TR11 525211 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TOLK_______7__525531_0 | 53 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7( 525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 525549 TO TOLK 6 525531 TO TOLK_TR 2 525538 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TUCO_INT___3__525816_0 | 54 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3( 525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT2 2 525816 TO TUCO_TR7 1 525814 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TUCO_INT___3__525826_0 | 55 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3( 525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT 2 525826 TO TUCO_TR6 1 525823 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TUCO_INT___6__525828_0 | 56 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6( 525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 525830 TO TUCO_INT 3 525828 TO TUCO_TR4 1 525821 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TUCO_INT___7__525830_0 | 57 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7( 525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 525832 TO TUCO_INT 6 525830 TO TUCO_TR2 1 525825 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | WOLFFORTH__6__526524_0 | 58 Phase fault on WOLFFORTH 6 (526525) 230 kV Bus a. Apply fault at the WOLFFORTH 6( 526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFFORTH 6 526525 TO WOLFFORTH 3 526524 TO WOLFRTH_TR11 526522 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | WWRDEHV4__515375_0 | 59 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4( 515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8 or reduce to 0.2.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | YOAKUM_345__526935_0 | 60 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345( 526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 526936 TO YOAKUM 6 526935 TO YOAKUM_TR1 526937 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | YOAKUM_____6__526934_0 | 61 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6( 526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 526935 TO YOAKUM 3 526934 TO YOAKUM_TR2 1 526932 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | 7_RIVERS___6__528094_0 | 3 Phase fault on 7-RIVERS 6 (528095) 230 kV Bus a. Apply fault at the 7-RIVERS 6( 528095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 7-RIVERS 6 528095 TO 7-RIVERS 3 528094 TO 7-RIVER_TR11 528090 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | AMA_SOUTH__6__524414_0 | 4 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6( 524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 524415 TO AMA_SOUTH 3 524414 TO AMA_SO_TR1 1 524410 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CARLISLE___3__526159_0 | 5 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3( 526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 526160 TO CARLISLE 2 526159 TO CRLSLE_TR2 1 526158 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CARLISLE___6__526160_0 | 6 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6( 526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 526161 TO CARLISLE 3 526160 TO CRLSLE_TR1 1 526157 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CARLSBAD___3__528159_0 | 7 Phase fault on CARLSBAD 3 (528160) 115 kV Bus a. Apply fault at the CARLSBAD 3( 528160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLSBAD 3 528160 TO CARLSBAD 2 528159 TO CRLSBAD_TR21 528158 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CHAVES_CNTY6__527482_0 | 8 Phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6( 527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY6 527483 TO CHAVES_CNTY3 527482 TO CHAVES_TR2 1 527479 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CHINA_DRAW_7__528222_0 | 9 Phase fault on CHINA_DRAW 7 (528223) 345 kV Bus a. Apply fault at the CHINA_DRAW 7( 528223) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHINA_DRAW 7 528223 TO CHINA_DRAW 3 528222 TO CHINA_DRAW 1 528219 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CHISHOLM6__511553_0 | 10 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6( 511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CUNNIGHM_S_6__527864_0 | 11 Phase fault on CUNNIGHM_S 6 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6( 527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 527867 TO CUNNINHAM 3 527864 TO CUNNHM_TR1 1 527863 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | DUNCAN_2__511453_0 | 12 Phase fault on DUNCAN-2 (511452) 69 kV Bus a. Apply fault at the DUNCAN-2( 511452) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-2 511452 TO DUNCAN-4 511453 TO DUNC2-1 511410 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | EDDY_CNTY__7__527799_0 | 13 Phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7( 527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 527802 TO EDDY_NORTH 6 527799 TO EDDY_TR 1 527796 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | EDDY_NORTH_6__527793_0 | 14 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6( 527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 527799 TO EDDY_STH 3 527793 TO EDDY_TR3 1 527795 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | EDDY_NORTH_6__527798_0 | 15 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6( 527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 527799 TO EDDY_NTH 3 527798 TO EDDY_TR2 1 527797 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | ELGINJT2__511486_0 | 16 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2( 511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | FLOYD_CNTY_3__525779_0 | 17 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3( 525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 525780 TO FLOYD_CNTY 2 525779 TO FLOYD_TR2 1 525778 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | GRACMNT4__515800_0 | 18 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4( 515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | GRASSLAND__6__526676_0 | 19 Phase fault on GRASSLAND 6 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6( 526677) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 6 526677 TO GRASSLAND 3 526676 TO GRASLND_TR11 526674 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | HALE_CNTY__3__525453_0 | 20 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3( 525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 525454 TO HALE_CNTY 2 525453 TO HALE_TR2 1 525452 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | HALE_WNDCL16__525931_0 | 21 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16( 525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL11 525931 TO HALE_WD_TR11 525930 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | HALE_WNDCL16__525981_0 | 22 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16( 525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL21 525981 TO HALE_WD_TR21 525980 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | HALE_WNDCL16__525990_0 | 23 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16( 525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL31 525990 TO HALE_WD_TR31 525989 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | HOBBS_INT__6__527891_0 | 24 Phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6( 527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 527894 TO HOBBS_INT 3 527891 TO HOBBS_TR1 1 527890 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | HOBBS_INT__7__527894_0 | 25 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7( 527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 527896 TO HOBBS_INT 6 527894 TO HOBBS_TR3 1 527895 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | INK_BASIN__6__527027_0 | 26 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6( 527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 527028 TO INK_BASIN 3 527027 TO INKBASN_TR 1 527026 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | KIOWA______7__527966_0 | 27 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7( 527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 527965 TO KIOWA 3 527966 TO KIOWA_TR1 1 527964 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LAMB_CNTY__6__525636_0 | 28 Phase fault on LAMB_CNTY 6 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6( 525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 6 525637 TO LAMB_CNTY 3 525636 TO LAMB_TR3 1 525633 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LE_WEST_SUB3__528337_0 | 29 Phase fault on LE-WEST_SUB3 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3( 528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3 528333 TO WC_SEC 1 528337 TO WC_TER 1 528336 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LUBBCK_EST_3__526297_0 | 30 Phase fault on LUBBCK_EST 3 (526298) 115 kV Bus a. Apply fault at the LUBBCK_EST 3( 526298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 3 526298 TO LUBBCK_EST 2 526297 TO LBB_EST TR31 526296 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LUBBCK_EST_6__526298_0 | 31 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6( 526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 526299 TO LUBBCK_EST 3 526298 TO LBB_EST TR11 526294 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LUBBCK_STH_6__526268_0 | 32 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6( 526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 526269 TO LUBBCK_STH 3 526268 TO LBB_STH TR11 526265 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | L_E_S__2__511467_0 | 33 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2( 511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | L_E_S__4__511468_0 | 34 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4( 511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | MUSTANG____6__527146_0 | 35 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6( 527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 527149 TO MUSTANG 3 527146 TO MUSTANG_TR11 527143 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | NEWHART____6__525460_0 | 36 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6( 525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 525461 TO NEWHART 3 525460 TO NEWHART_TR11 525459 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | N_LOVING___7__528182_0 | 37 Phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7( 528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 528185 TO NORTH_LOVNG3 528182 TO N_LOVING TR1 528186 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | OKLAUN_7__590003_0 | 38 Phase fault on OKLAUN 7 (599891) 345 kV Bus a. Apply fault at the OKLAUN 7( 599891) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OKLAUN 7 599891 TO OKLEHV14 590003 TO OK1TERT 590004 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | PCA________3__527929_0 | 39 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3( 527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 527930 TO PCA 2 527929 TO PCA_TR1 1 527928 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | PECOS______6__528178_0 | 40 Phase fault on PECOS 6 (528179) 230 kV Bus a. Apply fault at the PECOS 6( 528179) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECOS 6 528179 TO PECOS 3 528178 TO PECOS_TR1 1 528176 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | PHANTOM____7__528013_0 | 41 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7( 528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 528015 TO PHANTOM 3 528013 TO PHANTOM TR21 528012 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | PLANT_X____6__525480_0 | 42 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6( 525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 525481 TO PLANT_X 3 525480 TO PLANTX_TR1 1 525479 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | No | Yes | Yes | GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | POTASH_JCT_3__527961_0 | 43 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3( 527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 527962 TO POTASH_JCT 2 527961 TO POTASH_TR3 1 527960 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | POTASH_JCT_6__527962_0 | 44 Phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6( 527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6 527963 TO POTASH_JCT 3 527962 TO POTASH_TR1 1 527958 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | RDRUNNER___7__528025_0 | 45 Phase fault on RDRUNNER 7 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7( 528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7 528027 TO RDRUNNER 3 528025 TO RDRNNER_TR11 528023 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | ROOSEVELT__6__524908_0 | 46 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6( 524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 524909 TO ROOSEVELT 3 524908 TO ROSEVLT_TR11 524907 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | No | Yes | Yes | GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | RSHSPR1_COL1__511979_0 | 47 Phase fault on RSHSPR1_COL1 (511978) 34.5 kV Bus a. Apply fault at the RSHSPR1_COL1( 511978) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSHSPR1_COL1 511978 TO RSHSPR1_MPT1 511979 TO RSHSPR1_TER1 511583 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | RUSHSPR7__511965_0 | 48 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7( 511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 511571 TO RUSHSPRW1-1 511965 TO RUSHSPR1-1 511572 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | SUNDOWN____6__526434_0 | 49 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6( 526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 526435 TO SUNDOWN 3 526434 TO SUNDOWN_TR11 526432 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | SUNNYSD4__515136_0 | 50 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4( 515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | SUNNYSD7__515135_0 | 51 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7( 515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | SWISHER____6__525212_0 | 52 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6( 525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 525213 TO SWISHER 3 525212 TO SWISHER_TR11 525211 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TOLK_______7__525531_0 | 53 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7( 525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 525549 TO TOLK 6 525531 TO TOLK_TR 2 525538 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TUCO_INT___3__525816_0 | 54 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3( 525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT2 2 525816 TO TUCO_TR7 1 525814 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TUCO_INT___3__525826_0 | 55 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3( 525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT 2 525826 TO TUCO_TR6 1 525823 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TUCO_INT___6__525828_0 | 56 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6( 525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 525830 TO TUCO_INT 3 525828 TO TUCO_TR4 1 525821 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TUCO_INT___7__525830_0 | 57 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7( 525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 525832 TO TUCO_INT 6 525830 TO TUCO_TR2 1 525825 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | WOLFFORTH__6__526524_0 | 58 Phase fault on WOLFFORTH 6 (526525) 230 kV Bus a. Apply fault at the WOLFFORTH 6( 526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFFORTH 6 526525 TO WOLFFORTH 3 526524 TO WOLFRTH_TR11 526522 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | WWRDEHV4__515375_0 | 59 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4( 515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | YOAKUM_345__526935_0 | 60 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345( 526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 526936 TO YOAKUM 6 526935 TO YOAKUM_TR1 526937 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | YOAKUM_____6__526934_0 | 61 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6( 526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 526935 TO YOAKUM 3 526934 TO YOAKUM_TR2 1 526932 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_111_P4_2_CHINA_DRAW | Apply single-phase fault on LINE 528223 TO 528015 CKT 1, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and DISCONNECT 528219 and DISCONNECT 528219 and DISCONNECT 523823 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_113_P4_2_CHINA_DRAW | Apply single-phase fault on and DISCONNECT 528219, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528223 TO 528185 CKT 1 and LINE 528223 TO 528015 CKT 1 and DISCONNECT 528219 and DISCONNECT 523823 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_114_P4_2_EDDY_CNTY | Apply single-phase fault on LINE 527802 TO 527965 CKT 1, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and DISCONNECT 527796 and DISCONNECT 527796 and DISCONNECT 527802 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_115_P4_2_EDDY_CNTY | Apply single-phase fault on and DISCONNECT 527796, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and LINE 527802 TO 527965 CKT 1 and DISCONNECT 527796 and DISCONNECT 527802 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_120_P4_3_KIOWA | Apply single-phase fault on and DISCONNECT 527964, near KIOWA 7 for 5 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus . Clear Fault after 16 cycles and trip LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_122_P4_2_N_LOVING | Apply single-phase fault on LINE 528185 TO 528223 CKT 1, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528186 and DISCONNECT 528185 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_124_P4_2_N_LOVING | Apply single-phase fault on and DISCONNECT 528186, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 528223 CKT 1 and LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528185 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_126_P4_2_ROADRUNNER | Apply single-phase fault on LINE 528027 TO 528015 CKT 1, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528023 and DISCONNECT 528027 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_128_P4_2_ROADRUNNER | Apply single-phase fault on and DISCONNECT 528023, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 528015 CKT 1 and LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528027 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_129_P4_2_YOAKUM | Apply single-phase fault on LINE 526936 TO 525832 CKT 1, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764866 CKT 1 and DISCONNECT 526937 and DISCONNECT 526937 and DISCONNECT 526936 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_131_P4_2_YOAKUM | Apply single-phase fault on and DISCONNECT 526937, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764945 CKT 1 and LINE 526936 TO 527896 CKT 1 and DISCONNECT 526937 and DISCONNECT 526936 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_132_P4_3_TUCO | Apply single-phase fault on and DISCONNECT 525824, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 560022 TO 525832 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_133_P4_1_MUSTANG | Apply single-phase fault on and DISCONNECT 527162, near MUSTANG 3 for 5 cycles with stuck breaker at MUSTANG 3 (527146) 115 kV Bus . Clear Fault after 11 cycles and trip LINE 527202 TO 527146 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_135_P4_3_NICHOLS | Apply single-phase fault on and DISCONNECT 524041, near NICHOLS 6 for 5 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524023 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_137_P4_3_YOAKUM | Apply single-phase fault on and DISCONNECT 526931, near YOAKUM 6 for 5 cycles with stuck breaker at YOAKUM 6 (526935) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525586 TO 526935 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_141_P4_3_TUCO_INT | Apply single-phase fault on and DISCONNECT 525825, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 525832 TO 560022 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_142_P4_3_HITCHLAND | Apply single-phase fault on and DISCONNECT 523091, near HITCHLAND 7 for 5 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523091 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-100 and LANOGSU1 trip on voltage protection settings | Disabling voltage protection settings for GEN-2017-100 and LANOGSU1 prevents trips. There are no stability constraints when these generators trip offline or when the protection settings are disabled to prevent them from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_143_P4_3_WHEELER | Apply single-phase fault on WHEELER 523777 TO WHEELER 523776 TO WHEELER 523774 CKT 1 and DISCONNECT 523774, near WHEELER 6 for 5 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523777 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_148_P4_5_BUSHLAND | Apply single-phase fault on LINE 524267 TO 524290 CKT 1 and DISCONNECT 524263 and DISCONNECT 524285 and DISCONNECT 524287 and LINE 524267 TO 523959 CKT 1, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 16 cycles and trip LINE 524267 TO 524623 CKT 1 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_145_P4_4_BUSHLAND | Apply single-phase fault on and Drop Shunt at Bus 524267, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524267 and DISCONNECT 524285 and DISCONNECT 524287 and DISCONNECT 524263 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_146_P4_4_SWISHER | Apply single-phase fault on and Drop Shunt at Bus 525213, near SWISHER 6 for 5 cycles with stuck breaker at SWISHER 6 (525213) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525213 TO 525830 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_147_P4_4_TUCO_INT | Apply single-phase fault on and Drop Shunt at Bus 525830, near TUCO_INT 6 for 5 cycles with stuck breaker at TUCO_INT 6 (525830) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 525819 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_149_P4_1_HARRINGTON_G1 | Apply single-phase fault on LINE 523977 TO 524010 CKT 1 and LINE 523977 TO 524163 CKT 1 and LINE 523977 TO 524044 CKT 1 and DISCONNECT 523977 and DISCONNECT 523971, near HARRNG_WST 6 for 16 cycles with stuck breaker at HARRNG_WST 6 (523977) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_150_P4_1_HARRINGTON_G2 | Apply single-phase fault on LINE 523978 TO 524365 CKT 1 and LINE 523978 TO 524044 CKT 2 and DISCONNECT 523978 and DISCONNECT 523972, near HARRNG_MID 6 for 16 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_151_P4_1_HARRINGTON_G3 | Apply single-phase fault on LINE 523979 TO 523267 CKT 1 and LINE 523979 TO 523959 CKT 1 and DISCONNECT 523979 and DISCONNECT 523973, near HARRNG_EST 6 for 16 cycles with stuck breaker at HARRNG_EST 6 (523979) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_152_P4_1_JONES_G1 | Apply single-phase fault on and DISCONNECT 526331, near JONES 6 for 18 cycles with stuck breaker at JONES 6 (526337) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_153_P4_6_HARRINGTON_M | Apply single-phase fault on and DISCONNECT 523978 and trip GENERATOR 1 523972 and drop LOAD S1 523972 and DISCONNECT 523972, near HARRNG_MID 6 for 5 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_154_P4_6_MOORE_EAST | Apply single-phase fault on and DISCONNECT 523308 and trip GENERATOR 1 523297 and trip GENERATOR 3 523301 and drop LOAD F1 523297 and drop LOAD 1 523301 and drop LOAD A3 523301 and DISCONNECT 523294 and DISCONNECT 523295 and DISCONNECT 523296 and DISCONNECT 523297 and DISCONNECT 523301 and DISCONNECT 523302, near MOORE_E 3 for 5 cycles with stuck breaker at MOORE_E 3 (523308) 115 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_108_P4_2_CARPENTER | Apply single-phase fault on LINE 523823 TO 523853 CKT 1 and DISCONNECT 523823, near CARPENTER 7 for 21 cycles with stuck breaker at CARPENTER 7 (523823) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_109_P4_2_CROSSROADS | Apply single-phase fault on LINE 527802 TO 527656 CKT 1 and LINE 525549 TO 527656 CKT 1 and DISCONNECT 527655 and DISCONNECT 527653 and DISCONNECT 527651 and DISCONNECT 527652 and DISCONNECT 527654 and trip GENERATOR 1 527605 and trip GENERATOR 1 527607 and trip GENERATOR 1 527614 and trip GENERATOR 1 527615 and trip GENERATOR 1 527617 and trip GENERATOR 1 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629 and DISCONNECT 527656 and DISCONNECT 527658 and DISCONNECT 527659 and DISCONNECT 527660 and DISCONNECT 527661 and DISCONNECT 527662 and DISCONNECT 527663 and DISCONNECT 527666 and DISCONNECT 527667 and DISCONNECT 577120 and DISCONNECT 577121, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_110_P4_2_CROSSROADS | Apply single-phase fault on and LINE 527656 TO 525549 CKT 1 and LINE 527656 TO 527610 CKT 1 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_117_P4_2_FINNEY | Apply single-phase fault on LINE 531449 TO 523853 CKT 1 LINE 523823 TO 523853 CKT 1 and DISCONNECT 523853 and DISCONNECT 599950 and DISCONNECT 599951 and DISCONNECT 523118 and DISCONNECT 523114 and DISCONNECT 523115 and DISCONNECT 523116 and DISCONNECT 523117 and trip GENERATOR 1 523061 and trip GENERATOR 1 523062 and DISCONNECT 523061 and DISCONNECT 523062 and DISCONNECT 523063 and DISCONNECT 523064, near FINNEY 7 for 21 cycles with stuck breaker at FINNEY 7 (523853) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_118_P4_2_HITCHLAND | Apply single-phase fault on LINE 523097 TO 515554 CKT 2 and DISCONNECT 523112 and DISCONNECT 523111 and DISCONNECT 523109 and DISCONNECT 523107 and DISCONNECT 523110, near HITCHLAND 7 for 21 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_119_P4_2_HOBBS_INT | Apply single-phase fault on LINE 527896 TO 527965 CKT 1 and LINE 527896 TO 764866 CKT 1 and DISCONNECT 527895 and DISCONNECT 527896, near HOBBS_INT 7 for 21 cycles with stuck breaker at HOBBS_INT 7 (527896) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_125_P4_2_POTTERCO | Apply single-phase fault on LINE 523097 TO 523961 CKT 1 and DISCONNECT 523957 and DISCONNECT 523957 and DISCONNECT 523961 and DISCONNECT 524296 and DISCONNECT 524299 and DISCONNECT 524298 and DISCONNECT 524294 and DISCONNECT 524295 and DISCONNECT 524297, near POTTER_CO 7 for 21 cycles with stuck breaker at POTTER_CO 7 (523961) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_134_P4_2_NICHOLS | Apply single-phase fault on LINE 523978 TO 524044 CKT 2 and LINE 523551 TO 524044 CKT 1, near NICHOLS 6 for 21 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_136_P4_2_POTTERCO | Apply single-phase fault on LINE 524267 TO 523959 CKT 1 and LINE 524010 TO 523959 CKT 1, near POTTER_CO 6 for 21 cycles with stuck breaker at POTTER_CO 6 (523959) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_138_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 560022 CKT 1 and DISCONNECT 525824, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_139_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 560022 CKT 1 and DISCONNECT 525825, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_140_P4_2_WHEELER | Apply single-phase fault on LINE 523777 TO 511541 CKT &1 and DISCONNECT 523777 and DISCONNECT 523774, near WHEELER 6 for 21 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LT__SPS_All_121_P4_2_KIOWA | Apply single-phase fault on LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964, near KIOWA 7 for 20 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_111_P4_2_CHINA_DRAW | Apply single-phase fault on LINE 528223 TO 528015 CKT 1, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and DISCONNECT 528219 and DISCONNECT 528219 and DISCONNECT 523823 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_113_P4_2_CHINA_DRAW | Apply single-phase fault on and DISCONNECT 528219, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528223 TO 528185 CKT 1 and LINE 528223 TO 528015 CKT 1 and DISCONNECT 528219 and DISCONNECT 523823 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_114_P4_2_EDDY_CNTY | Apply single-phase fault on LINE 527802 TO 527965 CKT 1, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and DISCONNECT 527796 and DISCONNECT 527796 and DISCONNECT 527802 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_115_P4_2_EDDY_CNTY | Apply single-phase fault on and DISCONNECT 527796, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and LINE 527802 TO 527965 CKT 1 and DISCONNECT 527796 and DISCONNECT 527802 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_120_P4_3_KIOWA | Apply single-phase fault on and DISCONNECT 527964, near KIOWA 7 for 5 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus . Clear Fault after 16 cycles and trip LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_122_P4_2_N_LOVING | Apply single-phase fault on LINE 528185 TO 528223 CKT 1, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528186 and DISCONNECT 528185 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_124_P4_2_N_LOVING | Apply single-phase fault on and DISCONNECT 528186, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 528223 CKT 1 and LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528185 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_126_P4_2_ROADRUNNER | Apply single-phase fault on LINE 528027 TO 528015 CKT 1, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528023 and DISCONNECT 528027 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_128_P4_2_ROADRUNNER | Apply single-phase fault on and DISCONNECT 528023, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 528015 CKT 1 and LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528027 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_129_P4_2_YOAKUM | Apply single-phase fault on LINE 526936 TO 525832 CKT 1, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764866 CKT 1 and DISCONNECT 526937 and DISCONNECT 526937 and DISCONNECT 526936 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_131_P4_2_YOAKUM | Apply single-phase fault on and DISCONNECT 526937, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764945 CKT 1 and LINE 526936 TO 527896 CKT 1 and DISCONNECT 526937 and DISCONNECT 526936 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_132_P4_3_TUCO | Apply single-phase fault on and DISCONNECT 525824, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 560022 TO 525832 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_133_P4_1_MUSTANG | Apply single-phase fault on and DISCONNECT 527162, near MUSTANG 3 for 5 cycles with stuck breaker at MUSTANG 3 (527146) 115 kV Bus . Clear Fault after 11 cycles and trip LINE 527202 TO 527146 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_135_P4_3_NICHOLS | Apply single-phase fault on and DISCONNECT 524041, near NICHOLS 6 for 5 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524023 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_137_P4_3_YOAKUM | Apply single-phase fault on and DISCONNECT 526931, near YOAKUM 6 for 5 cycles with stuck breaker at YOAKUM 6 (526935) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525586 TO 526935 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_141_P4_3_TUCO_INT | Apply single-phase fault on and DISCONNECT 525825, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 525832 TO 560022 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_142_P4_3_HITCHLAND | Apply single-phase fault on and DISCONNECT 523091, near HITCHLAND 7 for 5 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523091 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-100 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-100 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_143_P4_3_WHEELER | Apply single-phase fault on WHEELER 523777 TO WHEELER 523776 TO WHEELER 523774 CKT 1 and DISCONNECT 523774, near WHEELER 6 for 5 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523777 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_148_P4_5_BUSHLAND | Apply single-phase fault on LINE 524267 TO 524290 CKT 1 and DISCONNECT 524263 and DISCONNECT 524285 and DISCONNECT 524287 and LINE 524267 TO 523959 CKT 1, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 16 cycles and trip LINE 524267 TO 524623 CKT 1 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_145_P4_4_BUSHLAND | Apply single-phase fault on and Drop Shunt at Bus 524267, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524267 and DISCONNECT 524285 and DISCONNECT 524287 and DISCONNECT 524263 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_146_P4_4_SWISHER | Apply single-phase fault on and Drop Shunt at Bus 525213, near SWISHER 6 for 5 cycles with stuck breaker at SWISHER 6 (525213) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525213 TO 525830 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_147_P4_4_TUCO_INT | Apply single-phase fault on and Drop Shunt at Bus 525830, near TUCO_INT 6 for 5 cycles with stuck breaker at TUCO_INT 6 (525830) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 525819 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_149_P4_1_HARRINGTON_G1 | Apply single-phase fault on LINE 523977 TO 524010 CKT 1 and LINE 523977 TO 524163 CKT 1 and LINE 523977 TO 524044 CKT 1 and DISCONNECT 523977 and DISCONNECT 523971, near HARRNG_WST 6 for 16 cycles with stuck breaker at HARRNG_WST 6 (523977) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_150_P4_1_HARRINGTON_G2 | Apply single-phase fault on LINE 523978 TO 524365 CKT 1 and LINE 523978 TO 524044 CKT 2 and DISCONNECT 523978 and DISCONNECT 523972, near HARRNG_MID 6 for 16 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_151_P4_1_HARRINGTON_G3 | Apply single-phase fault on LINE 523979 TO 523267 CKT 1 and LINE 523979 TO 523959 CKT 1 and DISCONNECT 523979 and DISCONNECT 523973, near HARRNG_EST 6 for 16 cycles with stuck breaker at HARRNG_EST 6 (523979) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_152_P4_1_JONES_G1 | Apply single-phase fault on and DISCONNECT 526331, near JONES 6 for 18 cycles with stuck breaker at JONES 6 (526337) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_153_P4_6_HARRINGTON_M | Apply single-phase fault on and DISCONNECT 523978 and trip GENERATOR 1 523972 and drop LOAD S1 523972 and DISCONNECT 523972, near HARRNG_MID 6 for 5 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_154_P4_6_MOORE_EAST | Apply single-phase fault on and DISCONNECT 523308 and trip GENERATOR 1 523297 and trip GENERATOR 3 523301 and drop LOAD F1 523297 and drop LOAD 1 523301 and drop LOAD A3 523301 and DISCONNECT 523294 and DISCONNECT 523295 and DISCONNECT 523296 and DISCONNECT 523297 and DISCONNECT 523301 and DISCONNECT 523302, near MOORE_E 3 for 5 cycles with stuck breaker at MOORE_E 3 (523308) 115 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_108_P4_2_CARPENTER | Apply single-phase fault on LINE 523823 TO 523853 CKT 1 and DISCONNECT 523823, near CARPENTER 7 for 21 cycles with stuck breaker at CARPENTER 7 (523823) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_109_P4_2_CROSSROADS | Apply single-phase fault on LINE 527802 TO 527656 CKT 1 and LINE 525549 TO 527656 CKT 1 and DISCONNECT 527655 and DISCONNECT 527653 and DISCONNECT 527651 and DISCONNECT 527652 and DISCONNECT 527654 and trip GENERATOR 1 527605 and trip GENERATOR 1 527607 and trip GENERATOR 1 527614 and trip GENERATOR 1 527615 and trip GENERATOR 1 527617 and trip GENERATOR 1 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629 and DISCONNECT 527656 and DISCONNECT 527658 and DISCONNECT 527659 and DISCONNECT 527660 and DISCONNECT 527661 and DISCONNECT 527662 and DISCONNECT 527663 and DISCONNECT 527666 and DISCONNECT 527667 and DISCONNECT 577120 and DISCONNECT 577121, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_110_P4_2_CROSSROADS | Apply single-phase fault on and LINE 527656 TO 525549 CKT 1 and LINE 527656 TO 527610 CKT 1 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_117_P4_2_FINNEY | Apply single-phase fault on LINE 531449 TO 523853 CKT 1 LINE 523823 TO 523853 CKT 1 and DISCONNECT 523853 and DISCONNECT 599950 and DISCONNECT 599951 and DISCONNECT 523118 and DISCONNECT 523114 and DISCONNECT 523115 and DISCONNECT 523116 and DISCONNECT 523117 and trip GENERATOR 1 523061 and trip GENERATOR 1 523062 and DISCONNECT 523061 and DISCONNECT 523062 and DISCONNECT 523063 and DISCONNECT 523064, near FINNEY 7 for 21 cycles with stuck breaker at FINNEY 7 (523853) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_118_P4_2_HITCHLAND | Apply single-phase fault on LINE 523097 TO 515554 CKT 2 and DISCONNECT 523112 and DISCONNECT 523111 and DISCONNECT 523109 and DISCONNECT 523107 and DISCONNECT 523110, near HITCHLAND 7 for 21 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_119_P4_2_HOBBS_INT | Apply single-phase fault on LINE 527896 TO 527965 CKT 1 and LINE 527896 TO 764866 CKT 1 and DISCONNECT 527895 and DISCONNECT 527896, near HOBBS_INT 7 for 21 cycles with stuck breaker at HOBBS_INT 7 (527896) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_125_P4_2_POTTERCO | Apply single-phase fault on LINE 523097 TO 523961 CKT 1 and DISCONNECT 523957 and DISCONNECT 523957 and DISCONNECT 523961 and DISCONNECT 524296 and DISCONNECT 524299 and DISCONNECT 524298 and DISCONNECT 524294 and DISCONNECT 524295 and DISCONNECT 524297, near POTTER_CO 7 for 21 cycles with stuck breaker at POTTER_CO 7 (523961) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_134_P4_2_NICHOLS | Apply single-phase fault on LINE 523978 TO 524044 CKT 2 and LINE 523551 TO 524044 CKT 1, near NICHOLS 6 for 21 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_136_P4_2_POTTERCO | Apply single-phase fault on LINE 524267 TO 523959 CKT 1 and LINE 524010 TO 523959 CKT 1, near POTTER_CO 6 for 21 cycles with stuck breaker at POTTER_CO 6 (523959) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_138_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 560022 CKT 1 and DISCONNECT 525824, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_139_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 560022 CKT 1 and DISCONNECT 525825, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_140_P4_2_WHEELER | Apply single-phase fault on LINE 523777 TO 511541 CKT &1 and DISCONNECT 523777 and DISCONNECT 523774, near WHEELER 6 for 21 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LT__SPS_All_121_P4_2_KIOWA | Apply single-phase fault on LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964, near KIOWA 7 for 20 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | BORDER7_345kV_515458 | a. Apply single-phase fault on: a.1. BORDER7 345KV 515458 TO TUCO_INT7 345KV 525832 CKT 1, b.with stuck breaker near BORDER 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1.BORDER7 345KV 515458 TO BECKHAM7 345KV 516059 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CUNNIGHM_N_6_115kV_527865 | a. Apply single-phase fault on: a.1. CUNNIGHMN6 115KV 527865 TO POTASHJCT6 115KV 527963 CKT 1, b.with stuck breaker near CUNNIGHM_N 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.CUNNIGHMN6 115KV 527865 TO CUNNIGHMS6 115KV 527867 CKT *1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CUNNIGHM_S_6_115kV_527867 | a. Apply single-phase fault on: a.1. CUNNIGHMN6 115KV 527867 TO HOBBSINT6 115KV 527894 CKT 1, b.with stuck breaker near CUNNIGHM_S 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.CUNNIGHMN6 115KV 527865 TO CUNNIGHMS6 115KV 527867 CKT *1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | Cunningham_115kV_527864 | a. Apply single-phase fault on: a.1. Cunningham 115KV 527864 TO Monument TP 115KV 528568 CKT 1, b.with stuck breaker near CUNNINHAM 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.Cunningham 115KV 527864 TO Quahada 115KV 528394 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CUSTERMTN_115kV_528239 | a. Apply single-phase fault on: a.1. CUSTERMTN 115KV 528239 TO WHITTEN 115KV 528540 CKT 1, b.with stuck breaker near CUSTERMTN 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.CUSTERMTN 115KV 528239 TO RDRUNNER 115KV 528025 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | ENRON_TP3_115kV_528317 | a. Apply single-phase fault on: a.1. Maddox 115KV 528355 TO PEARLE3 115KV 528392 CKT 1 a.2. ENRONTP3 115KV 528317 TO PEARLE3 115KV 528392 CKT 1, b.with stuck breaker near ENRON_TP 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.ENRONTP3 115KV 528317 TO LEANATIONL3 115KV 528399 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | KIOWA_345kV_527965 | a. Apply single-phase fault on: a.1. KIOWA 345KV 527965 TO HOBBSINT 345KV 527896 CKT 1, b.with stuck breaker near KIOWA 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1.KIOWA 345KV 527965 TO NLOVING 345KV 528185 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LEA_NATIONL3_115kV_528399 | a. Apply single-phase fault on: a.1. LEANATIONL3 115KV 528399 TO ENRONTP3 115KV 528317 CKT 1, b.with stuck breaker near LEA_NATIONL3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.QUAHADA3 115KV 528394 TO LEANATIONL3 115KV 528399 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | LES_345kV_511468 | a. Apply single-phase fault on: a.1. LES7 345KV 511468 TO G17171TAP 345.0 KV 760938 CKT 1, b.with stuck breaker near L.E.S.-7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1.OKU7 345KV 511456 TO LES7 345KV 511468 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | Maddox_115kV_528355 | a. Apply single-phase fault on: a.1. Maddox 115KV 528355 TO PEARLE3 115KV 528392 CKT 1 a.2. ENRONTP3 115KV 528317 TO PEARLE3 115KV 528392 CKT 1, b.with stuck breaker near MADDOX 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.Maddox 115KV 528355 TO Monument 115KV 528491 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | MONUMENT_115kV_528491 | a. Apply single-phase fault on: a.1. WHOBBS3 115KV 528498 TO MONUMENT3 115KV 528491 CKT 1, b.with stuck breaker near MONUMENT 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.MONUMENT3 115KV 528491 TO MADDOX3 115KV 528355 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | OKU7_345kV_511456 | a. Apply single-phase fault on: a.1. OKU7 345KV 511456 TO LES7 345.0 KV 511468 CKT 1, b.with stuck breaker near O.K.U.-7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1.OKU7 345KV 511456 TO G18015TAP 345KV 762467 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | PHANTOM_345kV_528015 | a. Apply single-phase fault on: a.1. PHANTOM 345KV 528015 TO CHINADRAW 345KV 528223 CKT 1, b.with stuck breaker near RDRUNNER 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1.RDRUNNER 345KV 528027 TO PHANTOM 345KV 528015 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | Rdrunner_115kV_528025 | a. Apply single-phase fault on: a.1. RDRUNNER 115KV 528025 TO AGAVERHILL 115KV 528230 CKT 1, b.with stuck breaker near RDRUNNER 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.RDRUNNER 115KV 528025 TO REDBLUFF 115KV 528018 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | RDRUNNER_345kV_528027 | a. Apply single-phase fault on: a.1. RDRUNNER 345KV 528027 TO KIOWA 345KV 527965 CKT 1, b.with stuck breaker near RDRUNNER 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1.RDRUNNER 345KV 528027 TO PHANTOM 345KV 528015 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | REDBLUFF_115kV_528018 | a. Apply single-phase fault on: a.1. REDBLUFF 115KV 528018 TO WOLFCAMPTP3 115KV 528235 CKT 1, b.with stuck breaker near RED_BLUFF 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.RDRUNNER 115KV 528025 TO REDBLUFF 115KV 528018 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | SANGERSW3_115kV_528463 | a. Apply single-phase fault on: a.1. WBENDER 115KV 528449 TO OXYNHURCF3 115KV 528574 CKT 1 a.2. OXYPERMIAN3 115KV 528575 TO OXYNHURCF3 115KV 528574 CKT 1 a.3. OXYPERMIAN3 115KV 528575 TO SANGERSW3 115KV 528463 CKT 1, b.with stuck breaker near SANGER_SW 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.SANGERSW3 115KV 528463 TO G18004TAP 115KV 762442 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TUCOINT6_230kV_525830 | a. Apply single-phase fault on: a.1. TUCOINT6 230.0 KV 525830 TO SWISHER6 230.0 KV 525213 CKT 1, b.with stuck breaker near TUCO_INT 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.TUCOINT6 230.0 KV 525830 TO CARLISLE6 230.0 KV 526161 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | TUCOINT7_345kV_525832 | a. Apply single-phase fault on: a.1. BORDER7 345KV 515458 TO TUCOINT7 345KV 525832 CKT 1, b.with stuck breaker near TUCO_INT 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1.TUCOINT7 345KV 525832 TO YOAKUM_345 345KV 526936 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | WBENDER_115kV_528449 | a. Apply single-phase fault on: a.1. WBENDER 115KV 528449 TO OXYNHURCF3 115KV 528574 CKT 1 a.2. OXYPERMIAN3 115KV 528575 TO OXYNHURCF3 115KV 528574 CKT 1 a.3. OXYPERMIAN3 115KV 528575 TO SANGERSW3 115KV 528463 CKT 1, b.with stuck breaker near W_BENDER 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.WBENDER 115KV 528449 TO NHOBBS3 115KV 528456 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | W_HOBBS_115kV_528498 | a. Apply single-phase fault on: a.1. WHOBBS3 115KV 528498 TO MONUMENT3 115KV 528491 CKT 1, b.with stuck breaker near W_HOBBS 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.WHOBBS3 115KV 528498 TO DRINKARDTP3 115KV 528533 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | BORDER7_345kV_515458 | a. Apply single-phase fault on: a.1. BORDER7 345KV 515458 TO TUCO_INT7 345KV 525832 CKT 1, b.with stuck breaker near BORDER 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1.BORDER7 345KV 515458 TO BECKHAM7 345KV 516059 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CUNNIGHM_N_6_115kV_527865 | a. Apply single-phase fault on: a.1. CUNNIGHMN6 115KV 527865 TO POTASHJCT6 115KV 527963 CKT 1, b.with stuck breaker near CUNNIGHM_N 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.CUNNIGHMN6 115KV 527865 TO CUNNIGHMS6 115KV 527867 CKT *1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CUNNIGHM_S_6_115kV_527867 | a. Apply single-phase fault on: a.1. CUNNIGHMN6 115KV 527867 TO HOBBSINT6 115KV 527894 CKT 1, b.with stuck breaker near CUNNIGHM_S 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.CUNNIGHMN6 115KV 527865 TO CUNNIGHMS6 115KV 527867 CKT *1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | Cunningham_115kV_527864 | a. Apply single-phase fault on: a.1. Cunningham 115KV 527864 TO Monument TP 115KV 528568 CKT 1, b.with stuck breaker near CUNNINHAM 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.Cunningham 115KV 527864 TO Quahada 115KV 528394 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | CUSTERMTN_115kV_528239 | a. Apply single-phase fault on: a.1. CUSTERMTN 115KV 528239 TO WHITTEN 115KV 528540 CKT 1, b.with stuck breaker near CUSTERMTN 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.CUSTERMTN 115KV 528239 TO RDRUNNER 115KV 528025 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | ENRON_TP3_115kV_528317 | a. Apply single-phase fault on: a.1. Maddox 115KV 528355 TO PEARLE3 115KV 528392 CKT 1 a.2. ENRONTP3 115KV 528317 TO PEARLE3 115KV 528392 CKT 1, b.with stuck breaker near ENRON_TP 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.ENRONTP3 115KV 528317 TO LEANATIONL3 115KV 528399 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | KIOWA_345kV_527965 | a. Apply single-phase fault on: a.1. KIOWA 345KV 527965 TO HOBBSINT 345KV 527896 CKT 1, b.with stuck breaker near KIOWA 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1.KIOWA 345KV 527965 TO NLOVING 345KV 528185 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LEA_NATIONL3_115kV_528399 | a. Apply single-phase fault on: a.1. LEANATIONL3 115KV 528399 TO ENRONTP3 115KV 528317 CKT 1, b.with stuck breaker near LEA_NATIONL3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.QUAHADA3 115KV 528394 TO LEANATIONL3 115KV 528399 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | LES_345kV_511468 | a. Apply single-phase fault on: a.1. LES7 345KV 511468 TO G17171TAP 345.0 KV 760938 CKT 1, b.with stuck breaker near L.E.S.-7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1.OKU7 345KV 511456 TO LES7 345KV 511468 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | Maddox_115kV_528355 | a. Apply single-phase fault on: a.1. Maddox 115KV 528355 TO PEARLE3 115KV 528392 CKT 1 a.2. ENRONTP3 115KV 528317 TO PEARLE3 115KV 528392 CKT 1, b.with stuck breaker near MADDOX 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.Maddox 115KV 528355 TO Monument 115KV 528491 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | MONUMENT_115kV_528491 | a. Apply single-phase fault on: a.1. WHOBBS3 115KV 528498 TO MONUMENT3 115KV 528491 CKT 1, b.with stuck breaker near MONUMENT 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.MONUMENT3 115KV 528491 TO MADDOX3 115KV 528355 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | OKU7_345kV_511456 | a. Apply single-phase fault on: a.1. OKU7 345KV 511456 TO LES7 345.0 KV 511468 CKT 1, b.with stuck breaker near O.K.U.-7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1.OKU7 345KV 511456 TO G18015TAP 345KV 762467 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | PHANTOM_345kV_528015 | a. Apply single-phase fault on: a.1. PHANTOM 345KV 528015 TO CHINADRAW 345KV 528223 CKT 1, b.with stuck breaker near RDRUNNER 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1.RDRUNNER 345KV 528027 TO PHANTOM 345KV 528015 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | Rdrunner_115kV_528025 | a. Apply single-phase fault on: a.1. RDRUNNER 115KV 528025 TO AGAVERHILL 115KV 528230 CKT 1, b.with stuck breaker near RDRUNNER 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.RDRUNNER 115KV 528025 TO REDBLUFF 115KV 528018 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | RDRUNNER_345kV_528027 | a. Apply single-phase fault on: a.1. RDRUNNER 345KV 528027 TO KIOWA 345KV 527965 CKT 1, b.with stuck breaker near RDRUNNER 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1.RDRUNNER 345KV 528027 TO PHANTOM 345KV 528015 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | REDBLUFF_115kV_528018 | a. Apply single-phase fault on: a.1. REDBLUFF 115KV 528018 TO WOLFCAMPTP3 115KV 528235 CKT 1, b.with stuck breaker near RED_BLUFF 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.RDRUNNER 115KV 528025 TO REDBLUFF 115KV 528018 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | SANGERSW3_115kV_528463 | a. Apply single-phase fault on: a.1. WBENDER 115KV 528449 TO OXYNHURCF3 115KV 528574 CKT 1 a.2. OXYPERMIAN3 115KV 528575 TO OXYNHURCF3 115KV 528574 CKT 1 a.3. OXYPERMIAN3 115KV 528575 TO SANGERSW3 115KV 528463 CKT 1, b.with stuck breaker near SANGER_SW 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.SANGERSW3 115KV 528463 TO G18004TAP 115KV 762442 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TUCOINT6_230kV_525830 | a. Apply single-phase fault on: a.1. TUCOINT6 230.0 KV 525830 TO SWISHER6 230.0 KV 525213 CKT 1, b.with stuck breaker near TUCO_INT 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.TUCOINT6 230.0 KV 525830 TO CARLISLE6 230.0 KV 526161 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | TUCOINT7_345kV_525832 | a. Apply single-phase fault on: a.1. BORDER7 345KV 515458 TO TUCOINT7 345KV 525832 CKT 1, b.with stuck breaker near TUCO_INT 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1.TUCOINT7 345KV 525832 TO YOAKUM_345 345KV 526936 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | WBENDER_115kV_528449 | a. Apply single-phase fault on: a.1. WBENDER 115KV 528449 TO OXYNHURCF3 115KV 528574 CKT 1 a.2. OXYPERMIAN3 115KV 528575 TO OXYNHURCF3 115KV 528574 CKT 1 a.3. OXYPERMIAN3 115KV 528575 TO SANGERSW3 115KV 528463 CKT 1, b.with stuck breaker near W_BENDER 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.WBENDER 115KV 528449 TO NHOBBS3 115KV 528456 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25W | Transfer | W_HOBBS_115kV_528498 | a. Apply single-phase fault on: a.1. WHOBBS3 115KV 528498 TO MONUMENT3 115KV 528491 CKT 1, b.with stuck breaker near W_HOBBS 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.WHOBBS3 115KV 528498 TO DRINKARDTP3 115KV 528533 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes

## Short Circuit Analysis
Gen Number | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 25SP Fault Current 3-Phase (kA) | Request In Service 25SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
ASGI-2017-013 | 01 NORTH | 652284 | HURON 8 | 69 | 3.8235 | 4.1101 | 0.2866
ASGI-2017-013 | 01 NORTH | 652515 | HURON 7 | 115 | 15.5909 | 15.7527 | 0.1618
ASGI-2017-013 | 01 NORTH | 655053 | MOS-MILR-ER8 | 69 | 2.4854 | 2.6016 | 0.1162
ASGI-2017-013 | 01 NORTH | 655055 | SW-YALE-ER8 | 69 | 1.2325 | 1.2578 | 0.0253
ASGI-2017-013 | 01 NORTH | 655058 | MOS-HRON-ER8 | 69 | 2.7563 | 3.0518 | 0.2955
ASGI-2017-013 | 01 NORTH | 655060 | MOS-POLO-ER8 | 69 | 1.0182 | 1.0368 | 0.0186
ASGI-2017-013 | 01 NORTH | 655062 | MOS-YALE-ER8 | 69 | 1.4656 | 1.5024 | 0.0368
ASGI-2017-013 | 01 NORTH | 655063 | SW-HURN1-ER8 | 69 | 3.7682 | 4.0552 | 0.287
ASGI-2017-013 | 01 NORTH | 655064 | SW-HURN4-ER8 | 69 | 3.7427 | 4.0167 | 0.274
ASGI-2017-013 | 01 NORTH | 655065 | MOS-YLTI-ER8 | 69 | 1.7045 | 1.7554 | 0.0509
ASGI-2017-013 | 01 NORTH | 655066 | SW-HURN2-ER8 | 69 | 3.8073 | 4.0914 | 0.2841
ASGI-2017-013 | 01 NORTH | 655067 | SW-HURN3-ER8 | 69 | 3.8114 | 4.0961 | 0.2847
ASGI-2017-013 | 01 NORTH | 655069 | MOS-WOLS-ER8 | 69 | 2.2713 | 2.5704 | 0.2991
ASGI-2017-013 | 01 NORTH | 655070 | MOS-VRCV-ER8 | 69 | 1.2526 | 1.339 | 0.0864
ASGI-2017-013 | 01 NORTH | 655071 | MOS-DAK-ER8 | 69 | 1.0692 | 1.1312 | 0.062
ASGI-2017-013 | 01 NORTH | 655228 | YALE-ER8 | 69 | 1.2137 | 1.2382 | 0.0245
ASGI-2017-013 | 01 NORTH | 655231 | HURON-ER8 | 69 | 2.7531 | 3.0479 | 0.2948
ASGI-2017-013 | 01 NORTH | 655234 | MILLER-ER8 | 69 | 1.0262 | 1.045 | 0.0188
ASGI-2017-013 | 01 NORTH | 655236 | MORNINGS-ER8 | 69 | 1.9499 | 2.0178 | 0.0679
ASGI-2017-013 | 01 NORTH | 655237 | BONILLA-ER8 | 69 | 1.6769 | 1.7281 | 0.0512
ASGI-2017-013 | 01 NORTH | 655239 | WOLSEY-ER8 | 69 | 1.349 | 1.6525 | 0.3035
ASGI-2017-013 | 01 NORTH | 655241 | VIRGIL-ER8 | 69 | 1.8812 | 2.0838 | 0.2026
ASGI-2017-013 | 01 NORTH | 655242 | CAVOUR-ER8 | 69 | 1.2042 | 1.2838 | 0.0796
ASGI-2017-013 | 01 NORTH | 655244 | DAKOTA-ER8 | 69 | 0.994 | 1.0473 | 0.0533
ASGI-2017-013 | 01 NORTH | 655378 | NWPS3680-ER8 | 69 | 1.0435 | 1.0631 | 0.0196
ASGI-2017-013 | 01 NORTH | 655509 | SW-MILRC-ER8 | 69 | 1.0554 | 1.0754 | 0.02
ASGI-2017-013 | 01 NORTH | 762350 | ASGI-2017-01 | 69 | 1.349 | 1.6524 | 0.3034
GEN-2018-010 | 01 NORTH | 587030 | GEN-2016-004 | 230 | 7.5281 | 7.5298 | 0.0017
GEN-2018-010 | 01 NORTH | 588210 | GEN-2016-130 | 345 | 12.014 | 12.0228 | 0.0088
GEN-2018-010 | 01 NORTH | 588870 | GEN-2017-048 | 230 | 8.9936 | 9.2131 | 0.2195
GEN-2018-010 | 01 NORTH | 603023 | MALLARD7 | 115 | 11.2712 | 11.2779 | 0.0067
GEN-2018-010 | 01 NORTH | 615901 | GRE-STANTON4 | 230 | 18.1827 | 18.1839 | 0.0012
GEN-2018-010 | 01 NORTH | 652216 | WATFORD4 | 230 | 6.6898 | 6.697 | 0.0072
GEN-2018-010 | 01 NORTH | 652257 | DEVAUL 8 | 69 | 1.1032 | 1.1032 | 0
GEN-2018-010 | 01 NORTH | 652391 | WILLISTON27 | 115 | 18.1076 | 18.1537 | 0.0461
GEN-2018-010 | 01 NORTH | 652400 | WILISTN4 | 230 | 10.8892 | 10.9321 | 0.0429
GEN-2018-010 | 01 NORTH | 652408 | WATFORD7 | 115 | 8.5924 | 8.5969 | 0.0045
GEN-2018-010 | 01 NORTH | 652421 | WILISTN7 | 115 | 18.1014 | 18.1473 | 0.0459
GEN-2018-010 | 01 NORTH | 652441 | GARRISN4 | 230 | 12.5067 | 12.5089 | 0.0022
GEN-2018-010 | 01 NORTH | 652456 | WASHBRN4 | 230 | 10.6182 | 10.6209 | 0.0027
GEN-2018-010 | 01 NORTH | 652651 | FAIRVIEW 7 | 115 | 5.0209 | 5.0222 | 0.0013
GEN-2018-010 | 01 NORTH | 655641 | BERTHOLD-CP7 | 115 | 6.2299 | 6.2389 | 0.009
GEN-2018-010 | 01 NORTH | 655657 | SW.MINOT-CP7 | 115 | 8.0975 | 8.1033 | 0.0058
GEN-2018-010 | 01 NORTH | 655731 | LARK -MG8 | 69 | 0.9751 | 0.9751 | 0
GEN-2018-010 | 01 NORTH | 655732 | FLASHER -MG8 | 69 | 0.9022 | 0.9022 | 0
GEN-2018-010 | 01 NORTH | 655740 | CANNON -MG8 | 69 | 0.909 | 0.909 | 0
GEN-2018-010 | 01 NORTH | 655741 | CEDAR -MG8 | 69 | 0.6891 | 0.6891 | 0
GEN-2018-010 | 01 NORTH | 655742 | GRANT -MG8 | 69 | 0.6174 | 0.6174 | 0
GEN-2018-010 | 01 NORTH | 655744 | DEVALTP -MG8 | 69 | 1.1095 | 1.1095 | 0
GEN-2018-010 | 01 NORTH | 655746 | DEVAUL -MG8 | 69 | 1.1153 | 1.1153 | 0
GEN-2018-010 | 01 NORTH | 655747 | DEVAUL -MG7 | 115 | 1.1059 | 1.1059 | 0
GEN-2018-010 | 01 NORTH | 655748 | NEWSALEM-MG7 | 115 | 1.5111 | 1.5111 | 0
GEN-2018-010 | 01 NORTH | 655749 | MANSWTCH-MG7 | 115 | 1.022 | 1.022 | 0
GEN-2018-010 | 01 NORTH | 655750 | ROUGHRDR-MG7 | 115 | 0.9895 | 0.9895 | 0
GEN-2018-010 | 01 NORTH | 655751 | NRWSTMDN-MG7 | 115 | 0.9899 | 0.9899 | 0
GEN-2018-010 | 01 NORTH | 655752 | NWMDNTAP-MG7 | 115 | 1.5486 | 1.5487 | 0.0001
GEN-2018-010 | 01 NORTH | 655780 | NORMANLK-BD7 | 115 | 3.1443 | 3.1484 | 0.0041
GEN-2018-010 | 01 NORTH | 655781 | LARSON -BD7 | 115 | 2.1801 | 2.1821 | 0.002
GEN-2018-010 | 01 NORTH | 655782 | LIGNIBRD-BD7 | 115 | 1.5327 | 1.5336 | 0.0009
GEN-2018-010 | 01 NORTH | 655783 | HAWKEYE -BD7 | 115 | 1.4636 | 1.4645 | 0.0009
GEN-2018-010 | 01 NORTH | 655784 | AMBROSE -BD7 | 115 | 1.24 | 1.2406 | 0.0006
GEN-2018-010 | 01 NORTH | 655791 | SPRINGLK-LY7 | 115 | 1.9827 | 1.9829 | 0.0002
GEN-2018-010 | 01 NORTH | 655792 | NOHLEY -LY7 | 115 | 3.5624 | 3.5631 | 0.0007
GEN-2018-010 | 01 NORTH | 655793 | MARLEY -LY7 | 115 | 5.9488 | 5.9537 | 0.0049
GEN-2018-010 | 01 NORTH | 655840 | CHRRYCRK-MK7 | 115 | 8.5924 | 8.5969 | 0.0045
GEN-2018-010 | 01 NORTH | 655841 | ARNEGARD-MK7 | 115 | 6.6911 | 6.6927 | 0.0016
GEN-2018-010 | 01 NORTH | 655845 | GRDNCRK2-MK7 | 115 | 4.6233 | 4.6246 | 0.0013
GEN-2018-010 | 01 NORTH | 655855 | ROOSEVLT-MK7 | 115 | 4.7627 | 4.7641 | 0.0014
GEN-2018-010 | 01 NORTH | 655875 | DPLWC___-MK7 | 115 | 7.5313 | 7.5348 | 0.0035
GEN-2018-010 | 01 NORTH | 655876 | DPLWCTAP-MK7 | 115 | 8.2668 | 8.2709 | 0.0041
GEN-2018-010 | 01 NORTH | 655877 | LITTLMS4-MK7 | 115 | 5.217 | 5.2187 | 0.0017
GEN-2018-010 | 01 NORTH | 655878 | CRESTWD_-MK7 | 115 | 3.8962 | 3.8971 | 0.0009
GEN-2018-010 | 01 NORTH | 655879 | OASIS___-MK7 | 115 | 4.6585 | 4.6598 | 0.0013
GEN-2018-010 | 01 NORTH | 655895 | GARDN-FB-MK7 | 115 | 4.2666 | 4.2677 | 0.0011
GEN-2018-010 | 01 NORTH | 655898 | SCHAFER -MK7 | 115 | 3.096 | 3.0966 | 0.0006
GEN-2018-010 | 01 NORTH | 655900 | MOE -MW7 | 115 | 7.021 | 7.0441 | 0.0231
GEN-2018-010 | 01 NORTH | 655901 | BROOKBNK-MW7 | 115 | 8.0349 | 8.0613 | 0.0264
GEN-2018-010 | 01 NORTH | 655902 | PLSNTV_T-MW7 | 115 | 7.3999 | 7.4262 | 0.0263
GEN-2018-010 | 01 NORTH | 655903 | ROSS -MW7 | 115 | 6.4705 | 6.4893 | 0.0188
GEN-2018-010 | 01 NORTH | 655904 | BELDEN -MW7 | 115 | 8.5093 | 8.5347 | 0.0254
GEN-2018-010 | 01 NORTH | 655905 | RBNSNLAK-MW7 | 115 | 9.4071 | 9.435 | 0.0279
GEN-2018-010 | 01 NORTH | 655906 | FINSTAD -MW7 | 115 | 18.0523 | 18.146 | 0.0937
GEN-2018-010 | 01 NORTH | 655907 | E.NEWTWN-MW7 | 115 | 10.8698 | 10.9065 | 0.0367
GEN-2018-010 | 01 NORTH | 655909 | HESS GAS-MW7 | 115 | 10.9349 | 10.9937 | 0.0588
GEN-2018-010 | 01 NORTH | 655910 | LINDAHLS-MW7 | 115 | 5.6839 | 5.6974 | 0.0135
GEN-2018-010 | 01 NORTH | 655911 | SIMPSON -MW7 | 115 | 3.8828 | 3.8891 | 0.0063
GEN-2018-010 | 01 NORTH | 655912 | AUSTIN -MW7 | 115 | 5.9764 | 5.9889 | 0.0125
GEN-2018-010 | 01 NORTH | 655913 | PLSNTVAL-MW7 | 115 | 7.3604 | 7.3864 | 0.026
GEN-2018-010 | 01 NORTH | 655914 | NE.ROSS_-MW7 | 115 | 4.1104 | 4.1159 | 0.0055
GEN-2018-010 | 01 NORTH | 655916 | PALERMO -MW7 | 115 | 6.9352 | 6.9502 | 0.015
GEN-2018-010 | 01 NORTH | 655917 | STANLEY -MW7 | 115 | 6.6121 | 6.6263 | 0.0142
GEN-2018-010 | 01 NORTH | 655918 | PALGASPL-MW7 | 115 | 5.8929 | 5.9037 | 0.0108
GEN-2018-010 | 01 NORTH | 655919 | OSBORN -MW7 | 115 | 10.8263 | 10.8622 | 0.0359
GEN-2018-010 | 01 NORTH | 655920 | VANHOOK -MW7 | 115 | 12.2597 | 12.3028 | 0.0431
GEN-2018-010 | 01 NORTH | 655921 | LOSTWOOD-MW7 | 115 | 3.4048 | 3.4086 | 0.0038
GEN-2018-010 | 01 NORTH | 655922 | W.BANK__-MW7 | 115 | 7.1646 | 7.1862 | 0.0216
GEN-2018-010 | 01 NORTH | 655923 | FARMVALE-MW7 | 115 | 4.5331 | 4.5415 | 0.0084
GEN-2018-010 | 01 NORTH | 655925 | JUDSON -MW7 | 115 | 14.396 | 14.4229 | 0.0269
GEN-2018-010 | 01 NORTH | 655926 | SW.WLSTN-MW7 | 115 | 8.3855 | 8.3946 | 0.0091
GEN-2018-010 | 01 NORTH | 655929 | RATLAKE -MW7 | 115 | 8.6625 | 8.6965 | 0.034
GEN-2018-010 | 01 NORTH | 655930 | WHTEARTH-MW7 | 115 | 11.6848 | 11.753 | 0.0682
GEN-2018-010 | 01 NORTH | 655935 | NW.WLSTN-MW7 | 115 | 11.7284 | 11.7519 | 0.0235
GEN-2018-010 | 01 NORTH | 655940 | MONT -MW7 | 115 | 13.7454 | 13.7692 | 0.0238
GEN-2018-010 | 01 NORTH | 655943 | FARMVL_T-MW7 | 115 | 7.0737 | 7.0941 | 0.0204
GEN-2018-010 | 01 NORTH | 655944 | PLAZA -MW7 | 115 | 6.7216 | 6.7322 | 0.0106
GEN-2018-010 | 01 NORTH | 655945 | WHEELS_T-MW7 | 115 | 8.7055 | 8.7319 | 0.0264
GEN-2018-010 | 01 NORTH | 655946 | POWERSLK-MW7 | 115 | 4.7578 | 4.7681 | 0.0103
GEN-2018-010 | 01 NORTH | 655947 | PWRSLKTP-MW7 | 115 | 7.3504 | 7.3748 | 0.0244
GEN-2018-010 | 01 NORTH | 655948 | LIBERTY -MW7 | 115 | 6.677 | 6.6967 | 0.0197
GEN-2018-010 | 01 NORTH | 655949 | BLAISDEL-MW7 | 115 | 8.5539 | 8.5755 | 0.0216
GEN-2018-010 | 01 NORTH | 655950 | LOSTWD_T-MW7 | 115 | 5.4774 | 5.4871 | 0.0097
GEN-2018-010 | 01 NORTH | 655951 | NE.ROS_T-MW7 | 115 | 4.592 | 4.5988 | 0.0068
GEN-2018-010 | 01 NORTH | 655952 | TIOGA.N_-MW7 | 115 | 10.9754 | 11.0346 | 0.0592
GEN-2018-010 | 01 NORTH | 655953 | W.BANK_T-MW7 | 115 | 8.4794 | 8.5127 | 0.0333
GEN-2018-010 | 01 NORTH | 655954 | ELLISVIL-MW7 | 115 | 5.7936 | 5.8033 | 0.0097
GEN-2018-010 | 01 NORTH | 655957 | EASTFORK-MW7 | 115 | 15.5536 | 15.6033 | 0.0497
GEN-2018-010 | 01 NORTH | 655959 | EPPING -MW7 | 115 | 7.7887 | 7.8089 | 0.0202
GEN-2018-010 | 01 NORTH | 655960 | BIGBEND -MW7 | 115 | 5.2192 | 5.2277 | 0.0085
GEN-2018-010 | 01 NORTH | 655961 | HESSRAIL-MW7 | 115 | 6.6513 | 6.6714 | 0.0201
GEN-2018-010 | 01 NORTH | 655962 | HESSRTAP-MW7 | 115 | 7.9477 | 7.9763 | 0.0286
GEN-2018-010 | 01 NORTH | 655963 | HOWIE -MW7 | 115 | 4.2601 | 4.2657 | 0.0056
GEN-2018-010 | 01 NORTH | 655965 | E.NESSON-MW7 | 115 | 5.397 | 5.4107 | 0.0137
GEN-2018-010 | 01 NORTH | 655966 | OLIVER -MW7 | 115 | 6.5199 | 6.5336 | 0.0137
GEN-2018-010 | 01 NORTH | 655967 | SATTER -MW7 | 115 | 7.9928 | 8.0157 | 0.0229
GEN-2018-010 | 01 NORTH | 655968 | MUSKRAT -MW7 | 115 | 4.3947 | 4.4007 | 0.006
GEN-2018-010 | 01 NORTH | 659060 | FINSTAD345 | 345 | 6.4918 | 6.5277 | 0.0359
GEN-2018-010 | 01 NORTH | 659101 | ANTELOPE-BE3 | 345 | 16.0756 | 16.0906 | 0.015
GEN-2018-010 | 01 NORTH | 659105 | LELAND_O-BE3 | 345 | 17.7756 | 17.7953 | 0.0197
GEN-2018-010 | 01 NORTH | 659106 | LELAND_O-BE4 | 230 | 24.1423 | 24.1622 | 0.0199
GEN-2018-010 | 01 NORTH | 659108 | LOGAN___-BE4 | 230 | 6.3342 | 6.343 | 0.0088
GEN-2018-010 | 01 NORTH | 659109 | BASIN___-BE7 | 115 | 5.3899 | 5.3904 | 0.0005
GEN-2018-010 | 01 NORTH | 659138 | NESET___-BE4 | 230 | 11.5452 | 11.7526 | 0.2074
GEN-2018-010 | 01 NORTH | 659139 | NESET___-BE7 | 115 | 12.3392 | 12.4153 | 0.0761
GEN-2018-010 | 01 NORTH | 659140 | NRTSHORE-BE4 | 230 | 5.1836 | 5.2189 | 0.0353
GEN-2018-010 | 01 NORTH | 659141 | NRTSHORE-BE7 | 115 | 9.6708 | 9.7127 | 0.0419
GEN-2018-010 | 01 NORTH | 659143 | BLAISDEL-BE4 | 230 | 5.938 | 5.9643 | 0.0263
GEN-2018-010 | 01 NORTH | 659144 | BLAISDEL-BE7 | 115 | 8.8307 | 8.8539 | 0.0232
GEN-2018-010 | 01 NORTH | 659154 | LC_CT4-5-BE7 | 115 | 6.503 | 6.5041 | 0.0011
GEN-2018-010 | 01 NORTH | 659155 | LOGAN___-BE7 | 115 | 11.0387 | 11.0476 | 0.0089
GEN-2018-010 | 01 NORTH | 659199 | BASIN___-BE4 | 230 | 21.9978 | 22.0142 | 0.0164
GEN-2018-010 | 01 NORTH | 659212 | DGC_____-BE3 | 345 | 15.3703 | 15.384 | 0.0137
GEN-2018-010 | 01 NORTH | 659218 | COTEAU__-RR3 | 345 | 16.0756 | 16.0906 | 0.015
GEN-2018-010 | 01 NORTH | 659222 | COTEAU_1-RR8 | 69 | 9.6263 | 9.6274 | 0.0011
GEN-2018-010 | 01 NORTH | 659233 | DGC_____-BE4 | 230 | 7.2116 | 7.2136 | 0.002
GEN-2018-010 | 01 NORTH | 659236 | DGC UREA-BE8 | 69 | 7.2638 | 7.2644 | 0.0006
GEN-2018-010 | 01 NORTH | 659262 | CULBSN.E-BE7 | 115 | 5.8026 | 5.8037 | 0.0011
GEN-2018-010 | 01 NORTH | 659269 | CULB_GEN-BE7 | 115 | 5.6955 | 5.6964 | 0.0009
GEN-2018-010 | 01 NORTH | 659302 | CHARL_CK-BE4 | 230 | 11.268 | 11.2803 | 0.0123
GEN-2018-010 | 01 NORTH | 659308 | KENASTON-BE7 | 115 | 3.4135 | 3.4171 | 0.0036
GEN-2018-010 | 01 NORTH | 659333 | JUDSON__-BE3 | 345 | 8.1401 | 8.1734 | 0.0333
GEN-2018-010 | 01 NORTH | 659334 | JUDSON__-BE4 | 230 | 10.8261 | 10.8679 | 0.0418
GEN-2018-010 | 01 NORTH | 659336 | TANDE___-BE3 | 345 | 7.914 | 7.9965 | 0.0825
GEN-2018-010 | 01 NORTH | 659337 | TANDE___-BE4 | 230 | 11.4165 | 11.6086 | 0.1921
GEN-2018-010 | 01 NORTH | 659346 | LC_SWY.S-BE7 | 115 | 6.4978 | 6.4988 | 0.001
GEN-2018-010 | 01 NORTH | 659362 | WHEELOCK-BE4 | 230 | 7.4191 | 7.466 | 0.0469
GEN-2018-010 | 01 NORTH | 659363 | WHEELOCK-BE7 | 115 | 8.9133 | 8.9412 | 0.0279
GEN-2018-010 | 01 NORTH | 659404 | BURKE___-PP3 | 345 | 4.5721 | 4.5975 | 0.0254
GEN-2018-010 | 01 NORTH | 659422 | LO.LS-GR-BE3 | 345 | 17.7756 | 17.7953 | 0.0197
GEN-2018-010 | 01 NORTH | 659424 | LO.LS-FT-BE3 | 345 | 17.7756 | 17.7953 | 0.0197
GEN-2018-010 | 01 NORTH | 659427 | TN.LS-JD-BE3 | 345 | 7.914 | 7.9965 | 0.0825
GEN-2018-010 | 01 NORTH | 659454 | LINDAHLWND 7 | 115 | 5.2515 | 5.2626 | 0.0111
GEN-2018-010 | 01 NORTH | 659479 | TRADEWND-UA3 | 345 | 5.8012 | 5.8431 | 0.0419
GEN-2018-010 | 01 NORTH | 659600 | EFORK_-BE334 | 345 | 7.4027 | 7.4403 | 0.0376
GEN-2018-010 | 01 NORTH | 661003 | WATFRDSOUTH4 | 230 | 6.6213 | 6.6283 | 0.007
GEN-2018-010 | 01 NORTH | 661052 | KENMARE7 | 115 | 3.3361 | 3.3397 | 0.0036
GEN-2018-010 | 01 NORTH | 661080 | STANLEY7 | 115 | 3.8648 | 3.8709 | 0.0061
GEN-2018-010 | 01 NORTH | 661084 | TIOGA4 4 | 230 | 11.5452 | 11.7526 | 0.2074
GEN-2018-010 | 01 NORTH | 661085 | TIOGA4 7 | 115 | 12.3001 | 12.3758 | 0.0757
GEN-2018-010 | 01 NORTH | 661086 | TIOGA7 7 | 115 | 9.6521 | 9.6964 | 0.0443
GEN-2018-010 | 01 NORTH | 661087 | RAY JCT7 | 115 | 5.6919 | 5.7033 | 0.0114
GEN-2018-010 | 01 NORTH | 661089 | LTLMUDY7 | 115 | 6.8963 | 6.9061 | 0.0098
GEN-2018-010 | 01 NORTH | 661281 | LIGNITE7 | 115 | 1.5778 | 1.5786 | 0.0008
GEN-2018-010 | 01 NORTH | 672401 | BD 8 | 72 | 6.4128 | 6.413 | 0.0002
GEN-2018-010 | 01 NORTH | 672413 | AUBURNTON 8 | 72 | 11.4628 | 11.4631 | 0.0003
GEN-2018-010 | 01 NORTH | 672501 | BD 6 | 138 | 14.0266 | 14.0283 | 0.0017
GEN-2018-010 | 01 NORTH | 672521 | HALBRITE 6 | 138 | 1.9055 | 1.9055 | 0
GEN-2018-010 | 01 NORTH | 672601 | BD 4 | 230 | 15.5814 | 15.5851 | 0.0037
GEN-2018-010 | 01 NORTH | 672602 | BDX 4 | 230 | 4.9584 | 4.9698 | 0.0114
GEN-2018-010 | 01 NORTH | 672603 | BDV 4 | 230 | 4.9563 | 4.9679 | 0.0116
GEN-2018-010 | 01 NORTH | 672613 | AUBURNTON 4 | 230 | 5.7659 | 5.7661 | 0.0002
GEN-2018-010 | 01 NORTH | 672621 | SHAND 4 | 230 | 10.9808 | 10.9822 | 0.0014
GEN-2018-010 | 01 NORTH | 672664 | ROWATT | 230 | 10.1669 | 10.1673 | 0.0004
GEN-2018-010 | 01 NORTH | 673601 | KISBEY TAP 4 | 230 | 5.6898 | 5.6901 | 0.0003
GEN-2018-010 | 01 NORTH | 673602 | KISBEY 4 | 230 | 4.853 | 4.8532 | 0.0002
GEN-2018-010 | 01 NORTH | 760998 | GEN-2017-214 | 230 | 3.1201 | 3.1219 | 0.0018
GEN-2018-025 | 02 NEBRASKA | 45906 | J1590 SUB | 345 | 14.9863 | 14.9897 | 0.0034
GEN-2018-025 | 02 NEBRASKA | 85831 | J583 | 345 | 6.1922 | 6.1929 | 0.0007
GEN-2018-025 | 02 NEBRASKA | 87486 | J748GENTIE | 345 | 13.9517 | 13.9544 | 0.0027
GEN-2018-025 | 02 NEBRASKA | 87487 | J748POI | 345 | 15.8344 | 15.838 | 0.0036
GEN-2018-025 | 02 NEBRASKA | 300039 | 7FAIRPT | 345 | 12.7332 | 12.7337 | 0.0005
GEN-2018-025 | 02 NEBRASKA | 541197 | MULLNCR7 | 345 | 8.4836 | 8.4842 | 0.0006
GEN-2018-025 | 02 NEBRASKA | 541199 | ST JOE 7 | 345 | 20.3832 | 20.384 | 0.0008
GEN-2018-025 | 02 NEBRASKA | 541411 | MC REAC1 | 345 | 8.0936 | 8.0942 | 0.0006
GEN-2018-025 | 02 NEBRASKA | 541412 | MC REAC2 | 345 | 8.0936 | 8.0942 | 0.0006
GEN-2018-025 | 02 NEBRASKA | 541413 | MC REAC3 | 345 | 8.0936 | 8.0942 | 0.0006
GEN-2018-025 | 02 NEBRASKA | 541510 | HOLT 7 | 345 | 10.0841 | 10.0852 | 0.0011
GEN-2018-025 | 02 NEBRASKA | 541511 | ROCKCK7 | 345 | 8.0086 | 8.0092 | 0.0006
GEN-2018-025 | 02 NEBRASKA | 541517 | HOLT_REACT7 | 345 | 10.0263 | 10.0274 | 0.0011
GEN-2018-025 | 02 NEBRASKA | 541543 | OUTLAW | 345 | 6.7533 | 6.7537 | 0.0004
GEN-2018-025 | 02 NEBRASKA | 585241 | GEN-2015-088 | 345 | 12.2266 | 12.2286 | 0.002
GEN-2018-025 | 02 NEBRASKA | 601006 | SPLT RK3 | 345 | 14.5318 | 14.5324 | 0.0006
GEN-2018-025 | 02 NEBRASKA | 635000 | CBLUFFS3 | 345 | 32.2592 | 32.3364 | 0.0772
GEN-2018-025 | 02 NEBRASKA | 635001 | CBLUFFS5 | 161 | 39.8812 | 39.94 | 0.0588
GEN-2018-025 | 02 NEBRASKA | 635002 | CBLUFFS8 | 69 | 25.2636 | 25.2738 | 0.0102
GEN-2018-025 | 02 NEBRASKA | 635003 | SUB701 5 | 161 | 21.6295 | 21.6517 | 0.0222
GEN-2018-025 | 02 NEBRASKA | 635011 | INDNCRK5 | 161 | 22.0885 | 22.1093 | 0.0208
GEN-2018-025 | 02 NEBRASKA | 635013 | PNYCRK 3 | 345 | 29.3549 | 29.4174 | 0.0625
GEN-2018-025 | 02 NEBRASKA | 635014 | OVRLND 3 | 345 | 27.5603 | 27.6146 | 0.0543
GEN-2018-025 | 02 NEBRASKA | 635015 | OVRLND 5 | 161 | 31.6069 | 31.6414 | 0.0345
GEN-2018-025 | 02 NEBRASKA | 635016 | STHLND 3 | 345 | 29.3193 | 29.3817 | 0.0624
GEN-2018-025 | 02 NEBRASKA | 635017 | ATCHSN 3 | 345 | 17.6843 | 17.6876 | 0.0033
GEN-2018-025 | 02 NEBRASKA | 635030 | RIVRBND5 | 161 | 36.3313 | 36.3795 | 0.0482
GEN-2018-025 | 02 NEBRASKA | 635100 | RLHILLS3 | 345 | 13.5306 | 13.5343 | 0.0037
GEN-2018-025 | 02 NEBRASKA | 635200 | RAUN 3 | 345 | 28.3358 | 28.3601 | 0.0243
GEN-2018-025 | 02 NEBRASKA | 635201 | RAUN 5 | 161 | 28.3093 | 28.3204 | 0.0111
GEN-2018-025 | 02 NEBRASKA | 635202 | NEAL S 5 | 161 | 23.3588 | 23.366 | 0.0072
GEN-2018-025 | 02 NEBRASKA | 635203 | NEAL N 5 | 161 | 26.7623 | 26.7721 | 0.0098
GEN-2018-025 | 02 NEBRASKA | 635204 | NEAL N 8 | 69 | 10.2474 | 10.248 | 0.0006
GEN-2018-025 | 02 NEBRASKA | 635206 | IDA CO 3 | 345 | 9.4855 | 9.4868 | 0.0013
GEN-2018-025 | 02 NEBRASKA | 635219 | GARD AVE 3 | 345 | 9.0676 | 9.0686 | 0.001
GEN-2018-025 | 02 NEBRASKA | 635220 | INTCHG 5 | 161 | 15.1871 | 15.1898 | 0.0027
GEN-2018-025 | 02 NEBRASKA | 635221 | KELLOGG5 | 161 | 17.8694 | 17.873 | 0.0036
GEN-2018-025 | 02 NEBRASKA | 635229 | AIRPORT 5 | 161 | 17.7546 | 17.7585 | 0.0039
GEN-2018-025 | 02 NEBRASKA | 635230 | LIBERTY5 | 161 | 26.0511 | 26.0604 | 0.0093
GEN-2018-025 | 02 NEBRASKA | 635235 | SALIX 5 | 161 | 15.278 | 15.2808 | 0.0028
GEN-2018-025 | 02 NEBRASKA | 635252 | J412 POI 3 | 345 | 9.9027 | 9.9042 | 0.0015
GEN-2018-025 | 02 NEBRASKA | 635300 | MONONA 5 | 161 | 5.7193 | 5.7196 | 0.0003
GEN-2018-025 | 02 NEBRASKA | 635398 | REMSEN 3 | 345 | 15.2221 | 15.2256 | 0.0035
GEN-2018-025 | 02 NEBRASKA | 635399 | CHEROKEE 3 | 345 | 16.7402 | 16.744 | 0.0038
GEN-2018-025 | 02 NEBRASKA | 635400 | HIGHLND 3 | 345 | 15.3051 | 15.307 | 0.0019
GEN-2018-025 | 02 NEBRASKA | 635589 | ECLIPSE3 | 345 | 9.3941 | 9.3957 | 0.0016
GEN-2018-025 | 02 NEBRASKA | 635590 | FALLOW 3 | 345 | 11.4628 | 11.4652 | 0.0024
GEN-2018-025 | 02 NEBRASKA | 637009 | GLACIAL EDGE | 345 | 16.4513 | 16.4549 | 0.0036
GEN-2018-025 | 02 NEBRASKA | 637024 | RICHLAND W | 345 | 8.9974 | 8.9984 | 0.001
GEN-2018-025 | 02 NEBRASKA | 640080 | BELDEN 7 | 115 | 6.3503 | 6.3504 | 0.0001
GEN-2018-025 | 02 NEBRASKA | 640081 | BELDEN 8 | 69 | 3.9026 | 3.9026 | 0
GEN-2018-025 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 10.6806 | 10.6823 | 0.0017
GEN-2018-025 | 02 NEBRASKA | 640127 | COLMB.E7 | 115 | 23.5846 | 23.5866 | 0.002
GEN-2018-025 | 02 NEBRASKA | 640139 | COOPER 3 | 345 | 27.688 | 27.697 | 0.009
GEN-2018-025 | 02 NEBRASKA | 640140 | COOPER 5 | 161 | 18.1825 | 18.1845 | 0.002
GEN-2018-025 | 02 NEBRASKA | 640141 | COOPER_ESST8 | 69 | 4.6838 | 4.6839 | 0.0001
GEN-2018-025 | 02 NEBRASKA | 640226 | HOSKINS3 | 345 | 13.7777 | 13.78 | 0.0023
GEN-2018-025 | 02 NEBRASKA | 640227 | HOSKINS4 | 230 | 10.6375 | 10.6384 | 0.0009
GEN-2018-025 | 02 NEBRASKA | 640228 | HOSKINS7 | 115 | 19.1635 | 19.165 | 0.0015
GEN-2018-025 | 02 NEBRASKA | 640271 | MCCOOL 3 | 345 | 11.4595 | 11.4607 | 0.0012
GEN-2018-025 | 02 NEBRASKA | 640277 | MOORE 3 | 345 | 23.896 | 23.9081 | 0.0121
GEN-2018-025 | 02 NEBRASKA | 640278 | SHELDON7 | 115 | 45.4022 | 45.4126 | 0.0104
GEN-2018-025 | 02 NEBRASKA | 640296 | NORFK.N7 | 115 | 13.9594 | 13.9602 | 0.0008
GEN-2018-025 | 02 NEBRASKA | 640298 | NORFOLK7 | 115 | 13.0916 | 13.0922 | 0.0006
GEN-2018-025 | 02 NEBRASKA | 640316 | PAWNEEL7 | 115 | 11.7873 | 11.7883 | 0.001
GEN-2018-025 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 10.9552 | 10.9568 | 0.0016
GEN-2018-025 | 02 NEBRASKA | 640343 | SHELCRK4 | 230 | 11.534 | 11.5349 | 0.0009
GEN-2018-025 | 02 NEBRASKA | 640363 | STNTN.N7 | 115 | 7.3444 | 7.3448 | 0.0004
GEN-2018-025 | 02 NEBRASKA | 640377 | TEKAMAH5 | 161 | 9.3073 | 9.3131 | 0.0058
GEN-2018-025 | 02 NEBRASKA | 640378 | TEKAMAH7 | 115 | 8.5941 | 8.5968 | 0.0027
GEN-2018-025 | 02 NEBRASKA | 640446 | COOPER 8 | 69 | 4.7815 | 4.7816 | 0.0001
GEN-2018-025 | 02 NEBRASKA | 640520 | ANTELOPE 3 | 345 | 7.0357 | 7.0362 | 0.0005
GEN-2018-025 | 02 NEBRASKA | 640521 | ANTELOPE 7 | 115 | 16.5838 | 16.5844 | 0.0006
GEN-2018-025 | 02 NEBRASKA | 640522 | ANTELOPE 8 | 69 | 5.5028 | 5.5028 | 0
GEN-2018-025 | 02 NEBRASKA | 640525 | TOBIAS 3 | 345 | 12.2266 | 12.2286 | 0.002
GEN-2018-025 | 02 NEBRASKA | 640560 | WAKEFIELD 4 | 230 | 8.3605 | 8.3609 | 0.0004
GEN-2018-025 | 02 NEBRASKA | 640561 | RTLSNAKE.W 4 | 230 | 7.465 | 7.4653 | 0.0003
GEN-2018-025 | 02 NEBRASKA | 640588 | TURTLE.CRK 3 | 345 | 12.1392 | 12.1407 | 0.0015
GEN-2018-025 | 02 NEBRASKA | 640589 | SHOLES.W 3 | 345 | 9.8863 | 9.8873 | 0.001
GEN-2018-025 | 02 NEBRASKA | 640590 | MONOLITH 3 | 345 | 23.3786 | 23.3899 | 0.0113
GEN-2018-025 | 02 NEBRASKA | 640598 | HAYSTACK.WD3 | 345 | 9.2758 | 9.2767 | 0.0009
GEN-2018-025 | 02 NEBRASKA | 643254 | UPSTREAM.W 7 | 115 | 15.8627 | 15.8632 | 0.0005
GEN-2018-025 | 02 NEBRASKA | 643271 | PLUMBCR.W 3 | 345 | 11.8905 | 11.892 | 0.0015
GEN-2018-025 | 02 NEBRASKA | 645100 | FC1A 5 | 161 | 29.8545 | 30.0624 | 0.2079
GEN-2018-025 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 22.4021 | 22.7625 | 0.3604
GEN-2018-025 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 29.39 | 29.5305 | 0.1405
GEN-2018-025 | 02 NEBRASKA | 645455 | S3455 3 | 345 | 32.5495 | 32.6973 | 0.1478
GEN-2018-025 | 02 NEBRASKA | 645456 | S3456 3 | 345 | 35.0793 | 35.2431 | 0.1638
GEN-2018-025 | 02 NEBRASKA | 645458 | S3458 3 | 345 | 30.8316 | 30.8631 | 0.0315
GEN-2018-025 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 25.5764 | 25.7478 | 0.1714
GEN-2018-025 | 02 NEBRASKA | 645740 | S3740 3 | 345 | 23.4017 | 23.4586 | 0.0569
GEN-2018-025 | 02 NEBRASKA | 645761 | S3761 3 | 345 | 23.2714 | 23.3458 | 0.0744
GEN-2018-025 | 02 NEBRASKA | 646201 | S1201 5 | 161 | 32.3075 | 32.3659 | 0.0584
GEN-2018-025 | 02 NEBRASKA | 646206 | S1206 5 | 161 | 45.2507 | 45.3515 | 0.1008
GEN-2018-025 | 02 NEBRASKA | 646209 | S1209 5 | 161 | 47.4359 | 47.6366 | 0.2007
GEN-2018-025 | 02 NEBRASKA | 646211 | S1211 5 | 161 | 36.8321 | 36.913 | 0.0809
GEN-2018-025 | 02 NEBRASKA | 646214 | S1214 5 | 161 | 12.5396 | 12.5464 | 0.0068
GEN-2018-025 | 02 NEBRASKA | 646216 | S1216 5 | 161 | 30.9242 | 30.9791 | 0.0549
GEN-2018-025 | 02 NEBRASKA | 646217 | S1217 5 | 161 | 33.6476 | 33.7168 | 0.0692
GEN-2018-025 | 02 NEBRASKA | 646220 | S1220 5 | 161 | 29.1019 | 29.15 | 0.0481
GEN-2018-025 | 02 NEBRASKA | 646221 | S1221 5 | 161 | 35.6965 | 35.7884 | 0.0919
GEN-2018-025 | 02 NEBRASKA | 646226 | S1226 5 | 161 | 25.1206 | 25.2213 | 0.1007
GEN-2018-025 | 02 NEBRASKA | 646227 | S1227 5 | 161 | 32.9021 | 32.9763 | 0.0742
GEN-2018-025 | 02 NEBRASKA | 646229 | S1229 5 | 161 | 29.1546 | 29.2027 | 0.0481
GEN-2018-025 | 02 NEBRASKA | 646231 | S1231 5 | 161 | 43.4366 | 43.5827 | 0.1461
GEN-2018-025 | 02 NEBRASKA | 646232 | S1232 5 | 161 | 26.8651 | 26.903 | 0.0379
GEN-2018-025 | 02 NEBRASKA | 646233 | S1233 5 | 161 | 29.5441 | 29.6045 | 0.0604
GEN-2018-025 | 02 NEBRASKA | 646234 | S1234 5 | 161 | 27.0317 | 27.0858 | 0.0541
GEN-2018-025 | 02 NEBRASKA | 646235 | S1235 5 | 161 | 34.2004 | 34.2933 | 0.0929
GEN-2018-025 | 02 NEBRASKA | 646236 | S1236 5 | 161 | 24.631 | 24.6833 | 0.0523
GEN-2018-025 | 02 NEBRASKA | 646237 | S1237 5 | 161 | 22.0016 | 22.0487 | 0.0471
GEN-2018-025 | 02 NEBRASKA | 646244 | S1244 5 | 161 | 22.3457 | 22.3688 | 0.0231
GEN-2018-025 | 02 NEBRASKA | 646249 | S1249 5 | 161 | 25.2648 | 25.309 | 0.0442
GEN-2018-025 | 02 NEBRASKA | 646250 | S1250 5 | 161 | 35.7535 | 35.8513 | 0.0978
GEN-2018-025 | 02 NEBRASKA | 646251 | S1251 5 | 161 | 32.4519 | 32.6975 | 0.2456
GEN-2018-025 | 02 NEBRASKA | 646252 | S1252 5 | 161 | 29.9161 | 29.9993 | 0.0832
GEN-2018-025 | 02 NEBRASKA | 646253 | S1253 5 | 161 | 27.709 | 27.7712 | 0.0622
GEN-2018-025 | 02 NEBRASKA | 646254 | S1254 5 | 161 | 32.7283 | 32.7985 | 0.0702
GEN-2018-025 | 02 NEBRASKA | 646255 | S1255 5 | 161 | 49.0868 | 49.2423 | 0.1555
GEN-2018-025 | 02 NEBRASKA | 646256 | S1256 5 | 161 | 22.8808 | 22.9197 | 0.0389
GEN-2018-025 | 02 NEBRASKA | 646259 | S1259 5 | 161 | 38.6889 | 38.7776 | 0.0887
GEN-2018-025 | 02 NEBRASKA | 646260 | S1260 5 | 161 | 38.8147 | 38.8984 | 0.0837
GEN-2018-025 | 02 NEBRASKA | 646278 | S1278 5 | 161 | 27.6496 | 27.693 | 0.0434
GEN-2018-025 | 02 NEBRASKA | 646281 | S1281 5 | 161 | 35.3224 | 35.3927 | 0.0703
GEN-2018-025 | 02 NEBRASKA | 646286 | S1286 5 | 161 | 26.9148 | 26.9559 | 0.0411
GEN-2018-025 | 02 NEBRASKA | 646287 | S1287 5 | 161 | 21.9022 | 21.9275 | 0.0253
GEN-2018-025 | 02 NEBRASKA | 646291 | S1291 5 | 161 | 7.1563 | 7.1619 | 0.0056
GEN-2018-025 | 02 NEBRASKA | 646297 | S1297 5 | 161 | 19.1068 | 19.1612 | 0.0544
GEN-2018-025 | 02 NEBRASKA | 646298 | S1298 5 | 161 | 29.6217 | 29.8127 | 0.191
GEN-2018-025 | 02 NEBRASKA | 646305 | S1305 5 | 161 | 28.1722 | 28.3468 | 0.1746
GEN-2018-025 | 02 NEBRASKA | 646341 | S1341 5 | 161 | 27.4167 | 27.5841 | 0.1674
GEN-2018-025 | 02 NEBRASKA | 646345 | S1345 5 | 161 | 22.6949 | 22.7438 | 0.0489
GEN-2018-025 | 02 NEBRASKA | 646347 | S1347 5 | 161 | 33.0884 | 33.1838 | 0.0954
GEN-2018-025 | 02 NEBRASKA | 646361 | S1361 5 | 161 | 40.6653 | 40.7607 | 0.0954
GEN-2018-025 | 02 NEBRASKA | 646362 | S1362 5 | 161 | 34.3045 | 34.3667 | 0.0622
GEN-2018-025 | 02 NEBRASKA | 646363 | S1363 5 | 161 | 32.069 | 32.1184 | 0.0494
GEN-2018-025 | 02 NEBRASKA | 646366 | S1366 5 | 161 | 16.4523 | 16.4642 | 0.0119
GEN-2018-025 | 02 NEBRASKA | 646367 | S1367 5 | 161 | 21.8179 | 21.86 | 0.0421
GEN-2018-025 | 02 NEBRASKA | 647006 | S906 N 8 | 69 | 32.6914 | 32.7125 | 0.0211
GEN-2018-025 | 02 NEBRASKA | 647015 | S6815T1&T2 8 | 69 | 12.1122 | 12.115 | 0.0028
GEN-2018-025 | 02 NEBRASKA | 647016 | 6815TP38 | 69 | 17.6295 | 17.6352 | 0.0057
GEN-2018-025 | 02 NEBRASKA | 647017 | 6815TP98 | 69 | 12.7034 | 12.7065 | 0.0031
GEN-2018-025 | 02 NEBRASKA | 647104 | MUD LNG8 | 69 | 14.6941 | 14.7002 | 0.0061
GEN-2018-025 | 02 NEBRASKA | 647291 | S991 E 8 | 69 | 12.8187 | 12.8228 | 0.0041
GEN-2018-025 | 02 NEBRASKA | 647815 | S6815T3 8 | 69 | 11.4699 | 11.4722 | 0.0023
GEN-2018-025 | 02 NEBRASKA | 647874 | S6874 8 | 69 | 8.6424 | 8.6438 | 0.0014
GEN-2018-025 | 02 NEBRASKA | 647901 | S901 8 | 69 | 27.1266 | 27.1385 | 0.0119
GEN-2018-025 | 02 NEBRASKA | 647902 | S902 8 | 69 | 9.0663 | 9.0677 | 0.0014
GEN-2018-025 | 02 NEBRASKA | 647904 | S904 8 | 69 | 8.7602 | 8.7614 | 0.0012
GEN-2018-025 | 02 NEBRASKA | 647906 | S906 S 8 | 69 | 33.199 | 33.2183 | 0.0193
GEN-2018-025 | 02 NEBRASKA | 647909 | S909 8 | 69 | 27.1588 | 27.1795 | 0.0207
GEN-2018-025 | 02 NEBRASKA | 647911 | S911 8 | 69 | 21.3824 | 21.3938 | 0.0114
GEN-2018-025 | 02 NEBRASKA | 647916 | S916 8 | 69 | 23.8801 | 23.8944 | 0.0143
GEN-2018-025 | 02 NEBRASKA | 647917 | S917 8 | 69 | 26.0395 | 26.0571 | 0.0176
GEN-2018-025 | 02 NEBRASKA | 647918 | S918 8 | 69 | 23.0072 | 23.0215 | 0.0143
GEN-2018-025 | 02 NEBRASKA | 647919 | S919 8 | 69 | 21.6007 | 21.6138 | 0.0131
GEN-2018-025 | 02 NEBRASKA | 647921 | S921 8 | 69 | 26.5367 | 26.5554 | 0.0187
GEN-2018-025 | 02 NEBRASKA | 647924 | S924 8 | 69 | 24.6818 | 24.6926 | 0.0108
GEN-2018-025 | 02 NEBRASKA | 647928 | S928 8 | 69 | 17.3119 | 17.3185 | 0.0066
GEN-2018-025 | 02 NEBRASKA | 647930 | S930 8 | 69 | 21.6288 | 21.6418 | 0.013
GEN-2018-025 | 02 NEBRASKA | 647937 | S937 8 | 69 | 9.1647 | 9.1663 | 0.0016
GEN-2018-025 | 02 NEBRASKA | 647938 | S938 8 | 69 | 21.9219 | 21.9309 | 0.009
GEN-2018-025 | 02 NEBRASKA | 647939 | S939 8 | 69 | 20.1848 | 20.1962 | 0.0114
GEN-2018-025 | 02 NEBRASKA | 647940 | S940 8 | 69 | 20.9677 | 20.979 | 0.0113
GEN-2018-025 | 02 NEBRASKA | 647942 | S942 8 | 69 | 16.2414 | 16.2476 | 0.0062
GEN-2018-025 | 02 NEBRASKA | 647950 | S950 8 | 69 | 20.4181 | 20.4303 | 0.0122
GEN-2018-025 | 02 NEBRASKA | 647995 | S995 8 | 69 | 9.5253 | 9.527 | 0.0017
GEN-2018-025 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 17.8183 | 17.8272 | 0.0089
GEN-2018-025 | 02 NEBRASKA | 650185 | WAGENER 3 | 345 | 21.3845 | 21.4055 | 0.021
GEN-2018-025 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 21.2573 | 21.2733 | 0.016
GEN-2018-025 | 02 NEBRASKA | 650210 | NW70FAIRFD7 | 115 | 21.6031 | 21.607 | 0.0039
GEN-2018-025 | 02 NEBRASKA | 650214 | NW68HOLDRG7 | 115 | 25.8963 | 25.9018 | 0.0055
GEN-2018-025 | 02 NEBRASKA | 650216 | SW27&F 7 | 115 | 22.3688 | 22.373 | 0.0042
GEN-2018-025 | 02 NEBRASKA | 650262 | 57&GARLAND7 | 115 | 25.785 | 25.7911 | 0.0061
GEN-2018-025 | 02 NEBRASKA | 650267 | 84LEIGHTON7 | 115 | 29.9931 | 30.0016 | 0.0085
GEN-2018-025 | 02 NEBRASKA | 650270 | 70&CALVERT7 | 115 | 27.8638 | 27.8707 | 0.0069
GEN-2018-025 | 02 NEBRASKA | 650271 | 81&OCHENEY7 | 115 | 25.4837 | 25.4894 | 0.0057
GEN-2018-025 | 02 NEBRASKA | 650272 | 91&A 7 | 115 | 22.1719 | 22.1763 | 0.0044
GEN-2018-025 | 02 NEBRASKA | 650273 | 93&O 7 | 115 | 22.948 | 22.9528 | 0.0048
GEN-2018-025 | 02 NEBRASKA | 650274 | 91&HWY2 7 | 115 | 22.0428 | 22.0468 | 0.004
GEN-2018-025 | 02 NEBRASKA | 650279 | 120&ALVO 7 | 115 | 21.9978 | 22.0026 | 0.0048
GEN-2018-025 | 02 NEBRASKA | 650283 | WAVERLY 7 | 115 | 21.5078 | 21.5123 | 0.0045
GEN-2018-025 | 02 NEBRASKA | 650284 | 84FLETCHER7 | 115 | 25.4238 | 25.4297 | 0.0059
GEN-2018-025 | 02 NEBRASKA | 650285 | WAGENER 7 | 115 | 32.665 | 32.6765 | 0.0115
GEN-2018-025 | 02 NEBRASKA | 650290 | ROKEBY 7 | 115 | 26.0583 | 26.0634 | 0.0051
GEN-2018-025 | 02 NEBRASKA | 652552 | SIOUXCY2 | 230 | 20.8204 | 20.8245 | 0.0041
GEN-2018-025 | 02 NEBRASKA | 652564 | SIOUXCY3 | 345 | 15.9162 | 15.9208 | 0.0046
GEN-2018-025 | 02 NEBRASKA | 652565 | SIOUXCY4 | 230 | 20.8204 | 20.8245 | 0.0041
GEN-2018-025 | 02 NEBRASKA | 652864 | SIOUXCY-LNX3 | 345 | 15.7257 | 15.7301 | 0.0044
GEN-2018-025 | 02 NEBRASKA | 659900 | EAGLE___-NI4 | 230 | 7.5055 | 7.5058 | 0.0003
GEN-2018-025 | 02 NEBRASKA | 760746 | GEN-2017-115 | 345 | 9.0501 | 9.051 | 0.0009
GEN-2018-025 | 02 NEBRASKA | 760788 | GEN-2017-201 | 345 | 8.9626 | 8.9634 | 0.0008
GEN-2018-025 | 02 NEBRASKA | 760872 | GEN-2017-198 | 69 | 25.6862 | 25.6969 | 0.0107
GEN-2018-025 | 02 NEBRASKA | 761208 | GEN-2017-210 | 345 | 10.0204 | 10.0213 | 0.0009
GEN-2018-025 | 02 NEBRASKA | 761292 | GEN-2017-181 | 345 | 6.8746 | 6.8752 | 0.0006
GEN-2018-025 | 02 NEBRASKA | 761313 | GEN-2017-182 | 345 | 5.7466 | 5.747 | 0.0004
GEN-2018-025 | 02 NEBRASKA | 762069 | G17-105TAP | 161 | 8.7273 | 8.732 | 0.0047
GEN-2018-025 | 02 NEBRASKA | 762070 | GEN-2017-105 | 161 | 8.7273 | 8.732 | 0.0047
GEN-2018-025 | 02 NEBRASKA | 762504 | GEN-2018-012 | 345 | 5.7763 | 5.7766 | 0.0003
GEN-2018-025 | 02 NEBRASKA | 762509 | G18-012-DUMY | 345 | 7.0357 | 7.0362 | 0.0005
GEN-2018-025 | 02 NEBRASKA | 762603 | GEN-2018-025 | 345 | 21.4052 | 21.7655 | 0.3603
GEN-2018-025 | 02 NEBRASKA | 762691 | GEN-2018-033 | 345 | 22.3843 | 22.4363 | 0.052
GEN-2018-025 | 02 NEBRASKA | 762712 | G18-037-TAP | 161 | 36.1702 | 36.2479 | 0.0777
GEN-2018-025 | 02 NEBRASKA | 762713 | GEN-2018-037 | 161 | 33.9286 | 33.9968 | 0.0682
GEN-2018-025 | 02 NEBRASKA | 762779 | G18-043-TAP | 345 | 16.4136 | 16.5371 | 0.1235
GEN-2018-025 | 02 NEBRASKA | 762780 | GEN-2018-043 | 345 | 16.3714 | 16.4943 | 0.1229
GEN-2018-033 | 02 NEBRASKA | 45906 | J1590 SUB | 345 | 14.989 | 14.9897 | 0.0007
GEN-2018-033 | 02 NEBRASKA | 85831 | J583 | 345 | 6.1923 | 6.1929 | 0.0006
GEN-2018-033 | 02 NEBRASKA | 87486 | J748GENTIE | 345 | 13.9539 | 13.9544 | 0.0005
GEN-2018-033 | 02 NEBRASKA | 87487 | J748POI | 345 | 15.8373 | 15.838 | 0.0007
GEN-2018-033 | 02 NEBRASKA | 300039 | 7FAIRPT | 345 | 12.7326 | 12.7337 | 0.0011
GEN-2018-033 | 02 NEBRASKA | 300076 | 5FAIRPTB2 | 161 | 16.7598 | 16.7604 | 0.0006
GEN-2018-033 | 02 NEBRASKA | 301347 | 5WINSLOW | 161 | 8.9062 | 8.9064 | 0.0002
GEN-2018-033 | 02 NEBRASKA | 301559 | 5FAIRPTXF3 | 161 | 16.7774 | 16.778 | 0.0006
GEN-2018-033 | 02 NEBRASKA | 541147 | ST JOE_CAP5 | 161 | 18.7813 | 18.7819 | 0.0006
GEN-2018-033 | 02 NEBRASKA | 541197 | MULLNCR7 | 345 | 8.4825 | 8.4842 | 0.0017
GEN-2018-033 | 02 NEBRASKA | 541199 | ST JOE 7 | 345 | 20.3822 | 20.384 | 0.0018
GEN-2018-033 | 02 NEBRASKA | 541201 | SIBLEY 7 | 345 | 21.4401 | 21.4406 | 0.0005
GEN-2018-033 | 02 NEBRASKA | 541253 | ST JOE 5 | 161 | 21.0694 | 21.0702 | 0.0008
GEN-2018-033 | 02 NEBRASKA | 541257 | COOK 5 | 161 | 14.668 | 14.6684 | 0.0004
GEN-2018-033 | 02 NEBRASKA | 541258 | WOODBIN5 | 161 | 17.6724 | 17.673 | 0.0006
GEN-2018-033 | 02 NEBRASKA | 541394 | AVENUECTY 5 | 161 | 7.0499 | 7.05 | 0.0001
GEN-2018-033 | 02 NEBRASKA | 541400 | EASTOWN7 | 345 | 18.9196 | 18.9208 | 0.0012
GEN-2018-033 | 02 NEBRASKA | 541401 | EASTOWN5 | 161 | 18.0151 | 18.0156 | 0.0005
GEN-2018-033 | 02 NEBRASKA | 541411 | MC REAC1 | 345 | 8.0926 | 8.0942 | 0.0016
GEN-2018-033 | 02 NEBRASKA | 541412 | MC REAC2 | 345 | 8.0926 | 8.0942 | 0.0016
GEN-2018-033 | 02 NEBRASKA | 541413 | MC REAC3 | 345 | 8.0926 | 8.0942 | 0.0016
GEN-2018-033 | 02 NEBRASKA | 541414 | SIB REA1 | 345 | 19.1141 | 19.1145 | 0.0004
GEN-2018-033 | 02 NEBRASKA | 541500 | KETCHEM7 | 345 | 8.2088 | 8.2095 | 0.0007
GEN-2018-033 | 02 NEBRASKA | 541501 | OSBORN7 | 345 | 7.3088 | 7.3094 | 0.0006
GEN-2018-033 | 02 NEBRASKA | 541510 | HOLT 7 | 345 | 10.0821 | 10.0852 | 0.0031
GEN-2018-033 | 02 NEBRASKA | 541511 | ROCKCK7 | 345 | 8.0075 | 8.0092 | 0.0017
GEN-2018-033 | 02 NEBRASKA | 541517 | HOLT_REACT7 | 345 | 10.0243 | 10.0274 | 0.0031
GEN-2018-033 | 02 NEBRASKA | 541543 | OUTLAW | 345 | 6.7526 | 6.7537 | 0.0011
GEN-2018-033 | 02 NEBRASKA | 542980 | NASHUA 7 | 345 | 23.7103 | 23.711 | 0.0007
GEN-2018-033 | 02 NEBRASKA | 542982 | IATAN 7 | 345 | 31.2418 | 31.2426 | 0.0008
GEN-2018-033 | 02 NEBRASKA | 560746 | G13-002-TAP | 115 | 44.0439 | 44.0601 | 0.0162
GEN-2018-033 | 02 NEBRASKA | 583700 | GEN-2013-019 | 115 | 19.3011 | 19.3041 | 0.003
GEN-2018-033 | 02 NEBRASKA | 585241 | GEN-2015-088 | 345 | 12.2253 | 12.2286 | 0.0033
GEN-2018-033 | 02 NEBRASKA | 635000 | CBLUFFS3 | 345 | 32.264 | 32.3364 | 0.0724
GEN-2018-033 | 02 NEBRASKA | 635001 | CBLUFFS5 | 161 | 39.8902 | 39.94 | 0.0498
GEN-2018-033 | 02 NEBRASKA | 635002 | CBLUFFS8 | 69 | 25.2657 | 25.2738 | 0.0081
GEN-2018-033 | 02 NEBRASKA | 635011 | INDNCRK5 | 161 | 22.0938 | 22.1093 | 0.0155
GEN-2018-033 | 02 NEBRASKA | 635013 | PNYCRK 3 | 345 | 29.3587 | 29.4174 | 0.0587
GEN-2018-033 | 02 NEBRASKA | 635014 | OVRLND 3 | 345 | 27.5639 | 27.6146 | 0.0507
GEN-2018-033 | 02 NEBRASKA | 635015 | OVRLND 5 | 161 | 31.6116 | 31.6414 | 0.0298
GEN-2018-033 | 02 NEBRASKA | 635016 | STHLND 3 | 345 | 29.3231 | 29.3817 | 0.0586
GEN-2018-033 | 02 NEBRASKA | 635017 | ATCHSN 3 | 345 | 17.6809 | 17.6876 | 0.0067
GEN-2018-033 | 02 NEBRASKA | 635018 | WESTBORO 3 | 345 | 16.8575 | 16.8635 | 0.006
GEN-2018-033 | 02 NEBRASKA | 635030 | RIVRBND5 | 161 | 36.3386 | 36.3795 | 0.0409
GEN-2018-033 | 02 NEBRASKA | 635100 | RLHILLS3 | 345 | 13.5306 | 13.5343 | 0.0037
GEN-2018-033 | 02 NEBRASKA | 635200 | RAUN 3 | 345 | 28.3552 | 28.3601 | 0.0049
GEN-2018-033 | 02 NEBRASKA | 635201 | RAUN 5 | 161 | 28.3179 | 28.3204 | 0.0025
GEN-2018-033 | 02 NEBRASKA | 635252 | J412 POI 3 | 345 | 9.9039 | 9.9042 | 0.0003
GEN-2018-033 | 02 NEBRASKA | 635398 | REMSEN 3 | 345 | 15.2249 | 15.2256 | 0.0007
GEN-2018-033 | 02 NEBRASKA | 635570 | ORIENT 3 | 345 | 18.5298 | 18.5339 | 0.0041
GEN-2018-033 | 02 NEBRASKA | 635589 | ECLIPSE3 | 345 | 9.3942 | 9.3957 | 0.0015
GEN-2018-033 | 02 NEBRASKA | 635590 | FALLOW 3 | 345 | 11.4629 | 11.4652 | 0.0023
GEN-2018-033 | 02 NEBRASKA | 637084 | J476 SHENHLL | 345 | 16.7713 | 16.7773 | 0.006
GEN-2018-033 | 02 NEBRASKA | 640088 | BPS SUB7 | 115 | 16.9204 | 16.9212 | 0.0008
GEN-2018-033 | 02 NEBRASKA | 640111 | CLATONA7 | 115 | 11.1131 | 11.1136 | 0.0005
GEN-2018-033 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 10.6807 | 10.6823 | 0.0016
GEN-2018-033 | 02 NEBRASKA | 640127 | COLMB.E7 | 115 | 23.5848 | 23.5866 | 0.0018
GEN-2018-033 | 02 NEBRASKA | 640139 | COOPER 3 | 345 | 27.6773 | 27.697 | 0.0197
GEN-2018-033 | 02 NEBRASKA | 640140 | COOPER 5 | 161 | 18.1806 | 18.1845 | 0.0039
GEN-2018-033 | 02 NEBRASKA | 640141 | COOPER_ESST8 | 69 | 4.6838 | 4.6839 | 0.0001
GEN-2018-033 | 02 NEBRASKA | 640143 | COOPER_602 8 | 69 | 2.0096 | 2.0096 | 0
GEN-2018-033 | 02 NEBRASKA | 640153 | CRETE__7 | 115 | 8.4622 | 8.4626 | 0.0004
GEN-2018-033 | 02 NEBRASKA | 640171 | FIRTH 7 | 115 | 7.0265 | 7.027 | 0.0005
GEN-2018-033 | 02 NEBRASKA | 640226 | HOSKINS3 | 345 | 13.7789 | 13.78 | 0.0011
GEN-2018-033 | 02 NEBRASKA | 640234 | HUMBOLT5 | 161 | 7.9754 | 7.9759 | 0.0005
GEN-2018-033 | 02 NEBRASKA | 640271 | MCCOOL 3 | 345 | 11.4588 | 11.4607 | 0.0019
GEN-2018-033 | 02 NEBRASKA | 640272 | MCCOOL 7 | 115 | 14.7657 | 14.7666 | 0.0009
GEN-2018-033 | 02 NEBRASKA | 640273 | MCCOOL 8 | 69 | 5.7349 | 5.735 | 0.0001
GEN-2018-033 | 02 NEBRASKA | 640277 | MOORE 3 | 345 | 23.8884 | 23.9081 | 0.0197
GEN-2018-033 | 02 NEBRASKA | 640278 | SHELDON7 | 115 | 45.3961 | 45.4126 | 0.0165
GEN-2018-033 | 02 NEBRASKA | 640312 | PAULINE3 | 345 | 8.3737 | 8.3742 | 0.0005
GEN-2018-033 | 02 NEBRASKA | 640316 | PAWNEEL7 | 115 | 11.7868 | 11.7883 | 0.0015
GEN-2018-033 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 10.9554 | 10.9568 | 0.0014
GEN-2018-033 | 02 NEBRASKA | 640446 | COOPER 8 | 69 | 4.7815 | 4.7816 | 0.0001
GEN-2018-033 | 02 NEBRASKA | 640525 | TOBIAS 3 | 345 | 12.2253 | 12.2286 | 0.0033
GEN-2018-033 | 02 NEBRASKA | 640588 | TURTLE.CRK 3 | 345 | 12.14 | 12.1407 | 0.0007
GEN-2018-033 | 02 NEBRASKA | 640589 | SHOLES.W 3 | 345 | 9.8868 | 9.8873 | 0.0005
GEN-2018-033 | 02 NEBRASKA | 640590 | MONOLITH 3 | 345 | 23.3713 | 23.3899 | 0.0186
GEN-2018-033 | 02 NEBRASKA | 640591 | MONOLITH 7 | 115 | 44.0439 | 44.0601 | 0.0162
GEN-2018-033 | 02 NEBRASKA | 640598 | HAYSTACK.WD3 | 345 | 9.2763 | 9.2767 | 0.0004
GEN-2018-033 | 02 NEBRASKA | 643271 | PLUMBCR.W 3 | 345 | 11.8913 | 11.892 | 0.0007
GEN-2018-033 | 02 NEBRASKA | 645100 | FC1A 5 | 161 | 30.0214 | 30.0624 | 0.041
GEN-2018-033 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 22.7075 | 22.7625 | 0.055
GEN-2018-033 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 29.3374 | 29.5305 | 0.1931
GEN-2018-033 | 02 NEBRASKA | 645455 | S3455 3 | 345 | 32.4783 | 32.6973 | 0.219
GEN-2018-033 | 02 NEBRASKA | 645456 | S3456 3 | 345 | 35.0842 | 35.2431 | 0.1589
GEN-2018-033 | 02 NEBRASKA | 645458 | S3458 3 | 345 | 30.7762 | 30.8631 | 0.0869
GEN-2018-033 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 25.6717 | 25.7478 | 0.0761
GEN-2018-033 | 02 NEBRASKA | 645740 | S3740 3 | 345 | 23.0881 | 23.4586 | 0.3705
GEN-2018-033 | 02 NEBRASKA | 645761 | S3761 3 | 345 | 23.2385 | 23.3458 | 0.1073
GEN-2018-033 | 02 NEBRASKA | 646201 | S1201 5 | 161 | 32.3277 | 32.3659 | 0.0382
GEN-2018-033 | 02 NEBRASKA | 646206 | S1206 5 | 161 | 45.2676 | 45.3515 | 0.0839
GEN-2018-033 | 02 NEBRASKA | 646209 | S1209 5 | 161 | 47.5269 | 47.6366 | 0.1097
GEN-2018-033 | 02 NEBRASKA | 646214 | S1214 5 | 161 | 12.5386 | 12.5464 | 0.0078
GEN-2018-033 | 02 NEBRASKA | 646216 | S1216 5 | 161 | 30.9383 | 30.9791 | 0.0408
GEN-2018-033 | 02 NEBRASKA | 646217 | S1217 5 | 161 | 33.6676 | 33.7168 | 0.0492
GEN-2018-033 | 02 NEBRASKA | 646220 | S1220 5 | 161 | 29.1195 | 29.15 | 0.0305
GEN-2018-033 | 02 NEBRASKA | 646221 | S1221 5 | 161 | 35.7144 | 35.7884 | 0.074
GEN-2018-033 | 02 NEBRASKA | 646226 | S1226 5 | 161 | 25.195 | 25.2213 | 0.0263
GEN-2018-033 | 02 NEBRASKA | 646227 | S1227 5 | 161 | 32.9249 | 32.9763 | 0.0514
GEN-2018-033 | 02 NEBRASKA | 646229 | S1229 5 | 161 | 29.1707 | 29.2027 | 0.032
GEN-2018-033 | 02 NEBRASKA | 646231 | S1231 5 | 161 | 43.4841 | 43.5827 | 0.0986
GEN-2018-033 | 02 NEBRASKA | 646232 | S1232 5 | 161 | 26.8679 | 26.903 | 0.0351
GEN-2018-033 | 02 NEBRASKA | 646233 | S1233 5 | 161 | 29.5462 | 29.6045 | 0.0583
GEN-2018-033 | 02 NEBRASKA | 646234 | S1234 5 | 161 | 27.0408 | 27.0858 | 0.045
GEN-2018-033 | 02 NEBRASKA | 646235 | S1235 5 | 161 | 34.2273 | 34.2933 | 0.066
GEN-2018-033 | 02 NEBRASKA | 646244 | S1244 5 | 161 | 22.3494 | 22.3688 | 0.0194
GEN-2018-033 | 02 NEBRASKA | 646249 | S1249 5 | 161 | 25.2646 | 25.309 | 0.0444
GEN-2018-033 | 02 NEBRASKA | 646250 | S1250 5 | 161 | 35.8016 | 35.8513 | 0.0497
GEN-2018-033 | 02 NEBRASKA | 646251 | S1251 5 | 161 | 32.649 | 32.6975 | 0.0485
GEN-2018-033 | 02 NEBRASKA | 646253 | S1253 5 | 161 | 27.7268 | 27.7712 | 0.0444
GEN-2018-033 | 02 NEBRASKA | 646254 | S1254 5 | 161 | 32.7197 | 32.7985 | 0.0788
GEN-2018-033 | 02 NEBRASKA | 646255 | S1255 5 | 161 | 49.0685 | 49.2423 | 0.1738
GEN-2018-033 | 02 NEBRASKA | 646256 | S1256 5 | 161 | 22.886 | 22.9197 | 0.0337
GEN-2018-033 | 02 NEBRASKA | 646259 | S1259 5 | 161 | 38.6794 | 38.7776 | 0.0982
GEN-2018-033 | 02 NEBRASKA | 646260 | S1260 5 | 161 | 38.8016 | 38.8984 | 0.0968
GEN-2018-033 | 02 NEBRASKA | 646263 | S1263 5 | 161 | 8.0949 | 8.0958 | 0.0009
GEN-2018-033 | 02 NEBRASKA | 646278 | S1278 5 | 161 | 27.6477 | 27.693 | 0.0453
GEN-2018-033 | 02 NEBRASKA | 646280 | S1280 5 | 161 | 10.2882 | 10.2894 | 0.0012
GEN-2018-033 | 02 NEBRASKA | 646281 | S1281 5 | 161 | 35.3117 | 35.3927 | 0.081
GEN-2018-033 | 02 NEBRASKA | 646286 | S1286 5 | 161 | 26.9298 | 26.9559 | 0.0261
GEN-2018-033 | 02 NEBRASKA | 646287 | S1287 5 | 161 | 21.8984 | 21.9275 | 0.0291
GEN-2018-033 | 02 NEBRASKA | 646297 | S1297 5 | 161 | 19.1457 | 19.1612 | 0.0155
GEN-2018-033 | 02 NEBRASKA | 646298 | S1298 5 | 161 | 29.7731 | 29.8127 | 0.0396
GEN-2018-033 | 02 NEBRASKA | 646305 | S1305 5 | 161 | 28.3109 | 28.3468 | 0.0359
GEN-2018-033 | 02 NEBRASKA | 646341 | S1341 5 | 161 | 27.55 | 27.5841 | 0.0341
GEN-2018-033 | 02 NEBRASKA | 646347 | S1347 5 | 161 | 33.1328 | 33.1838 | 0.051
GEN-2018-033 | 02 NEBRASKA | 646361 | S1361 5 | 161 | 40.6478 | 40.7607 | 0.1129
GEN-2018-033 | 02 NEBRASKA | 646362 | S1362 5 | 161 | 34.2948 | 34.3667 | 0.0719
GEN-2018-033 | 02 NEBRASKA | 646363 | S1363 5 | 161 | 32.0613 | 32.1184 | 0.0571
GEN-2018-033 | 02 NEBRASKA | 646366 | S1366 5 | 161 | 16.4542 | 16.4642 | 0.01
GEN-2018-033 | 02 NEBRASKA | 647006 | S906 N 8 | 69 | 32.696 | 32.7125 | 0.0165
GEN-2018-033 | 02 NEBRASKA | 647015 | S6815T1&T2 8 | 69 | 12.1128 | 12.115 | 0.0022
GEN-2018-033 | 02 NEBRASKA | 647016 | 6815TP38 | 69 | 17.6306 | 17.6352 | 0.0046
GEN-2018-033 | 02 NEBRASKA | 647017 | 6815TP98 | 69 | 12.704 | 12.7065 | 0.0025
GEN-2018-033 | 02 NEBRASKA | 647815 | S6815T3 8 | 69 | 11.4703 | 11.4722 | 0.0019
GEN-2018-033 | 02 NEBRASKA | 647874 | S6874 8 | 69 | 8.6427 | 8.6438 | 0.0011
GEN-2018-033 | 02 NEBRASKA | 647901 | S901 8 | 69 | 27.1304 | 27.1385 | 0.0081
GEN-2018-033 | 02 NEBRASKA | 647904 | S904 8 | 69 | 8.7603 | 8.7614 | 0.0011
GEN-2018-033 | 02 NEBRASKA | 647906 | S906 S 8 | 69 | 33.2029 | 33.2183 | 0.0154
GEN-2018-033 | 02 NEBRASKA | 647909 | S909 8 | 69 | 27.1664 | 27.1795 | 0.0131
GEN-2018-033 | 02 NEBRASKA | 647916 | S916 8 | 69 | 23.8842 | 23.8944 | 0.0102
GEN-2018-033 | 02 NEBRASKA | 647921 | S921 8 | 69 | 26.5418 | 26.5554 | 0.0136
GEN-2018-033 | 02 NEBRASKA | 647924 | S924 8 | 69 | 24.6843 | 24.6926 | 0.0083
GEN-2018-033 | 02 NEBRASKA | 647928 | S928 8 | 69 | 17.3135 | 17.3185 | 0.005
GEN-2018-033 | 02 NEBRASKA | 647938 | S938 8 | 69 | 21.9238 | 21.9309 | 0.0071
GEN-2018-033 | 02 NEBRASKA | 647940 | S940 8 | 69 | 20.9709 | 20.979 | 0.0081
GEN-2018-033 | 02 NEBRASKA | 647942 | S942 8 | 69 | 16.243 | 16.2476 | 0.0046
GEN-2018-033 | 02 NEBRASKA | 647960 | S960 8 | 69 | 7.4548 | 7.456 | 0.0012
GEN-2018-033 | 02 NEBRASKA | 647995 | S995 8 | 69 | 9.5257 | 9.527 | 0.0013
GEN-2018-033 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 17.8138 | 17.8272 | 0.0134
GEN-2018-033 | 02 NEBRASKA | 650185 | WAGENER 3 | 345 | 21.3729 | 21.4055 | 0.0326
GEN-2018-033 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 21.2462 | 21.2733 | 0.0271
GEN-2018-033 | 02 NEBRASKA | 650210 | NW70FAIRFD7 | 115 | 21.6013 | 21.607 | 0.0057
GEN-2018-033 | 02 NEBRASKA | 650214 | NW68HOLDRG7 | 115 | 25.8937 | 25.9018 | 0.0081
GEN-2018-033 | 02 NEBRASKA | 650216 | SW27&F 7 | 115 | 22.3668 | 22.373 | 0.0062
GEN-2018-033 | 02 NEBRASKA | 650242 | FOLSM&PHIL7 | 115 | 28.2033 | 28.2122 | 0.0089
GEN-2018-033 | 02 NEBRASKA | 650246 | SW7&BENNET7 | 115 | 23.6699 | 23.6759 | 0.006
GEN-2018-033 | 02 NEBRASKA | 650262 | 57&GARLAND7 | 115 | 25.7821 | 25.7911 | 0.009
GEN-2018-033 | 02 NEBRASKA | 650267 | 84LEIGHTON7 | 115 | 29.9891 | 30.0016 | 0.0125
GEN-2018-033 | 02 NEBRASKA | 650270 | 70&CALVERT7 | 115 | 27.8605 | 27.8707 | 0.0102
GEN-2018-033 | 02 NEBRASKA | 650271 | 81&OCHENEY7 | 115 | 25.4809 | 25.4894 | 0.0085
GEN-2018-033 | 02 NEBRASKA | 650272 | 91&A 7 | 115 | 22.1697 | 22.1763 | 0.0066
GEN-2018-033 | 02 NEBRASKA | 650273 | 93&O 7 | 115 | 22.9456 | 22.9528 | 0.0072
GEN-2018-033 | 02 NEBRASKA | 650274 | 91&HWY2 7 | 115 | 22.0408 | 22.0468 | 0.006
GEN-2018-033 | 02 NEBRASKA | 650279 | 120&ALVO 7 | 115 | 21.9955 | 22.0026 | 0.0071
GEN-2018-033 | 02 NEBRASKA | 650283 | WAVERLY 7 | 115 | 21.5058 | 21.5123 | 0.0065
GEN-2018-033 | 02 NEBRASKA | 650284 | 84FLETCHER7 | 115 | 25.4211 | 25.4297 | 0.0086
GEN-2018-033 | 02 NEBRASKA | 650285 | WAGENER 7 | 115 | 32.6592 | 32.6765 | 0.0173
GEN-2018-033 | 02 NEBRASKA | 650290 | ROKEBY 7 | 115 | 26.0558 | 26.0634 | 0.0076
GEN-2018-033 | 02 NEBRASKA | 652564 | SIOUXCY3 | 345 | 15.9198 | 15.9208 | 0.001
GEN-2018-033 | 02 NEBRASKA | 653571 | GR ISLD3 | 345 | 13.0464 | 13.0474 | 0.001
GEN-2018-033 | 02 NEBRASKA | 760746 | GEN-2017-115 | 345 | 9.0485 | 9.051 | 0.0025
GEN-2018-033 | 02 NEBRASKA | 760788 | GEN-2017-201 | 345 | 8.963 | 8.9634 | 0.0004
GEN-2018-033 | 02 NEBRASKA | 760872 | GEN-2017-198 | 69 | 25.6896 | 25.6969 | 0.0073
GEN-2018-033 | 02 NEBRASKA | 761208 | GEN-2017-210 | 345 | 10.0199 | 10.0213 | 0.0014
GEN-2018-033 | 02 NEBRASKA | 761292 | GEN-2017-181 | 345 | 6.8742 | 6.8752 | 0.001
GEN-2018-033 | 02 NEBRASKA | 761313 | GEN-2017-182 | 345 | 5.7463 | 5.747 | 0.0007
GEN-2018-033 | 02 NEBRASKA | 761376 | GEN-2017-183 | 345 | 7.6579 | 7.6581 | 0.0002
GEN-2018-033 | 02 NEBRASKA | 761383 | G17-183-TAP | 345 | 16.8635 | 16.8642 | 0.0007
GEN-2018-033 | 02 NEBRASKA | 762603 | GEN-2018-025 | 345 | 21.7152 | 21.7655 | 0.0503
GEN-2018-033 | 02 NEBRASKA | 762691 | GEN-2018-033 | 345 | 22.0656 | 22.4363 | 0.3707
GEN-2018-033 | 02 NEBRASKA | 762779 | G18-043-TAP | 345 | 16.5181 | 16.5371 | 0.019
GEN-2018-033 | 02 NEBRASKA | 762780 | GEN-2018-043 | 345 | 16.4754 | 16.4943 | 0.0189
GEN-2018-037 | 02 NEBRASKA | 635000 | CBLUFFS3 | 345 | 32.2897 | 32.3364 | 0.0467
GEN-2018-037 | 02 NEBRASKA | 635001 | CBLUFFS5 | 161 | 39.8728 | 39.94 | 0.0672
GEN-2018-037 | 02 NEBRASKA | 635002 | CBLUFFS8 | 69 | 25.2576 | 25.2738 | 0.0162
GEN-2018-037 | 02 NEBRASKA | 635003 | SUB701 5 | 161 | 21.585 | 21.6517 | 0.0667
GEN-2018-037 | 02 NEBRASKA | 635004 | SUB701 8 | 69 | 22.3869 | 22.4078 | 0.0209
GEN-2018-037 | 02 NEBRASKA | 635005 | SUB702 5 | 161 | 20.9347 | 20.987 | 0.0523
GEN-2018-037 | 02 NEBRASKA | 635006 | SUB703 8 | 69 | 10.7509 | 10.7548 | 0.0039
GEN-2018-037 | 02 NEBRASKA | 635007 | SUB704 8 | 69 | 13.1227 | 13.129 | 0.0063
GEN-2018-037 | 02 NEBRASKA | 635008 | SUB705 8 | 69 | 12.4909 | 12.4963 | 0.0054
GEN-2018-037 | 02 NEBRASKA | 635009 | SUB706 8 | 69 | 10.8401 | 10.8439 | 0.0038
GEN-2018-037 | 02 NEBRASKA | 635010 | MANAWA 5 | 161 | 21.7665 | 21.8104 | 0.0439
GEN-2018-037 | 02 NEBRASKA | 635011 | INDNCRK5 | 161 | 22.066 | 22.1093 | 0.0433
GEN-2018-037 | 02 NEBRASKA | 635015 | OVRLND 5 | 161 | 31.6057 | 31.6414 | 0.0357
GEN-2018-037 | 02 NEBRASKA | 635030 | RIVRBND5 | 161 | 36.3248 | 36.3795 | 0.0547
GEN-2018-037 | 02 NEBRASKA | 635075 | GLNWOOD8 | 69 | 6.3746 | 6.3753 | 0.0007
GEN-2018-037 | 02 NEBRASKA | 635076 | MALVERN8 | 69 | 7.2834 | 7.2839 | 0.0005
GEN-2018-037 | 02 NEBRASKA | 635080 | HONEYCK8 | 69 | 5.8508 | 5.8518 | 0.001
GEN-2018-037 | 02 NEBRASKA | 635081 | MOVALLY8 | 69 | 4.4823 | 4.4827 | 0.0004
GEN-2018-037 | 02 NEBRASKA | 635082 | LOGAN 8 | 69 | 4.6297 | 4.63 | 0.0003
GEN-2018-037 | 02 NEBRASKA | 645100 | FC1A 5 | 161 | 30.0237 | 30.0624 | 0.0387
GEN-2018-037 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 22.7289 | 22.7625 | 0.0336
GEN-2018-037 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 29.4885 | 29.5305 | 0.042
GEN-2018-037 | 02 NEBRASKA | 645455 | S3455 3 | 345 | 32.639 | 32.6973 | 0.0583
GEN-2018-037 | 02 NEBRASKA | 645456 | S3456 3 | 345 | 35.1706 | 35.2431 | 0.0725
GEN-2018-037 | 02 NEBRASKA | 645458 | S3458 3 | 345 | 30.8509 | 30.8631 | 0.0122
GEN-2018-037 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 25.6929 | 25.7478 | 0.0549
GEN-2018-037 | 02 NEBRASKA | 646201 | S1201 5 | 161 | 32.1869 | 32.3659 | 0.179
GEN-2018-037 | 02 NEBRASKA | 646206 | S1206 5 | 161 | 45.2337 | 45.3515 | 0.1178
GEN-2018-037 | 02 NEBRASKA | 646209 | S1209 5 | 161 | 47.4784 | 47.6366 | 0.1582
GEN-2018-037 | 02 NEBRASKA | 646210 | S1210 5 | 161 | 28.2903 | 28.3846 | 0.0943
GEN-2018-037 | 02 NEBRASKA | 646211 | S1211 5 | 161 | 36.5257 | 36.913 | 0.3873
GEN-2018-037 | 02 NEBRASKA | 646216 | S1216 5 | 161 | 30.9059 | 30.9791 | 0.0732
GEN-2018-037 | 02 NEBRASKA | 646217 | S1217 5 | 161 | 33.6203 | 33.7168 | 0.0965
GEN-2018-037 | 02 NEBRASKA | 646220 | S1220 5 | 161 | 28.981 | 29.15 | 0.169
GEN-2018-037 | 02 NEBRASKA | 646221 | S1221 5 | 161 | 35.7218 | 35.7884 | 0.0666
GEN-2018-037 | 02 NEBRASKA | 646222 | S1222 5 | 161 | 27.7991 | 27.9033 | 0.1042
GEN-2018-037 | 02 NEBRASKA | 646226 | S1226 5 | 161 | 25.196 | 25.2213 | 0.0253
GEN-2018-037 | 02 NEBRASKA | 646227 | S1227 5 | 161 | 32.8963 | 32.9763 | 0.08
GEN-2018-037 | 02 NEBRASKA | 646229 | S1229 5 | 161 | 29.0723 | 29.2027 | 0.1304
GEN-2018-037 | 02 NEBRASKA | 646231 | S1231 5 | 161 | 43.465 | 43.5827 | 0.1177
GEN-2018-037 | 02 NEBRASKA | 646232 | S1232 5 | 161 | 26.8677 | 26.903 | 0.0353
GEN-2018-037 | 02 NEBRASKA | 646234 | S1234 5 | 161 | 27.0533 | 27.0858 | 0.0325
GEN-2018-037 | 02 NEBRASKA | 646235 | S1235 5 | 161 | 34.2347 | 34.2933 | 0.0586
GEN-2018-037 | 02 NEBRASKA | 646236 | S1236 5 | 161 | 24.6519 | 24.6833 | 0.0314
GEN-2018-037 | 02 NEBRASKA | 646244 | S1244 5 | 161 | 22.3418 | 22.3688 | 0.027
GEN-2018-037 | 02 NEBRASKA | 646250 | S1250 5 | 161 | 35.6143 | 35.8513 | 0.237
GEN-2018-037 | 02 NEBRASKA | 646251 | S1251 5 | 161 | 32.6518 | 32.6975 | 0.0457
GEN-2018-037 | 02 NEBRASKA | 646252 | S1252 5 | 161 | 29.9515 | 29.9993 | 0.0478
GEN-2018-037 | 02 NEBRASKA | 646253 | S1253 5 | 161 | 27.7365 | 27.7712 | 0.0347
GEN-2018-037 | 02 NEBRASKA | 646255 | S1255 5 | 161 | 49.1585 | 49.2423 | 0.0838
GEN-2018-037 | 02 NEBRASKA | 646286 | S1286 5 | 161 | 26.8129 | 26.9559 | 0.143
GEN-2018-037 | 02 NEBRASKA | 646297 | S1297 5 | 161 | 19.1255 | 19.1612 | 0.0357
GEN-2018-037 | 02 NEBRASKA | 646298 | S1298 5 | 161 | 29.7752 | 29.8127 | 0.0375
GEN-2018-037 | 02 NEBRASKA | 646299 | S1299 5 | 161 | 28.2036 | 28.4231 | 0.2195
GEN-2018-037 | 02 NEBRASKA | 646305 | S1305 5 | 161 | 28.3129 | 28.3468 | 0.0339
GEN-2018-037 | 02 NEBRASKA | 646341 | S1341 5 | 161 | 27.5518 | 27.5841 | 0.0323
GEN-2018-037 | 02 NEBRASKA | 646345 | S1345 5 | 161 | 22.7177 | 22.7438 | 0.0261
GEN-2018-037 | 02 NEBRASKA | 646347 | S1347 5 | 161 | 33.1194 | 33.1838 | 0.0644
GEN-2018-037 | 02 NEBRASKA | 647006 | S906 N 8 | 69 | 32.6874 | 32.7125 | 0.0251
GEN-2018-037 | 02 NEBRASKA | 647104 | MUD LNG8 | 69 | 14.6921 | 14.7002 | 0.0081
GEN-2018-037 | 02 NEBRASKA | 647105 | JCT205 8 | 69 | 22.7426 | 22.7641 | 0.0215
GEN-2018-037 | 02 NEBRASKA | 647901 | S901 8 | 69 | 27.1096 | 27.1385 | 0.0289
GEN-2018-037 | 02 NEBRASKA | 647902 | S902 8 | 69 | 9.0667 | 9.0677 | 0.001
GEN-2018-037 | 02 NEBRASKA | 647906 | S906 S 8 | 69 | 33.1917 | 33.2183 | 0.0266
GEN-2018-037 | 02 NEBRASKA | 647907 | S907 8 | 69 | 18.0511 | 18.0751 | 0.024
GEN-2018-037 | 02 NEBRASKA | 647908 | S908 8 | 69 | 18.662 | 18.6807 | 0.0187
GEN-2018-037 | 02 NEBRASKA | 647909 | S909 8 | 69 | 27.1553 | 27.1795 | 0.0242
GEN-2018-037 | 02 NEBRASKA | 647910 | S910 8 | 69 | 26.1072 | 26.1392 | 0.032
GEN-2018-037 | 02 NEBRASKA | 647911 | S911 8 | 69 | 21.3577 | 21.3938 | 0.0361
GEN-2018-037 | 02 NEBRASKA | 647912 | S912 8 | 69 | 22.8973 | 22.9152 | 0.0179
GEN-2018-037 | 02 NEBRASKA | 647913 | S913 8 | 69 | 16.2514 | 16.2684 | 0.017
GEN-2018-037 | 02 NEBRASKA | 647917 | S917 8 | 69 | 26.0347 | 26.0571 | 0.0224
GEN-2018-037 | 02 NEBRASKA | 647918 | S918 8 | 69 | 23.0025 | 23.0215 | 0.019
GEN-2018-037 | 02 NEBRASKA | 647919 | S919 8 | 69 | 21.5855 | 21.6138 | 0.0283
GEN-2018-037 | 02 NEBRASKA | 647921 | S921 8 | 69 | 26.5361 | 26.5554 | 0.0193
GEN-2018-037 | 02 NEBRASKA | 647923 | S923 8 | 69 | 19.2714 | 19.2852 | 0.0138
GEN-2018-037 | 02 NEBRASKA | 647930 | S930 8 | 69 | 21.6217 | 21.6418 | 0.0201
GEN-2018-037 | 02 NEBRASKA | 647937 | S937 8 | 69 | 9.165 | 9.1663 | 0.0013
GEN-2018-037 | 02 NEBRASKA | 647939 | S939 8 | 69 | 20.1809 | 20.1962 | 0.0153
GEN-2018-037 | 02 NEBRASKA | 647940 | S940 8 | 69 | 20.9663 | 20.979 | 0.0127
GEN-2018-037 | 02 NEBRASKA | 647942 | S942 8 | 69 | 16.2408 | 16.2476 | 0.0068
GEN-2018-037 | 02 NEBRASKA | 647950 | S950 8 | 69 | 20.4033 | 20.4303 | 0.027
GEN-2018-037 | 02 NEBRASKA | 760872 | GEN-2017-198 | 69 | 25.6709 | 25.6969 | 0.026
GEN-2018-037 | 02 NEBRASKA | 762603 | GEN-2018-025 | 345 | 21.7348 | 21.7655 | 0.0307
GEN-2018-037 | 02 NEBRASKA | 762712 | G18-037-TAP | 161 | 35.8507 | 36.2479 | 0.3972
GEN-2018-037 | 02 NEBRASKA | 762713 | GEN-2018-037 | 161 | 33.5994 | 33.9968 | 0.3974
GEN-2018-037 | 02 NEBRASKA | 762779 | G18-043-TAP | 345 | 16.5255 | 16.5371 | 0.0116
GEN-2018-037 | 02 NEBRASKA | 762780 | GEN-2018-043 | 345 | 16.4828 | 16.4943 | 0.0115
GEN-2018-043 | 02 NEBRASKA | 45816 | J1581 SUB | 345 | 12.32 | 12.3215 | 0.0015
GEN-2018-043 | 02 NEBRASKA | 45906 | J1590 SUB | 345 | 14.9658 | 14.9897 | 0.0239
GEN-2018-043 | 02 NEBRASKA | 87486 | J748GENTIE | 345 | 13.9352 | 13.9544 | 0.0192
GEN-2018-043 | 02 NEBRASKA | 87487 | J748POI | 345 | 15.813 | 15.838 | 0.025
GEN-2018-043 | 02 NEBRASKA | 541510 | HOLT 7 | 345 | 10.0831 | 10.0852 | 0.0021
GEN-2018-043 | 02 NEBRASKA | 541511 | ROCKCK7 | 345 | 8.008 | 8.0092 | 0.0012
GEN-2018-043 | 02 NEBRASKA | 541517 | HOLT_REACT7 | 345 | 10.0253 | 10.0274 | 0.0021
GEN-2018-043 | 02 NEBRASKA | 541543 | OUTLAW | 345 | 6.7529 | 6.7537 | 0.0008
GEN-2018-043 | 02 NEBRASKA | 601006 | SPLT RK3 | 345 | 14.5289 | 14.5324 | 0.0035
GEN-2018-043 | 02 NEBRASKA | 601034 | NOBLES 3 | 345 | 12.32 | 12.3215 | 0.0015
GEN-2018-043 | 02 NEBRASKA | 603016 | SPLT RK7 | 115 | 39.0928 | 39.0988 | 0.006
GEN-2018-043 | 02 NEBRASKA | 603149 | ANSON4 | 115 | 37.0191 | 37.0245 | 0.0054
GEN-2018-043 | 02 NEBRASKA | 603200 | ANSON 7 | 115 | 35.5625 | 35.5672 | 0.0047
GEN-2018-043 | 02 NEBRASKA | 603228 | SPLITRK CAP7 | 115 | 38.4994 | 38.5052 | 0.0058
GEN-2018-043 | 02 NEBRASKA | 603264 | PROSE WIND7 | 115 | 5.0948 | 5.0948 | 0
GEN-2018-043 | 02 NEBRASKA | 603265 | PROSE CAP7 | 115 | 37.0791 | 37.0845 | 0.0054
GEN-2018-043 | 02 NEBRASKA | 635000 | CBLUFFS3 | 345 | 32.1933 | 32.3364 | 0.1431
GEN-2018-043 | 02 NEBRASKA | 635001 | CBLUFFS5 | 161 | 39.8308 | 39.94 | 0.1092
GEN-2018-043 | 02 NEBRASKA | 635013 | PNYCRK 3 | 345 | 29.3015 | 29.4174 | 0.1159
GEN-2018-043 | 02 NEBRASKA | 635014 | OVRLND 3 | 345 | 27.5137 | 27.6146 | 0.1009
GEN-2018-043 | 02 NEBRASKA | 635016 | STHLND 3 | 345 | 29.266 | 29.3817 | 0.1157
GEN-2018-043 | 02 NEBRASKA | 635200 | RAUN 3 | 345 | 28.1899 | 28.3601 | 0.1702
GEN-2018-043 | 02 NEBRASKA | 635201 | RAUN 5 | 161 | 28.2549 | 28.3204 | 0.0655
GEN-2018-043 | 02 NEBRASKA | 635202 | NEAL S 5 | 161 | 23.3235 | 23.366 | 0.0425
GEN-2018-043 | 02 NEBRASKA | 635203 | NEAL N 5 | 161 | 26.7139 | 26.7721 | 0.0582
GEN-2018-043 | 02 NEBRASKA | 635204 | NEAL N 8 | 69 | 10.2445 | 10.248 | 0.0035
GEN-2018-043 | 02 NEBRASKA | 635206 | IDA CO 3 | 345 | 9.4787 | 9.4868 | 0.0081
GEN-2018-043 | 02 NEBRASKA | 635219 | GARD AVE 3 | 345 | 9.0621 | 9.0686 | 0.0065
GEN-2018-043 | 02 NEBRASKA | 635220 | INTCHG 5 | 161 | 15.1733 | 15.1898 | 0.0165
GEN-2018-043 | 02 NEBRASKA | 635221 | KELLOGG5 | 161 | 17.8517 | 17.873 | 0.0213
GEN-2018-043 | 02 NEBRASKA | 635222 | KELLOGG8 | 69 | 18.5076 | 18.5168 | 0.0092
GEN-2018-043 | 02 NEBRASKA | 635225 | MORNSD 5 | 161 | 11.3213 | 11.3288 | 0.0075
GEN-2018-043 | 02 NEBRASKA | 635226 | LEEDS 5 | 161 | 16.5012 | 16.5174 | 0.0162
GEN-2018-043 | 02 NEBRASKA | 635227 | SBRIDGE T8 | 69 | 8.9453 | 8.9479 | 0.0026
GEN-2018-043 | 02 NEBRASKA | 635229 | AIRPORT 5 | 161 | 17.7351 | 17.7585 | 0.0234
GEN-2018-043 | 02 NEBRASKA | 635230 | LIBERTY5 | 161 | 26.0055 | 26.0604 | 0.0549
GEN-2018-043 | 02 NEBRASKA | 635235 | SALIX 5 | 161 | 15.2642 | 15.2808 | 0.0166
GEN-2018-043 | 02 NEBRASKA | 635236 | SALIX 8 | 69 | 13.8554 | 13.8606 | 0.0052
GEN-2018-043 | 02 NEBRASKA | 635237 | SLOAN 8 | 69 | 4.9052 | 4.9058 | 0.0006
GEN-2018-043 | 02 NEBRASKA | 635252 | J412 POI 3 | 345 | 9.8941 | 9.9042 | 0.0101
GEN-2018-043 | 02 NEBRASKA | 635300 | MONONA 5 | 161 | 5.7183 | 5.7196 | 0.0013
GEN-2018-043 | 02 NEBRASKA | 635301 | MONONA 8 | 69 | 4.7205 | 4.7208 | 0.0003
GEN-2018-043 | 02 NEBRASKA | 635302 | MAPLTN 8 | 69 | 3.1812 | 3.1814 | 0.0002
GEN-2018-043 | 02 NEBRASKA | 635303 | SMITHLD8 | 69 | 2.4719 | 2.472 | 0.0001
GEN-2018-043 | 02 NEBRASKA | 635330 | CRWFRD 5 | 161 | 5.1193 | 5.1199 | 0.0006
GEN-2018-043 | 02 NEBRASKA | 635368 | OBRIEN 3 | 345 | 15.8287 | 15.8371 | 0.0084
GEN-2018-043 | 02 NEBRASKA | 635398 | REMSEN 3 | 345 | 15.2009 | 15.2256 | 0.0247
GEN-2018-043 | 02 NEBRASKA | 635399 | CHEROKEE 3 | 345 | 16.7177 | 16.744 | 0.0263
GEN-2018-043 | 02 NEBRASKA | 635400 | HIGHLND 3 | 345 | 15.2944 | 15.307 | 0.0126
GEN-2018-043 | 02 NEBRASKA | 636010 | LEHIGH 3 | 345 | 13.6938 | 13.6977 | 0.0039
GEN-2018-043 | 02 NEBRASKA | 637009 | GLACIAL EDGE | 345 | 16.4295 | 16.4549 | 0.0254
GEN-2018-043 | 02 NEBRASKA | 637024 | RICHLAND W | 345 | 8.992 | 8.9984 | 0.0064
GEN-2018-043 | 02 NEBRASKA | 640072 | BATTLCR7 | 115 | 7.7876 | 7.7884 | 0.0008
GEN-2018-043 | 02 NEBRASKA | 640073 | BATTLCR8 | 69 | 4.1044 | 4.1045 | 0.0001
GEN-2018-043 | 02 NEBRASKA | 640080 | BELDEN 7 | 115 | 6.3499 | 6.3504 | 0.0005
GEN-2018-043 | 02 NEBRASKA | 640081 | BELDEN 8 | 69 | 3.9025 | 3.9026 | 0.0001
GEN-2018-043 | 02 NEBRASKA | 640115 | CO.LINE7 | 115 | 7.8321 | 7.8328 | 0.0007
GEN-2018-043 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 10.6772 | 10.6823 | 0.0051
GEN-2018-043 | 02 NEBRASKA | 640127 | COLMB.E7 | 115 | 23.5806 | 23.5866 | 0.006
GEN-2018-043 | 02 NEBRASKA | 640133 | COLMBUS4 | 230 | 12.2576 | 12.2606 | 0.003
GEN-2018-043 | 02 NEBRASKA | 640139 | COOPER 3 | 345 | 27.6797 | 27.697 | 0.0173
GEN-2018-043 | 02 NEBRASKA | 640149 | CREITON7 | 115 | 5.2714 | 5.2716 | 0.0002
GEN-2018-043 | 02 NEBRASKA | 640150 | CREITON8 | 69 | 4.738 | 4.7381 | 0.0001
GEN-2018-043 | 02 NEBRASKA | 640212 | HARTGTN7 | 115 | 5.5773 | 5.5776 | 0.0003
GEN-2018-043 | 02 NEBRASKA | 640213 | HARTGTN8 | 69 | 3.7103 | 3.7104 | 0.0001
GEN-2018-043 | 02 NEBRASKA | 640226 | HOSKINS3 | 345 | 13.7694 | 13.78 | 0.0106
GEN-2018-043 | 02 NEBRASKA | 640227 | HOSKINS4 | 230 | 10.6344 | 10.6384 | 0.004
GEN-2018-043 | 02 NEBRASKA | 640228 | HOSKINS7 | 115 | 19.1585 | 19.165 | 0.0065
GEN-2018-043 | 02 NEBRASKA | 640263 | MADISON7 | 115 | 6.4954 | 6.4961 | 0.0007
GEN-2018-043 | 02 NEBRASKA | 640277 | MOORE 3 | 345 | 23.8841 | 23.9081 | 0.024
GEN-2018-043 | 02 NEBRASKA | 640293 | NELIGH 7 | 115 | 11.3544 | 11.3554 | 0.001
GEN-2018-043 | 02 NEBRASKA | 640294 | NELIGH 8 | 69 | 6.3752 | 6.3753 | 0.0001
GEN-2018-043 | 02 NEBRASKA | 640296 | NORFK.N7 | 115 | 13.9569 | 13.9602 | 0.0033
GEN-2018-043 | 02 NEBRASKA | 640298 | NORFOLK7 | 115 | 13.0893 | 13.0922 | 0.0029
GEN-2018-043 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 10.9514 | 10.9568 | 0.0054
GEN-2018-043 | 02 NEBRASKA | 640343 | SHELCRK4 | 230 | 11.532 | 11.5349 | 0.0029
GEN-2018-043 | 02 NEBRASKA | 640357 | STANTON7 | 115 | 5.3784 | 5.3792 | 0.0008
GEN-2018-043 | 02 NEBRASKA | 640363 | STNTN.N7 | 115 | 7.3435 | 7.3448 | 0.0013
GEN-2018-043 | 02 NEBRASKA | 640377 | TEKAMAH5 | 161 | 9.2993 | 9.3131 | 0.0138
GEN-2018-043 | 02 NEBRASKA | 640378 | TEKAMAH7 | 115 | 8.5902 | 8.5968 | 0.0066
GEN-2018-043 | 02 NEBRASKA | 640386 | TWIN CH4 | 230 | 9.3298 | 9.3336 | 0.0038
GEN-2018-043 | 02 NEBRASKA | 640387 | TWIN CH7 | 115 | 11.3083 | 11.3113 | 0.003
GEN-2018-043 | 02 NEBRASKA | 640388 | TWIN CH8 | 69 | 8.1694 | 8.1704 | 0.001
GEN-2018-043 | 02 NEBRASKA | 640424 | S.SIOUXCITY7 | 115 | 7.7331 | 7.7345 | 0.0014
GEN-2018-043 | 02 NEBRASKA | 640425 | S.SIOUXCITY8 | 69 | 4.7205 | 4.7208 | 0.0003
GEN-2018-043 | 02 NEBRASKA | 640520 | ANTELOPE 3 | 345 | 7.034 | 7.0362 | 0.0022
GEN-2018-043 | 02 NEBRASKA | 640521 | ANTELOPE 7 | 115 | 16.5819 | 16.5844 | 0.0025
GEN-2018-043 | 02 NEBRASKA | 640522 | ANTELOPE 8 | 69 | 5.5027 | 5.5028 | 0.0001
GEN-2018-043 | 02 NEBRASKA | 640560 | WAKEFIELD 4 | 230 | 8.3587 | 8.3609 | 0.0022
GEN-2018-043 | 02 NEBRASKA | 640561 | RTLSNAKE.W 4 | 230 | 7.4637 | 7.4653 | 0.0016
GEN-2018-043 | 02 NEBRASKA | 640588 | TURTLE.CRK 3 | 345 | 12.1332 | 12.1407 | 0.0075
GEN-2018-043 | 02 NEBRASKA | 640589 | SHOLES.W 3 | 345 | 9.8826 | 9.8873 | 0.0047
GEN-2018-043 | 02 NEBRASKA | 640598 | HAYSTACK.WD3 | 345 | 9.2726 | 9.2767 | 0.0041
GEN-2018-043 | 02 NEBRASKA | 643254 | UPSTREAM.W 7 | 115 | 15.861 | 15.8632 | 0.0022
GEN-2018-043 | 02 NEBRASKA | 643271 | PLUMBCR.W 3 | 345 | 11.8848 | 11.892 | 0.0072
GEN-2018-043 | 02 NEBRASKA | 645100 | FC1A 5 | 161 | 29.6832 | 30.0624 | 0.3792
GEN-2018-043 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 22.1168 | 22.7625 | 0.6457
GEN-2018-043 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 29.2729 | 29.5305 | 0.2576
GEN-2018-043 | 02 NEBRASKA | 645455 | S3455 3 | 345 | 32.426 | 32.6973 | 0.2713
GEN-2018-043 | 02 NEBRASKA | 645456 | S3456 3 | 345 | 34.9426 | 35.2431 | 0.3005
GEN-2018-043 | 02 NEBRASKA | 645458 | S3458 3 | 345 | 30.8042 | 30.8631 | 0.0589
GEN-2018-043 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 25.436 | 25.7478 | 0.3118
GEN-2018-043 | 02 NEBRASKA | 645740 | S3740 3 | 345 | 23.3538 | 23.4586 | 0.1048
GEN-2018-043 | 02 NEBRASKA | 645761 | S3761 3 | 345 | 23.2092 | 23.3458 | 0.1366
GEN-2018-043 | 02 NEBRASKA | 646201 | S1201 5 | 161 | 32.2584 | 32.3659 | 0.1075
GEN-2018-043 | 02 NEBRASKA | 646206 | S1206 5 | 161 | 45.1657 | 45.3515 | 0.1858
GEN-2018-043 | 02 NEBRASKA | 646209 | S1209 5 | 161 | 47.2687 | 47.6366 | 0.3679
GEN-2018-043 | 02 NEBRASKA | 646211 | S1211 5 | 161 | 36.7642 | 36.913 | 0.1488
GEN-2018-043 | 02 NEBRASKA | 646216 | S1216 5 | 161 | 30.8779 | 30.9791 | 0.1012
GEN-2018-043 | 02 NEBRASKA | 646221 | S1221 5 | 161 | 35.6195 | 35.7884 | 0.1689
GEN-2018-043 | 02 NEBRASKA | 646226 | S1226 5 | 161 | 25.0331 | 25.2213 | 0.1882
GEN-2018-043 | 02 NEBRASKA | 646227 | S1227 5 | 161 | 32.8397 | 32.9763 | 0.1366
GEN-2018-043 | 02 NEBRASKA | 646231 | S1231 5 | 161 | 43.3142 | 43.5827 | 0.2685
GEN-2018-043 | 02 NEBRASKA | 646232 | S1232 5 | 161 | 26.8332 | 26.903 | 0.0698
GEN-2018-043 | 02 NEBRASKA | 646233 | S1233 5 | 161 | 29.4933 | 29.6045 | 0.1112
GEN-2018-043 | 02 NEBRASKA | 646235 | S1235 5 | 161 | 34.1223 | 34.2933 | 0.171
GEN-2018-043 | 02 NEBRASKA | 646237 | S1237 5 | 161 | 21.9616 | 22.0487 | 0.0871
GEN-2018-043 | 02 NEBRASKA | 646244 | S1244 5 | 161 | 22.3261 | 22.3688 | 0.0427
GEN-2018-043 | 02 NEBRASKA | 646249 | S1249 5 | 161 | 25.2275 | 25.309 | 0.0815
GEN-2018-043 | 02 NEBRASKA | 646250 | S1250 5 | 161 | 35.6718 | 35.8513 | 0.1795
GEN-2018-043 | 02 NEBRASKA | 646251 | S1251 5 | 161 | 32.2496 | 32.6975 | 0.4479
GEN-2018-043 | 02 NEBRASKA | 646252 | S1252 5 | 161 | 29.8458 | 29.9993 | 0.1535
GEN-2018-043 | 02 NEBRASKA | 646254 | S1254 5 | 161 | 32.6691 | 32.7985 | 0.1294
GEN-2018-043 | 02 NEBRASKA | 646255 | S1255 5 | 161 | 48.9564 | 49.2423 | 0.2859
GEN-2018-043 | 02 NEBRASKA | 646256 | S1256 5 | 161 | 22.848 | 22.9197 | 0.0717
GEN-2018-043 | 02 NEBRASKA | 646259 | S1259 5 | 161 | 38.6144 | 38.7776 | 0.1632
GEN-2018-043 | 02 NEBRASKA | 646281 | S1281 5 | 161 | 35.2632 | 35.3927 | 0.1295
GEN-2018-043 | 02 NEBRASKA | 646287 | S1287 5 | 161 | 21.8808 | 21.9275 | 0.0467
GEN-2018-043 | 02 NEBRASKA | 646291 | S1291 5 | 161 | 7.1513 | 7.1619 | 0.0106
GEN-2018-043 | 02 NEBRASKA | 646297 | S1297 5 | 161 | 19.0616 | 19.1612 | 0.0996
GEN-2018-043 | 02 NEBRASKA | 646298 | S1298 5 | 161 | 29.4628 | 29.8127 | 0.3499
GEN-2018-043 | 02 NEBRASKA | 646305 | S1305 5 | 161 | 28.0271 | 28.3468 | 0.3197
GEN-2018-043 | 02 NEBRASKA | 646341 | S1341 5 | 161 | 27.2778 | 27.5841 | 0.3063
GEN-2018-043 | 02 NEBRASKA | 646347 | S1347 5 | 161 | 33.0082 | 33.1838 | 0.1756
GEN-2018-043 | 02 NEBRASKA | 646361 | S1361 5 | 161 | 40.585 | 40.7607 | 0.1757
GEN-2018-043 | 02 NEBRASKA | 646363 | S1363 5 | 161 | 32.0273 | 32.1184 | 0.0911
GEN-2018-043 | 02 NEBRASKA | 647006 | S906 N 8 | 69 | 32.6737 | 32.7125 | 0.0388
GEN-2018-043 | 02 NEBRASKA | 647104 | MUD LNG8 | 69 | 14.6891 | 14.7002 | 0.0111
GEN-2018-043 | 02 NEBRASKA | 647906 | S906 S 8 | 69 | 33.1827 | 33.2183 | 0.0356
GEN-2018-043 | 02 NEBRASKA | 647909 | S909 8 | 69 | 27.1413 | 27.1795 | 0.0382
GEN-2018-043 | 02 NEBRASKA | 647918 | S918 8 | 69 | 22.995 | 23.0215 | 0.0265
GEN-2018-043 | 02 NEBRASKA | 647921 | S921 8 | 69 | 26.521 | 26.5554 | 0.0344
GEN-2018-043 | 02 NEBRASKA | 647937 | S937 8 | 69 | 9.1634 | 9.1663 | 0.0029
GEN-2018-043 | 02 NEBRASKA | 647939 | S939 8 | 69 | 20.1752 | 20.1962 | 0.021
GEN-2018-043 | 02 NEBRASKA | 647950 | S950 8 | 69 | 20.4079 | 20.4303 | 0.0224
GEN-2018-043 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 17.809 | 17.8272 | 0.0182
GEN-2018-043 | 02 NEBRASKA | 650185 | WAGENER 3 | 345 | 21.365 | 21.4055 | 0.0405
GEN-2018-043 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 21.2422 | 21.2733 | 0.0311
GEN-2018-043 | 02 NEBRASKA | 650214 | NW68HOLDRG7 | 115 | 25.8907 | 25.9018 | 0.0111
GEN-2018-043 | 02 NEBRASKA | 650267 | 84LEIGHTON7 | 115 | 29.9849 | 30.0016 | 0.0167
GEN-2018-043 | 02 NEBRASKA | 650271 | 81&OCHENEY7 | 115 | 25.4781 | 25.4894 | 0.0113
GEN-2018-043 | 02 NEBRASKA | 650279 | 120&ALVO 7 | 115 | 21.9931 | 22.0026 | 0.0095
GEN-2018-043 | 02 NEBRASKA | 650285 | WAGENER 7 | 115 | 32.6539 | 32.6765 | 0.0226
GEN-2018-043 | 02 NEBRASKA | 652509 | FTRANDL4 | 230 | 11.222 | 11.2228 | 0.0008
GEN-2018-043 | 02 NEBRASKA | 652537 | WHITE 3 | 345 | 19.9602 | 19.9606 | 0.0004
GEN-2018-043 | 02 NEBRASKA | 652552 | SIOUXCY2 | 230 | 20.7996 | 20.8245 | 0.0249
GEN-2018-043 | 02 NEBRASKA | 652564 | SIOUXCY3 | 345 | 15.8903 | 15.9208 | 0.0305
GEN-2018-043 | 02 NEBRASKA | 652565 | SIOUXCY4 | 230 | 20.7996 | 20.8245 | 0.0249
GEN-2018-043 | 02 NEBRASKA | 652566 | SIOUXCY5 | 161 | 21.655 | 21.6764 | 0.0214
GEN-2018-043 | 02 NEBRASKA | 652567 | DENISON4 | 230 | 4.7591 | 4.7599 | 0.0008
GEN-2018-043 | 02 NEBRASKA | 652864 | SIOUXCY-LNX3 | 345 | 15.7006 | 15.7301 | 0.0295
GEN-2018-043 | 02 NEBRASKA | 655126 | MOS-VERM-ER8 | 69 | 2.0197 | 2.0197 | 0
GEN-2018-043 | 02 NEBRASKA | 655129 | SW806-ER8 | 69 | 0.8786 | 0.8786 | 0
GEN-2018-043 | 02 NEBRASKA | 655130 | SW808-ER8 | 69 | 2.5377 | 2.5378 | 0.0001
GEN-2018-043 | 02 NEBRASKA | 655133 | SW822-ER8 | 69 | 2.1934 | 2.1934 | 0
GEN-2018-043 | 02 NEBRASKA | 655136 | SW832-ER8 | 69 | 2.6199 | 2.62 | 0.0001
GEN-2018-043 | 02 NEBRASKA | 655137 | SW833-ER8 | 69 | 2.0923 | 2.0924 | 0.0001
GEN-2018-043 | 02 NEBRASKA | 655145 | SW870-ER8 | 69 | 2.8849 | 2.885 | 0.0001
GEN-2018-043 | 02 NEBRASKA | 655146 | SW873-ER8 | 69 | 2.8837 | 2.8838 | 0.0001
GEN-2018-043 | 02 NEBRASKA | 655147 | MOS-JEFF-ER8 | 69 | 2.5384 | 2.5384 | 0
GEN-2018-043 | 02 NEBRASKA | 655151 | MOS-BGSP-ER8 | 69 | 1.364 | 1.364 | 0
GEN-2018-043 | 02 NEBRASKA | 655152 | SW894-ER8 | 69 | 2.0653 | 2.0654 | 0.0001
GEN-2018-043 | 02 NEBRASKA | 655308 | ALCESTER-ER8 | 69 | 1.026 | 1.026 | 0
GEN-2018-043 | 02 NEBRASKA | 655311 | AKRON-ER8 | 69 | 1.5302 | 1.5302 | 0
GEN-2018-043 | 02 NEBRASKA | 655313 | RICHLAND-ER8 | 69 | 2.5294 | 2.5295 | 0.0001
GEN-2018-043 | 02 NEBRASKA | 655314 | ELKPNTCY-ER8 | 69 | 1.9368 | 1.9368 | 0
GEN-2018-043 | 02 NEBRASKA | 655315 | ELKPOINT-ER8 | 69 | 1.9361 | 1.9361 | 0
GEN-2018-043 | 02 NEBRASKA | 655316 | BURBANK-ER8 | 69 | 1.8789 | 1.8789 | 0
GEN-2018-043 | 02 NEBRASKA | 655326 | BGSPRING-ER8 | 69 | 1.1803 | 1.1803 | 0
GEN-2018-043 | 02 NEBRASKA | 655327 | UNIONCRK-ER8 | 69 | 1.9997 | 1.9997 | 0
GEN-2018-043 | 02 NEBRASKA | 655359 | JEFERSON-ER8 | 69 | 1.6867 | 1.6867 | 0
GEN-2018-043 | 02 NEBRASKA | 655393 | SWR5123-ER8 | 69 | 0.9785 | 0.9786 | 0.0001
GEN-2018-043 | 02 NEBRASKA | 655427 | MOS-ALC2-ER8 | 69 | 1.026 | 1.026 | 0
GEN-2018-043 | 02 NEBRASKA | 655428 | BIGSPRGS-ER8 | 69 | 1.1803 | 1.1803 | 0
GEN-2018-043 | 02 NEBRASKA | 655484 | RASMUSN-ER4 | 230 | 6.8515 | 6.8533 | 0.0018
GEN-2018-043 | 02 NEBRASKA | 655485 | RASMUSN-ER8 | 69 | 3.3135 | 3.3137 | 0.0002
GEN-2018-043 | 02 NEBRASKA | 658122 | ROCKRPDMUNI8 | 69 | 2.8451 | 2.8452 | 0.0001
GEN-2018-043 | 02 NEBRASKA | 658124 | LUVERNEMUNW8 | 69 | 1.8253 | 1.8253 | 0
GEN-2018-043 | 02 NEBRASKA | 658126 | LUVERNEMUNE8 | 69 | 1.7281 | 1.7282 | 0.0001
GEN-2018-043 | 02 NEBRASKA | 658128 | LUVERNEMUNS8 | 69 | 1.831 | 1.831 | 0
GEN-2018-043 | 02 NEBRASKA | 659286 | DEERCREK-BE3 | 345 | 19.3606 | 19.361 | 0.0004
GEN-2018-043 | 02 NEBRASKA | 659311 | PAHOJA__-BE4 | 230 | 7.6243 | 7.6254 | 0.0011
GEN-2018-043 | 02 NEBRASKA | 659708 | LITLRCKT-LO8 | 69 | 1.9722 | 1.9723 | 0.0001
GEN-2018-043 | 02 NEBRASKA | 659709 | LITLRCK -LO8 | 69 | 1.9313 | 1.9313 | 0
GEN-2018-043 | 02 NEBRASKA | 659710 | GEORGETP-LO8 | 69 | 2.3892 | 2.3893 | 0.0001
GEN-2018-043 | 02 NEBRASKA | 659711 | GEORGE -LO8 | 69 | 2.3275 | 2.3275 | 0
GEN-2018-043 | 02 NEBRASKA | 659712 | RKRMUNTP-LO8 | 69 | 3.3887 | 3.3888 | 0.0001
GEN-2018-043 | 02 NEBRASKA | 659714 | RKRPDTAP-LO8 | 69 | 3.6031 | 3.6032 | 0.0001
GEN-2018-043 | 02 NEBRASKA | 659715 | ROCKRPDS-LO8 | 69 | 3.4469 | 3.4469 | 0
GEN-2018-043 | 02 NEBRASKA | 659726 | STEEN -LO8 | 69 | 2.3471 | 2.3471 | 0
GEN-2018-043 | 02 NEBRASKA | 659727 | LUVERNE -LO8 | 69 | 1.8643 | 1.8643 | 0
GEN-2018-043 | 02 NEBRASKA | 659735 | CLEVELND-LO4 | 230 | 5.0927 | 5.0932 | 0.0005
GEN-2018-043 | 02 NEBRASKA | 659736 | CLEVELND-LO8 | 69 | 4.4428 | 4.443 | 0.0002
GEN-2018-043 | 02 NEBRASKA | 659900 | EAGLE___-NI4 | 230 | 7.504 | 7.5058 | 0.0018
GEN-2018-043 | 02 NEBRASKA | 659901 | EAGLE___-NI8 | 69 | 14.4033 | 14.4053 | 0.002
GEN-2018-043 | 02 NEBRASKA | 760515 | GEN-2017-222 | 230 | 3.6209 | 3.6214 | 0.0005
GEN-2018-043 | 02 NEBRASKA | 760746 | GEN-2017-115 | 345 | 9.0493 | 9.051 | 0.0017
GEN-2018-043 | 02 NEBRASKA | 760788 | GEN-2017-201 | 345 | 8.9595 | 8.9634 | 0.0039
GEN-2018-043 | 02 NEBRASKA | 762069 | G17-105TAP | 161 | 8.7205 | 8.732 | 0.0115
GEN-2018-043 | 02 NEBRASKA | 762070 | GEN-2017-105 | 161 | 8.7205 | 8.732 | 0.0115
GEN-2018-043 | 02 NEBRASKA | 762504 | GEN-2018-012 | 345 | 5.7752 | 5.7766 | 0.0014
GEN-2018-043 | 02 NEBRASKA | 762509 | G18-012-DUMY | 345 | 7.034 | 7.0362 | 0.0022
GEN-2018-043 | 02 NEBRASKA | 762603 | GEN-2018-025 | 345 | 21.1748 | 21.7655 | 0.5907
GEN-2018-043 | 02 NEBRASKA | 762691 | GEN-2018-033 | 345 | 22.3406 | 22.4363 | 0.0957
GEN-2018-043 | 02 NEBRASKA | 762779 | G18-043-TAP | 345 | 15.5658 | 16.5371 | 0.9713
GEN-2018-043 | 02 NEBRASKA | 762780 | GEN-2018-043 | 345 | 15.5229 | 16.4943 | 0.9714
GEN-2018-060 | 02 NEBRASKA | 515852 | DGRASSE7 | 345 | 14.5253 | 14.5256 | 0.0003
GEN-2018-060 | 02 NEBRASKA | 523118 | BUFF_DUNES 7 | 345 | 5.6704 | 5.6707 | 0.0003
GEN-2018-060 | 02 NEBRASKA | 523853 | FINNEY 7 | 345 | 9.3553 | 9.3561 | 0.0008
GEN-2018-060 | 02 NEBRASKA | 530551 | SALINE 3 | 115 | 5.0672 | 5.0678 | 0.0006
GEN-2018-060 | 02 NEBRASKA | 530552 | GORHAM 3 | 115 | 3.2606 | 3.2609 | 0.0003
GEN-2018-060 | 02 NEBRASKA | 530553 | S HAYS 3 | 115 | 9.0286 | 9.0309 | 0.0023
GEN-2018-060 | 02 NEBRASKA | 530558 | KNOLL N 6 | 230 | 11.92 | 11.9312 | 0.0112
GEN-2018-060 | 02 NEBRASKA | 530560 | WKNNY 3 | 115 | 2.2616 | 2.2617 | 0.0001
GEN-2018-060 | 02 NEBRASKA | 530561 | KNOLL 3 | 115 | 11.1194 | 11.1229 | 0.0035
GEN-2018-060 | 02 NEBRASKA | 530562 | HAYS 3 | 115 | 8.18 | 8.1819 | 0.0019
GEN-2018-060 | 02 NEBRASKA | 530581 | N HAYS3 | 115 | 9.9457 | 9.9485 | 0.0028
GEN-2018-060 | 02 NEBRASKA | 530582 | S HAYS6 | 230 | 9.747 | 9.7522 | 0.0052
GEN-2018-060 | 02 NEBRASKA | 530583 | POSTROCK7 | 345 | 8.3014 | 8.3162 | 0.0148
GEN-2018-060 | 02 NEBRASKA | 530584 | POSTROCK6 | 230 | 12.0328 | 12.0443 | 0.0115
GEN-2018-060 | 02 NEBRASKA | 530590 | BEMIS 3 | 115 | 4.0579 | 4.0583 | 0.0004
GEN-2018-060 | 02 NEBRASKA | 530592 | SMOKYHL6 | 230 | 7.0201 | 7.0208 | 0.0007
GEN-2018-060 | 02 NEBRASKA | 530593 | SMKYP1 6 | 230 | 6.1368 | 6.1373 | 0.0005
GEN-2018-060 | 02 NEBRASKA | 530599 | SMKYP2 6 | 230 | 6.4985 | 6.499 | 0.0005
GEN-2018-060 | 02 NEBRASKA | 530605 | REDLIN 3 | 115 | 3.9101 | 3.9104 | 0.0003
GEN-2018-060 | 02 NEBRASKA | 530610 | SHAYS_230 | 230 | 4.4096 | 4.4103 | 0.0007
GEN-2018-060 | 02 NEBRASKA | 530676 | GMEC 3 | 115 | 10.4965 | 10.4996 | 0.0031
GEN-2018-060 | 02 NEBRASKA | 530677 | OGALATP3 | 115 | 2.6822 | 2.6824 | 0.0002
GEN-2018-060 | 02 NEBRASKA | 530680 | HEIZER 6 | 230 | 8.3706 | 8.3724 | 0.0018
GEN-2018-060 | 02 NEBRASKA | 530684 | RUSLPMP3 | 115 | 2.1238 | 2.1239 | 0.0001
GEN-2018-060 | 02 NEBRASKA | 530694 | VINE2 3 | 115 | 8.2757 | 8.2776 | 0.0019
GEN-2018-060 | 02 NEBRASKA | 530695 | CHETOLAH3 | 115 | 8.9608 | 8.963 | 0.0022
GEN-2018-060 | 02 NEBRASKA | 530702 | BUCKEYE_230 | 230 | 9.0409 | 9.0468 | 0.0059
GEN-2018-060 | 02 NEBRASKA | 530714 | ANGUS 3 | 115 | 5.5205 | 5.5214 | 0.0009
GEN-2018-060 | 02 NEBRASKA | 530720 | KNOLL S 6 | 230 | 11.92 | 11.9312 | 0.0112
GEN-2018-060 | 02 NEBRASKA | 530721 | VINEDE_N | 115 | 8.2757 | 8.2776 | 0.0019
GEN-2018-060 | 02 NEBRASKA | 530722 | VINEDE_S | 115 | 8.2757 | 8.2776 | 0.0019
GEN-2018-060 | 02 NEBRASKA | 530725 | PFEIFER 3 | 115 | 3.6012 | 3.6016 | 0.0004
GEN-2018-060 | 02 NEBRASKA | 531448 | HOLCOMB3 | 115 | 21.0931 | 21.0936 | 0.0005
GEN-2018-060 | 02 NEBRASKA | 531449 | HOLCOMB7 | 345 | 9.4745 | 9.4753 | 0.0008
GEN-2018-060 | 02 NEBRASKA | 531451 | MINGO 7 | 345 | 6.2897 | 6.2901 | 0.0004
GEN-2018-060 | 02 NEBRASKA | 531465 | SETAB 7 | 345 | 6.93 | 6.9305 | 0.0005
GEN-2018-060 | 02 NEBRASKA | 531469 | SPERVIL7 | 345 | 12.6925 | 12.6966 | 0.0041
GEN-2018-060 | 02 NEBRASKA | 531492 | OG ONEOK | 115 | 2.1815 | 2.1817 | 0.0002
GEN-2018-060 | 02 NEBRASKA | 531497 | TURKEYR3 | 115 | 1.8236 | 1.8237 | 0.0001
GEN-2018-060 | 02 NEBRASKA | 531501 | BUCKNER7 | 345 | 9.3506 | 9.3518 | 0.0012
GEN-2018-060 | 02 NEBRASKA | 531502 | CIMRRN 7 | 345 | 7.4429 | 7.4437 | 0.0008
GEN-2018-060 | 02 NEBRASKA | 531504 | CIMWD2 7 | 345 | 7.7288 | 7.7296 | 0.0008
GEN-2018-060 | 02 NEBRASKA | 531632 | GEN-2015-065 | 345 | 5.6215 | 5.6218 | 0.0003
GEN-2018-060 | 02 NEBRASKA | 532782 | BUFFALO7 | 345 | 19.0684 | 19.0688 | 0.0004
GEN-2018-060 | 02 NEBRASKA | 532783 | KINGMAN7 | 345 | 7.0868 | 7.0869 | 0.0001
GEN-2018-060 | 02 NEBRASKA | 532784 | NINN1WF7 | 345 | 5.9548 | 5.9548 | 0
GEN-2018-060 | 02 NEBRASKA | 532785 | PRATTWF7 | 345 | 4.9721 | 4.9721 | 0
GEN-2018-060 | 02 NEBRASKA | 532871 | CIRCLE 6 | 230 | 8.873 | 8.8733 | 0.0003
GEN-2018-060 | 02 NEBRASKA | 532873 | SUMMIT 6 | 230 | 13.3064 | 13.3069 | 0.0005
GEN-2018-060 | 02 NEBRASKA | 539117 | SPRVILL-EHVB | 230 | 11.808 | 11.8102 | 0.0022
GEN-2018-060 | 02 NEBRASKA | 539132 | SPRVILL-EHV2 | 230 | 10.164 | 10.1657 | 0.0017
GEN-2018-060 | 02 NEBRASKA | 539628 | NW-DGTP3 | 115 | 3.5247 | 3.5247 | 0
GEN-2018-060 | 02 NEBRASKA | 539641 | NW-DODG3 | 115 | 3.6375 | 3.6375 | 0
GEN-2018-060 | 02 NEBRASKA | 539645 | DCBEEF3 | 115 | 6.8429 | 6.8431 | 0.0002
GEN-2018-060 | 02 NEBRASKA | 539661 | 24-FREY3 | 115 | 5.472 | 5.4724 | 0.0004
GEN-2018-060 | 02 NEBRASKA | 539667 | HAGGARD3 | 115 | 2.4341 | 2.4341 | 0
GEN-2018-060 | 02 NEBRASKA | 539671 | FTDODGE3 | 115 | 9.3292 | 9.3296 | 0.0004
GEN-2018-060 | 02 NEBRASKA | 539678 | GRTBEND3 | 115 | 11.4928 | 11.4942 | 0.0014
GEN-2018-060 | 02 NEBRASKA | 539679 | GRTBEND6 | 230 | 8.4226 | 8.4244 | 0.0018
GEN-2018-060 | 02 NEBRASKA | 539680 | N-DODGE3 | 115 | 4.6559 | 4.656 | 0.0001
GEN-2018-060 | 02 NEBRASKA | 539681 | N-GBEND3 | 115 | 7.8484 | 7.8491 | 0.0007
GEN-2018-060 | 02 NEBRASKA | 539684 | OTISSUB3 | 115 | 2.9831 | 2.9832 | 0.0001
GEN-2018-060 | 02 NEBRASKA | 539688 | S-DODGE3 | 115 | 6.6703 | 6.6705 | 0.0002
GEN-2018-060 | 02 NEBRASKA | 539689 | 2ND-KS 3 | 115 | 4.9487 | 4.9489 | 0.0002
GEN-2018-060 | 02 NEBRASKA | 539694 | SPEARVL3 | 115 | 9.9424 | 9.9431 | 0.0007
GEN-2018-060 | 02 NEBRASKA | 539695 | SPEARVL6 | 230 | 12.0879 | 12.0902 | 0.0023
GEN-2018-060 | 02 NEBRASKA | 539699 | W-DODGE3 | 115 | 4.3081 | 4.3082 | 0.0001
GEN-2018-060 | 02 NEBRASKA | 539740 | EDODGE 3 | 115 | 6.269 | 6.2692 | 0.0002
GEN-2018-060 | 02 NEBRASKA | 539758 | FORD 3 | 115 | 5.2569 | 5.2571 | 0.0002
GEN-2018-060 | 02 NEBRASKA | 539759 | SPRVL 3 | 115 | 12.8508 | 12.852 | 0.0012
GEN-2018-060 | 02 NEBRASKA | 539771 | NFTDODG3 | 115 | 9.3816 | 9.382 | 0.0004
GEN-2018-060 | 02 NEBRASKA | 539778 | GYCOTAP3 | 115 | 2.4341 | 2.4341 | 0
GEN-2018-060 | 02 NEBRASKA | 539779 | GRAY CO3 | 115 | 2.4341 | 2.4341 | 0
GEN-2018-060 | 02 NEBRASKA | 539800 | CLARKCOUNTY7 | 345 | 12.7374 | 12.7396 | 0.0022
GEN-2018-060 | 02 NEBRASKA | 539801 | THISTLE7 | 345 | 16.269 | 16.2698 | 0.0008
GEN-2018-060 | 02 NEBRASKA | 539803 | IRONWOOD7 | 345 | 12.2015 | 12.2051 | 0.0036
GEN-2018-060 | 02 NEBRASKA | 539804 | THISTLE4 | 138 | 17.8662 | 17.8666 | 0.0004
GEN-2018-060 | 02 NEBRASKA | 539813 | TRANSFORMER | 345 | 10.7364 | 10.738 | 0.0016
GEN-2018-060 | 02 NEBRASKA | 539815 | IRONWOOD WF7 | 345 | 11.0691 | 11.072 | 0.0029
GEN-2018-060 | 02 NEBRASKA | 539840 | GEN-2011-008 | 345 | 10.9464 | 10.9479 | 0.0015
GEN-2018-060 | 02 NEBRASKA | 539841 | G-2011-008-1 | 345 | 10.9464 | 10.9479 | 0.0015
GEN-2018-060 | 02 NEBRASKA | 539855 | G-2011-008-2 | 345 | 9.3251 | 9.3262 | 0.0011
GEN-2018-060 | 02 NEBRASKA | 539857 | G-2011-008-3 | 345 | 8.6038 | 8.6047 | 0.0009
GEN-2018-060 | 02 NEBRASKA | 539944 | LOCHS | 115 | 3.2599 | 3.2599 | 0
GEN-2018-060 | 02 NEBRASKA | 560080 | G16-046-TAP | 345 | 11.163 | 11.1651 | 0.0021
GEN-2018-060 | 02 NEBRASKA | 560082 | G16-050-TAP | 345 | 7.4606 | 7.5471 | 0.0865
GEN-2018-060 | 02 NEBRASKA | 579480 | GEN-2008-124 | 345 | 11.8066 | 11.81 | 0.0034
GEN-2018-060 | 02 NEBRASKA | 584650 | GEN-2015-023 | 345 | 8.0763 | 8.0771 | 0.0008
GEN-2018-060 | 02 NEBRASKA | 585241 | GEN-2015-088 | 345 | 12.2238 | 12.2286 | 0.0048
GEN-2018-060 | 02 NEBRASKA | 587310 | GEN-2016-046 | 345 | 9.8623 | 9.8639 | 0.0016
GEN-2018-060 | 02 NEBRASKA | 587311 | G16-046XFMR1 | 115 | 15.1314 | 15.1325 | 0.0011
GEN-2018-060 | 02 NEBRASKA | 587350 | GEN-2016-050 | 345 | 6.2866 | 6.3767 | 0.0901
GEN-2018-060 | 02 NEBRASKA | 587680 | GEN-2016-074 | 345 | 6.7016 | 6.7074 | 0.0058
GEN-2018-060 | 02 NEBRASKA | 588630 | GEN-2017-018 | 345 | 16.269 | 16.2698 | 0.0008
GEN-2018-060 | 02 NEBRASKA | 599950 | LAMAR7 | 345 | 2.4481 | 2.4482 | 0.0001
GEN-2018-060 | 02 NEBRASKA | 640065 | AXTELL 3 | 345 | 9.8948 | 9.9499 | 0.0551
GEN-2018-060 | 02 NEBRASKA | 640066 | AXTELL 7 | 115 | 14.9016 | 14.9242 | 0.0226
GEN-2018-060 | 02 NEBRASKA | 640103 | CANADAY7 | 115 | 14.3621 | 14.3648 | 0.0027
GEN-2018-060 | 02 NEBRASKA | 640131 | COLMB.W4 | 230 | 10.4565 | 10.4569 | 0.0004
GEN-2018-060 | 02 NEBRASKA | 640161 | ELMCRK_7 | 115 | 6.2247 | 6.2259 | 0.0012
GEN-2018-060 | 02 NEBRASKA | 640162 | ELMCRK 8 | 69 | 3.8749 | 3.8752 | 0.0003
GEN-2018-060 | 02 NEBRASKA | 640183 | GENTLMN3 | 345 | 16.2899 | 16.2956 | 0.0057
GEN-2018-060 | 02 NEBRASKA | 640184 | GENTLMN4 | 230 | 19.7874 | 19.7909 | 0.0035
GEN-2018-060 | 02 NEBRASKA | 640194 | GOSPER 7 | 115 | 4.5328 | 4.533 | 0.0002
GEN-2018-060 | 02 NEBRASKA | 640200 | GR ISLD4 | 230 | 17.4767 | 17.4839 | 0.0072
GEN-2018-060 | 02 NEBRASKA | 640201 | GR ISLD7 | 115 | 23.9687 | 23.9746 | 0.0059
GEN-2018-060 | 02 NEBRASKA | 640206 | GUIDE R7 | 115 | 4.3826 | 4.3831 | 0.0005
GEN-2018-060 | 02 NEBRASKA | 640207 | GUIDE R8 | 69 | 2.2466 | 2.2467 | 0.0001
GEN-2018-060 | 02 NEBRASKA | 640214 | HASTING4 | 230 | 7.6335 | 7.6352 | 0.0017
GEN-2018-060 | 02 NEBRASKA | 640215 | HASTING7 | 115 | 20.0095 | 20.0165 | 0.007
GEN-2018-060 | 02 NEBRASKA | 640222 | HILDRTH7 | 115 | 4.3994 | 4.4004 | 0.001
GEN-2018-060 | 02 NEBRASKA | 640223 | HILDRTH8 | 69 | 3.5548 | 3.5552 | 0.0004
GEN-2018-060 | 02 NEBRASKA | 640224 | HOLDREG7 | 115 | 6.3234 | 6.3256 | 0.0022
GEN-2018-060 | 02 NEBRASKA | 640242 | JOHN.2 7 | 115 | 13.11 | 13.1123 | 0.0023
GEN-2018-060 | 02 NEBRASKA | 640244 | JOHN.LK7 | 115 | 9.0467 | 9.0477 | 0.001
GEN-2018-060 | 02 NEBRASKA | 640245 | JOHN.LK8 | 69 | 4.301 | 4.3012 | 0.0002
GEN-2018-060 | 02 NEBRASKA | 640248 | KEAR.NE7 | 115 | 9.8158 | 9.8195 | 0.0037
GEN-2018-060 | 02 NEBRASKA | 640250 | KEARNEY7 | 115 | 12.4706 | 12.4781 | 0.0075
GEN-2018-060 | 02 NEBRASKA | 640252 | KEYSTON3 | 345 | 8.8147 | 8.816 | 0.0013
GEN-2018-060 | 02 NEBRASKA | 640253 | KEYSTON7 | 115 | 14.8327 | 14.8337 | 0.001
GEN-2018-060 | 02 NEBRASKA | 640255 | KINGSLY7 | 115 | 9.2611 | 9.2614 | 0.0003
GEN-2018-060 | 02 NEBRASKA | 640261 | LOWELL 7 | 115 | 8.4695 | 8.4732 | 0.0037
GEN-2018-060 | 02 NEBRASKA | 640262 | LOWELL 8 | 69 | 4.2196 | 4.2202 | 0.0006
GEN-2018-060 | 02 NEBRASKA | 640271 | MCCOOL 3 | 345 | 11.458 | 11.4607 | 0.0027
GEN-2018-060 | 02 NEBRASKA | 640272 | MCCOOL 7 | 115 | 14.7652 | 14.7666 | 0.0014
GEN-2018-060 | 02 NEBRASKA | 640273 | MCCOOL 8 | 69 | 5.7348 | 5.735 | 0.0002
GEN-2018-060 | 02 NEBRASKA | 640275 | MINDEN 7 | 115 | 7.4754 | 7.4795 | 0.0041
GEN-2018-060 | 02 NEBRASKA | 640277 | MOORE 3 | 345 | 23.9029 | 23.9081 | 0.0052
GEN-2018-060 | 02 NEBRASKA | 640278 | SHELDON7 | 115 | 45.4089 | 45.4126 | 0.0037
GEN-2018-060 | 02 NEBRASKA | 640286 | N.PLATT4 | 230 | 13.501 | 13.5029 | 0.0019
GEN-2018-060 | 02 NEBRASKA | 640302 | OGALALA4 | 230 | 7.9032 | 7.9037 | 0.0005
GEN-2018-060 | 02 NEBRASKA | 640310 | ORLEANS7 | 115 | 2.4676 | 2.4679 | 0.0003
GEN-2018-060 | 02 NEBRASKA | 640311 | ORLEANS8 | 69 | 2.4699 | 2.4701 | 0.0002
GEN-2018-060 | 02 NEBRASKA | 640312 | PAULINE3 | 345 | 8.3596 | 8.3742 | 0.0146
GEN-2018-060 | 02 NEBRASKA | 640313 | PAULINE7 | 115 | 16.9273 | 16.9386 | 0.0113
GEN-2018-060 | 02 NEBRASKA | 640314 | PAULINE8 | 69 | 4.9426 | 4.9432 | 0.0006
GEN-2018-060 | 02 NEBRASKA | 640321 | PROSSER7 | 115 | 6.9953 | 6.9969 | 0.0016
GEN-2018-060 | 02 NEBRASKA | 640322 | PROSSER8 | 69 | 3.8981 | 3.8984 | 0.0003
GEN-2018-060 | 02 NEBRASKA | 640325 | REDWILO3 | 345 | 6.5082 | 6.5088 | 0.0006
GEN-2018-060 | 02 NEBRASKA | 640326 | REDWILO7 | 115 | 11.7175 | 11.7182 | 0.0007
GEN-2018-060 | 02 NEBRASKA | 640330 | RIVERDL4 | 230 | 7.5985 | 7.6006 | 0.0021
GEN-2018-060 | 02 NEBRASKA | 640331 | RIVERDL7 | 115 | 13.4134 | 13.418 | 0.0046
GEN-2018-060 | 02 NEBRASKA | 640332 | RIVERDL8 | 69 | 6.7192 | 6.7199 | 0.0007
GEN-2018-060 | 02 NEBRASKA | 640374 | SWEET W3 | 345 | 11.2274 | 11.2455 | 0.0181
GEN-2018-060 | 02 NEBRASKA | 640381 | THEDFRD7 | 115 | 9.068 | 9.0684 | 0.0004
GEN-2018-060 | 02 NEBRASKA | 640383 | TOWER 7 | 115 | 9.4346 | 9.4381 | 0.0035
GEN-2018-060 | 02 NEBRASKA | 640407 | WESTMIN7 | 115 | 8.2287 | 8.2295 | 0.0008
GEN-2018-060 | 02 NEBRASKA | 640448 | HOLDREGE 8 | 69 | 3.8373 | 3.8378 | 0.0005
GEN-2018-060 | 02 NEBRASKA | 640500 | THEDFRD3 | 345 | 5.2775 | 5.2779 | 0.0004
GEN-2018-060 | 02 NEBRASKA | 640510 | HOLT.CO3 | 345 | 8.1409 | 8.1417 | 0.0008
GEN-2018-060 | 02 NEBRASKA | 640525 | TOBIAS 3 | 345 | 12.2238 | 12.2286 | 0.0048
GEN-2018-060 | 02 NEBRASKA | 640583 | ROSEMONT 7 | 115 | 6.7877 | 6.789 | 0.0013
GEN-2018-060 | 02 NEBRASKA | 640584 | COTTONWD 7 | 115 | 5.4817 | 5.4825 | 0.0008
GEN-2018-060 | 02 NEBRASKA | 640590 | MONOLITH 3 | 345 | 23.3851 | 23.3899 | 0.0048
GEN-2018-060 | 02 NEBRASKA | 641087 | EGYCNTR7 | 115 | 18.7306 | 18.7357 | 0.0051
GEN-2018-060 | 02 NEBRASKA | 641088 | HASTCTY7 | 115 | 20.0095 | 20.0165 | 0.007
GEN-2018-060 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 17.8254 | 17.8272 | 0.0018
GEN-2018-060 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 21.2712 | 21.2733 | 0.0021
GEN-2018-060 | 02 NEBRASKA | 653571 | GR ISLD3 | 345 | 13.0409 | 13.0474 | 0.0065
GEN-2018-060 | 02 NEBRASKA | 653871 | GR ISLD-LNX3 | 345 | 12.9098 | 12.9161 | 0.0063
GEN-2018-060 | 02 NEBRASKA | 659425 | SD.LS-KS-MB3 | 345 | 5.9766 | 5.9769 | 0.0003
GEN-2018-060 | 02 NEBRASKA | 760284 | GEN-2017-220 | 345 | 18.9711 | 18.9715 | 0.0004
GEN-2018-060 | 02 NEBRASKA | 760767 | GEN-2017-144 | 345 | 7.8051 | 7.8058 | 0.0007
GEN-2018-060 | 02 NEBRASKA | 761208 | GEN-2017-210 | 345 | 10.0193 | 10.0213 | 0.002
GEN-2018-060 | 02 NEBRASKA | 761292 | GEN-2017-181 | 345 | 6.8738 | 6.8752 | 0.0014
GEN-2018-060 | 02 NEBRASKA | 761313 | GEN-2017-182 | 345 | 5.746 | 5.747 | 0.001
GEN-2018-060 | 02 NEBRASKA | 762834 | GEN-2018-049 | 345 | 7.0894 | 7.0895 | 0.0001
ASGI-2018-003 | 03 CENTRAL | 300070 | 5CLARK | 161 | 8.2028 | 8.2114 | 0.0086
ASGI-2018-003 | 03 CENTRAL | 300071 | 5CLINTN | 161 | 14.0873 | 14.1096 | 0.0223
ASGI-2018-003 | 03 CENTRAL | 300118 | 5STKAEC | 161 | 9.2569 | 9.2606 | 0.0037
ASGI-2018-003 | 03 CENTRAL | 300645 | 2BRONA | 69 | 2.2564 | 2.2565 | 0.0001
ASGI-2018-003 | 03 CENTRAL | 300651 | 2LAMR | 69 | 10.1403 | 10.1416 | 0.0013
ASGI-2018-003 | 03 CENTRAL | 300652 | 2LAMRCTS | 69 | 3.9469 | 3.9472 | 0.0003
ASGI-2018-003 | 03 CENTRAL | 300654 | 2MILO | 69 | 5.4613 | 5.4621 | 0.0008
ASGI-2018-003 | 03 CENTRAL | 300685 | 2LAMARPT | 69 | 8.5611 | 8.562 | 0.0009
ASGI-2018-003 | 03 CENTRAL | 300689 | 2BUTLER | 69 | 6.0477 | 6.049 | 0.0013
ASGI-2018-003 | 03 CENTRAL | 300690 | 2BUTLERE | 69 | 4.8389 | 4.8398 | 0.0009
ASGI-2018-003 | 03 CENTRAL | 300697 | 2CRESTH | 69 | 3.2783 | 3.2786 | 0.0003
ASGI-2018-003 | 03 CENTRAL | 300707 | 2PL GAP | 69 | 4.3348 | 4.3355 | 0.0007
ASGI-2018-003 | 03 CENTRAL | 300793 | 5HYDERHL | 161 | 8.5942 | 8.5979 | 0.0037
ASGI-2018-003 | 03 CENTRAL | 300794 | 5LAMAR | 161 | 8.9181 | 8.9213 | 0.0032
ASGI-2018-003 | 03 CENTRAL | 300798 | 2HYDERHL | 69 | 8.5531 | 8.5545 | 0.0014
ASGI-2018-003 | 03 CENTRAL | 300802 | 2CLARK | 69 | 6.7135 | 6.7149 | 0.0014
ASGI-2018-003 | 03 CENTRAL | 300814 | 2WALKER | 69 | 5.2133 | 5.2141 | 0.0008
ASGI-2018-003 | 03 CENTRAL | 300950 | 5JASPER | 161 | 13.0045 | 13.0066 | 0.0021
ASGI-2018-003 | 03 CENTRAL | 301342 | 5BUTLER | 161 | 6.9768 | 6.9821 | 0.0053
ASGI-2018-003 | 03 CENTRAL | 503507 | 2BUTLEREGEN | 69 | 4.8363 | 4.8372 | 0.0009
ASGI-2018-003 | 03 CENTRAL | 541138 | CLNTPLT_CAP2 | 69 | 8.5076 | 8.5618 | 0.0542
ASGI-2018-003 | 03 CENTRAL | 541207 | ARCHIE 5 | 161 | 17.4708 | 17.4781 | 0.0073
ASGI-2018-003 | 03 CENTRAL | 541208 | NEVADA 5 | 161 | 6.3332 | 6.3468 | 0.0136
ASGI-2018-003 | 03 CENTRAL | 541240 | ADRIAN 5 | 161 | 8.655 | 8.6596 | 0.0046
ASGI-2018-003 | 03 CENTRAL | 541242 | CLINTON5 | 161 | 14.032 | 14.0543 | 0.0223
ASGI-2018-003 | 03 CENTRAL | 541268 | WBURGP 2 | 69 | 6.9988 | 7.0013 | 0.0025
ASGI-2018-003 | 03 CENTRAL | 541269 | WBURGE 2 | 69 | 6.8503 | 6.852 | 0.0017
ASGI-2018-003 | 03 CENTRAL | 541300 | POSTOAK2 | 69 | 4.3914 | 4.3968 | 0.0054
ASGI-2018-003 | 03 CENTRAL | 541301 | CLNTPLT2 | 69 | 8.6907 | 8.7473 | 0.0566
ASGI-2018-003 | 03 CENTRAL | 541302 | CLNTGRN2 | 69 | 8.4219 | 8.469 | 0.0471
ASGI-2018-003 | 03 CENTRAL | 541303 | CLNTN N2 | 69 | 8.2098 | 8.2465 | 0.0367
ASGI-2018-003 | 03 CENTRAL | 541304 | URICHTP2 | 69 | 3.2326 | 3.3197 | 0.0871
ASGI-2018-003 | 03 CENTRAL | 541305 | URICH 2 | 69 | 2.3157 | 2.3604 | 0.0447
ASGI-2018-003 | 03 CENTRAL | 541306 | APCITY 2 | 69 | 2.5429 | 2.7034 | 0.1605
ASGI-2018-003 | 03 CENTRAL | 541307 | NEVPLT 2 | 69 | 5.2971 | 5.3391 | 0.042
ASGI-2018-003 | 03 CENTRAL | 541308 | NEVADA 2 | 69 | 5.7079 | 5.7565 | 0.0486
ASGI-2018-003 | 03 CENTRAL | 541309 | METZ 2 | 69 | 4.225 | 4.2513 | 0.0263
ASGI-2018-003 | 03 CENTRAL | 541310 | 3M 2 | 69 | 3.7743 | 3.7954 | 0.0211
ASGI-2018-003 | 03 CENTRAL | 541311 | NEVJCT 2 | 69 | 4.0759 | 4.101 | 0.0251
ASGI-2018-003 | 03 CENTRAL | 541320 | CLNTN S2 | 69 | 8.4774 | 8.5243 | 0.0469
ASGI-2018-003 | 03 CENTRAL | 541383 | FAYETVLTP2 | 69 | 4.9987 | 4.9994 | 0.0007
ASGI-2018-003 | 03 CENTRAL | 541385 | CNTRVIEW2 | 69 | 5.1848 | 5.1859 | 0.0011
ASGI-2018-003 | 03 CENTRAL | 541499 | SHELDON_69 | 69 | 1.7422 | 1.7466 | 0.0044
ASGI-2018-003 | 03 CENTRAL | 762361 | ASGI-2018-00 | 69 | 2.5429 | 2.7033 | 0.1604
ASGI-2018-003 | 03 CENTRAL | 762372 | ASGI-2018-00 | 69 | 4.222 | 4.2483 | 0.0263
ASGI-2018-006 | 03 CENTRAL | 300070 | 5CLARK | 161 | 8.1874 | 8.2114 | 0.024
ASGI-2018-006 | 03 CENTRAL | 300118 | 5STKAEC | 161 | 9.2542 | 9.2606 | 0.0064
ASGI-2018-006 | 03 CENTRAL | 300645 | 2BRONA | 69 | 2.2562 | 2.2565 | 0.0003
ASGI-2018-006 | 03 CENTRAL | 300651 | 2LAMR | 69 | 10.1382 | 10.1416 | 0.0034
ASGI-2018-006 | 03 CENTRAL | 300652 | 2LAMRCTS | 69 | 3.9466 | 3.9472 | 0.0006
ASGI-2018-006 | 03 CENTRAL | 300654 | 2MILO | 69 | 5.4601 | 5.4621 | 0.002
ASGI-2018-006 | 03 CENTRAL | 300685 | 2LAMARPT | 69 | 8.5596 | 8.562 | 0.0024
ASGI-2018-006 | 03 CENTRAL | 300689 | 2BUTLER | 69 | 6.0465 | 6.049 | 0.0025
ASGI-2018-006 | 03 CENTRAL | 300690 | 2BUTLERE | 69 | 4.8383 | 4.8398 | 0.0015
ASGI-2018-006 | 03 CENTRAL | 300697 | 2CRESTH | 69 | 3.278 | 3.2786 | 0.0006
ASGI-2018-006 | 03 CENTRAL | 300707 | 2PL GAP | 69 | 4.3342 | 4.3355 | 0.0013
ASGI-2018-006 | 03 CENTRAL | 300793 | 5HYDERHL | 161 | 8.5908 | 8.5979 | 0.0071
ASGI-2018-006 | 03 CENTRAL | 300794 | 5LAMAR | 161 | 8.913 | 8.9213 | 0.0083
ASGI-2018-006 | 03 CENTRAL | 300798 | 2HYDERHL | 69 | 8.5522 | 8.5545 | 0.0023
ASGI-2018-006 | 03 CENTRAL | 300802 | 2CLARK | 69 | 6.7113 | 6.7149 | 0.0036
ASGI-2018-006 | 03 CENTRAL | 300814 | 2WALKER | 69 | 5.2124 | 5.2141 | 0.0017
ASGI-2018-006 | 03 CENTRAL | 300950 | 5JASPER | 161 | 13.0014 | 13.0066 | 0.0052
ASGI-2018-006 | 03 CENTRAL | 301342 | 5BUTLER | 161 | 6.9693 | 6.9821 | 0.0128
ASGI-2018-006 | 03 CENTRAL | 503507 | 2BUTLEREGEN | 69 | 4.8357 | 4.8372 | 0.0015
ASGI-2018-006 | 03 CENTRAL | 541138 | CLNTPLT_CAP2 | 69 | 8.5576 | 8.5618 | 0.0042
ASGI-2018-006 | 03 CENTRAL | 541207 | ARCHIE 5 | 161 | 17.4695 | 17.4781 | 0.0086
ASGI-2018-006 | 03 CENTRAL | 541208 | NEVADA 5 | 161 | 6.3049 | 6.3468 | 0.0419
ASGI-2018-006 | 03 CENTRAL | 541240 | ADRIAN 5 | 161 | 8.6503 | 8.6596 | 0.0093
ASGI-2018-006 | 03 CENTRAL | 541300 | POSTOAK2 | 69 | 4.3964 | 4.3968 | 0.0004
ASGI-2018-006 | 03 CENTRAL | 541301 | CLNTPLT2 | 69 | 8.743 | 8.7473 | 0.0043
ASGI-2018-006 | 03 CENTRAL | 541302 | CLNTGRN2 | 69 | 8.4653 | 8.469 | 0.0037
ASGI-2018-006 | 03 CENTRAL | 541304 | URICHTP2 | 69 | 3.3144 | 3.3197 | 0.0053
ASGI-2018-006 | 03 CENTRAL | 541305 | URICH 2 | 69 | 2.3577 | 2.3604 | 0.0027
ASGI-2018-006 | 03 CENTRAL | 541306 | APCITY 2 | 69 | 2.6929 | 2.7034 | 0.0105
ASGI-2018-006 | 03 CENTRAL | 541307 | NEVPLT 2 | 69 | 5.1932 | 5.3391 | 0.1459
ASGI-2018-006 | 03 CENTRAL | 541308 | NEVADA 2 | 69 | 5.5876 | 5.7565 | 0.1689
ASGI-2018-006 | 03 CENTRAL | 541309 | METZ 2 | 69 | 4.082 | 4.2513 | 0.1693
ASGI-2018-006 | 03 CENTRAL | 541310 | 3M 2 | 69 | 3.6593 | 3.7954 | 0.1361
ASGI-2018-006 | 03 CENTRAL | 541311 | NEVJCT 2 | 69 | 4.0141 | 4.101 | 0.0869
ASGI-2018-006 | 03 CENTRAL | 541320 | CLNTN S2 | 69 | 8.5207 | 8.5243 | 0.0036
ASGI-2018-006 | 03 CENTRAL | 541499 | SHELDON_69 | 69 | 1.7315 | 1.7466 | 0.0151
ASGI-2018-006 | 03 CENTRAL | 762361 | ASGI-2018-00 | 69 | 2.6929 | 2.7033 | 0.0104
ASGI-2018-006 | 03 CENTRAL | 762372 | ASGI-2018-00 | 69 | 4.079 | 4.2483 | 0.1693
ASGI-2018-007 | 03 CENTRAL | 41453 | J1145 SUB | 345 | 24.3648 | 24.3673 | 0.0025
ASGI-2018-007 | 03 CENTRAL | 44882 | J1488_INV | 345 | 22.9054 | 22.9076 | 0.0022
ASGI-2018-007 | 03 CENTRAL | 44887 | J1490_INV | 345 | 23.0219 | 23.0241 | 0.0022
ASGI-2018-007 | 03 CENTRAL | 44888 | J1490_POI | 345 | 24.3648 | 24.3673 | 0.0025
ASGI-2018-007 | 03 CENTRAL | 300043 | 7KINGDM | 345 | 19.9547 | 19.957 | 0.0023
ASGI-2018-007 | 03 CENTRAL | 300044 | 7MCCRED | 345 | 24.9434 | 24.9469 | 0.0035
ASGI-2018-007 | 03 CENTRAL | 300049 | 7THOMHL | 345 | 15.4751 | 15.4846 | 0.0095
ASGI-2018-007 | 03 CENTRAL | 300066 | 5HIGBEEB1 | 161 | 12.9575 | 12.9663 | 0.0088
ASGI-2018-007 | 03 CENTRAL | 300082 | 5GEORGE | 161 | 8.2362 | 8.2392 | 0.003
ASGI-2018-007 | 03 CENTRAL | 300098 | 5MOCITYB2 | 161 | 19.5372 | 19.5388 | 0.0016
ASGI-2018-007 | 03 CENTRAL | 300105 | 5NORTON | 161 | 6.6999 | 6.7094 | 0.0095
ASGI-2018-007 | 03 CENTRAL | 300120 | 5THMHILB1 | 161 | 32.0776 | 32.1145 | 0.0369
ASGI-2018-007 | 03 CENTRAL | 300126 | 5MOBTAP | 161 | 16.0581 | 16.0796 | 0.0215
ASGI-2018-007 | 03 CENTRAL | 300132 | 5THMHLB2 | 161 | 32.2222 | 32.2594 | 0.0372
ASGI-2018-007 | 03 CENTRAL | 300133 | 5THMHLB3 | 161 | 32.1243 | 32.1611 | 0.0368
ASGI-2018-007 | 03 CENTRAL | 300172 | 2TMHILL | 69 | 23.6618 | 23.6693 | 0.0075
ASGI-2018-007 | 03 CENTRAL | 300201 | 2INGROV | 69 | 3.0059 | 3.0059 | 0
ASGI-2018-007 | 03 CENTRAL | 300207 | 5MEADVLB1 | 161 | 5.1346 | 5.135 | 0.0004
ASGI-2018-007 | 03 CENTRAL | 300381 | 5BEVIER | 161 | 7.9444 | 7.9463 | 0.0019
ASGI-2018-007 | 03 CENTRAL | 300387 | 2BEVIER | 69 | 10.0651 | 10.066 | 0.0009
ASGI-2018-007 | 03 CENTRAL | 300389 | 2BYNUMV | 69 | 5.4196 | 5.4199 | 0.0003
ASGI-2018-007 | 03 CENTRAL | 300405 | 2MCNPLT | 69 | 7.126 | 7.1265 | 0.0005
ASGI-2018-007 | 03 CENTRAL | 300499 | 5HINTON | 161 | 9.2971 | 9.2992 | 0.0021
ASGI-2018-007 | 03 CENTRAL | 300500 | 5HUNTSDL | 161 | 11.0199 | 11.0209 | 0.001
ASGI-2018-007 | 03 CENTRAL | 300505 | 2STURGN | 69 | 7.3947 | 7.3951 | 0.0004
ASGI-2018-007 | 03 CENTRAL | 300508 | 5STURGN | 161 | 6.7205 | 6.7227 | 0.0022
ASGI-2018-007 | 03 CENTRAL | 300531 | 2GEORGE | 69 | 7.8724 | 7.8735 | 0.0011
ASGI-2018-007 | 03 CENTRAL | 300535 | 2MALTAB | 69 | 3.0028 | 3.0033 | 0.0005
ASGI-2018-007 | 03 CENTRAL | 300536 | 2MALTAJ | 69 | 4.9633 | 4.9646 | 0.0013
ASGI-2018-007 | 03 CENTRAL | 300537 | 2MARSHL | 69 | 3.9811 | 3.9818 | 0.0007
ASGI-2018-007 | 03 CENTRAL | 300538 | 2NAPTON | 69 | 3.7868 | 3.7875 | 0.0007
ASGI-2018-007 | 03 CENTRAL | 300540 | 2NORTON | 69 | 6.1209 | 6.1231 | 0.0022
ASGI-2018-007 | 03 CENTRAL | 300560 | 2PILOTG | 69 | 3.0434 | 3.0436 | 0.0002
ASGI-2018-007 | 03 CENTRAL | 300615 | 2YATES | 69 | 5.2787 | 5.279 | 0.0003
ASGI-2018-007 | 03 CENTRAL | 300953 | 5HARRSBRG | 161 | 9.3772 | 9.3802 | 0.003
ASGI-2018-007 | 03 CENTRAL | 301318 | 2THMINTP | 69 | 19.0266 | 19.0314 | 0.0048
ASGI-2018-007 | 03 CENTRAL | 301443 | 5THMHLB4 | 161 | 31.8399 | 31.8773 | 0.0374
ASGI-2018-007 | 03 CENTRAL | 301489 | 5MCBAINB2 | 161 | 14.3363 | 14.3377 | 0.0014
ASGI-2018-007 | 03 CENTRAL | 301494 | 5HIGBEEB2 | 161 | 12.9577 | 12.9665 | 0.0088
ASGI-2018-007 | 03 CENTRAL | 301503 | 7THOMHLGSU3 | 345 | 15.3506 | 15.3599 | 0.0093
ASGI-2018-007 | 03 CENTRAL | 301504 | 5THOMHLGSU1 | 161 | 31.0446 | 31.0787 | 0.0341
ASGI-2018-007 | 03 CENTRAL | 301505 | 5THOMHLGSU2 | 161 | 31.0191 | 31.0533 | 0.0342
ASGI-2018-007 | 03 CENTRAL | 301506 | 5THOMHLXF3 | 161 | 31.5952 | 31.6304 | 0.0352
ASGI-2018-007 | 03 CENTRAL | 301507 | 5THOMHLU3SU | 161 | 30.5159 | 30.5491 | 0.0332
ASGI-2018-007 | 03 CENTRAL | 301508 | 5THOMHLXF1 | 161 | 30.7418 | 30.7757 | 0.0339
ASGI-2018-007 | 03 CENTRAL | 301509 | 2THOMHLXF1 | 69 | 23.3738 | 23.3812 | 0.0074
ASGI-2018-007 | 03 CENTRAL | 301510 | 5THOMHLXF4 | 161 | 31.5268 | 31.5632 | 0.0364
ASGI-2018-007 | 03 CENTRAL | 301511 | 5THMHILTFERB | 161 | 31.8053 | 31.8416 | 0.0363
ASGI-2018-007 | 03 CENTRAL | 301562 | 5MEADVLB2 | 161 | 5.1342 | 5.1346 | 0.0004
ASGI-2018-007 | 03 CENTRAL | 301567 | 5NORTONTP | 161 | 6.2145 | 6.2213 | 0.0068
ASGI-2018-007 | 03 CENTRAL | 301623 | 2BEVIERTP | 69 | 10.0326 | 10.0336 | 0.001
ASGI-2018-007 | 03 CENTRAL | 301624 | 2BEVIERLD | 69 | 9.9198 | 9.9207 | 0.0009
ASGI-2018-007 | 03 CENTRAL | 343001 | 5BOLSTAD | 161 | 10.4516 | 10.4533 | 0.0017
ASGI-2018-007 | 03 CENTRAL | 343004 | 5PERCHE | 161 | 9.7975 | 9.7983 | 0.0008
ASGI-2018-007 | 03 CENTRAL | 343005 | 2PERCHE | 69 | 15.5251 | 15.5259 | 0.0008
ASGI-2018-007 | 03 CENTRAL | 343052 | 2PERCHE2 | 69 | 15.5251 | 15.5259 | 0.0008
ASGI-2018-007 | 03 CENTRAL | 344001 | 5ADAIR2 | 161 | 15.3511 | 15.3516 | 0.0005
ASGI-2018-007 | 03 CENTRAL | 344004 | 5ADAIR1 | 161 | 15.3511 | 15.3516 | 0.0005
ASGI-2018-007 | 03 CENTRAL | 344041 | 5LOYMART 2 | 161 | 10.9485 | 10.949 | 0.0005
ASGI-2018-007 | 03 CENTRAL | 344233 | 5CALIF UE 1 | 161 | 10.8955 | 10.8961 | 0.0006
ASGI-2018-007 | 03 CENTRAL | 344234 | 5CALIF UE 2 | 161 | 10.8955 | 10.8961 | 0.0006
ASGI-2018-007 | 03 CENTRAL | 344557 | 5MAURER 1 | 161 | 8.2642 | 8.2655 | 0.0013
ASGI-2018-007 | 03 CENTRAL | 344558 | 5MAURER 2 | 161 | 8.2642 | 8.2655 | 0.0013
ASGI-2018-007 | 03 CENTRAL | 345071 | 5MCBAIN T | 161 | 14.9322 | 14.9337 | 0.0015
ASGI-2018-007 | 03 CENTRAL | 345221 | 5MOBERLY | 161 | 16.0477 | 16.0691 | 0.0214
ASGI-2018-007 | 03 CENTRAL | 345222 | 2MOBERLY | 69 | 8.0501 | 8.0519 | 0.0018
ASGI-2018-007 | 03 CENTRAL | 345408 | 7OVERTON | 345 | 14.5921 | 14.5939 | 0.0018
ASGI-2018-007 | 03 CENTRAL | 345409 | 5OVERTON | 161 | 22.2985 | 22.3028 | 0.0043
ASGI-2018-007 | 03 CENTRAL | 345411 | 5OVERTON 2 | 161 | 22.2985 | 22.3028 | 0.0043
ASGI-2018-007 | 03 CENTRAL | 346005 | 2ADAIR 1 | 69 | 5.6112 | 5.6113 | 0.0001
ASGI-2018-007 | 03 CENTRAL | 346025 | 2BRKFLD | 69 | 1.855 | 1.8551 | 0.0001
ASGI-2018-007 | 03 CENTRAL | 346048 | 2MAURER | 69 | 3.301 | 3.3011 | 0.0001
ASGI-2018-007 | 03 CENTRAL | 346065 | 2HARRISON | 69 | 3.2102 | 3.2102 | 0
ASGI-2018-007 | 03 CENTRAL | 346067 | 2HORNER | 69 | 6.6845 | 6.6856 | 0.0011
ASGI-2018-007 | 03 CENTRAL | 346096 | 2MACON_AM | 69 | 1.6188 | 1.6188 | 0
ASGI-2018-007 | 03 CENTRAL | 346099 | 2MARCELIN | 69 | 1.8312 | 1.8312 | 0
ASGI-2018-007 | 03 CENTRAL | 346117 | 2OVERTON | 69 | 3.6987 | 3.6987 | 0
ASGI-2018-007 | 03 CENTRAL | 346142 | 2SINNOCK | 69 | 6.3186 | 6.3196 | 0.001
ASGI-2018-007 | 03 CENTRAL | 346168 | 2RTE EE | 69 | 3.7649 | 3.7652 | 0.0003
ASGI-2018-007 | 03 CENTRAL | 346169 | 2DUPONT | 69 | 6.9797 | 6.981 | 0.0013
ASGI-2018-007 | 03 CENTRAL | 346170 | 2ROTH TAP | 69 | 1.8432 | 1.8433 | 0.0001
ASGI-2018-007 | 03 CENTRAL | 346171 | 2SPRK TAP | 69 | 7.1963 | 7.1977 | 0.0014
ASGI-2018-007 | 03 CENTRAL | 541146 | SEDLIAW_CAP5 | 161 | 9.1191 | 9.1217 | 0.0026
ASGI-2018-007 | 03 CENTRAL | 541200 | PHILL 7 | 345 | 19.0852 | 19.0855 | 0.0003
ASGI-2018-007 | 03 CENTRAL | 541201 | SIBLEY 7 | 345 | 21.6502 | 21.6508 | 0.0006
ASGI-2018-007 | 03 CENTRAL | 541202 | SIBLEY 5 | 161 | 27.5882 | 27.5893 | 0.0011
ASGI-2018-007 | 03 CENTRAL | 541209 | SEDALIA5 | 161 | 9.6262 | 9.6291 | 0.0029
ASGI-2018-007 | 03 CENTRAL | 541241 | SEDEAST5 | 161 | 7.6669 | 7.6685 | 0.0016
ASGI-2018-007 | 03 CENTRAL | 541395 | NUCOR5 | 161 | 7.194 | 7.1953 | 0.0013
ASGI-2018-007 | 03 CENTRAL | 541414 | SIB REA1 | 345 | 19.2809 | 19.2814 | 0.0005
ASGI-2018-007 | 03 CENTRAL | 541500 | KETCHEM7 | 345 | 8.2418 | 8.2418 | 0
ASGI-2018-007 | 03 CENTRAL | 541501 | OSBORN7 | 345 | 7.3403 | 7.3403 | 0
ASGI-2018-007 | 03 CENTRAL | 542972 | HAWTH 7 | 345 | 23.7336 | 23.7341 | 0.0005
ASGI-2018-007 | 03 CENTRAL | 543012 | SWAVCAP2 | 69 | 3.8733 | 3.8739 | 0.0006
ASGI-2018-007 | 03 CENTRAL | 543013 | SWAVCAP5 | 161 | 3.4272 | 3.4294 | 0.0022
ASGI-2018-007 | 03 CENTRAL | 543059 | MALTABN5 | 161 | 4.1153 | 4.1187 | 0.0034
ASGI-2018-007 | 03 CENTRAL | 543060 | CAROLTN5 | 161 | 4.5666 | 4.5712 | 0.0046
ASGI-2018-007 | 03 CENTRAL | 543061 | BRUNSWK5 | 161 | 5.8529 | 5.8649 | 0.012
ASGI-2018-007 | 03 CENTRAL | 543062 | SALSBRY5 | 161 | 12.0348 | 12.1076 | 0.0728
ASGI-2018-007 | 03 CENTRAL | 543063 | SWAVRLY5 | 161 | 3.4965 | 3.4988 | 0.0023
ASGI-2018-007 | 03 CENTRAL | 543064 | NORTON 5 | 161 | 6.7225 | 6.7322 | 0.0097
ASGI-2018-007 | 03 CENTRAL | 543070 | WEST---5 | 161 | 4.697 | 4.7017 | 0.0047
ASGI-2018-007 | 03 CENTRAL | 543071 | S EAST 5 | 161 | 4.8829 | 4.888 | 0.0051
ASGI-2018-007 | 03 CENTRAL | 543072 | MRSHLJT5 | 161 | 5.8704 | 5.8778 | 0.0074
ASGI-2018-007 | 03 CENTRAL | 543073 | MIAMI_ 5 | 161 | 4.7661 | 4.771 | 0.0049
ASGI-2018-007 | 03 CENTRAL | 543094 | SWAVRLY2 | 69 | 3.875 | 3.8756 | 0.0006
ASGI-2018-007 | 03 CENTRAL | 543101 | DOVER2 | 69 | 3.6657 | 3.6661 | 0.0004
ASGI-2018-007 | 03 CENTRAL | 543658 | DOVER_TAP2 | 69 | 3.8578 | 3.8583 | 0.0005
ASGI-2018-007 | 03 CENTRAL | 762383 | ASG-2018-007 | 161 | 12.0237 | 12.0965 | 0.0728
ASGI-2018-007 | 03 CENTRAL | 999101 | GI083 | 345 | 16.6863 | 16.6868 | 0.0005
ASGI-2018-007 | 03 CENTRAL | 999950 | GI-86_SUB | 69 | 7.5223 | 7.523 | 0.0007
ASGI-2018-010 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 17.3982 | 17.3988 | 0.0006
ASGI-2018-010 | 03 CENTRAL | 532769 | LANG 7 | 345 | 17.1991 | 17.1997 | 0.0006
ASGI-2018-010 | 03 CENTRAL | 532770 | MORRIS 7 | 345 | 13.1902 | 13.1905 | 0.0003
ASGI-2018-010 | 03 CENTRAL | 532772 | STRANGR7 | 345 | 28.4579 | 28.4608 | 0.0029
ASGI-2018-010 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 17.0353 | 17.0373 | 0.002
ASGI-2018-010 | 03 CENTRAL | 532775 | 87TH 7 | 345 | 22.5969 | 22.604 | 0.0071
ASGI-2018-010 | 03 CENTRAL | 532776 | READWF 7 | 345 | 14.4503 | 14.4507 | 0.0004
ASGI-2018-010 | 03 CENTRAL | 532793 | NEOSHO 7 | 345 | 18.172 | 18.1722 | 0.0002
ASGI-2018-010 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 18.6618 | 18.662 | 0.0002
ASGI-2018-010 | 03 CENTRAL | 532799 | WAVERLY7 | 345 | 16.5258 | 16.5261 | 0.0003
ASGI-2018-010 | 03 CENTRAL | 532802 | WAVERTX7 | 345 | 13.7778 | 13.778 | 0.0002
ASGI-2018-010 | 03 CENTRAL | 532803 | EXPEDITION7 | 345 | 10.9006 | 10.9007 | 0.0001
ASGI-2018-010 | 03 CENTRAL | 532851 | AUBURN 6 | 230 | 13.8251 | 13.8255 | 0.0004
ASGI-2018-010 | 03 CENTRAL | 532853 | LAWHILL6 | 230 | 14.0689 | 14.0693 | 0.0004
ASGI-2018-010 | 03 CENTRAL | 532854 | LEC U5 6 | 230 | 13.9375 | 13.9379 | 0.0004
ASGI-2018-010 | 03 CENTRAL | 532856 | SWISVAL6 | 230 | 22.0639 | 22.0654 | 0.0015
ASGI-2018-010 | 03 CENTRAL | 532857 | TECHILL6 | 230 | 11.109 | 11.1093 | 0.0003
ASGI-2018-010 | 03 CENTRAL | 532863 | MORRIS 6 | 230 | 14.333 | 14.3332 | 0.0002
ASGI-2018-010 | 03 CENTRAL | 532912 | EDWRDVL5 | 161 | 22.4108 | 22.4132 | 0.0024
ASGI-2018-010 | 03 CENTRAL | 533283 | 87TH 3 | 115 | 27.959 | 27.9617 | 0.0027
ASGI-2018-010 | 03 CENTRAL | 541200 | PHILL 7 | 345 | 19.0828 | 19.0855 | 0.0027
ASGI-2018-010 | 03 CENTRAL | 541341 | S.HARP 5 | 161 | 21.3619 | 21.3642 | 0.0023
ASGI-2018-010 | 03 CENTRAL | 541342 | PECULR 5 | 161 | 23.4061 | 23.4089 | 0.0028
ASGI-2018-010 | 03 CENTRAL | 541541 | LAC_LAKE_2 | 69 | 2.6766 | 2.6766 | 0
ASGI-2018-010 | 03 CENTRAL | 542945 | CRAIG_CAP 5 | 161 | 35.4913 | 35.5053 | 0.014
ASGI-2018-010 | 03 CENTRAL | 542947 | MERRIAM_CAP5 | 161 | 27.5488 | 27.5544 | 0.0056
ASGI-2018-010 | 03 CENTRAL | 542965 | W.GRDNR7 | 345 | 28.486 | 28.5039 | 0.0179
ASGI-2018-010 | 03 CENTRAL | 542966 | WGARDNR5 | 161 | 30.364 | 30.4469 | 0.0829
ASGI-2018-010 | 03 CENTRAL | 542968 | STILWEL7 | 345 | 25.9526 | 25.9619 | 0.0093
ASGI-2018-010 | 03 CENTRAL | 542969 | STILWEL5 | 161 | 40.9463 | 40.9619 | 0.0156
ASGI-2018-010 | 03 CENTRAL | 542977 | CRAIG 7 | 345 | 24.4007 | 24.4108 | 0.0101
ASGI-2018-010 | 03 CENTRAL | 542978 | CRAIG 5 | 161 | 44.6641 | 44.6862 | 0.0221
ASGI-2018-010 | 03 CENTRAL | 542979 | PFLUMM 5 | 161 | 30.3282 | 30.3373 | 0.0091
ASGI-2018-010 | 03 CENTRAL | 542981 | LACYGNE7 | 345 | 27.5236 | 27.5276 | 0.004
ASGI-2018-010 | 03 CENTRAL | 542994 | HICKMAN5 | 161 | 20.0994 | 20.1018 | 0.0024
ASGI-2018-010 | 03 CENTRAL | 543031 | SHWNMSN5 | 161 | 37.3326 | 37.3434 | 0.0108
ASGI-2018-010 | 03 CENTRAL | 543032 | MERRIAM5 | 161 | 32.7758 | 32.7837 | 0.0079
ASGI-2018-010 | 03 CENTRAL | 543036 | OLATHE 5 | 161 | 27.5765 | 27.5888 | 0.0123
ASGI-2018-010 | 03 CENTRAL | 543037 | QUARRY 5 | 161 | 16.292 | 16.3033 | 0.0113
ASGI-2018-010 | 03 CENTRAL | 543038 | LENEXA 5 | 161 | 37.9504 | 37.9649 | 0.0145
ASGI-2018-010 | 03 CENTRAL | 543040 | ROEPARK5 | 161 | 30.9122 | 30.9171 | 0.0049
ASGI-2018-010 | 03 CENTRAL | 543041 | SHAWNEE5 | 161 | 28.0559 | 28.0611 | 0.0052
ASGI-2018-010 | 03 CENTRAL | 543043 | MURLEN 5 | 161 | 18.5825 | 18.5916 | 0.0091
ASGI-2018-010 | 03 CENTRAL | 543044 | MOONLT 5 | 161 | 18.0218 | 18.0411 | 0.0193
ASGI-2018-010 | 03 CENTRAL | 543047 | OVERLPK5 | 161 | 33.0461 | 33.0559 | 0.0098
ASGI-2018-010 | 03 CENTRAL | 543048 | COLLEGE5 | 161 | 30.8829 | 30.8952 | 0.0123
ASGI-2018-010 | 03 CENTRAL | 543049 | CEDRCRK5 | 161 | 31.321 | 31.3364 | 0.0154
ASGI-2018-010 | 03 CENTRAL | 543050 | ANTIOCH5 | 161 | 23.2678 | 23.2739 | 0.0061
ASGI-2018-010 | 03 CENTRAL | 543052 | REEDER 5 | 161 | 21.5645 | 21.5686 | 0.0041
ASGI-2018-010 | 03 CENTRAL | 543053 | REDEL 5 | 161 | 25.1654 | 25.1701 | 0.0047
ASGI-2018-010 | 03 CENTRAL | 543054 | CEDARNL5 | 161 | 10.8826 | 10.8932 | 0.0106
ASGI-2018-010 | 03 CENTRAL | 543055 | SEOTTWA5 | 161 | 7.5569 | 7.5893 | 0.0324
ASGI-2018-010 | 03 CENTRAL | 543056 | GARDNER5 | 161 | 16.7844 | 16.8011 | 0.0167
ASGI-2018-010 | 03 CENTRAL | 543057 | BUCYRUS5 | 161 | 21.0149 | 21.0225 | 0.0076
ASGI-2018-010 | 03 CENTRAL | 543058 | NLOUISB5 | 161 | 9.3285 | 9.33 | 0.0015
ASGI-2018-010 | 03 CENTRAL | 543065 | CNTRVIL5 | 161 | 6.1619 | 6.1634 | 0.0015
ASGI-2018-010 | 03 CENTRAL | 543066 | S.OTTWA5 | 161 | 7.5395 | 7.5673 | 0.0278
ASGI-2018-010 | 03 CENTRAL | 543067 | CENTENL5 | 161 | 10.7709 | 10.7798 | 0.0089
ASGI-2018-010 | 03 CENTRAL | 543068 | WAGSTAF5 | 161 | 14.48 | 14.4863 | 0.0063
ASGI-2018-010 | 03 CENTRAL | 543069 | PAOLA 5 | 161 | 10.8509 | 10.8618 | 0.0109
ASGI-2018-010 | 03 CENTRAL | 543077 | PLSTVAL5 | 161 | 10.2477 | 10.368 | 0.1203
ASGI-2018-010 | 03 CENTRAL | 543105 | BULLCRK5 | 161 | 29.433 | 29.5093 | 0.0763
ASGI-2018-010 | 03 CENTRAL | 543112 | OSAWAT 5 | 161 | 10.7597 | 10.7705 | 0.0108
ASGI-2018-010 | 03 CENTRAL | 543126 | LACKMAN5 | 161 | 13.8574 | 13.8591 | 0.0017
ASGI-2018-010 | 03 CENTRAL | 543132 | BNSF 5 | 161 | 22.3504 | 22.3887 | 0.0383
ASGI-2018-010 | 03 CENTRAL | 543135 | OSAWTM_CAP5 | 161 | 10.1289 | 10.1384 | 0.0095
ASGI-2018-010 | 03 CENTRAL | 543166 | NEASTOTTW5 | 161 | 6.5157 | 6.5398 | 0.0241
ASGI-2018-010 | 03 CENTRAL | 543629 | LACYGNE11_7 | 345 | 26.8021 | 26.8059 | 0.0038
ASGI-2018-010 | 03 CENTRAL | 543632 | LACYGNE22_7 | 345 | 26.8021 | 26.8059 | 0.0038
ASGI-2018-010 | 03 CENTRAL | 543650 | DAKOTA_5 | 161 | 6.8938 | 6.8946 | 0.0008
ASGI-2018-010 | 03 CENTRAL | 543651 | PRQN_WIND5 | 161 | 5.4351 | 5.4355 | 0.0004
ASGI-2018-010 | 03 CENTRAL | 543659 | LACYGNE2 | 69 | 2.8155 | 2.8155 | 0
ASGI-2018-010 | 03 CENTRAL | 543667 | LAC3_STAR7 | 345 | 0.6733 | 0.6733 | 0
ASGI-2018-010 | 03 CENTRAL | 543669 | LAC8_STAR7 | 345 | 0.6449 | 0.6449 | 0
ASGI-2018-010 | 03 CENTRAL | 546651 | BARBER 5 | 161 | 30.901 | 30.905 | 0.004
ASGI-2018-010 | 03 CENTRAL | 546655 | KAW W 5 | 161 | 24.3566 | 24.3591 | 0.0025
ASGI-2018-010 | 03 CENTRAL | 546722 | MAYSOTH5 | 161 | 22.6501 | 22.652 | 0.0019
ASGI-2018-010 | 03 CENTRAL | 546742 | METRO 5 | 161 | 27.6361 | 27.6399 | 0.0038
ASGI-2018-010 | 03 CENTRAL | 583850 | GEN-2014-001 | 345 | 6.7825 | 6.7825 | 0
ASGI-2018-010 | 03 CENTRAL | 583859 | GEN-2014-001 | 345 | 8.4417 | 8.4418 | 0.0001
ASGI-2018-010 | 03 CENTRAL | 588240 | GEN-2016-149 | 345 | 4.4343 | 4.4343 | 0
ASGI-2018-010 | 03 CENTRAL | 588250 | GEN-2016-174 | 345 | 13.3775 | 13.378 | 0.0005
ASGI-2018-010 | 03 CENTRAL | 588260 | GEN-2016-176 | 345 | 8.2369 | 8.2371 | 0.0002
ASGI-2018-010 | 03 CENTRAL | 588270 | GEN-2016-150 | 345 | 4.1248 | 4.1248 | 0
ASGI-2018-010 | 03 CENTRAL | 760914 | GEN-2017-209 | 345 | 19.1881 | 19.1898 | 0.0017
ASGI-2018-010 | 03 CENTRAL | 760921 | G17-209-TAP | 345 | 19.6893 | 19.691 | 0.0017
ASGI-2018-010 | 03 CENTRAL | 761271 | GEN-2017-108 | 161 | 13.3127 | 13.313 | 0.0003
ASGI-2018-010 | 03 CENTRAL | 761278 | G17-108-TAP | 161 | 13.3127 | 13.313 | 0.0003
ASGI-2018-010 | 03 CENTRAL | 762279 | GEN-2017-195 | 345 | 28.4086 | 28.4265 | 0.0179
ASGI-2018-010 | 03 CENTRAL | 762405 | ASG-2018-010 | 161 | 3.318 | 3.4283 | 0.1103
ASGI-2018-010 | 03 CENTRAL | 762416 | ASG-2018-011 | 161 | 3.078 | 3.0823 | 0.0043
ASGI-2018-010 | 03 CENTRAL | 762680 | GEN-2018-032 | 345 | 11.9865 | 11.9867 | 0.0002
ASGI-2018-011 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 17.0359 | 17.0373 | 0.0014
ASGI-2018-011 | 03 CENTRAL | 532934 | MARMTNE5 | 161 | 8.2038 | 8.2057 | 0.0019
ASGI-2018-011 | 03 CENTRAL | 532935 | MARMTNW5 | 161 | 8.2006 | 8.2024 | 0.0018
ASGI-2018-011 | 03 CENTRAL | 541541 | LAC_LAKE_2 | 69 | 2.6766 | 2.6766 | 0
ASGI-2018-011 | 03 CENTRAL | 542945 | CRAIG_CAP 5 | 161 | 35.4959 | 35.5053 | 0.0094
ASGI-2018-011 | 03 CENTRAL | 542965 | W.GRDNR7 | 345 | 28.4918 | 28.5039 | 0.0121
ASGI-2018-011 | 03 CENTRAL | 542966 | WGARDNR5 | 161 | 30.4067 | 30.4469 | 0.0402
ASGI-2018-011 | 03 CENTRAL | 542968 | STILWEL7 | 345 | 25.9528 | 25.9619 | 0.0091
ASGI-2018-011 | 03 CENTRAL | 542969 | STILWEL5 | 161 | 40.9395 | 40.9619 | 0.0224
ASGI-2018-011 | 03 CENTRAL | 542977 | CRAIG 7 | 345 | 24.4038 | 24.4108 | 0.007
ASGI-2018-011 | 03 CENTRAL | 542978 | CRAIG 5 | 161 | 44.6713 | 44.6862 | 0.0149
ASGI-2018-011 | 03 CENTRAL | 542981 | LACYGNE7 | 345 | 27.5242 | 27.5276 | 0.0034
ASGI-2018-011 | 03 CENTRAL | 543031 | SHWNMSN5 | 161 | 37.3359 | 37.3434 | 0.0075
ASGI-2018-011 | 03 CENTRAL | 543044 | MOONLT 5 | 161 | 18.0312 | 18.0411 | 0.0099
ASGI-2018-011 | 03 CENTRAL | 543049 | CEDRCRK5 | 161 | 31.3269 | 31.3364 | 0.0095
ASGI-2018-011 | 03 CENTRAL | 543054 | CEDARNL5 | 161 | 10.8881 | 10.8932 | 0.0051
ASGI-2018-011 | 03 CENTRAL | 543055 | SEOTTWA5 | 161 | 7.4862 | 7.5893 | 0.1031
ASGI-2018-011 | 03 CENTRAL | 543056 | GARDNER5 | 161 | 16.7925 | 16.8011 | 0.0086
ASGI-2018-011 | 03 CENTRAL | 543057 | BUCYRUS5 | 161 | 21.0052 | 21.0225 | 0.0173
ASGI-2018-011 | 03 CENTRAL | 543058 | NLOUISB5 | 161 | 9.3266 | 9.33 | 0.0034
ASGI-2018-011 | 03 CENTRAL | 543065 | CNTRVIL5 | 161 | 6.1574 | 6.1634 | 0.006
ASGI-2018-011 | 03 CENTRAL | 543066 | S.OTTWA5 | 161 | 7.4472 | 7.5673 | 0.1201
ASGI-2018-011 | 03 CENTRAL | 543067 | CENTENL5 | 161 | 10.7458 | 10.7798 | 0.034
ASGI-2018-011 | 03 CENTRAL | 543068 | WAGSTAF5 | 161 | 14.4678 | 14.4863 | 0.0185
ASGI-2018-011 | 03 CENTRAL | 543069 | PAOLA 5 | 161 | 10.8188 | 10.8618 | 0.043
ASGI-2018-011 | 03 CENTRAL | 543077 | PLSTVAL5 | 161 | 10.3159 | 10.368 | 0.0521
ASGI-2018-011 | 03 CENTRAL | 543105 | BULLCRK5 | 161 | 29.4723 | 29.5093 | 0.037
ASGI-2018-011 | 03 CENTRAL | 543112 | OSAWAT 5 | 161 | 10.7283 | 10.7705 | 0.0422
ASGI-2018-011 | 03 CENTRAL | 543132 | BNSF 5 | 161 | 22.3697 | 22.3887 | 0.019
ASGI-2018-011 | 03 CENTRAL | 543135 | OSAWTM_CAP5 | 161 | 10.101 | 10.1384 | 0.0374
ASGI-2018-011 | 03 CENTRAL | 543166 | NEASTOTTW5 | 161 | 6.4631 | 6.5398 | 0.0767
ASGI-2018-011 | 03 CENTRAL | 543629 | LACYGNE11_7 | 345 | 26.8026 | 26.8059 | 0.0033
ASGI-2018-011 | 03 CENTRAL | 543632 | LACYGNE22_7 | 345 | 26.8026 | 26.8059 | 0.0033
ASGI-2018-011 | 03 CENTRAL | 543650 | DAKOTA_5 | 161 | 6.8917 | 6.8946 | 0.0029
ASGI-2018-011 | 03 CENTRAL | 543651 | PRQN_WIND5 | 161 | 5.4339 | 5.4355 | 0.0016
ASGI-2018-011 | 03 CENTRAL | 543659 | LACYGNE2 | 69 | 2.8155 | 2.8155 | 0
ASGI-2018-011 | 03 CENTRAL | 543667 | LAC3_STAR7 | 345 | 0.6733 | 0.6733 | 0
ASGI-2018-011 | 03 CENTRAL | 543669 | LAC8_STAR7 | 345 | 0.6449 | 0.6449 | 0
ASGI-2018-011 | 03 CENTRAL | 588500 | GEN-2017-005 | 161 | 6.9005 | 6.9013 | 0.0008
ASGI-2018-011 | 03 CENTRAL | 588504 | G17-005-TAP | 161 | 6.984 | 6.9847 | 0.0007
ASGI-2018-011 | 03 CENTRAL | 762279 | GEN-2017-195 | 345 | 28.4144 | 28.4265 | 0.0121
ASGI-2018-011 | 03 CENTRAL | 762416 | ASG-2018-011 | 161 | 2.9702 | 3.0823 | 0.1121
GEN-2018-009 | 03 CENTRAL | 522912 | Y ROAD 3 | 115 | 4.5262 | 4.5364 | 0.0102
GEN-2018-009 | 03 CENTRAL | 522926 | BOURK 2 | 69 | 8.1767 | 8.1966 | 0.0199
GEN-2018-009 | 03 CENTRAL | 522930 | RED DEVIL 3 | 115 | 2.3944 | 2.3972 | 0.0028
GEN-2018-009 | 03 CENTRAL | 522931 | REED 2 | 69 | 8.1767 | 8.1966 | 0.0199
GEN-2018-009 | 03 CENTRAL | 522935 | GOODWELL 3 | 115 | 3.4676 | 3.4736 | 0.006
GEN-2018-009 | 03 CENTRAL | 523089 | TC-TXCOUNTY2 | 69 | 8.1767 | 8.1966 | 0.0199
GEN-2018-009 | 03 CENTRAL | 523090 | TEXAS_CNTY 3 | 115 | 7.91 | 7.9415 | 0.0315
GEN-2018-009 | 03 CENTRAL | 523093 | HITCHLAND 3 | 115 | 16.0843 | 16.1234 | 0.0391
GEN-2018-009 | 03 CENTRAL | 523097 | HITCHLAND 7 | 345 | 11.8985 | 11.9312 | 0.0327
GEN-2018-009 | 03 CENTRAL | 523101 | NOBLE_WND 7 | 345 | 11.8598 | 11.8923 | 0.0325
GEN-2018-009 | 03 CENTRAL | 523103 | NOBLE_WND 3 | 115 | 9.2757 | 9.2823 | 0.0066
GEN-2018-009 | 03 CENTRAL | 523106 | TXPHSF 3 | 115 | 4.2387 | 4.2752 | 0.0365
GEN-2018-009 | 03 CENTRAL | 523111 | NOVUS1 3 | 115 | 6.5894 | 6.5927 | 0.0033
GEN-2018-009 | 03 CENTRAL | 523112 | NOVUS1 7 | 345 | 11.6995 | 11.7312 | 0.0317
GEN-2018-009 | 03 CENTRAL | 523113 | TC-MCMURRY 3 | 115 | 6.2169 | 6.2351 | 0.0182
GEN-2018-009 | 03 CENTRAL | 523118 | BUFF_DUNES 7 | 345 | 6.7821 | 6.7936 | 0.0115
GEN-2018-009 | 03 CENTRAL | 523130 | GRPLNS-HV4-3 | 115 | 6.3416 | 6.3446 | 0.003
GEN-2018-009 | 03 CENTRAL | 523131 | GRPLNS-HV2-3 | 115 | 8.5048 | 8.5103 | 0.0055
GEN-2018-009 | 03 CENTRAL | 523174 | GOODWELLWND3 | 115 | 6.6677 | 6.6722 | 0.0045
GEN-2018-009 | 03 CENTRAL | 523215 | GEN-2011-022 | 345 | 8.4145 | 8.4309 | 0.0164
GEN-2018-009 | 03 CENTRAL | 523823 | CARPENTER 7 | 345 | 6.5166 | 6.5644 | 0.0478
GEN-2018-009 | 03 CENTRAL | 523853 | FINNEY 7 | 345 | 10.4003 | 10.4315 | 0.0312
GEN-2018-009 | 03 CENTRAL | 531374 | HASKELL3 | 115 | 5.0564 | 5.2195 | 0.1631
GEN-2018-009 | 03 CENTRAL | 531375 | PUCKET 3 | 115 | 5.0572 | 5.0713 | 0.0141
GEN-2018-009 | 03 CENTRAL | 531377 | HICKOCK2 | 69 | 2.8823 | 2.8868 | 0.0045
GEN-2018-009 | 03 CENTRAL | 531378 | HICKOCK3 | 115 | 5.6386 | 5.6677 | 0.0291
GEN-2018-009 | 03 CENTRAL | 531380 | HUGOTON2 | 69 | 2.9746 | 2.9817 | 0.0071
GEN-2018-009 | 03 CENTRAL | 531384 | MOSCOW 2 | 69 | 2.2372 | 2.2418 | 0.0046
GEN-2018-009 | 03 CENTRAL | 531385 | MOSCOWT2 | 69 | 2.3532 | 2.3583 | 0.0051
GEN-2018-009 | 03 CENTRAL | 531388 | NORTH6 2 | 69 | 2.6465 | 2.653 | 0.0065
GEN-2018-009 | 03 CENTRAL | 531389 | NORTH6T2 | 69 | 3.0954 | 3.1044 | 0.009
GEN-2018-009 | 03 CENTRAL | 531390 | PIONEER2 | 69 | 4.0729 | 4.0805 | 0.0076
GEN-2018-009 | 03 CENTRAL | 531391 | PIONEER3 | 115 | 6.1079 | 6.1365 | 0.0286
GEN-2018-009 | 03 CENTRAL | 531392 | PIONTAP3 | 115 | 6.8826 | 6.9879 | 0.1053
GEN-2018-009 | 03 CENTRAL | 531394 | PRAXAIR2 | 69 | 2.5633 | 2.5669 | 0.0036
GEN-2018-009 | 03 CENTRAL | 531395 | ROLLA 2 | 115 | 2.6407 | 2.65 | 0.0093
GEN-2018-009 | 03 CENTRAL | 531398 | SUBLETE3 | 115 | 6.1544 | 6.2385 | 0.0841
GEN-2018-009 | 03 CENTRAL | 531400 | PK_GOAB3 | 115 | 5.0712 | 5.0854 | 0.0142
GEN-2018-009 | 03 CENTRAL | 531401 | ULU E 2 | 69 | 3.819 | 3.8257 | 0.0067
GEN-2018-009 | 03 CENTRAL | 531402 | ULU NW 2 | 69 | 3.2183 | 3.223 | 0.0047
GEN-2018-009 | 03 CENTRAL | 531403 | ULU PLT2 | 69 | 3.1336 | 3.1381 | 0.0045
GEN-2018-009 | 03 CENTRAL | 531404 | WALKMYR2 | 69 | 8.6401 | 8.7129 | 0.0728
GEN-2018-009 | 03 CENTRAL | 531405 | WALKMYR3 | 115 | 10.1141 | 10.2823 | 0.1682
GEN-2018-009 | 03 CENTRAL | 531406 | WOODS 2 | 69 | 6.3589 | 6.3983 | 0.0394
GEN-2018-009 | 03 CENTRAL | 531442 | SAT-TAP3 | 115 | 5.1116 | 5.2672 | 0.1556
GEN-2018-009 | 03 CENTRAL | 531454 | MOSCCMS2 | 69 | 1.9484 | 1.9685 | 0.0201
GEN-2018-009 | 03 CENTRAL | 531463 | SANTCMS2 | 69 | 1.3296 | 1.3386 | 0.009
GEN-2018-009 | 03 CENTRAL | 531466 | CMSSWRD2 | 69 | 3.4932 | 3.5565 | 0.0633
GEN-2018-009 | 03 CENTRAL | 531467 | SEWARD-3 | 115 | 4.9292 | 5.1493 | 0.2201
GEN-2018-009 | 03 CENTRAL | 531472 | AMOCO 3 | 115 | 5.0317 | 5.0549 | 0.0232
GEN-2018-009 | 03 CENTRAL | 531479 | CHUGTON2 | 69 | 2.678 | 2.6838 | 0.0058
GEN-2018-009 | 03 CENTRAL | 531481 | HUGOTON3 | 115 | 5.8163 | 5.862 | 0.0457
GEN-2018-009 | 03 CENTRAL | 531483 | GRANTTP3 | 115 | 5.0114 | 5.0359 | 0.0245
GEN-2018-009 | 03 CENTRAL | 531484 | GRANT 3 | 115 | 4.7223 | 4.744 | 0.0217
GEN-2018-009 | 03 CENTRAL | 531490 | ULYSPLT3 | 115 | 4.0887 | 4.0999 | 0.0112
GEN-2018-009 | 03 CENTRAL | 531494 | ABBK 2 | 115 | 5.2364 | 5.2734 | 0.037
GEN-2018-009 | 03 CENTRAL | 531510 | HARBNGR3 | 115 | 10.7399 | 10.899 | 0.1591
GEN-2018-009 | 03 CENTRAL | 531512 | HARBNGR7 | 345 | 6.4976 | 6.5455 | 0.0479
GEN-2018-009 | 03 CENTRAL | 539640 | HAYNE3 | 115 | 5.1944 | 5.6609 | 0.4665
GEN-2018-009 | 03 CENTRAL | 539641 | NW-DODG3 | 115 | 3.6421 | 3.6466 | 0.0045
GEN-2018-009 | 03 CENTRAL | 539645 | DCBEEF3 | 115 | 6.8594 | 6.8756 | 0.0162
GEN-2018-009 | 03 CENTRAL | 539646 | KISMET 3 | 115 | 5.0681 | 5.4211 | 0.353
GEN-2018-009 | 03 CENTRAL | 539652 | CMRIVTP3 | 115 | 5.5872 | 6.0726 | 0.4854
GEN-2018-009 | 03 CENTRAL | 539654 | CIM-PLT3 | 115 | 6.1267 | 6.8272 | 0.7005
GEN-2018-009 | 03 CENTRAL | 539659 | CUDAHY 3 | 115 | 4.2061 | 4.2951 | 0.089
GEN-2018-009 | 03 CENTRAL | 539671 | FTDODGE3 | 115 | 9.3598 | 9.3903 | 0.0305
GEN-2018-009 | 03 CENTRAL | 539672 | E-LIBER3 | 115 | 4.7593 | 5.0731 | 0.3138
GEN-2018-009 | 03 CENTRAL | 539680 | N-DODGE3 | 115 | 4.6635 | 4.6709 | 0.0074
GEN-2018-009 | 03 CENTRAL | 539690 | E-PINE 3 | 115 | 4.0958 | 4.3264 | 0.2306
GEN-2018-009 | 03 CENTRAL | 539691 | SATMKEC3 | 115 | 5.1019 | 5.2569 | 0.155
GEN-2018-009 | 03 CENTRAL | 539700 | W-LIBER3 | 115 | 3.7725 | 3.9868 | 0.2143
GEN-2018-009 | 03 CENTRAL | 539737 | NLIB 3 | 115 | 4.596 | 4.9175 | 0.3215
GEN-2018-009 | 03 CENTRAL | 539740 | EDODGE 3 | 115 | 6.2828 | 6.2963 | 0.0135
GEN-2018-009 | 03 CENTRAL | 539749 | N-CIMRN3 | 115 | 6.0698 | 6.7482 | 0.6784
GEN-2018-009 | 03 CENTRAL | 539751 | NATBEEF3 | 115 | 4.6933 | 5.0035 | 0.3102
GEN-2018-009 | 03 CENTRAL | 539783 | CRKCK 3 | 115 | 4.7334 | 4.7958 | 0.0624
GEN-2018-009 | 03 CENTRAL | 539784 | ENSNGW 3 | 115 | 3.5233 | 3.5531 | 0.0298
GEN-2018-009 | 03 CENTRAL | 560577 | G06-44 | 115 | 6.5894 | 6.5927 | 0.0033
GEN-2018-009 | 03 CENTRAL | 576395 | GEN-2010-014 | 345 | 8.4145 | 8.4309 | 0.0164
GEN-2018-009 | 03 CENTRAL | 576397 | G10014G11022 | 345 | 8.4145 | 8.4309 | 0.0164
GEN-2018-009 | 03 CENTRAL | 589380 | GEN-2017-100 | 115 | 4.8184 | 4.8301 | 0.0117
GEN-2018-009 | 03 CENTRAL | 599950 | LAMAR7 | 345 | 2.5142 | 2.516 | 0.0018
GEN-2018-009 | 03 CENTRAL | 762471 | GEN-2018-009 | 115 | 2.3362 | 3.2068 | 0.8706
GEN-2018-013 | 03 CENTRAL | 530592 | SMOKYHL6 | 230 | 7.0667 | 7.0727 | 0.006
GEN-2018-013 | 03 CENTRAL | 530593 | SMKYP1 6 | 230 | 6.1708 | 6.1752 | 0.0044
GEN-2018-013 | 03 CENTRAL | 530599 | SMKYP2 6 | 230 | 6.5373 | 6.5423 | 0.005
GEN-2018-013 | 03 CENTRAL | 530720 | KNOLL S 6 | 230 | 11.9217 | 11.9238 | 0.0021
GEN-2018-013 | 03 CENTRAL | 532767 | GEARY 7 | 345 | 10.5897 | 10.623 | 0.0333
GEN-2018-013 | 03 CENTRAL | 532773 | SUMMIT 7 | 345 | 11.5901 | 11.6259 | 0.0358
GEN-2018-013 | 03 CENTRAL | 532863 | MORRIS 6 | 230 | 14.3192 | 14.3332 | 0.014
GEN-2018-013 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 9.0202 | 9.0293 | 0.0091
GEN-2018-013 | 03 CENTRAL | 532872 | EMCPHER6 | 230 | 8.1786 | 8.193 | 0.0144
GEN-2018-013 | 03 CENTRAL | 532873 | SUMMIT 6 | 230 | 13.8186 | 13.8909 | 0.0723
GEN-2018-013 | 03 CENTRAL | 532874 | UNIONRG6 | 230 | 8.462 | 8.4747 | 0.0127
GEN-2018-013 | 03 CENTRAL | 532875 | DVISTA 6 | 230 | 5.0406 | 5.0443 | 0.0037
GEN-2018-013 | 03 CENTRAL | 533320 | CLAYCSS3 | 115 | 2.4367 | 2.4429 | 0.0062
GEN-2018-013 | 03 CENTRAL | 533323 | CLAYCTR3 | 115 | 3.1054 | 3.1154 | 0.01
GEN-2018-013 | 03 CENTRAL | 533324 | TCRILEY 3 | 115 | 2.1376 | 2.1424 | 0.0048
GEN-2018-013 | 03 CENTRAL | 533325 | CLAYGEN3 | 115 | 2.3638 | 2.3696 | 0.0058
GEN-2018-013 | 03 CENTRAL | 533328 | FT JCT 3 | 115 | 15.9537 | 16.0552 | 0.1015
GEN-2018-013 | 03 CENTRAL | 533329 | NCFOUND3 | 115 | 12.2488 | 12.3215 | 0.0727
GEN-2018-013 | 03 CENTRAL | 533335 | MCDOWEL3 | 115 | 19.3713 | 19.4336 | 0.0623
GEN-2018-013 | 03 CENTRAL | 533336 | GEARY 3 | 115 | 20.0126 | 20.1268 | 0.1142
GEN-2018-013 | 03 CENTRAL | 533342 | WJCCTY 3 | 115 | 14.3634 | 14.4621 | 0.0987
GEN-2018-013 | 03 CENTRAL | 533344 | WJCCTYW3 | 115 | 14.2688 | 14.3674 | 0.0986
GEN-2018-013 | 03 CENTRAL | 533359 | UNIONRG3 | 115 | 3.8992 | 3.9005 | 0.0013
GEN-2018-013 | 03 CENTRAL | 533360 | TCHOPE 3 | 115 | 3.4737 | 3.4747 | 0.001
GEN-2018-013 | 03 CENTRAL | 533361 | AEC 3 | 115 | 8.7544 | 9.0826 | 0.3282
GEN-2018-013 | 03 CENTRAL | 533362 | CHAPMAN3 | 115 | 11.8391 | 11.9886 | 0.1495
GEN-2018-013 | 03 CENTRAL | 533364 | CRAWFRD3 | 115 | 9.9462 | 10.0183 | 0.0721
GEN-2018-013 | 03 CENTRAL | 533365 | EABILEN3 | 115 | 8.8292 | 9.0949 | 0.2657
GEN-2018-013 | 03 CENTRAL | 533367 | BERG 3 | 115 | 11.6312 | 11.6987 | 0.0675
GEN-2018-013 | 03 CENTRAL | 533370 | NORTHST3 | 115 | 10.4471 | 10.5504 | 0.1033
GEN-2018-013 | 03 CENTRAL | 533371 | NORTHVW3 | 115 | 12.3869 | 12.5568 | 0.1699
GEN-2018-013 | 03 CENTRAL | 533374 | MENTOR 3 | 115 | 12.809 | 12.8924 | 0.0834
GEN-2018-013 | 03 CENTRAL | 533376 | SALINA 3 | 115 | 10.0042 | 10.0908 | 0.0866
GEN-2018-013 | 03 CENTRAL | 533377 | SCHILNG3 | 115 | 10.8168 | 10.8878 | 0.071
GEN-2018-013 | 03 CENTRAL | 533378 | SMOKYHLLS3 | 115 | 11.1418 | 11.2031 | 0.0613
GEN-2018-013 | 03 CENTRAL | 533379 | SO GATE3 | 115 | 10.6716 | 10.7266 | 0.055
GEN-2018-013 | 03 CENTRAL | 533381 | SUMMIT 3 | 115 | 18.1622 | 18.3069 | 0.1447
GEN-2018-013 | 03 CENTRAL | 533394 | CORONAD3 | 115 | 7.304 | 7.3192 | 0.0152
GEN-2018-013 | 03 CENTRAL | 533417 | EMCPHER3 | 115 | 11.7779 | 11.7939 | 0.016
GEN-2018-013 | 03 CENTRAL | 533438 | WMCPHER3 | 115 | 11.4426 | 11.4584 | 0.0158
GEN-2018-013 | 03 CENTRAL | 587880 | GEN-2016-111 | 345 | 6.8278 | 6.834 | 0.0062
GEN-2018-013 | 03 CENTRAL | 587884 | G16-111-TAP | 345 | 10.2733 | 10.2885 | 0.0152
GEN-2018-013 | 03 CENTRAL | 588490 | GEN-2017-004 | 345 | 8.5496 | 8.5675 | 0.0179
GEN-2018-013 | 03 CENTRAL | 588494 | G17-004-TAP | 345 | 9.9309 | 9.9553 | 0.0244
GEN-2018-013 | 03 CENTRAL | 760000 | GEN-2017-120 | 115 | 8.9923 | 9.4449 | 0.4526
GEN-2018-013 | 03 CENTRAL | 760007 | G17-120-TAP | 115 | 8.9923 | 9.4449 | 0.4526
GEN-2018-031 | 03 CENTRAL | 300044 | 7MCCRED | 345 | 24.9464 | 24.9469 | 0.0005
GEN-2018-031 | 03 CENTRAL | 300098 | 5MOCITYB2 | 161 | 19.5146 | 19.5388 | 0.0242
GEN-2018-031 | 03 CENTRAL | 345408 | 7OVERTON | 345 | 14.5932 | 14.5939 | 0.0007
GEN-2018-031 | 03 CENTRAL | 345409 | 5OVERTON | 161 | 22.3022 | 22.3028 | 0.0006
GEN-2018-031 | 03 CENTRAL | 532772 | STRANGR7 | 345 | 28.4567 | 28.4608 | 0.0041
GEN-2018-031 | 03 CENTRAL | 541144 | NASHUA_CAP5 | 161 | 28.9468 | 28.9583 | 0.0115
GEN-2018-031 | 03 CENTRAL | 541145 | RNRIDGE_CAP5 | 161 | 21.7622 | 21.7686 | 0.0064
GEN-2018-031 | 03 CENTRAL | 541197 | MULLNCR7 | 345 | 8.4934 | 8.4938 | 0.0004
GEN-2018-031 | 03 CENTRAL | 541198 | PECULR 7 | 345 | 20.9298 | 20.9352 | 0.0054
GEN-2018-031 | 03 CENTRAL | 541199 | ST JOE 7 | 345 | 20.7897 | 20.7926 | 0.0029
GEN-2018-031 | 03 CENTRAL | 541200 | PHILL 7 | 345 | 19.0794 | 19.0855 | 0.0061
GEN-2018-031 | 03 CENTRAL | 541201 | SIBLEY 7 | 345 | 21.6362 | 21.6508 | 0.0146
GEN-2018-031 | 03 CENTRAL | 541202 | SIBLEY 5 | 161 | 27.551 | 27.5893 | 0.0383
GEN-2018-031 | 03 CENTRAL | 541203 | NASHUA 5 | 161 | 34.7702 | 34.7869 | 0.0167
GEN-2018-031 | 03 CENTRAL | 541224 | LNGVW 5 | 161 | 24.298 | 24.3041 | 0.0061
GEN-2018-031 | 03 CENTRAL | 541225 | PHILL 5 | 161 | 35.3899 | 35.3985 | 0.0086
GEN-2018-031 | 03 CENTRAL | 541230 | RNRIDGE5 | 161 | 24.8987 | 24.9071 | 0.0084
GEN-2018-031 | 03 CENTRAL | 541248 | LBRTYST5 | 161 | 19.5572 | 19.5752 | 0.018
GEN-2018-031 | 03 CENTRAL | 541250 | SIBLEYPL | 161 | 29.1634 | 29.2106 | 0.0472
GEN-2018-031 | 03 CENTRAL | 541282 | LNGVW 2 | 69 | 10.6989 | 10.7001 | 0.0012
GEN-2018-031 | 03 CENTRAL | 541283 | BRMALL 2 | 69 | 15.5283 | 15.5372 | 0.0089
GEN-2018-031 | 03 CENTRAL | 541284 | GRDVWTP2 | 69 | 9.4968 | 9.4973 | 0.0005
GEN-2018-031 | 03 CENTRAL | 541350 | IATAN5 | 161 | 15.665 | 15.6663 | 0.0013
GEN-2018-031 | 03 CENTRAL | 541400 | EASTOWN7 | 345 | 19.2056 | 19.208 | 0.0024
GEN-2018-031 | 03 CENTRAL | 541411 | MC REAC1 | 345 | 8.1025 | 8.1029 | 0.0004
GEN-2018-031 | 03 CENTRAL | 541412 | MC REAC2 | 345 | 8.1025 | 8.1029 | 0.0004
GEN-2018-031 | 03 CENTRAL | 541413 | MC REAC3 | 345 | 8.1025 | 8.1029 | 0.0004
GEN-2018-031 | 03 CENTRAL | 541414 | SIB REA1 | 345 | 19.2698 | 19.2814 | 0.0116
GEN-2018-031 | 03 CENTRAL | 541500 | KETCHEM7 | 345 | 8.2411 | 8.2418 | 0.0007
GEN-2018-031 | 03 CENTRAL | 541501 | OSBORN7 | 345 | 7.3397 | 7.3403 | 0.0006
GEN-2018-031 | 03 CENTRAL | 542946 | GLADSTN_CAP5 | 161 | 17.3161 | 17.322 | 0.0059
GEN-2018-031 | 03 CENTRAL | 542948 | NEASTS_CAP5 | 161 | 37.6856 | 37.7125 | 0.0269
GEN-2018-031 | 03 CENTRAL | 542950 | STHTOWN_CAP5 | 161 | 30.9917 | 31.0045 | 0.0128
GEN-2018-031 | 03 CENTRAL | 542972 | HAWTH 7 | 345 | 23.7129 | 23.7341 | 0.0212
GEN-2018-031 | 03 CENTRAL | 542973 | HAWTHS5 | 161 | 59.5529 | 59.6682 | 0.1153
GEN-2018-031 | 03 CENTRAL | 542976 | LEVEE 5 | 161 | 53.7807 | 53.8675 | 0.0868
GEN-2018-031 | 03 CENTRAL | 542980 | NASHUA 7 | 345 | 24.0745 | 24.0865 | 0.012
GEN-2018-031 | 03 CENTRAL | 542982 | IATAN 7 | 345 | 31.6526 | 31.6585 | 0.0059
GEN-2018-031 | 03 CENTRAL | 542985 | NEASTS5 | 161 | 48.1962 | 48.2402 | 0.044
GEN-2018-031 | 03 CENTRAL | 542986 | TROOST 5 | 161 | 34.4538 | 34.4725 | 0.0187
GEN-2018-031 | 03 CENTRAL | 542987 | GRAND 5 | 161 | 44.0091 | 44.0425 | 0.0334
GEN-2018-031 | 03 CENTRAL | 542988 | GRAND W5 | 161 | 44.4209 | 44.4548 | 0.0339
GEN-2018-031 | 03 CENTRAL | 542989 | NAVY 5 | 161 | 44.3581 | 44.3919 | 0.0338
GEN-2018-031 | 03 CENTRAL | 542990 | CROSTWN5 | 161 | 40.0695 | 40.0965 | 0.027
GEN-2018-031 | 03 CENTRAL | 542993 | STHTOWN5 | 161 | 37.7672 | 37.7861 | 0.0189
GEN-2018-031 | 03 CENTRAL | 542996 | MIDTOWN5 | 161 | 36.083 | 36.1015 | 0.0185
GEN-2018-031 | 03 CENTRAL | 542997 | LEEDS 5 | 161 | 36.0879 | 36.1188 | 0.0309
GEN-2018-031 | 03 CENTRAL | 542998 | LVISTA 5 | 161 | 25.5054 | 25.517 | 0.0116
GEN-2018-031 | 03 CENTRAL | 543000 | BLUEVLY5 | 161 | 39.9182 | 39.97 | 0.0518
GEN-2018-031 | 03 CENTRAL | 543001 | FOREST 5 | 161 | 32.2832 | 32.2976 | 0.0144
GEN-2018-031 | 03 CENTRAL | 543004 | BLUMILS5 | 161 | 17.4649 | 17.5662 | 0.1013
GEN-2018-031 | 03 CENTRAL | 543006 | SWOPE N5 | 161 | 22.5601 | 22.5707 | 0.0106
GEN-2018-031 | 03 CENTRAL | 543007 | SWOPE S5 | 161 | 22.3647 | 22.3744 | 0.0097
GEN-2018-031 | 03 CENTRAL | 543009 | WINJT N5 | 161 | 24.641 | 24.6537 | 0.0127
GEN-2018-031 | 03 CENTRAL | 543010 | WINJT S5 | 161 | 23.9625 | 23.9737 | 0.0112
GEN-2018-031 | 03 CENTRAL | 543011 | CHOUTEU5 | 161 | 37.4422 | 37.4754 | 0.0332
GEN-2018-031 | 03 CENTRAL | 543015 | AVONDAL5 | 161 | 30.8205 | 30.842 | 0.0215
GEN-2018-031 | 03 CENTRAL | 543016 | GLADSTN5 | 161 | 19.2452 | 19.2524 | 0.0072
GEN-2018-031 | 03 CENTRAL | 543018 | NKANCTY5 | 161 | 35.1612 | 35.1861 | 0.0249
GEN-2018-031 | 03 CENTRAL | 543020 | BRMGHAM5 | 161 | 27.28 | 27.3088 | 0.0288
GEN-2018-031 | 03 CENTRAL | 543021 | RIVRSID5 | 161 | 19.5459 | 19.5523 | 0.0064
GEN-2018-031 | 03 CENTRAL | 543022 | CLAYCM15 | 161 | 11.8207 | 11.8231 | 0.0024
GEN-2018-031 | 03 CENTRAL | 543023 | CLAYCM25 | 161 | 13.9979 | 14.0055 | 0.0076
GEN-2018-031 | 03 CENTRAL | 543025 | LINECRK5 | 161 | 17.8204 | 17.8254 | 0.005
GEN-2018-031 | 03 CENTRAL | 543027 | RANDLPH5 | 161 | 34.2372 | 34.2695 | 0.0323
GEN-2018-031 | 03 CENTRAL | 543028 | NASHUA-5 | 161 | 34.9766 | 34.9934 | 0.0168
GEN-2018-031 | 03 CENTRAL | 543029 | SHOLCRK5 | 161 | 18.695 | 18.701 | 0.006
GEN-2018-031 | 03 CENTRAL | 543040 | ROEPARK5 | 161 | 30.9049 | 30.9171 | 0.0122
GEN-2018-031 | 03 CENTRAL | 543080 | HAWTH 2 | 69 | 13.9022 | 13.9096 | 0.0074
GEN-2018-031 | 03 CENTRAL | 543095 | LIBRTYS2 | 69 | 12.4862 | 12.4922 | 0.006
GEN-2018-031 | 03 CENTRAL | 543116 | BLUEMLS2 | 69 | 7.6658 | 7.6741 | 0.0083
GEN-2018-031 | 03 CENTRAL | 543129 | HAWTHS_G65 | 161 | 58.7013 | 58.8132 | 0.1119
GEN-2018-031 | 03 CENTRAL | 543130 | HAWTHS_XF5 | 161 | 58.6393 | 58.7512 | 0.1119
GEN-2018-031 | 03 CENTRAL | 543133 | CHARLOT5 | 161 | 35.3285 | 35.3495 | 0.021
GEN-2018-031 | 03 CENTRAL | 543663 | HAWT11_2 | 69 | 13.9022 | 13.9096 | 0.0074
GEN-2018-031 | 03 CENTRAL | 543664 | HAWT12_2 | 69 | 13.9022 | 13.9096 | 0.0074
GEN-2018-031 | 03 CENTRAL | 543665 | HAWTHN5 | 161 | 60.2382 | 60.3523 | 0.1141
GEN-2018-031 | 03 CENTRAL | 543666 | NEASTN5 | 161 | 48.6106 | 48.6554 | 0.0448
GEN-2018-031 | 03 CENTRAL | 548800 | SUB I | 69 | 19.1792 | 19.2032 | 0.024
GEN-2018-031 | 03 CENTRAL | 548802 | SUB H | 69 | 22.3274 | 22.3622 | 0.0348
GEN-2018-031 | 03 CENTRAL | 548803 | SUB F | 69 | 15.4303 | 15.4409 | 0.0106
GEN-2018-031 | 03 CENTRAL | 548804 | SUB E | 69 | 16.1965 | 16.207 | 0.0105
GEN-2018-031 | 03 CENTRAL | 548806 | BLUVLY | 69 | 23.8901 | 23.9456 | 0.0555
GEN-2018-031 | 03 CENTRAL | 548807 | BLUVLY-161 | 161 | 18.4595 | 18.6597 | 0.2002
GEN-2018-031 | 03 CENTRAL | 548809 | SHRNKRD | 69 | 18.8594 | 18.8843 | 0.0249
GEN-2018-031 | 03 CENTRAL | 548811 | SUB J | 69 | 18.5267 | 18.5534 | 0.0267
GEN-2018-031 | 03 CENTRAL | 548814 | SUB M-161 | 161 | 21.1485 | 21.2764 | 0.1279
GEN-2018-031 | 03 CENTRAL | 548815 | SUB M | 69 | 22.9156 | 22.9549 | 0.0393
GEN-2018-031 | 03 CENTRAL | 548820 | SUB N-161 | 161 | 17.1663 | 17.1772 | 0.0109
GEN-2018-031 | 03 CENTRAL | 548821 | SUB N | 69 | 18.0987 | 18.1115 | 0.0128
GEN-2018-031 | 03 CENTRAL | 548825 | SUB C | 69 | 16.3777 | 16.3923 | 0.0146
GEN-2018-031 | 03 CENTRAL | 548826 | STRLNGRD | 69 | 16.5879 | 16.6001 | 0.0122
GEN-2018-031 | 03 CENTRAL | 548832 | KCPL JCT | 69 | 14.4241 | 14.4332 | 0.0091
GEN-2018-031 | 03 CENTRAL | 588240 | GEN-2016-149 | 345 | 4.4342 | 4.4343 | 0.0001
GEN-2018-031 | 03 CENTRAL | 588250 | GEN-2016-174 | 345 | 13.3773 | 13.378 | 0.0007
GEN-2018-031 | 03 CENTRAL | 588260 | GEN-2016-176 | 345 | 8.2369 | 8.2371 | 0.0002
GEN-2018-031 | 03 CENTRAL | 588270 | GEN-2016-150 | 345 | 4.1248 | 4.1248 | 0
GEN-2018-031 | 03 CENTRAL | 761376 | GEN-2017-183 | 345 | 8.8634 | 8.8643 | 0.0009
GEN-2018-031 | 03 CENTRAL | 761383 | G17-183-TAP | 345 | 17.8911 | 17.8955 | 0.0044
GEN-2018-031 | 03 CENTRAL | 762669 | GEN-2018-031 | 161 | 18.4574 | 18.6576 | 0.2002
GEN-2018-031 | 03 CENTRAL | 999101 | GI083 | 345 | 16.6867 | 16.6868 | 0.0001
GEN-2018-032 | 03 CENTRAL | 300042 | 7HUBEN | 345 | 10.4925 | 10.4925 | 0
GEN-2018-032 | 03 CENTRAL | 300045 | 7MORGAN | 345 | 13.3977 | 13.3977 | 0
GEN-2018-032 | 03 CENTRAL | 300051 | 7FRANKSRCTP | 345 | 16.2528 | 16.2528 | 0
GEN-2018-032 | 03 CENTRAL | 300069 | 5CHOTEAU1 | 161 | 42.6067 | 42.6067 | 0
GEN-2018-032 | 03 CENTRAL | 300070 | 5CLARK | 161 | 8.2114 | 8.2114 | 0
GEN-2018-032 | 03 CENTRAL | 300088 | 5HUBEN | 161 | 15.8852 | 15.8852 | 0
GEN-2018-032 | 03 CENTRAL | 300101 | 5MORGAN | 161 | 18.7776 | 18.7776 | 0
GEN-2018-032 | 03 CENTRAL | 300651 | 2LAMR | 69 | 10.1416 | 10.1416 | 0
GEN-2018-032 | 03 CENTRAL | 300652 | 2LAMRCTS | 69 | 3.9472 | 3.9472 | 0
GEN-2018-032 | 03 CENTRAL | 300685 | 2LAMARPT | 69 | 8.562 | 8.562 | 0
GEN-2018-032 | 03 CENTRAL | 300739 | 7BLACKBERRY | 345 | 15.7377 | 15.7378 | 0.0001
GEN-2018-032 | 03 CENTRAL | 300740 | 7SPORTSMAN | 345 | 24.7786 | 24.7786 | 0
GEN-2018-032 | 03 CENTRAL | 300741 | 5SPORTSMAN | 161 | 41.0131 | 41.0132 | 0.0001
GEN-2018-032 | 03 CENTRAL | 300794 | 5LAMAR | 161 | 8.9213 | 8.9213 | 0
GEN-2018-032 | 03 CENTRAL | 300949 | 7JASPER | 345 | 12.7837 | 12.7837 | 0
GEN-2018-032 | 03 CENTRAL | 300950 | 5JASPER | 161 | 13.0065 | 13.0066 | 0.0001
GEN-2018-032 | 03 CENTRAL | 301348 | 5CHOTEAU2 | 161 | 42.6067 | 42.6067 | 0
GEN-2018-032 | 03 CENTRAL | 301554 | 7FRANKSRCT | 345 | 16.2076 | 16.2076 | 0
GEN-2018-032 | 03 CENTRAL | 301622 | 5MORGANXF2 | 161 | 18.7778 | 18.7778 | 0
GEN-2018-032 | 03 CENTRAL | 506935 | FLINTCR7 | 345 | 15.84 | 15.84 | 0
GEN-2018-032 | 03 CENTRAL | 506945 | CHAMSPR7 | 345 | 10.5975 | 10.5975 | 0
GEN-2018-032 | 03 CENTRAL | 509721 | BA.NO-S4 | 138 | 12.6955 | 12.6955 | 0
GEN-2018-032 | 03 CENTRAL | 509737 | BA101 S4 | 138 | 18.7186 | 18.7186 | 0
GEN-2018-032 | 03 CENTRAL | 509743 | DENVR-E4 | 138 | 8.3049 | 8.3049 | 0
GEN-2018-032 | 03 CENTRAL | 509745 | CLARKSV7 | 345 | 20.5976 | 20.5977 | 0.0001
GEN-2018-032 | 03 CENTRAL | 509746 | DENVTAP4 | 138 | 9.7401 | 9.7401 | 0
GEN-2018-032 | 03 CENTRAL | 509755 | WEKIWA-7 | 345 | 22.4663 | 22.4663 | 0
GEN-2018-032 | 03 CENTRAL | 509757 | WEKIWA-4 | 138 | 33.7501 | 33.7501 | 0
GEN-2018-032 | 03 CENTRAL | 509768 | BA101ST4 | 138 | 19.4219 | 19.4219 | 0
GEN-2018-032 | 03 CENTRAL | 509769 | BA101-N4 | 138 | 20.3193 | 20.3193 | 0
GEN-2018-032 | 03 CENTRAL | 509773 | RSS T1 4 | 138 | 52.5972 | 52.5972 | 0
GEN-2018-032 | 03 CENTRAL | 509782 | R.S.S.-7 | 345 | 30.9363 | 30.9363 | 0
GEN-2018-032 | 03 CENTRAL | 509786 | BA.N-ST4 | 138 | 24.7209 | 24.7209 | 0
GEN-2018-032 | 03 CENTRAL | 509806 | ONETA--4 | 138 | 51.3265 | 51.3265 | 0
GEN-2018-032 | 03 CENTRAL | 509807 | ONETA--7 | 345 | 29.7179 | 29.7179 | 0
GEN-2018-032 | 03 CENTRAL | 509817 | T.NO.--4 | 138 | 35.8857 | 35.8857 | 0
GEN-2018-032 | 03 CENTRAL | 509822 | W.ED.-E4 | 138 | 8.1376 | 8.1376 | 0
GEN-2018-032 | 03 CENTRAL | 509834 | COGENT 7 | 345 | 28.8791 | 28.8791 | 0
GEN-2018-032 | 03 CENTRAL | 509836 | OEC 7 | 345 | 29.4435 | 29.4435 | 0
GEN-2018-032 | 03 CENTRAL | 509852 | T.NO.--7 | 345 | 24.3916 | 24.3916 | 0
GEN-2018-032 | 03 CENTRAL | 509869 | 121LYNN4 | 138 | 18.32 | 18.32 | 0
GEN-2018-032 | 03 CENTRAL | 509870 | SAPLPRD7 | 345 | 22.7834 | 22.7834 | 0
GEN-2018-032 | 03 CENTRAL | 509875 | RSS T2 4 | 138 | 53.5277 | 53.5277 | 0
GEN-2018-032 | 03 CENTRAL | 509891 | BA_71ST4 | 138 | 24.0691 | 24.0691 | 0
GEN-2018-032 | 03 CENTRAL | 509895 | T.NO.2-4 | 138 | 35.8273 | 35.8273 | 0
GEN-2018-032 | 03 CENTRAL | 510378 | SCOFCTY4 | 138 | 8.8614 | 8.8614 | 0
GEN-2018-032 | 03 CENTRAL | 510379 | DELWARE4 | 138 | 11.502 | 11.502 | 0
GEN-2018-032 | 03 CENTRAL | 510380 | DELWARE7 | 345 | 12.1342 | 12.1343 | 0.0001
GEN-2018-032 | 03 CENTRAL | 510406 | N.E.S.-7 | 345 | 19.6408 | 19.6409 | 0.0001
GEN-2018-032 | 03 CENTRAL | 510420 | SCOFFEYV4 | 138 | 8.4721 | 8.4721 | 0
GEN-2018-032 | 03 CENTRAL | 510422 | COFFEYT4 | 138 | 10.2607 | 10.2607 | 0
GEN-2018-032 | 03 CENTRAL | 512631 | MIAMI 5 | 161 | 9.7102 | 9.7102 | 0
GEN-2018-032 | 03 CENTRAL | 512648 | MAID 5 | 161 | 44.8542 | 44.8542 | 0
GEN-2018-032 | 03 CENTRAL | 512650 | GRDA1 7 | 345 | 27.2218 | 27.2218 | 0
GEN-2018-032 | 03 CENTRAL | 512656 | GRDA1 5 | 161 | 44.3989 | 44.3989 | 0
GEN-2018-032 | 03 CENTRAL | 512694 | CLEVLND7 | 345 | 15.0692 | 15.0692 | 0
GEN-2018-032 | 03 CENTRAL | 512700 | WAGNOR 5 | 161 | 9.9473 | 9.9473 | 0
GEN-2018-032 | 03 CENTRAL | 512727 | GRDA1 2 | 69 | 12.5401 | 12.5401 | 0
GEN-2018-032 | 03 CENTRAL | 512728 | ARKLIN2 | 69 | 3.8389 | 3.8389 | 0
GEN-2018-032 | 03 CENTRAL | 512729 | CLEVLND 4 | 138 | 17.2281 | 17.2281 | 0
GEN-2018-032 | 03 CENTRAL | 512734 | FARML 4 | 138 | 8.4437 | 8.4437 | 0
GEN-2018-032 | 03 CENTRAL | 512735 | COFCTY2 | 69 | 9.0575 | 9.0575 | 0
GEN-2018-032 | 03 CENTRAL | 512742 | WMAIN ST5 | 161 | 28.2152 | 28.2152 | 0
GEN-2018-032 | 03 CENTRAL | 512745 | SSLINC2 | 69 | 2.8874 | 2.8874 | 0
GEN-2018-032 | 03 CENTRAL | 512746 | SSNORT2 | 69 | 2.9435 | 2.9435 | 0
GEN-2018-032 | 03 CENTRAL | 512747 | SSNEWN2 | 69 | 3.1928 | 3.1928 | 0
GEN-2018-032 | 03 CENTRAL | 512750 | TONECE7 | 345 | 15.6029 | 15.6029 | 0
GEN-2018-032 | 03 CENTRAL | 512751 | TONECE5 | 161 | 15.6229 | 15.6229 | 0
GEN-2018-032 | 03 CENTRAL | 512753 | TONNEC2 | 69 | 4.962 | 4.962 | 0
GEN-2018-032 | 03 CENTRAL | 512756 | TONECESTR2 | 69 | 3.9528 | 3.9528 | 0
GEN-2018-032 | 03 CENTRAL | 512865 | GREC TAP5 | 345 | 26.0105 | 26.0106 | 0.0001
GEN-2018-032 | 03 CENTRAL | 513570 | CHOUTEAUCRK5 | 161 | 20.7211 | 20.7211 | 0
GEN-2018-032 | 03 CENTRAL | 513590 | CUSTDAY1 5 | 161 | 16.8777 | 16.8777 | 0
GEN-2018-032 | 03 CENTRAL | 513591 | HERRON 5 | 161 | 17.2968 | 17.2968 | 0
GEN-2018-032 | 03 CENTRAL | 513593 | IGLOOV1 5 | 161 | 17.4947 | 17.4947 | 0
GEN-2018-032 | 03 CENTRAL | 513595 | IGLOOV2 5 | 161 | 17.4947 | 17.4947 | 0
GEN-2018-032 | 03 CENTRAL | 513596 | IGLOOV 7 | 345 | 20.6342 | 20.6342 | 0
GEN-2018-032 | 03 CENTRAL | 514803 | SOONER 7 | 345 | 25.841 | 25.841 | 0
GEN-2018-032 | 03 CENTRAL | 514825 | KAYWIND7 | 345 | 12.0554 | 12.0554 | 0
GEN-2018-032 | 03 CENTRAL | 514909 | REDBUD 7 | 345 | 26.7096 | 26.7096 | 0
GEN-2018-032 | 03 CENTRAL | 515224 | MUSKOGE7 | 345 | 27.4688 | 27.4688 | 0
GEN-2018-032 | 03 CENTRAL | 515235 | PECANCK7 | 345 | 21.946 | 21.946 | 0
GEN-2018-032 | 03 CENTRAL | 515621 | OPENSKY7 | 345 | 12.0855 | 12.0855 | 0
GEN-2018-032 | 03 CENTRAL | 515894 | THUNDER7 | 345 | 10.4842 | 10.4842 | 0
GEN-2018-032 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 17.3988 | 17.3988 | 0
GEN-2018-032 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.5961 | 11.5961 | 0
GEN-2018-032 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 17.0373 | 17.0373 | 0
GEN-2018-032 | 03 CENTRAL | 532775 | 87TH 7 | 345 | 22.604 | 22.604 | 0
GEN-2018-032 | 03 CENTRAL | 532776 | READWF 7 | 345 | 14.4507 | 14.4507 | 0
GEN-2018-032 | 03 CENTRAL | 532777 | G17-009-TAP | 345 | 11.9964 | 11.9966 | 0.0002
GEN-2018-032 | 03 CENTRAL | 532778 | GEN-2017-009 | 345 | 11.1086 | 11.1088 | 0.0002
GEN-2018-032 | 03 CENTRAL | 532780 | CANEYRV7 | 345 | 9.7619 | 9.762 | 0.0001
GEN-2018-032 | 03 CENTRAL | 532781 | CANEYWF7 | 345 | 9.4894 | 9.4894 | 0
GEN-2018-032 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 20.5277 | 20.5277 | 0
GEN-2018-032 | 03 CENTRAL | 532783 | KINGMAN7 | 345 | 7.2273 | 7.2273 | 0
GEN-2018-032 | 03 CENTRAL | 532784 | NINN1WF7 | 345 | 6.0468 | 6.0468 | 0
GEN-2018-032 | 03 CENTRAL | 532785 | PRATTWF7 | 345 | 5.0335 | 5.0335 | 0
GEN-2018-032 | 03 CENTRAL | 532791 | BENTON 7 | 345 | 18.996 | 18.996 | 0
GEN-2018-032 | 03 CENTRAL | 532792 | FR2EAST7 | 345 | 6.8252 | 6.8252 | 0
GEN-2018-032 | 03 CENTRAL | 532793 | NEOSHO 7 | 345 | 18.1716 | 18.1722 | 0.0006
GEN-2018-032 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 18.7455 | 18.7456 | 0.0001
GEN-2018-032 | 03 CENTRAL | 532795 | FR2WEST7 | 345 | 5.5195 | 5.5195 | 0
GEN-2018-032 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 23.5186 | 23.5186 | 0
GEN-2018-032 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 18.662 | 18.662 | 0
GEN-2018-032 | 03 CENTRAL | 532798 | VIOLA 7 | 345 | 13.8306 | 13.8306 | 0
GEN-2018-032 | 03 CENTRAL | 532799 | WAVERLY7 | 345 | 16.5261 | 16.5261 | 0
GEN-2018-032 | 03 CENTRAL | 532800 | LATHAMS7 | 345 | 10.3826 | 10.3826 | 0
GEN-2018-032 | 03 CENTRAL | 532801 | ELKRVR17 | 345 | 9.2154 | 9.2154 | 0
GEN-2018-032 | 03 CENTRAL | 532802 | WAVERTX7 | 345 | 13.778 | 13.778 | 0
GEN-2018-032 | 03 CENTRAL | 532803 | EXPEDITION7 | 345 | 10.9007 | 10.9007 | 0
GEN-2018-032 | 03 CENTRAL | 532856 | SWISVAL6 | 230 | 22.0654 | 22.0654 | 0
GEN-2018-032 | 03 CENTRAL | 532926 | BAKER 2 | 69 | 5.1271 | 5.1271 | 0
GEN-2018-032 | 03 CENTRAL | 532934 | MARMTNE5 | 161 | 8.2057 | 8.2057 | 0
GEN-2018-032 | 03 CENTRAL | 532935 | MARMTNW5 | 161 | 8.2024 | 8.2024 | 0
GEN-2018-032 | 03 CENTRAL | 532937 | NEOSHO 5 | 161 | 23.6654 | 23.6657 | 0.0003
GEN-2018-032 | 03 CENTRAL | 532938 | FRANKLIN5 | 161 | 8.0153 | 8.0153 | 0
GEN-2018-032 | 03 CENTRAL | 532986 | BENTON 4 | 138 | 28.234 | 28.234 | 0
GEN-2018-032 | 03 CENTRAL | 532988 | BELAIRE4 | 138 | 19.2161 | 19.2161 | 0
GEN-2018-032 | 03 CENTRAL | 532990 | MIDIAN 4 | 138 | 11.2801 | 11.2801 | 0
GEN-2018-032 | 03 CENTRAL | 532991 | WEAVER 4 | 138 | 22.3902 | 22.3902 | 0
GEN-2018-032 | 03 CENTRAL | 532994 | TCBURNS4 | 138 | 4.1372 | 4.1372 | 0
GEN-2018-032 | 03 CENTRAL | 533001 | ALTOONA4 | 138 | 9.4082 | 9.4082 | 0
GEN-2018-032 | 03 CENTRAL | 533002 | DEARING4 | 138 | 9.6306 | 9.6306 | 0
GEN-2018-032 | 03 CENTRAL | 533003 | LIBERTY4 | 138 | 7.619 | 7.619 | 0
GEN-2018-032 | 03 CENTRAL | 533005 | NEPARSN4 | 138 | 13.1358 | 13.1359 | 0.0001
GEN-2018-032 | 03 CENTRAL | 533008 | TV1MNDV4 | 138 | 7.2627 | 7.2627 | 0
GEN-2018-032 | 03 CENTRAL | 533020 | NEOSHOS4 | 138 | 25.2937 | 25.2939 | 0.0002
GEN-2018-032 | 03 CENTRAL | 533021 | NEOSHO 4 | 138 | 25.3365 | 25.3368 | 0.0003
GEN-2018-032 | 03 CENTRAL | 533022 | NEOSHON4 | 138 | 25.2187 | 25.219 | 0.0003
GEN-2018-032 | 03 CENTRAL | 533024 | 29TH 4 | 138 | 19.8532 | 19.8532 | 0
GEN-2018-032 | 03 CENTRAL | 533039 | ELPASO 4 | 138 | 25.0218 | 25.0218 | 0
GEN-2018-032 | 03 CENTRAL | 533040 | EVANS N4 | 138 | 32.0782 | 32.0782 | 0
GEN-2018-032 | 03 CENTRAL | 533052 | PARKCTY4 | 138 | 20.5064 | 20.5064 | 0
GEN-2018-032 | 03 CENTRAL | 533062 | ROSEHIL4 | 138 | 31.2189 | 31.2189 | 0
GEN-2018-032 | 03 CENTRAL | 533068 | STEARMN4 | 138 | 19.7561 | 19.7561 | 0
GEN-2018-032 | 03 CENTRAL | 533624 | BURLING2 | 69 | 3.5476 | 3.5476 | 0
GEN-2018-032 | 03 CENTRAL | 533625 | BURLIND2 | 69 | 3.1627 | 3.1627 | 0
GEN-2018-032 | 03 CENTRAL | 533626 | BURLJCT2 | 69 | 5.156 | 5.156 | 0
GEN-2018-032 | 03 CENTRAL | 533628 | CC1BURL2 | 69 | 3.5462 | 3.5462 | 0
GEN-2018-032 | 03 CENTRAL | 533629 | CC2SHAR2 | 69 | 4.8209 | 4.8209 | 0
GEN-2018-032 | 03 CENTRAL | 533630 | CC3WEST2 | 69 | 4.7617 | 4.7617 | 0
GEN-2018-032 | 03 CENTRAL | 533639 | MARMATN2 | 69 | 8.9641 | 8.9641 | 0
GEN-2018-032 | 03 CENTRAL | 533640 | MCKEE 2 | 69 | 4.3522 | 4.3522 | 0
GEN-2018-032 | 03 CENTRAL | 533645 | SE9HIAT2 | 69 | 3.8696 | 3.8696 | 0
GEN-2018-032 | 03 CENTRAL | 533647 | UN1ELSM2 | 69 | 8.0732 | 8.0732 | 0
GEN-2018-032 | 03 CENTRAL | 533650 | UN8HUMB2 | 69 | 4.5462 | 4.5462 | 0
GEN-2018-032 | 03 CENTRAL | 533653 | WOLFCRK2 | 69 | 6.2331 | 6.2331 | 0
GEN-2018-032 | 03 CENTRAL | 533654 | ZILAJCT2 | 69 | 6.4532 | 6.4532 | 0
GEN-2018-032 | 03 CENTRAL | 533671 | ALTAMNT2 | 69 | 2.9333 | 2.9333 | 0
GEN-2018-032 | 03 CENTRAL | 533672 | ALTAMNS2 | 69 | 4.2046 | 4.2046 | 0
GEN-2018-032 | 03 CENTRAL | 533673 | ALTOO E2 | 69 | 4.3777 | 4.3777 | 0
GEN-2018-032 | 03 CENTRAL | 533674 | ALTOO W2 | 69 | 3.1772 | 3.1772 | 0
GEN-2018-032 | 03 CENTRAL | 533675 | ARGO 2 | 69 | 3.1009 | 3.1009 | 0
GEN-2018-032 | 03 CENTRAL | 533692 | YELLOWJ2 | 69 | 1.4671 | 1.4671 | 0
GEN-2018-032 | 03 CENTRAL | 533695 | LABETTE2 | 69 | 4.2174 | 4.2174 | 0
GEN-2018-032 | 03 CENTRAL | 533696 | LABETTS2 | 69 | 6.3923 | 6.3923 | 0
GEN-2018-032 | 03 CENTRAL | 533697 | LIBERT-2 | 69 | 8.7222 | 8.7222 | 0
GEN-2018-032 | 03 CENTRAL | 533699 | NEODESH2 | 69 | 2.7849 | 2.7849 | 0
GEN-2018-032 | 03 CENTRAL | 533700 | NEODJCT2 | 69 | 3.7672 | 3.7672 | 0
GEN-2018-032 | 03 CENTRAL | 533701 | NEW ALB2 | 69 | 1.5568 | 1.5568 | 0
GEN-2018-032 | 03 CENTRAL | 533702 | ORDNCE 2 | 69 | 6.3264 | 6.3264 | 0
GEN-2018-032 | 03 CENTRAL | 533703 | ORDNJCT2 | 69 | 8.7604 | 8.7604 | 0
GEN-2018-032 | 03 CENTRAL | 533704 | PARSONS2 | 69 | 5.0863 | 5.0863 | 0
GEN-2018-032 | 03 CENTRAL | 533705 | STUDBKR2 | 69 | 1.8876 | 1.8876 | 0
GEN-2018-032 | 03 CENTRAL | 533706 | RA5HIPR2 | 69 | 4.3755 | 4.3755 | 0
GEN-2018-032 | 03 CENTRAL | 533707 | RA6BROO2 | 69 | 2.6734 | 2.6734 | 0
GEN-2018-032 | 03 CENTRAL | 533758 | CRAWFOR2 | 69 | 7.5649 | 7.5649 | 0
GEN-2018-032 | 03 CENTRAL | 533761 | GIRARD 2 | 69 | 4.6776 | 4.6776 | 0
GEN-2018-032 | 03 CENTRAL | 533762 | GIR JCT2 | 69 | 6.6801 | 6.6801 | 0
GEN-2018-032 | 03 CENTRAL | 533763 | HUDSON-2 | 69 | 4.8043 | 4.8044 | 0.0001
GEN-2018-032 | 03 CENTRAL | 533766 | LITCH S2 | 69 | 13.1079 | 13.1079 | 0
GEN-2018-032 | 03 CENTRAL | 533768 | NEOSHON2 | 69 | 23.9524 | 23.9525 | 0.0001
GEN-2018-032 | 03 CENTRAL | 533772 | SE1GREE2 | 69 | 6.3084 | 6.3084 | 0
GEN-2018-032 | 03 CENTRAL | 533773 | SOPITT 2 | 69 | 5.7461 | 5.7461 | 0
GEN-2018-032 | 03 CENTRAL | 533778 | NEOSHOS2 | 69 | 23.9773 | 23.9774 | 0.0001
GEN-2018-032 | 03 CENTRAL | 541198 | PECULR 7 | 345 | 20.9352 | 20.9352 | 0
GEN-2018-032 | 03 CENTRAL | 541200 | PHILL 7 | 345 | 19.0855 | 19.0855 | 0
GEN-2018-032 | 03 CENTRAL | 541341 | S.HARP 5 | 161 | 21.3642 | 21.3642 | 0
GEN-2018-032 | 03 CENTRAL | 541342 | PECULR 5 | 161 | 23.4089 | 23.4089 | 0
GEN-2018-032 | 03 CENTRAL | 541541 | LAC_LAKE_2 | 69 | 2.6766 | 2.6766 | 0
GEN-2018-032 | 03 CENTRAL | 542945 | CRAIG_CAP 5 | 161 | 35.5053 | 35.5053 | 0
GEN-2018-032 | 03 CENTRAL | 542965 | W.GRDNR7 | 345 | 28.5039 | 28.5039 | 0
GEN-2018-032 | 03 CENTRAL | 542966 | WGARDNR5 | 161 | 30.4469 | 30.4469 | 0
GEN-2018-032 | 03 CENTRAL | 542968 | STILWEL7 | 345 | 25.9619 | 25.9619 | 0
GEN-2018-032 | 03 CENTRAL | 542969 | STILWEL5 | 161 | 40.9619 | 40.9619 | 0
GEN-2018-032 | 03 CENTRAL | 542977 | CRAIG 7 | 345 | 24.4108 | 24.4108 | 0
GEN-2018-032 | 03 CENTRAL | 542978 | CRAIG 5 | 161 | 44.6862 | 44.6862 | 0
GEN-2018-032 | 03 CENTRAL | 542981 | LACYGNE7 | 345 | 27.5276 | 27.5276 | 0
GEN-2018-032 | 03 CENTRAL | 542994 | HICKMAN5 | 161 | 20.1018 | 20.1018 | 0
GEN-2018-032 | 03 CENTRAL | 543049 | CEDRCRK5 | 161 | 31.3364 | 31.3364 | 0
GEN-2018-032 | 03 CENTRAL | 543050 | ANTIOCH5 | 161 | 23.2739 | 23.2739 | 0
GEN-2018-032 | 03 CENTRAL | 543053 | REDEL 5 | 161 | 25.1701 | 25.1701 | 0
GEN-2018-032 | 03 CENTRAL | 543054 | CEDARNL5 | 161 | 10.8932 | 10.8932 | 0
GEN-2018-032 | 03 CENTRAL | 543057 | BUCYRUS5 | 161 | 21.0225 | 21.0225 | 0
GEN-2018-032 | 03 CENTRAL | 543058 | NLOUISB5 | 161 | 9.33 | 9.33 | 0
GEN-2018-032 | 03 CENTRAL | 543065 | CNTRVIL5 | 161 | 6.1634 | 6.1634 | 0
GEN-2018-032 | 03 CENTRAL | 543077 | PLSTVAL5 | 161 | 10.368 | 10.368 | 0
GEN-2018-032 | 03 CENTRAL | 543105 | BULLCRK5 | 161 | 29.5093 | 29.5093 | 0
GEN-2018-032 | 03 CENTRAL | 543126 | LACKMAN5 | 161 | 13.8591 | 13.8591 | 0
GEN-2018-032 | 03 CENTRAL | 543132 | BNSF 5 | 161 | 22.3887 | 22.3887 | 0
GEN-2018-032 | 03 CENTRAL | 543629 | LACYGNE11_7 | 345 | 26.8058 | 26.8059 | 0.0001
GEN-2018-032 | 03 CENTRAL | 543632 | LACYGNE22_7 | 345 | 26.8058 | 26.8059 | 0.0001
GEN-2018-032 | 03 CENTRAL | 543650 | DAKOTA_5 | 161 | 6.8946 | 6.8946 | 0
GEN-2018-032 | 03 CENTRAL | 543651 | PRQN_WIND5 | 161 | 5.4355 | 5.4355 | 0
GEN-2018-032 | 03 CENTRAL | 543659 | LACYGNE2 | 69 | 2.8155 | 2.8155 | 0
GEN-2018-032 | 03 CENTRAL | 543667 | LAC3_STAR7 | 345 | 0.6733 | 0.6733 | 0
GEN-2018-032 | 03 CENTRAL | 543669 | LAC8_STAR7 | 345 | 0.6449 | 0.6449 | 0
GEN-2018-032 | 03 CENTRAL | 547409 | SCAM66 2 | 69 | 2.5533 | 2.5533 | 0
GEN-2018-032 | 03 CENTRAL | 547411 | COL282 2 | 69 | 4.705 | 4.705 | 0
GEN-2018-032 | 03 CENTRAL | 547412 | SEK225T2 | 69 | 3.6232 | 3.6232 | 0
GEN-2018-032 | 03 CENTRAL | 547413 | SEK225 2 | 69 | 3.5759 | 3.5759 | 0
GEN-2018-032 | 03 CENTRAL | 547414 | SMN425 2 | 69 | 2.0374 | 2.0374 | 0
GEN-2018-032 | 03 CENTRAL | 547415 | SHR444 2 | 69 | 2.8101 | 2.8101 | 0
GEN-2018-032 | 03 CENTRAL | 547416 | CHE299T2 | 69 | 1.9091 | 1.9091 | 0
GEN-2018-032 | 03 CENTRAL | 547417 | CHE299 2 | 69 | 1.8285 | 1.8285 | 0
GEN-2018-032 | 03 CENTRAL | 547418 | CHE300 2 | 69 | 1.87 | 1.87 | 0
GEN-2018-032 | 03 CENTRAL | 547419 | TWN388 2 | 69 | 1.8167 | 1.8167 | 0
GEN-2018-032 | 03 CENTRAL | 547420 | WEL186 2 | 69 | 1.1681 | 1.1681 | 0
GEN-2018-032 | 03 CENTRAL | 547431 | WEB105 2 | 69 | 8.1556 | 8.1556 | 0
GEN-2018-032 | 03 CENTRAL | 547455 | SCM66T 2 | 69 | 4.5271 | 4.5271 | 0
GEN-2018-032 | 03 CENTRAL | 547459 | WWR477 | 161 | 23.4857 | 23.4857 | 0
GEN-2018-032 | 03 CENTRAL | 547462 | SVRCK469 5 | 161 | 14.7633 | 14.7633 | 0
GEN-2018-032 | 03 CENTRAL | 547466 | ATL109 5 | 161 | 16.7858 | 16.7858 | 0
GEN-2018-032 | 03 CENTRAL | 547467 | ORO110 5 | 161 | 20.4976 | 20.4977 | 0.0001
GEN-2018-032 | 03 CENTRAL | 547469 | RIV4525 | 161 | 25.2693 | 25.2693 | 0
GEN-2018-032 | 03 CENTRAL | 547470 | JOP145 5 | 161 | 19.7895 | 19.7896 | 0.0001
GEN-2018-032 | 03 CENTRAL | 547472 | TIP292 5 | 161 | 18.1557 | 18.1557 | 0
GEN-2018-032 | 03 CENTRAL | 547477 | CJ 366 5 | 161 | 12.8502 | 12.8503 | 0.0001
GEN-2018-032 | 03 CENTRAL | 547483 | JOP389 5 | 161 | 20.8326 | 20.8326 | 0
GEN-2018-032 | 03 CENTRAL | 547486 | HOC404 4 | 138 | 6.7764 | 6.7764 | 0
GEN-2018-032 | 03 CENTRAL | 547487 | HOC404 5 | 161 | 13.6845 | 13.6845 | 0
GEN-2018-032 | 03 CENTRAL | 547490 | FIR417 5 | 161 | 14.8464 | 14.8464 | 0
GEN-2018-032 | 03 CENTRAL | 547494 | OAK432 5 | 161 | 18.5046 | 18.5046 | 0
GEN-2018-032 | 03 CENTRAL | 547498 | STL439 5 | 161 | 25.795 | 25.7951 | 0.0001
GEN-2018-032 | 03 CENTRAL | 547501 | RIV453 5 | 161 | 23.9123 | 23.9123 | 0
GEN-2018-032 | 03 CENTRAL | 547502 | RIV167 5 | 161 | 23.3931 | 23.3932 | 0.0001
GEN-2018-032 | 03 CENTRAL | 547503 | RIV452T 5 | 161 | 24.8127 | 24.8128 | 0.0001
GEN-2018-032 | 03 CENTRAL | 547525 | JOP 59 2 | 69 | 20.1613 | 20.1613 | 0
GEN-2018-032 | 03 CENTRAL | 547526 | JOP 64 2 | 69 | 19.7926 | 19.7926 | 0
GEN-2018-032 | 03 CENTRAL | 547527 | WEB436 2 | 69 | 9.7402 | 9.7402 | 0
GEN-2018-032 | 03 CENTRAL | 547530 | COL 94 2 | 69 | 6.6025 | 6.6025 | 0
GEN-2018-032 | 03 CENTRAL | 547534 | ORO110 2 | 69 | 18.4161 | 18.4161 | 0
GEN-2018-032 | 03 CENTRAL | 547539 | JOP145 2 | 69 | 21.4964 | 21.4964 | 0
GEN-2018-032 | 03 CENTRAL | 547541 | RIV167 2 | 69 | 18.1114 | 18.1114 | 0
GEN-2018-032 | 03 CENTRAL | 547551 | GAT258 2 | 69 | 14.7786 | 14.7786 | 0
GEN-2018-032 | 03 CENTRAL | 547554 | BAX271 2 | 69 | 9.7352 | 9.7352 | 0
GEN-2018-032 | 03 CENTRAL | 547555 | GAL278 2 | 69 | 13.4145 | 13.4145 | 0
GEN-2018-032 | 03 CENTRAL | 547556 | OAK280 2 | 69 | 16.2939 | 16.2939 | 0
GEN-2018-032 | 03 CENTRAL | 547574 | JOP341 2 | 69 | 18.5904 | 18.5904 | 0
GEN-2018-032 | 03 CENTRAL | 547592 | JOP389 2 | 69 | 15.7202 | 15.7202 | 0
GEN-2018-032 | 03 CENTRAL | 547601 | HOC404 2 | 69 | 9.8518 | 9.8518 | 0
GEN-2018-032 | 03 CENTRAL | 547602 | RIV406 2 | 69 | 16.061 | 16.0611 | 0.0001
GEN-2018-032 | 03 CENTRAL | 547608 | JOP430 2 | 69 | 16.2258 | 16.2258 | 0
GEN-2018-032 | 03 CENTRAL | 547690 | GLF339 2 | 69 | 12.1857 | 12.1857 | 0
GEN-2018-032 | 03 CENTRAL | 547728 | GAL278T | 69 | 13.7121 | 13.7121 | 0
GEN-2018-032 | 03 CENTRAL | 547729 | BAX488 5 | 161 | 15.4124 | 15.4124 | 0
GEN-2018-032 | 03 CENTRAL | 549969 | BROOKLINE 5 | 161 | 28.8227 | 28.8227 | 0
GEN-2018-032 | 03 CENTRAL | 549984 | BROOKLINE 7 | 345 | 11.8203 | 11.8203 | 0
GEN-2018-032 | 03 CENTRAL | 560053 | G15-052T | 345 | 13.0382 | 13.0382 | 0
GEN-2018-032 | 03 CENTRAL | 560056 | G15-066T | 345 | 18.2418 | 18.2418 | 0
GEN-2018-032 | 03 CENTRAL | 560389 | GEN-2010-055 | 138 | 33.7501 | 33.7501 | 0
GEN-2018-032 | 03 CENTRAL | 578530 | FR3HV | 345 | 5.0735 | 5.0735 | 0
GEN-2018-032 | 03 CENTRAL | 583850 | GEN-2014-001 | 345 | 6.7825 | 6.7825 | 0
GEN-2018-032 | 03 CENTRAL | 583859 | GEN-2014-001 | 345 | 8.4418 | 8.4418 | 0
GEN-2018-032 | 03 CENTRAL | 584900 | GEN-2015-052 | 345 | 12.9916 | 12.9916 | 0
GEN-2018-032 | 03 CENTRAL | 585040 | GEN-2015-066 | 345 | 18.0721 | 18.0721 | 0
GEN-2018-032 | 03 CENTRAL | 588039 | G16133G16146 | 345 | 30.9363 | 30.9363 | 0
GEN-2018-032 | 03 CENTRAL | 588040 | G16133_345GS | 345 | 16.0765 | 16.0765 | 0
GEN-2018-032 | 03 CENTRAL | 588041 | G16133_765GS | 765 | 5.3115 | 5.3115 | 0
GEN-2018-032 | 03 CENTRAL | 588043 | G16133_765MP | 765 | 2.7696 | 2.7696 | 0
GEN-2018-032 | 03 CENTRAL | 588045 | G16133_765CS | 765 | 1.7236 | 1.7236 | 0
GEN-2018-032 | 03 CENTRAL | 588046 | G16133_345CS | 345 | 3.5165 | 3.5165 | 0
GEN-2018-032 | 03 CENTRAL | 588050 | ZONE-1 SUB | 345 | 3.0918 | 3.0918 | 0
GEN-2018-032 | 03 CENTRAL | 588060 | ZONE-2 SUB | 345 | 3.095 | 3.095 | 0
GEN-2018-032 | 03 CENTRAL | 588070 | ZONE-3 SUB | 345 | 3.1589 | 3.1589 | 0
GEN-2018-032 | 03 CENTRAL | 588080 | ZONE-4 SUB | 345 | 3.4897 | 3.4897 | 0
GEN-2018-032 | 03 CENTRAL | 588090 | ZONE-5 SUB | 345 | 3.1518 | 3.1518 | 0
GEN-2018-032 | 03 CENTRAL | 588100 | ZONE-6 SUB | 345 | 3.2918 | 3.2918 | 0
GEN-2018-032 | 03 CENTRAL | 588360 | GEN-2016-153 | 345 | 8.1338 | 8.1338 | 0
GEN-2018-032 | 03 CENTRAL | 588364 | G16-153-TAP | 345 | 8.1338 | 8.1338 | 0
GEN-2018-032 | 03 CENTRAL | 588500 | GEN-2017-005 | 161 | 6.9012 | 6.9013 | 0.0001
GEN-2018-032 | 03 CENTRAL | 588504 | G17-005-TAP | 161 | 6.9847 | 6.9847 | 0
GEN-2018-032 | 03 CENTRAL | 588660 | GEN-2017-022 | 138 | 9.0117 | 9.0117 | 0
GEN-2018-032 | 03 CENTRAL | 588664 | G17-022-TAP | 138 | 9.3753 | 9.3754 | 0.0001
GEN-2018-032 | 03 CENTRAL | 588990 | GEN-2017-061 | 161 | 17.5438 | 17.5438 | 0
GEN-2018-032 | 03 CENTRAL | 589060 | GEN-2017-068 | 138 | 29.2048 | 29.2048 | 0
GEN-2018-032 | 03 CENTRAL | 589240 | GEN-2017-086 | 345 | 8.1338 | 8.1338 | 0
GEN-2018-032 | 03 CENTRAL | 709500 | GI-95_POI | 345 | 7.8354 | 7.8354 | 0
GEN-2018-032 | 03 CENTRAL | 709501 | GI-95_HV | 345 | 7.8354 | 7.8354 | 0
GEN-2018-032 | 03 CENTRAL | 760284 | GEN-2017-220 | 345 | 20.4213 | 20.4213 | 0
GEN-2018-032 | 03 CENTRAL | 760641 | GEN-2017-226 | 138 | 31.9082 | 31.9082 | 0
GEN-2018-032 | 03 CENTRAL | 760914 | GEN-2017-209 | 345 | 19.1898 | 19.1898 | 0
GEN-2018-032 | 03 CENTRAL | 760921 | G17-209-TAP | 345 | 19.691 | 19.691 | 0
GEN-2018-032 | 03 CENTRAL | 761271 | GEN-2017-108 | 161 | 13.313 | 13.313 | 0
GEN-2018-032 | 03 CENTRAL | 761278 | G17-108-TAP | 161 | 13.313 | 13.313 | 0
GEN-2018-032 | 03 CENTRAL | 762279 | GEN-2017-195 | 345 | 28.4265 | 28.4265 | 0
GEN-2018-032 | 03 CENTRAL | 762405 | ASG-2018-010 | 161 | 3.4283 | 3.4283 | 0
GEN-2018-032 | 03 CENTRAL | 762636 | GEN-2018-028 | 138 | 35.8108 | 35.8108 | 0
GEN-2018-032 | 03 CENTRAL | 762680 | GEN-2018-032 | 345 | 11.9861 | 11.9867 | 0.0006
GEN-2018-032 | 03 CENTRAL | 762823 | GEN-2018-048 | 345 | 16.0145 | 16.0145 | 0
GEN-2018-032 | 03 CENTRAL | 762922 | GEN-2018-057 | 138 | 17.5874 | 17.5874 | 0
GEN-2018-049 | 03 CENTRAL | 300739 | 7BLACKBERRY | 345 | 15.7375 | 15.7378 | 0.0003
GEN-2018-049 | 03 CENTRAL | 511553 | CHISHOLM7 | 345 | 10.5729 | 10.5748 | 0.0019
GEN-2018-049 | 03 CENTRAL | 511557 | CHISHOLM6 | 230 | 11.7226 | 11.7237 | 0.0011
GEN-2018-049 | 03 CENTRAL | 514771 | TANGIER2 | 69 | 3.8551 | 3.8552 | 0.0001
GEN-2018-049 | 03 CENTRAL | 514773 | NEWMAN 2 | 69 | 1.6231 | 1.6231 | 0
GEN-2018-049 | 03 CENTRAL | 514775 | TANGRTP2 | 69 | 5.0122 | 5.0123 | 0.0001
GEN-2018-049 | 03 CENTRAL | 514776 | NEWGRTP2 | 69 | 5.7227 | 5.7229 | 0.0002
GEN-2018-049 | 03 CENTRAL | 514778 | CLEOCOR4 | 138 | 5.7859 | 5.7862 | 0.0003
GEN-2018-049 | 03 CENTRAL | 514779 | WDNITRO2 | 69 | 4.9995 | 4.9997 | 0.0002
GEN-2018-049 | 03 CENTRAL | 514781 | CEDARAV2 | 69 | 5.9753 | 5.9755 | 0.0002
GEN-2018-049 | 03 CENTRAL | 514782 | WODWRD 2 | 69 | 11.4382 | 11.439 | 0.0008
GEN-2018-049 | 03 CENTRAL | 514785 | WOODWRD4 | 138 | 13.638 | 13.6407 | 0.0027
GEN-2018-049 | 03 CENTRAL | 514788 | GLASMTN4 | 138 | 5.1885 | 5.1887 | 0.0002
GEN-2018-049 | 03 CENTRAL | 514792 | ALVAOGE2 | 69 | 7.6925 | 7.6938 | 0.0013
GEN-2018-049 | 03 CENTRAL | 514794 | KNOBHIL2 | 69 | 9.032 | 9.0341 | 0.0021
GEN-2018-049 | 03 CENTRAL | 514795 | KNOBHIL4 | 138 | 9.8173 | 9.824 | 0.0067
GEN-2018-049 | 03 CENTRAL | 514796 | IODINE-4 | 138 | 7.6901 | 7.691 | 0.0009
GEN-2018-049 | 03 CENTRAL | 514880 | NORTWST7 | 345 | 32.025 | 32.0294 | 0.0044
GEN-2018-049 | 03 CENTRAL | 514901 | CIMARON7 | 345 | 33.5506 | 33.5558 | 0.0052
GEN-2018-049 | 03 CENTRAL | 515363 | CENT 4 | 138 | 3.2663 | 3.2664 | 0.0001
GEN-2018-049 | 03 CENTRAL | 515375 | WWRDEHV7 | 345 | 20.0637 | 20.0964 | 0.0327
GEN-2018-049 | 03 CENTRAL | 515376 | WWRDEHV4 | 138 | 24.8831 | 24.8979 | 0.0148
GEN-2018-049 | 03 CENTRAL | 515394 | KEENAN 4 | 138 | 9.229 | 9.2308 | 0.0018
GEN-2018-049 | 03 CENTRAL | 515398 | OUSPRT 4 | 138 | 9.8862 | 9.8884 | 0.0022
GEN-2018-049 | 03 CENTRAL | 515407 | TATONGA7 | 345 | 17.6903 | 17.7005 | 0.0102
GEN-2018-049 | 03 CENTRAL | 515425 | WWDPST 4 | 138 | 18.1569 | 18.1638 | 0.0069
GEN-2018-049 | 03 CENTRAL | 515448 | CRSRDSW7 | 345 | 12.3861 | 12.391 | 0.0049
GEN-2018-049 | 03 CENTRAL | 515458 | BORDER 7 | 345 | 7.6019 | 7.6028 | 0.0009
GEN-2018-049 | 03 CENTRAL | 515476 | HUNTERS7 | 345 | 12.2107 | 12.2138 | 0.0031
GEN-2018-049 | 03 CENTRAL | 515477 | CHSHLMV7 | 345 | 12.1936 | 12.1968 | 0.0032
GEN-2018-049 | 03 CENTRAL | 515497 | MATHWSN7 | 345 | 31.3188 | 31.3258 | 0.007
GEN-2018-049 | 03 CENTRAL | 515533 | REDCLFT4 | 138 | 7.0092 | 7.0098 | 0.0006
GEN-2018-049 | 03 CENTRAL | 515543 | RENFROW7 | 345 | 11.9587 | 11.9635 | 0.0048
GEN-2018-049 | 03 CENTRAL | 515544 | RENFROW4 | 138 | 14.2298 | 14.2327 | 0.0029
GEN-2018-049 | 03 CENTRAL | 515554 | BVRCNTY7 | 345 | 12.5533 | 12.5573 | 0.004
GEN-2018-049 | 03 CENTRAL | 515560 | CZYCRVT2 | 69 | 3.378 | 3.3782 | 0.0002
GEN-2018-049 | 03 CENTRAL | 515582 | SLNGWND7 | 345 | 8.7253 | 8.7276 | 0.0023
GEN-2018-049 | 03 CENTRAL | 515585 | MAMTHPW7 | 345 | 14.0216 | 14.0279 | 0.0063
GEN-2018-049 | 03 CENTRAL | 515590 | PALDR2W7 | 345 | 11.2693 | 11.2724 | 0.0031
GEN-2018-049 | 03 CENTRAL | 515599 | G07621119-20 | 345 | 12.2908 | 12.3031 | 0.0123
GEN-2018-049 | 03 CENTRAL | 515600 | KNGFSHR7 | 345 | 12.2236 | 12.2241 | 0.0005
GEN-2018-049 | 03 CENTRAL | 515605 | CANADN7 | 345 | 13.2882 | 13.2889 | 0.0007
GEN-2018-049 | 03 CENTRAL | 515618 | BALKOW 7 | 345 | 10.8072 | 10.81 | 0.0028
GEN-2018-049 | 03 CENTRAL | 515634 | PALDR1W7 | 345 | 10.1667 | 10.1691 | 0.0024
GEN-2018-049 | 03 CENTRAL | 515646 | GRNTWD 7 | 345 | 10.5712 | 10.5749 | 0.0037
GEN-2018-049 | 03 CENTRAL | 515677 | BADGER 7 | 345 | 12.2868 | 12.2919 | 0.0051
GEN-2018-049 | 03 CENTRAL | 515686 | BLUWND 7 | 345 | 11.1436 | 11.1478 | 0.0042
GEN-2018-049 | 03 CENTRAL | 515785 | WINDFRM4 | 138 | 20.6606 | 20.6637 | 0.0031
GEN-2018-049 | 03 CENTRAL | 515786 | FPLWIND4 | 138 | 7.1215 | 7.1218 | 0.0003
GEN-2018-049 | 03 CENTRAL | 515825 | GRTWSRN7 | 345 | 8.908 | 8.9144 | 0.0064
GEN-2018-049 | 03 CENTRAL | 515852 | DGRASSE7 | 345 | 14.6085 | 14.6775 | 0.069
GEN-2018-049 | 03 CENTRAL | 515853 | DGRASSE4 | 138 | 14.851 | 14.8696 | 0.0186
GEN-2018-049 | 03 CENTRAL | 515863 | REDCLF 4 | 138 | 6.9941 | 6.9947 | 0.0006
GEN-2018-049 | 03 CENTRAL | 515875 | REDNGTN7 | 345 | 16.2548 | 16.2573 | 0.0025
GEN-2018-049 | 03 CENTRAL | 515877 | REDDIRT7 | 345 | 16.2509 | 16.2534 | 0.0025
GEN-2018-049 | 03 CENTRAL | 515951 | PERSIMN7 | 345 | 10.7278 | 10.7371 | 0.0093
GEN-2018-049 | 03 CENTRAL | 515961 | GUTHRIE7 | 345 | 12.3166 | 12.3289 | 0.0123
GEN-2018-049 | 03 CENTRAL | 516025 | SUNDANC4 | 138 | 3.7857 | 3.7858 | 0.0001
GEN-2018-049 | 03 CENTRAL | 516059 | BECKHAM7 | 345 | 10.5606 | 10.5626 | 0.002
GEN-2018-049 | 03 CENTRAL | 516146 | 25MILE 7 | 345 | 11.2189 | 11.2257 | 0.0068
GEN-2018-049 | 03 CENTRAL | 516159 | 25MILZ 7 | 345 | 11.2079 | 11.2147 | 0.0068
GEN-2018-049 | 03 CENTRAL | 520425 | PIC4 | 138 | 8.3506 | 8.351 | 0.0004
GEN-2018-049 | 03 CENTRAL | 520430 | NOELSW 4 | 138 | 9.8819 | 9.8887 | 0.0068
GEN-2018-049 | 03 CENTRAL | 520436 | ROSEVLY4 | 138 | 11.3697 | 11.3801 | 0.0104
GEN-2018-049 | 03 CENTRAL | 520437 | SALTPLN4 | 138 | 6.3642 | 6.3663 | 0.0021
GEN-2018-049 | 03 CENTRAL | 520462 | ASPEN 4 | 138 | 20.3718 | 20.3748 | 0.003
GEN-2018-049 | 03 CENTRAL | 520480 | CURTIS 2 | 69 | 4.1214 | 4.1215 | 0.0001
GEN-2018-049 | 03 CENTRAL | 520500 | BEARCAT4 | 138 | 14.9982 | 14.9998 | 0.0016
GEN-2018-049 | 03 CENTRAL | 520507 | CEDRDAL4 | 138 | 4.7892 | 4.7893 | 0.0001
GEN-2018-049 | 03 CENTRAL | 520553 | SEILING4 | 138 | 7.0469 | 7.0473 | 0.0004
GEN-2018-049 | 03 CENTRAL | 520601 | AVARD 4 | 138 | 6.68 | 6.6836 | 0.0036
GEN-2018-049 | 03 CENTRAL | 520848 | CDRDLTP4 | 138 | 5.9497 | 5.9499 | 0.0002
GEN-2018-049 | 03 CENTRAL | 520920 | FTSUPLY4 | 138 | 5.7915 | 5.7917 | 0.0002
GEN-2018-049 | 03 CENTRAL | 520922 | SLEEPBR4 | 138 | 4.6434 | 4.6435 | 0.0001
GEN-2018-049 | 03 CENTRAL | 520957 | IODINE 4 | 138 | 8.2466 | 8.247 | 0.0004
GEN-2018-049 | 03 CENTRAL | 520995 | MOORLND2 | 69 | 8.9651 | 8.9654 | 0.0003
GEN-2018-049 | 03 CENTRAL | 520999 | MOORLND4 | 138 | 21.1172 | 21.1203 | 0.0031
GEN-2018-049 | 03 CENTRAL | 521065 | TALOGA 4 | 138 | 7.7158 | 7.7163 | 0.0005
GEN-2018-049 | 03 CENTRAL | 521197 | CRTSJCT2 | 69 | 8.5532 | 8.5535 | 0.0003
GEN-2018-049 | 03 CENTRAL | 523118 | BUFF_DUNES 7 | 345 | 6.7925 | 6.7936 | 0.0011
GEN-2018-049 | 03 CENTRAL | 523853 | FINNEY 7 | 345 | 10.4284 | 10.4315 | 0.0031
GEN-2018-049 | 03 CENTRAL | 525832 | TUCO_INT 7 | 345 | 12.7944 | 12.7945 | 0.0001
GEN-2018-049 | 03 CENTRAL | 525850 | ELK_CT1 | 345 | 12.6944 | 12.6945 | 0.0001
GEN-2018-049 | 03 CENTRAL | 530558 | KNOLL N 6 | 230 | 11.9209 | 11.9238 | 0.0029
GEN-2018-049 | 03 CENTRAL | 530582 | S HAYS6 | 230 | 9.7677 | 9.7697 | 0.002
GEN-2018-049 | 03 CENTRAL | 530583 | POSTROCK7 | 345 | 8.2596 | 8.2624 | 0.0028
GEN-2018-049 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 12.0331 | 12.0361 | 0.003
GEN-2018-049 | 03 CENTRAL | 530610 | SHAYS_230 | 230 | 4.4121 | 4.4124 | 0.0003
GEN-2018-049 | 03 CENTRAL | 530680 | HEIZER 6 | 230 | 8.4236 | 8.4258 | 0.0022
GEN-2018-049 | 03 CENTRAL | 530702 | BUCKEYE_230 | 230 | 9.0409 | 9.0424 | 0.0015
GEN-2018-049 | 03 CENTRAL | 530720 | KNOLL S 6 | 230 | 11.9209 | 11.9238 | 0.0029
GEN-2018-049 | 03 CENTRAL | 531448 | HOLCOMB3 | 115 | 21.7038 | 21.7056 | 0.0018
GEN-2018-049 | 03 CENTRAL | 531449 | HOLCOMB7 | 345 | 10.5388 | 10.542 | 0.0032
GEN-2018-049 | 03 CENTRAL | 531465 | SETAB 7 | 345 | 7.2494 | 7.2504 | 0.001
GEN-2018-049 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 13.2756 | 13.2975 | 0.0219
GEN-2018-049 | 03 CENTRAL | 531501 | BUCKNER7 | 345 | 9.845 | 9.8511 | 0.0061
GEN-2018-049 | 03 CENTRAL | 531502 | CIMRRN 7 | 345 | 7.7528 | 7.7566 | 0.0038
GEN-2018-049 | 03 CENTRAL | 531504 | CIMWD2 7 | 345 | 8.0492 | 8.0531 | 0.0039
GEN-2018-049 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 17.3967 | 17.3988 | 0.0021
GEN-2018-049 | 03 CENTRAL | 532769 | LANG 7 | 345 | 17.1976 | 17.1997 | 0.0021
GEN-2018-049 | 03 CENTRAL | 532770 | MORRIS 7 | 345 | 13.1896 | 13.1905 | 0.0009
GEN-2018-049 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.5891 | 11.5961 | 0.007
GEN-2018-049 | 03 CENTRAL | 532773 | SUMMIT 7 | 345 | 11.6236 | 11.6259 | 0.0023
GEN-2018-049 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 17.0367 | 17.0373 | 0.0006
GEN-2018-049 | 03 CENTRAL | 532776 | READWF 7 | 345 | 14.4492 | 14.4507 | 0.0015
GEN-2018-049 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 20.459 | 20.5277 | 0.0687
GEN-2018-049 | 03 CENTRAL | 532783 | KINGMAN7 | 345 | 7.221 | 7.2273 | 0.0063
GEN-2018-049 | 03 CENTRAL | 532784 | NINN1WF7 | 345 | 6.0427 | 6.0468 | 0.0041
GEN-2018-049 | 03 CENTRAL | 532785 | PRATTWF7 | 345 | 5.0308 | 5.0335 | 0.0027
GEN-2018-049 | 03 CENTRAL | 532791 | BENTON 7 | 345 | 18.9772 | 18.996 | 0.0188
GEN-2018-049 | 03 CENTRAL | 532792 | FR2EAST7 | 345 | 6.8229 | 6.8252 | 0.0023
GEN-2018-049 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 18.7345 | 18.7456 | 0.0111
GEN-2018-049 | 03 CENTRAL | 532795 | FR2WEST7 | 345 | 5.5181 | 5.5195 | 0.0014
GEN-2018-049 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 23.4593 | 23.5186 | 0.0593
GEN-2018-049 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 18.6601 | 18.662 | 0.0019
GEN-2018-049 | 03 CENTRAL | 532798 | VIOLA 7 | 345 | 13.8187 | 13.8306 | 0.0119
GEN-2018-049 | 03 CENTRAL | 532799 | WAVERLY7 | 345 | 16.5248 | 16.5261 | 0.0013
GEN-2018-049 | 03 CENTRAL | 532800 | LATHAMS7 | 345 | 10.3806 | 10.3826 | 0.002
GEN-2018-049 | 03 CENTRAL | 532801 | ELKRVR17 | 345 | 9.2138 | 9.2154 | 0.0016
GEN-2018-049 | 03 CENTRAL | 532802 | WAVERTX7 | 345 | 13.7771 | 13.778 | 0.0009
GEN-2018-049 | 03 CENTRAL | 532803 | EXPEDITION7 | 345 | 10.8947 | 10.9007 | 0.006
GEN-2018-049 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 9.0275 | 9.0293 | 0.0018
GEN-2018-049 | 03 CENTRAL | 532984 | SUMNER 4 | 138 | 11.9691 | 11.9712 | 0.0021
GEN-2018-049 | 03 CENTRAL | 532986 | BENTON 4 | 138 | 28.218 | 28.234 | 0.016
GEN-2018-049 | 03 CENTRAL | 532988 | BELAIRE4 | 138 | 19.2088 | 19.2161 | 0.0073
GEN-2018-049 | 03 CENTRAL | 532990 | MIDIAN 4 | 138 | 11.278 | 11.2801 | 0.0021
GEN-2018-049 | 03 CENTRAL | 532994 | TCBURNS4 | 138 | 4.1369 | 4.1372 | 0.0003
GEN-2018-049 | 03 CENTRAL | 533015 | BENTLEY4 | 138 | 11.0184 | 11.0217 | 0.0033
GEN-2018-049 | 03 CENTRAL | 533016 | WWUPLNT4 | 138 | 8.3721 | 8.3739 | 0.0018
GEN-2018-049 | 03 CENTRAL | 533024 | 29TH 4 | 138 | 19.8454 | 19.8532 | 0.0078
GEN-2018-049 | 03 CENTRAL | 533035 | CHISHLM4 | 138 | 21.6628 | 21.6734 | 0.0106
GEN-2018-049 | 03 CENTRAL | 533036 | CLEARWT4 | 138 | 14.4871 | 14.4924 | 0.0053
GEN-2018-049 | 03 CENTRAL | 533040 | EVANS N4 | 138 | 32.0484 | 32.0782 | 0.0298
GEN-2018-049 | 03 CENTRAL | 533041 | EVANS S4 | 138 | 31.9733 | 32.003 | 0.0297
GEN-2018-049 | 03 CENTRAL | 533047 | GILL 4 | 138 | 22.094 | 22.1057 | 0.0117
GEN-2018-049 | 03 CENTRAL | 533052 | PARKCTY4 | 138 | 20.4971 | 20.5064 | 0.0093
GEN-2018-049 | 03 CENTRAL | 533053 | LAKERDG4 | 138 | 17.4442 | 17.4524 | 0.0082
GEN-2018-049 | 03 CENTRAL | 533054 | MAIZE 4 | 138 | 21.1129 | 21.1247 | 0.0118
GEN-2018-049 | 03 CENTRAL | 533062 | ROSEHIL4 | 138 | 31.2043 | 31.2189 | 0.0146
GEN-2018-049 | 03 CENTRAL | 533065 | SG12COL4 | 138 | 19.6468 | 19.6578 | 0.011
GEN-2018-049 | 03 CENTRAL | 533074 | 45TH ST4 | 138 | 23.8032 | 23.8194 | 0.0162
GEN-2018-049 | 03 CENTRAL | 533075 | VIOLA 4 | 138 | 24.8331 | 24.8508 | 0.0177
GEN-2018-049 | 03 CENTRAL | 533413 | CIRCLE 3 | 115 | 19.3063 | 19.3116 | 0.0053
GEN-2018-049 | 03 CENTRAL | 533415 | DAVIS 3 | 115 | 8.4365 | 8.4375 | 0.001
GEN-2018-049 | 03 CENTRAL | 533416 | RENO 3 | 115 | 23.2561 | 23.2643 | 0.0082
GEN-2018-049 | 03 CENTRAL | 533429 | MOUNDRG3 | 115 | 8.805 | 8.8063 | 0.0013
GEN-2018-049 | 03 CENTRAL | 533430 | MNDRGCT3 | 115 | 6.7929 | 6.7936 | 0.0007
GEN-2018-049 | 03 CENTRAL | 533438 | WMCPHER3 | 115 | 11.4573 | 11.4584 | 0.0011
GEN-2018-049 | 03 CENTRAL | 533629 | CC2SHAR2 | 69 | 4.8209 | 4.8209 | 0
GEN-2018-049 | 03 CENTRAL | 533653 | WOLFCRK2 | 69 | 6.2331 | 6.2331 | 0
GEN-2018-049 | 03 CENTRAL | 539000 | RAGO 4 | 138 | 4.1258 | 4.1277 | 0.0019
GEN-2018-049 | 03 CENTRAL | 539001 | ANTHONY4 | 138 | 5.2346 | 5.237 | 0.0024
GEN-2018-049 | 03 CENTRAL | 539002 | BLF-CRK4 | 138 | 4.8996 | 4.9012 | 0.0016
GEN-2018-049 | 03 CENTRAL | 539008 | MILAN_GOAB | 138 | 12.1394 | 12.1443 | 0.0049
GEN-2018-049 | 03 CENTRAL | 539009 | CONWAY | 138 | 11.6502 | 11.6555 | 0.0053
GEN-2018-049 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 12.0685 | 12.0785 | 0.01
GEN-2018-049 | 03 CENTRAL | 539132 | SPRVILL-EHV2 | 230 | 10.3545 | 10.3618 | 0.0073
GEN-2018-049 | 03 CENTRAL | 539628 | NW-DGTP3 | 115 | 3.5319 | 3.5322 | 0.0003
GEN-2018-049 | 03 CENTRAL | 539631 | FLATRWD4 | 138 | 10.748 | 10.7748 | 0.0268
GEN-2018-049 | 03 CENTRAL | 539638 | FLATRDG4 | 138 | 15.9903 | 16.0515 | 0.0612
GEN-2018-049 | 03 CENTRAL | 539641 | NW-DODG3 | 115 | 3.6462 | 3.6466 | 0.0004
GEN-2018-049 | 03 CENTRAL | 539645 | DCBEEF3 | 115 | 6.8741 | 6.8756 | 0.0015
GEN-2018-049 | 03 CENTRAL | 539649 | SAWYER 3 | 115 | 4.7129 | 4.7149 | 0.002
GEN-2018-049 | 03 CENTRAL | 539661 | 24-FREY3 | 115 | 5.4835 | 5.484 | 0.0005
GEN-2018-049 | 03 CENTRAL | 539667 | HAGGARD3 | 115 | 2.4367 | 2.4368 | 0.0001
GEN-2018-049 | 03 CENTRAL | 539668 | HARPER 4 | 138 | 7.5121 | 7.5183 | 0.0062
GEN-2018-049 | 03 CENTRAL | 539671 | FTDODGE3 | 115 | 9.3876 | 9.3903 | 0.0027
GEN-2018-049 | 03 CENTRAL | 539673 | MED-LDG3 | 115 | 8.2282 | 8.2378 | 0.0096
GEN-2018-049 | 03 CENTRAL | 539674 | BARBER 4 | 138 | 8.5156 | 8.5298 | 0.0142
GEN-2018-049 | 03 CENTRAL | 539675 | MILANTP4 | 138 | 10.2961 | 10.3007 | 0.0046
GEN-2018-049 | 03 CENTRAL | 539676 | MILAN 4 | 138 | 10.7881 | 10.792 | 0.0039
GEN-2018-049 | 03 CENTRAL | 539678 | GRTBEND3 | 115 | 11.5441 | 11.5463 | 0.0022
GEN-2018-049 | 03 CENTRAL | 539679 | GRTBEND6 | 230 | 8.4762 | 8.4785 | 0.0023
GEN-2018-049 | 03 CENTRAL | 539680 | N-DODGE3 | 115 | 4.6702 | 4.6709 | 0.0007
GEN-2018-049 | 03 CENTRAL | 539681 | N-GBEND3 | 115 | 7.8721 | 7.8731 | 0.001
GEN-2018-049 | 03 CENTRAL | 539684 | OTISSUB3 | 115 | 2.9865 | 2.9866 | 0.0001
GEN-2018-049 | 03 CENTRAL | 539688 | S-DODGE3 | 115 | 6.6988 | 6.7001 | 0.0013
GEN-2018-049 | 03 CENTRAL | 539689 | 2ND-KS 3 | 115 | 4.958 | 4.9584 | 0.0004
GEN-2018-049 | 03 CENTRAL | 539694 | SPEARVL3 | 115 | 10.0245 | 10.0278 | 0.0033
GEN-2018-049 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 12.3621 | 12.3726 | 0.0105
GEN-2018-049 | 03 CENTRAL | 539699 | W-DODGE3 | 115 | 4.3189 | 4.3194 | 0.0005
GEN-2018-049 | 03 CENTRAL | 539740 | EDODGE 3 | 115 | 6.2951 | 6.2963 | 0.0012
GEN-2018-049 | 03 CENTRAL | 539758 | FORD 3 | 115 | 5.2716 | 5.2726 | 0.001
GEN-2018-049 | 03 CENTRAL | 539759 | SPRVL 3 | 115 | 13.0192 | 13.0257 | 0.0065
GEN-2018-049 | 03 CENTRAL | 539760 | BARBER 3 | 115 | 8.4102 | 8.4202 | 0.01
GEN-2018-049 | 03 CENTRAL | 539771 | NFTDODG3 | 115 | 9.4408 | 9.4435 | 0.0027
GEN-2018-049 | 03 CENTRAL | 539778 | GYCOTAP3 | 115 | 2.4367 | 2.4368 | 0.0001
GEN-2018-049 | 03 CENTRAL | 539779 | GRAY CO3 | 115 | 2.4367 | 2.4368 | 0.0001
GEN-2018-049 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 13.08 | 13.1183 | 0.0383
GEN-2018-049 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 16.4653 | 16.6971 | 0.2318
GEN-2018-049 | 03 CENTRAL | 539803 | IRONWOOD7 | 345 | 12.7799 | 12.8009 | 0.021
GEN-2018-049 | 03 CENTRAL | 539804 | THISTLE4 | 138 | 17.9862 | 18.0705 | 0.0843
GEN-2018-049 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 10.9763 | 11.003 | 0.0267
GEN-2018-049 | 03 CENTRAL | 539815 | IRONWOOD WF7 | 345 | 11.543 | 11.5602 | 0.0172
GEN-2018-049 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 11.1802 | 11.2062 | 0.026
GEN-2018-049 | 03 CENTRAL | 539841 | G-2011-008-1 | 345 | 11.1802 | 11.2062 | 0.026
GEN-2018-049 | 03 CENTRAL | 539855 | G-2011-008-2 | 345 | 9.4892 | 9.5074 | 0.0182
GEN-2018-049 | 03 CENTRAL | 539857 | G-2011-008-3 | 345 | 8.7443 | 8.7598 | 0.0155
GEN-2018-049 | 03 CENTRAL | 539944 | LOCHS | 115 | 3.2661 | 3.2663 | 0.0002
GEN-2018-049 | 03 CENTRAL | 560053 | G15-052T | 345 | 13.0351 | 13.0382 | 0.0031
GEN-2018-049 | 03 CENTRAL | 560071 | G16-003-TAP | 345 | 15.4726 | 15.4867 | 0.0141
GEN-2018-049 | 03 CENTRAL | 560078 | G16-037-TAP | 345 | 9.1295 | 9.1303 | 0.0008
GEN-2018-049 | 03 CENTRAL | 560080 | G16-046-TAP | 345 | 11.4901 | 11.5137 | 0.0236
GEN-2018-049 | 03 CENTRAL | 560082 | G16-050-TAP | 345 | 6.8174 | 6.8178 | 0.0004
GEN-2018-049 | 03 CENTRAL | 578530 | FR3HV | 345 | 5.0723 | 5.0735 | 0.0012
GEN-2018-049 | 03 CENTRAL | 579480 | GEN-2008-124 | 345 | 12.3744 | 12.394 | 0.0196
GEN-2018-049 | 03 CENTRAL | 583850 | GEN-2014-001 | 345 | 6.7803 | 6.7825 | 0.0022
GEN-2018-049 | 03 CENTRAL | 583859 | GEN-2014-001 | 345 | 8.4383 | 8.4418 | 0.0035
GEN-2018-049 | 03 CENTRAL | 584900 | GEN-2015-052 | 345 | 12.9885 | 12.9916 | 0.0031
GEN-2018-049 | 03 CENTRAL | 585190 | GEN-2015-082 | 345 | 6.5469 | 6.5484 | 0.0015
GEN-2018-049 | 03 CENTRAL | 585410 | GREAT_WESTRN | 345 | 8.926 | 8.9325 | 0.0065
GEN-2018-049 | 03 CENTRAL | 585420 | COWBOY_RIDGE | 345 | 6.8695 | 6.8734 | 0.0039
GEN-2018-049 | 03 CENTRAL | 585430 | PRSIMN_CRK1 | 345 | 10.8289 | 10.8384 | 0.0095
GEN-2018-049 | 03 CENTRAL | 585440 | PRSIMN_CRK2 | 345 | 9.9419 | 9.95 | 0.0081
GEN-2018-049 | 03 CENTRAL | 587140 | GEN-2016-020 | 138 | 7.2143 | 7.2147 | 0.0004
GEN-2018-049 | 03 CENTRAL | 587230 | GEN-2016-037 | 345 | 8.7156 | 8.7163 | 0.0007
GEN-2018-049 | 03 CENTRAL | 587310 | GEN-2016-046 | 345 | 10.1122 | 10.1302 | 0.018
GEN-2018-049 | 03 CENTRAL | 587311 | G16-046XFMR1 | 115 | 15.2953 | 15.3069 | 0.0116
GEN-2018-049 | 03 CENTRAL | 587350 | GEN-2016-050 | 345 | 5.6712 | 5.6715 | 0.0003
GEN-2018-049 | 03 CENTRAL | 587880 | GEN-2016-111 | 345 | 6.8325 | 6.834 | 0.0015
GEN-2018-049 | 03 CENTRAL | 587884 | G16-111-TAP | 345 | 10.2847 | 10.2885 | 0.0038
GEN-2018-049 | 03 CENTRAL | 588360 | GEN-2016-153 | 345 | 8.1304 | 8.1338 | 0.0034
GEN-2018-049 | 03 CENTRAL | 588364 | G16-153-TAP | 345 | 8.1304 | 8.1338 | 0.0034
GEN-2018-049 | 03 CENTRAL | 588560 | GEN-2017-011 | 345 | 12.5311 | 12.5403 | 0.0092
GEN-2018-049 | 03 CENTRAL | 588630 | GEN-2017-018 | 345 | 16.4653 | 16.6971 | 0.2318
GEN-2018-049 | 03 CENTRAL | 589060 | GEN-2017-068 | 138 | 29.1802 | 29.2048 | 0.0246
GEN-2018-049 | 03 CENTRAL | 589240 | GEN-2017-086 | 345 | 8.1304 | 8.1338 | 0.0034
GEN-2018-049 | 03 CENTRAL | 599950 | LAMAR7 | 345 | 2.5159 | 2.516 | 0.0001
GEN-2018-049 | 03 CENTRAL | 640065 | AXTELL 3 | 345 | 9.1922 | 9.1925 | 0.0003
GEN-2018-049 | 03 CENTRAL | 760284 | GEN-2017-220 | 345 | 20.3534 | 20.4213 | 0.0679
GEN-2018-049 | 03 CENTRAL | 760641 | GEN-2017-226 | 138 | 31.8787 | 31.9082 | 0.0295
GEN-2018-049 | 03 CENTRAL | 760809 | GEN-2017-203 | 345 | 8.5998 | 8.6023 | 0.0025
GEN-2018-049 | 03 CENTRAL | 761838 | GEN-2017-121 | 138 | 9.1004 | 9.1015 | 0.0011
GEN-2018-049 | 03 CENTRAL | 762834 | GEN-2018-049 | 345 | 6.9299 | 7.1664 | 0.2365
GEN-2018-049 | 03 CENTRAL | 762922 | GEN-2018-057 | 138 | 17.5789 | 17.5874 | 0.0085
GEN-2018-049 | 03 CENTRAL | 900001 | TRAVERSE3 | 345 | 5.4567 | 5.4569 | 0.0002
GEN-2018-049 | 03 CENTRAL | 900002 | TRAVERSE-2 | 345 | 4.0892 | 4.0893 | 0.0001
GEN-2018-049 | 03 CENTRAL | 900003 | TRAVERSE1 | 345 | 3.8013 | 3.8014 | 0.0001
GEN-2018-049 | 03 CENTRAL | 900004 | TRW2-TRW3 | 345 | 4.7474 | 4.7476 | 0.0002
GEN-2018-057 | 03 CENTRAL | 300739 | 7BLACKBERRY | 345 | 15.7356 | 15.7378 | 0.0022
GEN-2018-057 | 03 CENTRAL | 300740 | 7SPORTSMAN | 345 | 24.7781 | 24.7786 | 0.0005
GEN-2018-057 | 03 CENTRAL | 300949 | 7JASPER | 345 | 12.7827 | 12.7837 | 0.001
GEN-2018-057 | 03 CENTRAL | 514715 | WOODRNG7 | 345 | 17.0779 | 17.0868 | 0.0089
GEN-2018-057 | 03 CENTRAL | 514825 | KAYWIND7 | 345 | 12.0457 | 12.0554 | 0.0097
GEN-2018-057 | 03 CENTRAL | 515375 | WWRDEHV7 | 345 | 20.09 | 20.0964 | 0.0064
GEN-2018-057 | 03 CENTRAL | 515476 | HUNTERS7 | 345 | 12.2036 | 12.2138 | 0.0102
GEN-2018-057 | 03 CENTRAL | 515477 | CHSHLMV7 | 345 | 12.1866 | 12.1968 | 0.0102
GEN-2018-057 | 03 CENTRAL | 515543 | RENFROW7 | 345 | 11.946 | 11.9635 | 0.0175
GEN-2018-057 | 03 CENTRAL | 515544 | RENFROW4 | 138 | 14.2248 | 14.2327 | 0.0079
GEN-2018-057 | 03 CENTRAL | 515546 | GRANTCO4 | 138 | 6.5942 | 6.5957 | 0.0015
GEN-2018-057 | 03 CENTRAL | 515569 | MDFRDTP4 | 138 | 11.3378 | 11.3426 | 0.0048
GEN-2018-057 | 03 CENTRAL | 515599 | G07621119-20 | 345 | 12.3007 | 12.3031 | 0.0024
GEN-2018-057 | 03 CENTRAL | 515621 | OPENSKY7 | 345 | 12.0757 | 12.0855 | 0.0098
GEN-2018-057 | 03 CENTRAL | 515646 | GRNTWD 7 | 345 | 10.5614 | 10.5749 | 0.0135
GEN-2018-057 | 03 CENTRAL | 515825 | GRTWSRN7 | 345 | 8.9132 | 8.9144 | 0.0012
GEN-2018-057 | 03 CENTRAL | 515852 | DGRASSE7 | 345 | 14.6662 | 14.6775 | 0.0113
GEN-2018-057 | 03 CENTRAL | 515853 | DGRASSE4 | 138 | 14.8657 | 14.8696 | 0.0039
GEN-2018-057 | 03 CENTRAL | 515951 | PERSIMN7 | 345 | 10.7353 | 10.7371 | 0.0018
GEN-2018-057 | 03 CENTRAL | 515961 | GUTHRIE7 | 345 | 12.3265 | 12.3289 | 0.0024
GEN-2018-057 | 03 CENTRAL | 515990 | SKELTON7 | 345 | 4.2643 | 4.2648 | 0.0005
GEN-2018-057 | 03 CENTRAL | 520409 | WFEC_RNFRO4 | 138 | 10.6549 | 10.6591 | 0.0042
GEN-2018-057 | 03 CENTRAL | 522397 | MEDFORD4 | 138 | 7.5521 | 7.5542 | 0.0021
GEN-2018-057 | 03 CENTRAL | 522398 | PONDCRK4 | 138 | 5.2006 | 5.2017 | 0.0011
GEN-2018-057 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 13.2933 | 13.2975 | 0.0042
GEN-2018-057 | 03 CENTRAL | 532766 | JEC N 7 | 345 | 24.8236 | 24.8272 | 0.0036
GEN-2018-057 | 03 CENTRAL | 532767 | GEARY 7 | 345 | 10.6201 | 10.623 | 0.0029
GEN-2018-057 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 17.3894 | 17.3988 | 0.0094
GEN-2018-057 | 03 CENTRAL | 532769 | LANG 7 | 345 | 17.1905 | 17.1997 | 0.0092
GEN-2018-057 | 03 CENTRAL | 532770 | MORRIS 7 | 345 | 13.1868 | 13.1905 | 0.0037
GEN-2018-057 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.5666 | 11.5961 | 0.0295
GEN-2018-057 | 03 CENTRAL | 532773 | SUMMIT 7 | 345 | 11.6171 | 11.6259 | 0.0088
GEN-2018-057 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 17.0343 | 17.0373 | 0.003
GEN-2018-057 | 03 CENTRAL | 532776 | READWF 7 | 345 | 14.4442 | 14.4507 | 0.0065
GEN-2018-057 | 03 CENTRAL | 532780 | CANEYRV7 | 345 | 9.7507 | 9.762 | 0.0113
GEN-2018-057 | 03 CENTRAL | 532781 | CANEYWF7 | 345 | 9.4788 | 9.4894 | 0.0106
GEN-2018-057 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 20.3703 | 20.5277 | 0.1574
GEN-2018-057 | 03 CENTRAL | 532783 | KINGMAN7 | 345 | 7.2128 | 7.2273 | 0.0145
GEN-2018-057 | 03 CENTRAL | 532784 | NINN1WF7 | 345 | 6.0374 | 6.0468 | 0.0094
GEN-2018-057 | 03 CENTRAL | 532785 | PRATTWF7 | 345 | 5.0273 | 5.0335 | 0.0062
GEN-2018-057 | 03 CENTRAL | 532791 | BENTON 7 | 345 | 18.8762 | 18.996 | 0.1198
GEN-2018-057 | 03 CENTRAL | 532792 | FR2EAST7 | 345 | 6.8149 | 6.8252 | 0.0103
GEN-2018-057 | 03 CENTRAL | 532793 | NEOSHO 7 | 345 | 18.1678 | 18.1722 | 0.0044
GEN-2018-057 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 18.6635 | 18.7456 | 0.0821
GEN-2018-057 | 03 CENTRAL | 532795 | FR2WEST7 | 345 | 5.5131 | 5.5195 | 0.0064
GEN-2018-057 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 23.2694 | 23.5186 | 0.2492
GEN-2018-057 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 18.6489 | 18.662 | 0.0131
GEN-2018-057 | 03 CENTRAL | 532798 | VIOLA 7 | 345 | 13.777 | 13.8306 | 0.0536
GEN-2018-057 | 03 CENTRAL | 532799 | WAVERLY7 | 345 | 16.5171 | 16.5261 | 0.009
GEN-2018-057 | 03 CENTRAL | 532800 | LATHAMS7 | 345 | 10.3677 | 10.3826 | 0.0149
GEN-2018-057 | 03 CENTRAL | 532801 | ELKRVR17 | 345 | 9.2037 | 9.2154 | 0.0117
GEN-2018-057 | 03 CENTRAL | 532802 | WAVERTX7 | 345 | 13.7718 | 13.778 | 0.0062
GEN-2018-057 | 03 CENTRAL | 532803 | EXPEDITION7 | 345 | 10.8752 | 10.9007 | 0.0255
GEN-2018-057 | 03 CENTRAL | 532856 | SWISVAL6 | 230 | 22.0625 | 22.0654 | 0.0029
GEN-2018-057 | 03 CENTRAL | 532863 | MORRIS 6 | 230 | 14.3301 | 14.3332 | 0.0031
GEN-2018-057 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 9.0239 | 9.0293 | 0.0054
GEN-2018-057 | 03 CENTRAL | 532873 | SUMMIT 6 | 230 | 13.8843 | 13.8909 | 0.0066
GEN-2018-057 | 03 CENTRAL | 532982 | OXFORD 4 | 138 | 10.566 | 10.579 | 0.013
GEN-2018-057 | 03 CENTRAL | 532984 | SUMNER 4 | 138 | 11.9535 | 11.9712 | 0.0177
GEN-2018-057 | 03 CENTRAL | 532985 | TCROCK 4 | 138 | 6.0051 | 6.0095 | 0.0044
GEN-2018-057 | 03 CENTRAL | 532986 | BENTON 4 | 138 | 28.0723 | 28.234 | 0.1617
GEN-2018-057 | 03 CENTRAL | 532987 | BUTLER 4 | 138 | 11.2095 | 11.2298 | 0.0203
GEN-2018-057 | 03 CENTRAL | 532988 | BELAIRE4 | 138 | 19.1402 | 19.2161 | 0.0759
GEN-2018-057 | 03 CENTRAL | 532990 | MIDIAN 4 | 138 | 11.2585 | 11.2801 | 0.0216
GEN-2018-057 | 03 CENTRAL | 532991 | WEAVER 4 | 138 | 22.3031 | 22.3902 | 0.0871
GEN-2018-057 | 03 CENTRAL | 532992 | TIMBJCT4 | 138 | 6.4547 | 6.4598 | 0.0051
GEN-2018-057 | 03 CENTRAL | 532994 | TCBURNS4 | 138 | 4.1343 | 4.1372 | 0.0029
GEN-2018-057 | 03 CENTRAL | 533011 | HALSTD 4 | 138 | 8.4976 | 8.5417 | 0.0441
GEN-2018-057 | 03 CENTRAL | 533013 | MOUND 4 | 138 | 7.1063 | 7.127 | 0.0207
GEN-2018-057 | 03 CENTRAL | 533015 | BENTLEY4 | 138 | 10.9315 | 11.0217 | 0.0902
GEN-2018-057 | 03 CENTRAL | 533016 | WWUPLNT4 | 138 | 8.3217 | 8.3739 | 0.0522
GEN-2018-057 | 03 CENTRAL | 533024 | 29TH 4 | 138 | 19.7723 | 19.8532 | 0.0809
GEN-2018-057 | 03 CENTRAL | 533033 | CANAL 4 | 138 | 16.5721 | 16.6544 | 0.0823
GEN-2018-057 | 03 CENTRAL | 533034 | CENTENN4 | 138 | 14.8194 | 14.9601 | 0.1407
GEN-2018-057 | 03 CENTRAL | 533035 | CHISHLM4 | 138 | 21.483 | 21.6734 | 0.1904
GEN-2018-057 | 03 CENTRAL | 533036 | CLEARWT4 | 138 | 14.4332 | 14.4924 | 0.0592
GEN-2018-057 | 03 CENTRAL | 533037 | COMOTAR4 | 138 | 18.8527 | 18.9266 | 0.0739
GEN-2018-057 | 03 CENTRAL | 533038 | COWSKIN4 | 138 | 17.4145 | 17.6408 | 0.2263
GEN-2018-057 | 03 CENTRAL | 533039 | ELPASO 4 | 138 | 24.8987 | 25.0218 | 0.1231
GEN-2018-057 | 03 CENTRAL | 533040 | EVANS N4 | 138 | 31.1141 | 32.0782 | 0.9641
GEN-2018-057 | 03 CENTRAL | 533041 | EVANS S4 | 138 | 31.0445 | 32.003 | 0.9585
GEN-2018-057 | 03 CENTRAL | 533043 | FOWLER 4 | 138 | 16.3333 | 16.4191 | 0.0858
GEN-2018-057 | 03 CENTRAL | 533045 | GILL W 4 | 138 | 21.9404 | 22.1116 | 0.1712
GEN-2018-057 | 03 CENTRAL | 533046 | GILL S 4 | 138 | 21.9378 | 22.1087 | 0.1709
GEN-2018-057 | 03 CENTRAL | 533047 | GILL 4 | 138 | 21.9349 | 22.1057 | 0.1708
GEN-2018-057 | 03 CENTRAL | 533049 | HOOVERN4 | 138 | 17.2059 | 17.3713 | 0.1654
GEN-2018-057 | 03 CENTRAL | 533050 | HOOVERS4 | 138 | 17.2024 | 17.3675 | 0.1651
GEN-2018-057 | 03 CENTRAL | 533051 | INTERST4 | 138 | 15.8562 | 15.9789 | 0.1227
GEN-2018-057 | 03 CENTRAL | 533052 | PARKCTY4 | 138 | 20.3558 | 20.5064 | 0.1506
GEN-2018-057 | 03 CENTRAL | 533053 | LAKERDG4 | 138 | 17.2419 | 17.4524 | 0.2105
GEN-2018-057 | 03 CENTRAL | 533054 | MAIZE 4 | 138 | 20.8103 | 21.1247 | 0.3144
GEN-2018-057 | 03 CENTRAL | 533060 | NOEASTE4 | 138 | 20.6906 | 20.7801 | 0.0895
GEN-2018-057 | 03 CENTRAL | 533062 | ROSEHIL4 | 138 | 31.0808 | 31.2189 | 0.1381
GEN-2018-057 | 03 CENTRAL | 533063 | SC10BEL4 | 138 | 11.8384 | 11.8564 | 0.018
GEN-2018-057 | 03 CENTRAL | 533064 | 17TH 4 | 138 | 17.7742 | 17.8883 | 0.1141
GEN-2018-057 | 03 CENTRAL | 533065 | SG12COL4 | 138 | 19.3154 | 19.6578 | 0.3424
GEN-2018-057 | 03 CENTRAL | 533068 | STEARMN4 | 138 | 19.6729 | 19.7561 | 0.0832
GEN-2018-057 | 03 CENTRAL | 533073 | WACO N 4 | 138 | 19.095 | 19.2349 | 0.1399
GEN-2018-057 | 03 CENTRAL | 533074 | 45TH ST4 | 138 | 23.3261 | 23.8194 | 0.4933
GEN-2018-057 | 03 CENTRAL | 533075 | VIOLA 4 | 138 | 24.7578 | 24.8508 | 0.093
GEN-2018-057 | 03 CENTRAL | 533304 | LANG 3 | 115 | 15.7959 | 15.7993 | 0.0034
GEN-2018-057 | 03 CENTRAL | 533369 | HILSBOR3 | 115 | 2.6615 | 2.6625 | 0.001
GEN-2018-057 | 03 CENTRAL | 533380 | SPRGCRK3 | 115 | 3.9747 | 3.9769 | 0.0022
GEN-2018-057 | 03 CENTRAL | 533394 | CORONAD3 | 115 | 7.3179 | 7.3192 | 0.0013
GEN-2018-057 | 03 CENTRAL | 533411 | ARKVAL 3 | 115 | 9.9473 | 9.9526 | 0.0053
GEN-2018-057 | 03 CENTRAL | 533412 | ARKVALJ3 | 115 | 10.1396 | 10.145 | 0.0054
GEN-2018-057 | 03 CENTRAL | 533413 | CIRCLE 3 | 115 | 19.2909 | 19.3116 | 0.0207
GEN-2018-057 | 03 CENTRAL | 533414 | CITIES 3 | 115 | 8.2456 | 8.2497 | 0.0041
GEN-2018-057 | 03 CENTRAL | 533415 | DAVIS 3 | 115 | 8.4331 | 8.4375 | 0.0044
GEN-2018-057 | 03 CENTRAL | 533416 | RENO 3 | 115 | 23.2276 | 23.2643 | 0.0367
GEN-2018-057 | 03 CENTRAL | 533419 | HEC 3 | 115 | 18.0369 | 18.0551 | 0.0182
GEN-2018-057 | 03 CENTRAL | 533421 | HEC GT 3 | 115 | 18.755 | 18.7746 | 0.0196
GEN-2018-057 | 03 CENTRAL | 533426 | MANVILE3 | 115 | 8.7361 | 8.7384 | 0.0023
GEN-2018-057 | 03 CENTRAL | 533428 | MCPHER 3 | 115 | 11.0621 | 11.0659 | 0.0038
GEN-2018-057 | 03 CENTRAL | 533430 | MNDRGCT3 | 115 | 6.7839 | 6.7936 | 0.0097
GEN-2018-057 | 03 CENTRAL | 533438 | WMCPHER3 | 115 | 11.4543 | 11.4584 | 0.0041
GEN-2018-057 | 03 CENTRAL | 533439 | WHEATLD3 | 115 | 7.0534 | 7.0548 | 0.0014
GEN-2018-057 | 03 CENTRAL | 533504 | CITYSVC2 | 69 | 4.0446 | 4.0452 | 0.0006
GEN-2018-057 | 03 CENTRAL | 533505 | NCTYSVC2 | 69 | 4.0715 | 4.0721 | 0.0006
GEN-2018-057 | 03 CENTRAL | 533506 | DAVIS 2 | 69 | 7.5224 | 7.5245 | 0.0021
GEN-2018-057 | 03 CENTRAL | 533518 | MWIRON 2 | 69 | 6.3711 | 6.3726 | 0.0015
GEN-2018-057 | 03 CENTRAL | 533519 | MWIRONJ2 | 69 | 6.1752 | 6.1766 | 0.0014
GEN-2018-057 | 03 CENTRAL | 533529 | MWIRNJ22 | 69 | 6.5521 | 6.5537 | 0.0016
GEN-2018-057 | 03 CENTRAL | 533597 | MIDIANW2 | 69 | 14.5758 | 14.5948 | 0.019
GEN-2018-057 | 03 CENTRAL | 533624 | BURLING2 | 69 | 3.5476 | 3.5476 | 0
GEN-2018-057 | 03 CENTRAL | 533625 | BURLIND2 | 69 | 3.1627 | 3.1627 | 0
GEN-2018-057 | 03 CENTRAL | 533626 | BURLJCT2 | 69 | 5.1559 | 5.156 | 0.0001
GEN-2018-057 | 03 CENTRAL | 533628 | CC1BURL2 | 69 | 3.5461 | 3.5462 | 0.0001
GEN-2018-057 | 03 CENTRAL | 533629 | CC2SHAR2 | 69 | 4.8207 | 4.8209 | 0.0002
GEN-2018-057 | 03 CENTRAL | 533653 | WOLFCRK2 | 69 | 6.2329 | 6.2331 | 0.0002
GEN-2018-057 | 03 CENTRAL | 533732 | BURRTON2 | 69 | 2.9971 | 2.9996 | 0.0025
GEN-2018-057 | 03 CENTRAL | 533736 | HALSTED2 | 69 | 7.5493 | 7.5652 | 0.0159
GEN-2018-057 | 03 CENTRAL | 533742 | MOUND 2 | 69 | 7.3201 | 7.3315 | 0.0114
GEN-2018-057 | 03 CENTRAL | 533743 | MUD CRK2 | 69 | 5.4537 | 5.4612 | 0.0075
GEN-2018-057 | 03 CENTRAL | 533744 | MUDCRKJ2 | 69 | 6.1653 | 6.1749 | 0.0096
GEN-2018-057 | 03 CENTRAL | 533786 | CHISHLM2 | 69 | 20.3066 | 20.3834 | 0.0768
GEN-2018-057 | 03 CENTRAL | 533788 | COWSKIN2 | 69 | 16.2919 | 16.3723 | 0.0804
GEN-2018-057 | 03 CENTRAL | 533799 | GRANT 2 | 69 | 12.7355 | 12.7641 | 0.0286
GEN-2018-057 | 03 CENTRAL | 533800 | GRANT J2 | 69 | 10.0018 | 10.0213 | 0.0195
GEN-2018-057 | 03 CENTRAL | 533805 | HOOVERN2 | 69 | 30.8672 | 31.0863 | 0.2191
GEN-2018-057 | 03 CENTRAL | 533806 | HOOVERS2 | 69 | 30.8904 | 31.1099 | 0.2195
GEN-2018-057 | 03 CENTRAL | 533814 | MASCOT 2 | 69 | 20.0735 | 20.1489 | 0.0754
GEN-2018-057 | 03 CENTRAL | 533818 | MEAD N 2 | 69 | 25.743 | 25.874 | 0.131
GEN-2018-057 | 03 CENTRAL | 533820 | MOSSMAN2 | 69 | 18.2065 | 18.2596 | 0.0531
GEN-2018-057 | 03 CENTRAL | 533831 | RENEW 2 | 69 | 17.7877 | 17.8438 | 0.0561
GEN-2018-057 | 03 CENTRAL | 533835 | 17TH TP2 | 69 | 25.0966 | 25.2184 | 0.1218
GEN-2018-057 | 03 CENTRAL | 533840 | 17TH 2 | 69 | 27.2912 | 27.431 | 0.1398
GEN-2018-057 | 03 CENTRAL | 533849 | VISTAPK2 | 69 | 17.2982 | 17.362 | 0.0638
GEN-2018-057 | 03 CENTRAL | 533854 | WESTLNK2 | 69 | 15.3706 | 15.4365 | 0.0659
GEN-2018-057 | 03 CENTRAL | 533855 | WATER1 2 | 69 | 23.892 | 24.0089 | 0.1169
GEN-2018-057 | 03 CENTRAL | 533859 | RIPLEYE2 | 69 | 22.8489 | 22.9464 | 0.0975
GEN-2018-057 | 03 CENTRAL | 533860 | RIPLEYM2 | 69 | 22.8521 | 22.9497 | 0.0976
GEN-2018-057 | 03 CENTRAL | 533861 | BU5FURL2 | 69 | 7.2724 | 7.2801 | 0.0077
GEN-2018-057 | 03 CENTRAL | 533874 | SG9STMK2 | 69 | 16.2616 | 16.3417 | 0.0801
GEN-2018-057 | 03 CENTRAL | 533879 | GODDTAP2 | 69 | 8.2966 | 8.3162 | 0.0196
GEN-2018-057 | 03 CENTRAL | 533880 | GODDARD2 | 69 | 6.3935 | 6.4052 | 0.0117
GEN-2018-057 | 03 CENTRAL | 539003 | CLDWELL4 | 138 | 5.8088 | 5.8132 | 0.0044
GEN-2018-057 | 03 CENTRAL | 539008 | MILAN_GOAB | 138 | 12.1228 | 12.1443 | 0.0215
GEN-2018-057 | 03 CENTRAL | 539009 | CONWAY | 138 | 11.6369 | 11.6555 | 0.0186
GEN-2018-057 | 03 CENTRAL | 539631 | FLATRWD4 | 138 | 10.769 | 10.7748 | 0.0058
GEN-2018-057 | 03 CENTRAL | 539638 | FLATRDG4 | 138 | 16.0383 | 16.0515 | 0.0132
GEN-2018-057 | 03 CENTRAL | 539675 | MILANTP4 | 138 | 10.2865 | 10.3007 | 0.0142
GEN-2018-057 | 03 CENTRAL | 539676 | MILAN 4 | 138 | 10.7751 | 10.792 | 0.0169
GEN-2018-057 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 13.1119 | 13.1183 | 0.0064
GEN-2018-057 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 16.663 | 16.6971 | 0.0341
GEN-2018-057 | 03 CENTRAL | 539804 | THISTLE4 | 138 | 18.0539 | 18.0705 | 0.0166
GEN-2018-057 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 10.9985 | 11.003 | 0.0045
GEN-2018-057 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 11.2019 | 11.2062 | 0.0043
GEN-2018-057 | 03 CENTRAL | 539841 | G-2011-008-1 | 345 | 11.2019 | 11.2062 | 0.0043
GEN-2018-057 | 03 CENTRAL | 539855 | G-2011-008-2 | 345 | 9.5044 | 9.5074 | 0.003
GEN-2018-057 | 03 CENTRAL | 539857 | G-2011-008-3 | 345 | 8.7572 | 8.7598 | 0.0026
GEN-2018-057 | 03 CENTRAL | 541541 | LAC_LAKE_2 | 69 | 2.6766 | 2.6766 | 0
GEN-2018-057 | 03 CENTRAL | 542965 | W.GRDNR7 | 345 | 28.5015 | 28.5039 | 0.0024
GEN-2018-057 | 03 CENTRAL | 542981 | LACYGNE7 | 345 | 27.5243 | 27.5276 | 0.0033
GEN-2018-057 | 03 CENTRAL | 543629 | LACYGNE11_7 | 345 | 26.8028 | 26.8059 | 0.0031
GEN-2018-057 | 03 CENTRAL | 543632 | LACYGNE22_7 | 345 | 26.8028 | 26.8059 | 0.0031
GEN-2018-057 | 03 CENTRAL | 543659 | LACYGNE2 | 69 | 2.8155 | 2.8155 | 0
GEN-2018-057 | 03 CENTRAL | 543667 | LAC3_STAR7 | 345 | 0.6733 | 0.6733 | 0
GEN-2018-057 | 03 CENTRAL | 543669 | LAC8_STAR7 | 345 | 0.6449 | 0.6449 | 0
GEN-2018-057 | 03 CENTRAL | 560053 | G15-052T | 345 | 13.0168 | 13.0382 | 0.0214
GEN-2018-057 | 03 CENTRAL | 560080 | G16-046-TAP | 345 | 11.5096 | 11.5137 | 0.0041
GEN-2018-057 | 03 CENTRAL | 578530 | FR3HV | 345 | 5.0682 | 5.0735 | 0.0053
GEN-2018-057 | 03 CENTRAL | 583850 | GEN-2014-001 | 345 | 6.7731 | 6.7825 | 0.0094
GEN-2018-057 | 03 CENTRAL | 583859 | GEN-2014-001 | 345 | 8.4269 | 8.4418 | 0.0149
GEN-2018-057 | 03 CENTRAL | 584900 | GEN-2015-052 | 345 | 12.9704 | 12.9916 | 0.0212
GEN-2018-057 | 03 CENTRAL | 585410 | GREAT_WESTRN | 345 | 8.9312 | 8.9325 | 0.0013
GEN-2018-057 | 03 CENTRAL | 585420 | COWBOY_RIDGE | 345 | 6.8726 | 6.8734 | 0.0008
GEN-2018-057 | 03 CENTRAL | 585430 | PRSIMN_CRK1 | 345 | 10.8366 | 10.8384 | 0.0018
GEN-2018-057 | 03 CENTRAL | 585440 | PRSIMN_CRK2 | 345 | 9.9484 | 9.95 | 0.0016
GEN-2018-057 | 03 CENTRAL | 587310 | GEN-2016-046 | 345 | 10.1271 | 10.1302 | 0.0031
GEN-2018-057 | 03 CENTRAL | 587311 | G16-046XFMR1 | 115 | 15.3049 | 15.3069 | 0.002
GEN-2018-057 | 03 CENTRAL | 587880 | GEN-2016-111 | 345 | 6.8276 | 6.834 | 0.0064
GEN-2018-057 | 03 CENTRAL | 587884 | G16-111-TAP | 345 | 10.2731 | 10.2885 | 0.0154
GEN-2018-057 | 03 CENTRAL | 588190 | GEN-2016-128 | 345 | 4.0664 | 4.0669 | 0.0005
GEN-2018-057 | 03 CENTRAL | 588360 | GEN-2016-153 | 345 | 8.1183 | 8.1338 | 0.0155
GEN-2018-057 | 03 CENTRAL | 588364 | G16-153-TAP | 345 | 8.1183 | 8.1338 | 0.0155
GEN-2018-057 | 03 CENTRAL | 588490 | GEN-2017-004 | 345 | 8.5632 | 8.5675 | 0.0043
GEN-2018-057 | 03 CENTRAL | 588494 | G17-004-TAP | 345 | 9.9494 | 9.9553 | 0.0059
GEN-2018-057 | 03 CENTRAL | 588630 | GEN-2017-018 | 345 | 16.663 | 16.6971 | 0.0341
GEN-2018-057 | 03 CENTRAL | 589060 | GEN-2017-068 | 138 | 28.406 | 29.2048 | 0.7988
GEN-2018-057 | 03 CENTRAL | 589240 | GEN-2017-086 | 345 | 8.1183 | 8.1338 | 0.0155
GEN-2018-057 | 03 CENTRAL | 760284 | GEN-2017-220 | 345 | 20.2656 | 20.4213 | 0.1557
GEN-2018-057 | 03 CENTRAL | 760641 | GEN-2017-226 | 138 | 30.9546 | 31.9082 | 0.9536
GEN-2018-057 | 03 CENTRAL | 760809 | GEN-2017-203 | 345 | 8.5933 | 8.6023 | 0.009
GEN-2018-057 | 03 CENTRAL | 761838 | GEN-2017-121 | 138 | 9.0917 | 9.1015 | 0.0098
GEN-2018-057 | 03 CENTRAL | 762279 | GEN-2017-195 | 345 | 28.4241 | 28.4265 | 0.0024
GEN-2018-057 | 03 CENTRAL | 762321 | GEN-2017-164 | 345 | 10.4548 | 10.4581 | 0.0033
GEN-2018-057 | 03 CENTRAL | 762342 | GEN-2017-178 | 345 | 7.5332 | 7.5349 | 0.0017
GEN-2018-057 | 03 CENTRAL | 762680 | GEN-2018-032 | 345 | 11.9847 | 11.9867 | 0.002
GEN-2018-057 | 03 CENTRAL | 762834 | GEN-2018-049 | 345 | 7.1603 | 7.1664 | 0.0061
GEN-2018-057 | 03 CENTRAL | 762922 | GEN-2018-057 | 138 | 16.5977 | 17.5874 | 0.9897
GEN-2018-003 | 04 SOUTHEAST | 5917 | SPPMAINBUS | 345 | 21.2911 | 21.3538 | 0.0627
GEN-2018-003 | 04 SOUTHEAST | 507455 | TURK 7 | 345 | 9.3484 | 9.405 | 0.0566
GEN-2018-003 | 04 SOUTHEAST | 508072 | NWTXARK7 | 345 | 13.6129 | 13.7572 | 0.1443
GEN-2018-003 | 04 SOUTHEAST | 508298 | LYDIA 7 | 345 | 13.0257 | 13.0796 | 0.0539
GEN-2018-003 | 04 SOUTHEAST | 508359 | WELSH 7 | 345 | 21.2911 | 21.3538 | 0.0627
GEN-2018-003 | 04 SOUTHEAST | 508832 | DIANA 7 | 345 | 19.5784 | 19.6098 | 0.0314
GEN-2018-003 | 04 SOUTHEAST | 508841 | WILKES 7 | 345 | 15.6735 | 15.696 | 0.0225
GEN-2018-003 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 14.7604 | 14.7659 | 0.0055
GEN-2018-003 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 13.6428 | 13.6809 | 0.0381
GEN-2018-003 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 11.4395 | 11.4594 | 0.0199
GEN-2018-003 | 04 SOUTHEAST | 337672 | 4MURFBORO | 138 | 3.0759 | 3.079 | 0.0031
GEN-2018-003 | 04 SOUTHEAST | 504029 | SFOREMAN 4 | 138 | 8.7195 | 8.9016 | 0.1821
GEN-2018-003 | 04 SOUTHEAST | 504123 | LOCKSBRG 4 | 138 | 6.129 | 6.1562 | 0.0272
GEN-2018-003 | 04 SOUTHEAST | 504124 | ASHDWN_W 4 | 138 | 10.2669 | 10.3415 | 0.0746
GEN-2018-003 | 04 SOUTHEAST | 507402 | ASHDWNR4 | 138 | 10.5072 | 10.5807 | 0.0735
GEN-2018-003 | 04 SOUTHEAST | 507428 | OKAY 4 | 138 | 10.3255 | 10.3675 | 0.042
GEN-2018-003 | 04 SOUTHEAST | 507431 | PATTERS4 | 138 | 13.5622 | 13.7109 | 0.1487
GEN-2018-003 | 04 SOUTHEAST | 507434 | SNASHVL4 | 138 | 3.8988 | 3.9067 | 0.0079
GEN-2018-003 | 04 SOUTHEAST | 507454 | TURK 4 | 138 | 24.9737 | 25.11 | 0.1363
GEN-2018-003 | 04 SOUTHEAST | 507463 | BARITERDTP 4 | 138 | 3.8195 | 3.8286 | 0.0091
GEN-2018-003 | 04 SOUTHEAST | 508049 | NASH 4 | 138 | 20.0828 | 20.3557 | 0.2729
GEN-2018-003 | 04 SOUTHEAST | 508050 | ANDRSNC4 | 138 | 7.8111 | 7.9719 | 0.1608
GEN-2018-003 | 04 SOUTHEAST | 508054 | BANN 4 | 138 | 21.0153 | 21.3138 | 0.2985
GEN-2018-003 | 04 SOUTHEAST | 508056 | BRYANML4 | 138 | 7.3961 | 7.4708 | 0.0747
GEN-2018-003 | 04 SOUTHEAST | 508059 | IPC T 4 | 138 | 8.428 | 8.4646 | 0.0366
GEN-2018-003 | 04 SOUTHEAST | 508060 | IPC-DOM4 | 138 | 8.9254 | 8.9682 | 0.0428
GEN-2018-003 | 04 SOUTHEAST | 508064 | MUNZCTY4 | 138 | 7.5157 | 7.584 | 0.0683
GEN-2018-003 | 04 SOUTHEAST | 508069 | NNBOSTN4 | 138 | 10.6362 | 11.1715 | 0.5353
GEN-2018-003 | 04 SOUTHEAST | 508070 | NWT-BNT4 | 138 | 24.597 | 25.0419 | 0.4449
GEN-2018-003 | 04 SOUTHEAST | 508071 | NWTXARK4 | 138 | 25.6223 | 26.0698 | 0.4475
GEN-2018-003 | 04 SOUTHEAST | 508075 | REDSPRG4 | 138 | 14.4357 | 14.5681 | 0.1324
GEN-2018-003 | 04 SOUTHEAST | 508078 | SETEXAR4 | 138 | 11.1993 | 11.2638 | 0.0645
GEN-2018-003 | 04 SOUTHEAST | 508080 | SUGARHL4 | 138 | 12.5258 | 12.6068 | 0.081
GEN-2018-003 | 04 SOUTHEAST | 508091 | ALUMAX 4 | 138 | 17.7782 | 17.9915 | 0.2133
GEN-2018-003 | 04 SOUTHEAST | 508104 | RIFFIN REC4 | 138 | 10.1158 | 10.5682 | 0.4524
GEN-2018-003 | 04 SOUTHEAST | 508105 | MANDEVILTP4 | 138 | 9.7024 | 9.7381 | 0.0357
GEN-2018-003 | 04 SOUTHEAST | 509654 | REDWATR4 | 138 | 5.7573 | 5.7782 | 0.0209
GEN-2018-003 | 04 SOUTHEAST | 509655 | EYLAU 4 | 138 | 8.997 | 9.0481 | 0.0511
GEN-2018-003 | 04 SOUTHEAST | 509656 | BUCHANN4 | 138 | 6.3886 | 6.4143 | 0.0257
GEN-2018-003 | 04 SOUTHEAST | 510890 | CRAIGJT4 | 138 | 9.045 | 9.06 | 0.015
GEN-2018-003 | 04 SOUTHEAST | 510918 | VALIANT4 | 138 | 15.1115 | 15.1296 | 0.0181
GEN-2018-003 | 04 SOUTHEAST | 762427 | GEN-2018-003 | 138 | 11.2132 | 11.8175 | 0.6043
GEN-2018-003 | 04 SOUTHEAST | 762431 | G18-003-TAP | 138 | 11.2132 | 11.8175 | 0.6043
GEN-2018-003 | 04 SOUTHEAST | 507456 | TURK 3 | 115 | 17.0503 | 17.0906 | 0.0403
GEN-2018-003 | 04 SOUTHEAST | 504030 | SFORE_1 2 | 69 | 2.9444 | 2.9525 | 0.0081
GEN-2018-003 | 04 SOUTHEAST | 504363 | NE-TEXARK2 | 69 | 5.5614 | 5.5672 | 0.0058
GEN-2018-003 | 04 SOUTHEAST | 507421 | FOREMAN2 | 69 | 3.8048 | 3.809 | 0.0042
GEN-2018-003 | 04 SOUTHEAST | 507429 | PATTERS2 | 69 | 14.2558 | 14.33 | 0.0742
GEN-2018-003 | 04 SOUTHEAST | 508051 | ASHDOWN2 | 69 | 11.9654 | 12.0169 | 0.0515
GEN-2018-003 | 04 SOUTHEAST | 508053 | BANN 2 | 69 | 19.1747 | 19.3201 | 0.1454
GEN-2018-003 | 04 SOUTHEAST | 508057 | HOOKS 2 | 69 | 8.1313 | 8.1681 | 0.0368
GEN-2018-003 | 04 SOUTHEAST | 508061 | KINGHWY2 | 69 | 11.8338 | 11.885 | 0.0512
GEN-2018-003 | 04 SOUTHEAST | 508063 | LSORDTP2 | 69 | 9.0269 | 9.0689 | 0.042
GEN-2018-003 | 04 SOUTHEAST | 508065 | NEKOOSA2 | 69 | 6.623 | 6.638 | 0.015
GEN-2018-003 | 04 SOUTHEAST | 508067 | NEWBOST2 | 69 | 7.2019 | 7.238 | 0.0361
GEN-2018-003 | 04 SOUTHEAST | 508068 | NNBOSTN2 | 69 | 7.0868 | 7.1246 | 0.0378
GEN-2018-003 | 04 SOUTHEAST | 508073 | REDLICK2 | 69 | 16.6071 | 16.7135 | 0.1064
GEN-2018-003 | 04 SOUTHEAST | 508074 | REDRVR-2 | 69 | 7.1334 | 7.1655 | 0.0321
GEN-2018-003 | 04 SOUTHEAST | 508076 | RICHMND2 | 69 | 14.3551 | 14.4301 | 0.075
GEN-2018-003 | 04 SOUTHEAST | 508077 | SETEXAR2 | 69 | 14.5566 | 14.6209 | 0.0643
GEN-2018-003 | 04 SOUTHEAST | 508079 | SUGARHL2 | 69 | 17.0337 | 17.1296 | 0.0959
GEN-2018-003 | 04 SOUTHEAST | 508081 | SUGHLET2 | 69 | 16.362 | 16.4505 | 0.0885
GEN-2018-003 | 04 SOUTHEAST | 508082 | SUGHLWT2 | 69 | 16.3214 | 16.4116 | 0.0902
GEN-2018-003 | 04 SOUTHEAST | 508086 | TEXARK 2 | 69 | 14.9746 | 15.043 | 0.0684
GEN-2018-003 | 04 SOUTHEAST | 508087 | TEXOPER2 | 69 | 11.5788 | 11.6256 | 0.0468
GEN-2018-003 | 04 SOUTHEAST | 508093 | LSORD 2 | 69 | 7.3393 | 7.3686 | 0.0293
GEN-2018-003 | 04 SOUTHEAST | 508287 | BUFORDR2 | 69 | 3.9391 | 3.9417 | 0.0026
GEN-2018-003 | 04 SOUTHEAST | 508289 | DEKALB 2 | 69 | 4.038 | 4.0444 | 0.0064
GEN-2018-003 | 04 SOUTHEAST | 509657 | MAUD 2 | 69 | 3.5535 | 3.5698 | 0.0163
GEN-2018-003 | 04 SOUTHEAST | 509658 | ANDRCKT2 | 69 | 8.5811 | 8.6674 | 0.0863
GEN-2018-003 | 04 SOUTHEAST | 509659 | SIMMS 2 | 69 | 6.8875 | 6.9449 | 0.0574
GEN-2018-024 | 04 SOUTHEAST | 337909 | 8ANO% | 500 | 18.2513 | 18.2518 | 0.0005
GEN-2018-024 | 04 SOUTHEAST | 515305 | FTSMITH8 | 500 | 8.7387 | 8.7399 | 0.0012
GEN-2018-024 | 04 SOUTHEAST | 506945 | CHAMSPR7 | 345 | 10.6392 | 10.6404 | 0.0012
GEN-2018-024 | 04 SOUTHEAST | 506959 | TONTITN7 | 345 | 9.5858 | 9.5866 | 0.0008
GEN-2018-024 | 04 SOUTHEAST | 508072 | NWTXARK7 | 345 | 13.7568 | 13.7572 | 0.0004
GEN-2018-024 | 04 SOUTHEAST | 508298 | LYDIA 7 | 345 | 13.0791 | 13.0796 | 0.0005
GEN-2018-024 | 04 SOUTHEAST | 509745 | CLARKSV7 | 345 | 20.8706 | 20.892 | 0.0214
GEN-2018-024 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 33.0707 | 33.0851 | 0.0144
GEN-2018-024 | 04 SOUTHEAST | 509807 | ONETA--7 | 345 | 30.5293 | 30.5423 | 0.013
GEN-2018-024 | 04 SOUTHEAST | 509834 | COGENT 7 | 345 | 30.6983 | 30.7104 | 0.0121
GEN-2018-024 | 04 SOUTHEAST | 509836 | OEC 7 | 345 | 30.2348 | 30.2476 | 0.0128
GEN-2018-024 | 04 SOUTHEAST | 509870 | SAPLPRD7 | 345 | 23.633 | 23.6381 | 0.0051
GEN-2018-024 | 04 SOUTHEAST | 510406 | N.E.S.-7 | 345 | 19.727 | 19.7286 | 0.0016
GEN-2018-024 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 14.753 | 14.7659 | 0.0129
GEN-2018-024 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 13.6792 | 13.6809 | 0.0017
GEN-2018-024 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 14.4859 | 14.4983 | 0.0124
GEN-2018-024 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 24.338 | 24.3392 | 0.0012
GEN-2018-024 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 11.1911 | 11.1932 | 0.0021
GEN-2018-024 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 35.3054 | 35.3073 | 0.0019
GEN-2018-024 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 24.875 | 24.8759 | 0.0009
GEN-2018-024 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 37.9065 | 37.909 | 0.0025
GEN-2018-024 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 27.8045 | 27.8065 | 0.002
GEN-2018-024 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 26.9165 | 26.9184 | 0.0019
GEN-2018-024 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 26.8111 | 26.8166 | 0.0055
GEN-2018-024 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 29.4627 | 29.4803 | 0.0176
GEN-2018-024 | 04 SOUTHEAST | 515136 | SUNNYSD7 | 345 | 11.5355 | 11.5368 | 0.0013
GEN-2018-024 | 04 SOUTHEAST | 515224 | MUSKOGE7 | 345 | 28.0227 | 28.1299 | 0.1072
GEN-2018-024 | 04 SOUTHEAST | 515235 | PECANCK7 | 345 | 22.3942 | 22.4382 | 0.044
GEN-2018-024 | 04 SOUTHEAST | 515302 | FTSMITH7 | 345 | 10.463 | 10.4652 | 0.0022
GEN-2018-024 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 11.523 | 11.5494 | 0.0264
GEN-2018-024 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 35.7182 | 35.7199 | 0.0017
GEN-2018-024 | 04 SOUTHEAST | 516006 | DMNDSPG7 | 345 | 8.0406 | 8.0416 | 0.001
GEN-2018-024 | 04 SOUTHEAST | 516096 | NORMHLL7 | 345 | 27.8198 | 27.8237 | 0.0039
GEN-2018-024 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 11.4584 | 11.4594 | 0.001
GEN-2018-024 | 04 SOUTHEAST | 588039 | G16133G16146 | 345 | 33.0707 | 33.0851 | 0.0144
GEN-2018-024 | 04 SOUTHEAST | 588810 | GEN-2017-040 | 345 | 18.0588 | 18.2318 | 0.173
GEN-2018-024 | 04 SOUTHEAST | 588838 | G17-092-SWYD | 345 | 18.461 | 18.642 | 0.181
GEN-2018-024 | 04 SOUTHEAST | 588839 | FIREWHL-TAP | 345 | 18.461 | 18.642 | 0.181
GEN-2018-024 | 04 SOUTHEAST | 589300 | GEN-2017-092 | 345 | 15.1018 | 15.2219 | 0.1201
GEN-2018-024 | 04 SOUTHEAST | 760032 | GEN-2017-133 | 345 | 5.6949 | 5.6949 | 0
GEN-2018-024 | 04 SOUTHEAST | 760389 | GEN-2017-140 | 345 | 1.7037 | 1.7038 | 0.0001
GEN-2018-024 | 04 SOUTHEAST | 760393 | G17-140-BUS | 345 | 1.693 | 1.6931 | 0.0001
GEN-2018-024 | 04 SOUTHEAST | 760830 | GEN-2017-149 | 345 | 4.1532 | 4.1534 | 0.0002
GEN-2018-024 | 04 SOUTHEAST | 762592 | GEN-2018-024 | 345 | 17.9147 | 18.0953 | 0.1806
GEN-2018-024 | 04 SOUTHEAST | 762823 | GEN-2018-048 | 345 | 16.2406 | 16.2633 | 0.0227
GEN-2018-024 | 04 SOUTHEAST | 506944 | CHAMSPR5 | 161 | 24.379 | 24.3805 | 0.0015
GEN-2018-024 | 04 SOUTHEAST | 515228 | 5TRIBES5 | 161 | 16.0737 | 16.0797 | 0.006
GEN-2018-024 | 04 SOUTHEAST | 515230 | AGENCY 5 | 161 | 14.6267 | 14.6312 | 0.0045
GEN-2018-024 | 04 SOUTHEAST | 515234 | PECANCK5 | 161 | 21.6853 | 21.6982 | 0.0129
GEN-2018-024 | 04 SOUTHEAST | 515300 | FTSMTHE5 | 161 | 24.0138 | 24.0164 | 0.0026
GEN-2018-024 | 04 SOUTHEAST | 515301 | FTSMTHW5 | 161 | 23.877 | 23.8796 | 0.0026
GEN-2018-024 | 04 SOUTHEAST | 515306 | ARKOMA 5 | 161 | 16.7859 | 16.7871 | 0.0012
GEN-2018-024 | 04 SOUTHEAST | 509773 | RSS T1 4 | 138 | 52.4249 | 52.4342 | 0.0093
GEN-2018-024 | 04 SOUTHEAST | 509806 | ONETA--4 | 138 | 50.3261 | 50.3382 | 0.0121
GEN-2018-024 | 04 SOUTHEAST | 509875 | RSS T2 4 | 138 | 53.3594 | 53.369 | 0.0096
GEN-2018-024 | 04 SOUTHEAST | 510908 | MCALEST4 | 138 | 10.1852 | 10.1878 | 0.0026
GEN-2018-024 | 04 SOUTHEAST | 510909 | MCALESTIND 4 | 138 | 5.887 | 5.8882 | 0.0012
GEN-2018-024 | 04 SOUTHEAST | 510918 | VALIANT4 | 138 | 15.1289 | 15.1296 | 0.0007
GEN-2018-024 | 04 SOUTHEAST | 510946 | C-RIVER4 | 138 | 14.0207 | 14.0325 | 0.0118
GEN-2018-024 | 04 SOUTHEAST | 510948 | EARLSBORO 4 | 138 | 8.7701 | 8.7704 | 0.0003
GEN-2018-024 | 04 SOUTHEAST | 510951 | TALAWANDA 4 | 138 | 10.118 | 10.1215 | 0.0035
GEN-2018-024 | 04 SOUTHEAST | 511508 | BLANCHD4 | 138 | 6.9281 | 6.9282 | 0.0001
GEN-2018-024 | 04 SOUTHEAST | 514808 | JOHNCO 4 | 138 | 16.1161 | 16.1174 | 0.0013
GEN-2018-024 | 04 SOUTHEAST | 514827 | CTNWOOD4 | 138 | 19.0911 | 19.0914 | 0.0003
GEN-2018-024 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 46.3878 | 46.3893 | 0.0015
GEN-2018-024 | 04 SOUTHEAST | 514906 | JNSKAMO4 | 138 | 21.3896 | 21.39 | 0.0004
GEN-2018-024 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 42.789 | 42.7907 | 0.0017
GEN-2018-024 | 04 SOUTHEAST | 514933 | DRAPER 4 | 138 | 42.0083 | 42.0123 | 0.004
GEN-2018-024 | 04 SOUTHEAST | 514946 | MIDWEST4 | 138 | 31.1358 | 31.1376 | 0.0018
GEN-2018-024 | 04 SOUTHEAST | 514949 | SOONRTP4 | 138 | 23.0029 | 23.0037 | 0.0008
GEN-2018-024 | 04 SOUTHEAST | 514961 | GM 4 | 138 | 20.4428 | 20.4434 | 0.0006
GEN-2018-024 | 04 SOUTHEAST | 515003 | BARNES 4 | 138 | 16.8633 | 16.8637 | 0.0004
GEN-2018-024 | 04 SOUTHEAST | 515044 | SEMINOL4 | 138 | 41.7011 | 41.7083 | 0.0072
GEN-2018-024 | 04 SOUTHEAST | 515055 | MAUD 4 | 138 | 21.0154 | 21.0169 | 0.0015
GEN-2018-024 | 04 SOUTHEAST | 515075 | FRSTHIL4 | 138 | 14.524 | 14.5245 | 0.0005
GEN-2018-024 | 04 SOUTHEAST | 515097 | WLNUTCK4 | 138 | 9.8983 | 9.8985 | 0.0002
GEN-2018-024 | 04 SOUTHEAST | 515100 | PAOLI- 4 | 138 | 10.8314 | 10.8317 | 0.0003
GEN-2018-024 | 04 SOUTHEAST | 515114 | CHIGLEY4 | 138 | 8.5733 | 8.5735 | 0.0002
GEN-2018-024 | 04 SOUTHEAST | 515117 | ARBUCKL4 | 138 | 16.4304 | 16.4314 | 0.001
GEN-2018-024 | 04 SOUTHEAST | 515124 | MAYSVIL4 | 138 | 6.4465 | 6.4466 | 0.0001
GEN-2018-024 | 04 SOUTHEAST | 515174 | VANOSS 4 | 138 | 13.7568 | 13.7575 | 0.0007
GEN-2018-024 | 04 SOUTHEAST | 515178 | PARKLN 4 | 138 | 16.9752 | 16.9763 | 0.0011
GEN-2018-024 | 04 SOUTHEAST | 515233 | PECANCK4 | 138 | 9.9988 | 10.0007 | 0.0019
GEN-2018-024 | 04 SOUTHEAST | 515461 | RNDBARN4 | 138 | 40.7364 | 40.7379 | 0.0015
GEN-2018-024 | 04 SOUTHEAST | 515465 | LGARBER4 | 138 | 22.0608 | 22.0612 | 0.0004
GEN-2018-024 | 04 SOUTHEAST | 515531 | VANOSTP4 | 138 | 13.8877 | 13.8884 | 0.0007
GEN-2018-024 | 04 SOUTHEAST | 515977 | LKKONWA4 | 138 | 40.7714 | 40.7783 | 0.0069
GEN-2018-024 | 04 SOUTHEAST | 516097 | NORMHLL4 | 138 | 37.9073 | 37.9092 | 0.0019
GEN-2018-024 | 04 SOUTHEAST | 515054 | MAUD 2 | 69 | 11.0537 | 11.0539 | 0.0002
GEN-2018-024 | 04 SOUTHEAST | 515099 | PALIOGE2 | 69 | 9.0566 | 9.0567 | 0.0001
GEN-2018-026 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 24.3299 | 24.3392 | 0.0093
GEN-2018-026 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 35.2765 | 35.3073 | 0.0308
GEN-2018-026 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 37.872 | 37.909 | 0.037
GEN-2018-026 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 35.6948 | 35.7199 | 0.0251
GEN-2018-026 | 04 SOUTHEAST | 515610 | FSHRTAP7 | 345 | 18.8713 | 18.8789 | 0.0076
GEN-2018-026 | 04 SOUTHEAST | 516096 | NORMHLL7 | 345 | 27.8048 | 27.8237 | 0.0189
GEN-2018-026 | 04 SOUTHEAST | 511425 | TUTCONT4 | 138 | 10.9319 | 10.9344 | 0.0025
GEN-2018-026 | 04 SOUTHEAST | 511501 | TUTTLE4 | 138 | 10.7783 | 10.7805 | 0.0022
GEN-2018-026 | 04 SOUTHEAST | 511576 | CEMRD_TP4 | 138 | 7.1977 | 7.1987 | 0.001
GEN-2018-026 | 04 SOUTHEAST | 514819 | EL-RENO4 | 138 | 17.6473 | 17.6579 | 0.0106
GEN-2018-026 | 04 SOUTHEAST | 514820 | JENSENT4 | 138 | 19.1834 | 19.1944 | 0.011
GEN-2018-026 | 04 SOUTHEAST | 514821 | JENSEN 4 | 138 | 16.3448 | 16.3504 | 0.0056
GEN-2018-026 | 04 SOUTHEAST | 514828 | KETCHTP4 | 138 | 28.0619 | 28.0826 | 0.0207
GEN-2018-026 | 04 SOUTHEAST | 514835 | MEMRIAL4 | 138 | 37.7552 | 37.8167 | 0.0615
GEN-2018-026 | 04 SOUTHEAST | 514836 | WILSHIR4 | 138 | 23.4929 | 23.527 | 0.0341
GEN-2018-026 | 04 SOUTHEAST | 514838 | TENNESE4 | 138 | 24.802 | 24.8355 | 0.0335
GEN-2018-026 | 04 SOUTHEAST | 514844 | BELISLE4 | 138 | 28.6703 | 28.7276 | 0.0573
GEN-2018-026 | 04 SOUTHEAST | 514846 | 38TH ST4 | 138 | 24.0416 | 24.0812 | 0.0396
GEN-2018-026 | 04 SOUTHEAST | 514847 | TULSA 4 | 138 | 23.7496 | 23.7867 | 0.0371
GEN-2018-026 | 04 SOUTHEAST | 514848 | HEFNER 4 | 138 | 26.0078 | 26.0516 | 0.0438
GEN-2018-026 | 04 SOUTHEAST | 514849 | LAKESID4 | 138 | 25.8904 | 25.9352 | 0.0448
GEN-2018-026 | 04 SOUTHEAST | 514850 | SKYLINE4 | 138 | 33.9169 | 33.9632 | 0.0463
GEN-2018-026 | 04 SOUTHEAST | 514851 | QUAILCK4 | 138 | 31.0239 | 31.0628 | 0.0389
GEN-2018-026 | 04 SOUTHEAST | 514852 | SLVRLAK4 | 138 | 34.5518 | 34.6105 | 0.0587
GEN-2018-026 | 04 SOUTHEAST | 514853 | DVISION4 | 138 | 38.0113 | 38.1154 | 0.1041
GEN-2018-026 | 04 SOUTHEAST | 514854 | BRADEN 4 | 138 | 33.1379 | 33.179 | 0.0411
GEN-2018-026 | 04 SOUTHEAST | 514861 | MUSTANG4 | 138 | 40.5813 | 41.0095 | 0.4282
GEN-2018-026 | 04 SOUTHEAST | 514862 | RICHRDS4 | 138 | 22.9035 | 22.933 | 0.0295
GEN-2018-026 | 04 SOUTHEAST | 514863 | HAYMAKR4 | 138 | 27.9079 | 27.9548 | 0.0469
GEN-2018-026 | 04 SOUTHEAST | 514864 | PIEDMNT4 | 138 | 23.5816 | 23.6033 | 0.0217
GEN-2018-026 | 04 SOUTHEAST | 514865 | COUNCIL4 | 138 | 30.9308 | 31.1517 | 0.2209
GEN-2018-026 | 04 SOUTHEAST | 514866 | WESTOAK4 | 138 | 25.7592 | 25.8891 | 0.1299
GEN-2018-026 | 04 SOUTHEAST | 514867 | MERIDAN4 | 138 | 24.5275 | 24.6261 | 0.0986
GEN-2018-026 | 04 SOUTHEAST | 514868 | DOUGLTP4 | 138 | 32.4305 | 32.5476 | 0.1171
GEN-2018-026 | 04 SOUTHEAST | 514869 | WESTERN4 | 138 | 31.495 | 31.5767 | 0.0817
GEN-2018-026 | 04 SOUTHEAST | 514870 | STNWAL 4 | 138 | 27.9056 | 27.9572 | 0.0516
GEN-2018-026 | 04 SOUTHEAST | 514873 | LNEOAK 4 | 138 | 28.4419 | 28.4681 | 0.0262
GEN-2018-026 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 46.3305 | 46.3893 | 0.0588
GEN-2018-026 | 04 SOUTHEAST | 514887 | WESTMOR4 | 138 | 29.5035 | 29.5385 | 0.035
GEN-2018-026 | 04 SOUTHEAST | 514888 | 36&MER 4 | 138 | 28.8669 | 28.9798 | 0.1129
GEN-2018-026 | 04 SOUTHEAST | 514889 | WRAIRPT4 | 138 | 27.009 | 27.0853 | 0.0763
GEN-2018-026 | 04 SOUTHEAST | 514891 | SMITHCO4 | 138 | 26.6526 | 26.7821 | 0.1295
GEN-2018-026 | 04 SOUTHEAST | 514892 | DAYTON 4 | 138 | 27.165 | 27.2999 | 0.1349
GEN-2018-026 | 04 SOUTHEAST | 514893 | XEROX 4 | 138 | 31.3851 | 31.5698 | 0.1847
GEN-2018-026 | 04 SOUTHEAST | 514894 | CZECHAL4 | 138 | 30.0065 | 30.1496 | 0.1431
GEN-2018-026 | 04 SOUTHEAST | 514895 | SARA 4 | 138 | 20.0685 | 20.0818 | 0.0133
GEN-2018-026 | 04 SOUTHEAST | 514896 | MORGAN 4 | 138 | 34.8355 | 35.1078 | 0.2723
GEN-2018-026 | 04 SOUTHEAST | 514898 | CIMARON4 | 138 | 46.8066 | 46.9051 | 0.0985
GEN-2018-026 | 04 SOUTHEAST | 514902 | MCCLAIN4 | 138 | 32.2793 | 32.3017 | 0.0224
GEN-2018-026 | 04 SOUTHEAST | 514920 | SW 5TH 4 | 138 | 31.4218 | 31.5791 | 0.1573
GEN-2018-026 | 04 SOUTHEAST | 514922 | CLASSEN4 | 138 | 32.2713 | 32.3884 | 0.1171
GEN-2018-026 | 04 SOUTHEAST | 514923 | LIGHTCK4 | 138 | 25.9597 | 26.0157 | 0.056
GEN-2018-026 | 04 SOUTHEAST | 514925 | PENN 4 | 138 | 31.0657 | 31.1273 | 0.0616
GEN-2018-026 | 04 SOUTHEAST | 514926 | SANTAFE4 | 138 | 27.5072 | 27.5485 | 0.0413
GEN-2018-026 | 04 SOUTHEAST | 514963 | TROSPER4 | 138 | 29.3471 | 29.3978 | 0.0507
GEN-2018-026 | 04 SOUTHEAST | 515338 | HOBBYLO4 | 138 | 26.2289 | 26.3405 | 0.1116
GEN-2018-026 | 04 SOUTHEAST | 515367 | CHEMTRN4 | 138 | 22.5407 | 22.6228 | 0.0821
GEN-2018-026 | 04 SOUTHEAST | 515374 | CHISHOM4 | 138 | 23.8091 | 23.8277 | 0.0186
GEN-2018-026 | 04 SOUTHEAST | 515851 | CROSTWN4 | 138 | 26.4679 | 26.5309 | 0.063
GEN-2018-026 | 04 SOUTHEAST | 515962 | OMEGA 4 | 138 | 6.1044 | 6.105 | 0.0006
GEN-2018-026 | 04 SOUTHEAST | 762614 | GEN-2018-026 | 138 | 37.9739 | 38.4029 | 0.429
GEN-2018-026 | 04 SOUTHEAST | 514816 | YUKON 2 | 69 | 7.7321 | 7.7346 | 0.0025
GEN-2018-026 | 04 SOUTHEAST | 514817 | SVCELRN2 | 69 | 6.7665 | 6.7678 | 0.0013
GEN-2018-026 | 04 SOUTHEAST | 514818 | ELRENO 2 | 69 | 7.7765 | 7.7779 | 0.0014
GEN-2018-026 | 04 SOUTHEAST | 514845 | 38TH ST2 | 69 | 18.5176 | 18.5328 | 0.0152
GEN-2018-026 | 04 SOUTHEAST | 514860 | MSTANG 2 | 69 | 22.764 | 22.7917 | 0.0277
GEN-2018-026 | 04 SOUTHEAST | 514913 | MAY AVE2 | 69 | 17.1126 | 17.1261 | 0.0135
GEN-2018-026 | 04 SOUTHEAST | 514914 | BETHANY2 | 69 | 13.4557 | 13.4642 | 0.0085
GEN-2018-026 | 04 SOUTHEAST | 514915 | WODLAWN2 | 69 | 13.4073 | 13.4162 | 0.0089
GEN-2018-026 | 04 SOUTHEAST | 514916 | WILROGR2 | 69 | 6.1472 | 6.1492 | 0.002
GEN-2018-026 | 04 SOUTHEAST | 514917 | MCARTHR2 | 69 | 12.1 | 12.1069 | 0.0069
GEN-2018-026 | 04 SOUTHEAST | 514918 | SW 64TH2 | 69 | 12.795 | 12.802 | 0.007
GEN-2018-026 | 04 SOUTHEAST | 514919 | SW 5TH 2 | 69 | 19.1287 | 19.147 | 0.0183
GEN-2018-026 | 04 SOUTHEAST | 514924 | PENN 2 | 69 | 18.2994 | 18.3126 | 0.0132
GEN-2018-026 | 04 SOUTHEAST | 514975 | SW22ND 2 | 69 | 16.2122 | 16.2242 | 0.012
GEN-2018-026 | 04 SOUTHEAST | 514976 | KENTUKY2 | 69 | 17.1808 | 17.1928 | 0.012
GEN-2018-026 | 04 SOUTHEAST | 514977 | KENTUKT2 | 69 | 17.8368 | 17.8494 | 0.0126
GEN-2018-026 | 04 SOUTHEAST | 515506 | OKRCHET2 | 69 | 3.879 | 3.8792 | 0.0002
GEN-2018-027 | 04 SOUTHEAST | 509755 | WEKIWA-7 | 345 | 23.2454 | 23.2689 | 0.0235
GEN-2018-027 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 33.0307 | 33.0851 | 0.0544
GEN-2018-027 | 04 SOUTHEAST | 509807 | ONETA--7 | 345 | 30.5128 | 30.5423 | 0.0295
GEN-2018-027 | 04 SOUTHEAST | 509834 | COGENT 7 | 345 | 30.6644 | 30.7104 | 0.046
GEN-2018-027 | 04 SOUTHEAST | 509852 | T.NO.--7 | 345 | 25.0125 | 25.0254 | 0.0129
GEN-2018-027 | 04 SOUTHEAST | 509870 | SAPLPRD7 | 345 | 23.6026 | 23.6381 | 0.0355
GEN-2018-027 | 04 SOUTHEAST | 514803 | SOONER 7 | 345 | 30.1298 | 30.1337 | 0.0039
GEN-2018-027 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 26.9171 | 26.9184 | 0.0013
GEN-2018-027 | 04 SOUTHEAST | 515235 | PECANCK7 | 345 | 22.4306 | 22.4382 | 0.0076
GEN-2018-027 | 04 SOUTHEAST | 588039 | G16133G16146 | 345 | 33.0307 | 33.0851 | 0.0544
GEN-2018-027 | 04 SOUTHEAST | 509716 | S52DEL 4 | 138 | 20.6593 | 20.7255 | 0.0662
GEN-2018-027 | 04 SOUTHEAST | 509724 | 36&OLY-4 | 138 | 33.8883 | 34.1789 | 0.2906
GEN-2018-027 | 04 SOUTHEAST | 509727 | OAKS W4 | 138 | 16.1381 | 16.1935 | 0.0554
GEN-2018-027 | 04 SOUTHEAST | 509731 | S.HIL E4 | 138 | 22.2343 | 22.2656 | 0.0313
GEN-2018-027 | 04 SOUTHEAST | 509732 | ORU W4 | 138 | 24.1495 | 24.1853 | 0.0358
GEN-2018-027 | 04 SOUTHEAST | 509734 | 53GARN 4 | 138 | 19.343 | 19.3703 | 0.0273
GEN-2018-027 | 04 SOUTHEAST | 509738 | ORU E4 | 138 | 25.5411 | 25.5786 | 0.0375
GEN-2018-027 | 04 SOUTHEAST | 509739 | CARSN-T4 | 138 | 33.335 | 33.6133 | 0.2783
GEN-2018-027 | 04 SOUTHEAST | 509740 | UNIONAV4 | 138 | 21.5698 | 21.686 | 0.1162
GEN-2018-027 | 04 SOUTHEAST | 509742 | DENVR-C4 | 138 | 13.275 | 13.3234 | 0.0484
GEN-2018-027 | 04 SOUTHEAST | 509748 | DENVR-W4 | 138 | 9.9064 | 9.9157 | 0.0093
GEN-2018-027 | 04 SOUTHEAST | 509749 | CARSN-C4 | 138 | 17.6643 | 17.7421 | 0.0778
GEN-2018-027 | 04 SOUTHEAST | 509753 | 116JENK4 | 138 | 44.1617 | 44.2743 | 0.1126
GEN-2018-027 | 04 SOUTHEAST | 509754 | WHORSE-4 | 138 | 4.0909 | 4.0925 | 0.0016
GEN-2018-027 | 04 SOUTHEAST | 509756 | CARSN-S4 | 138 | 18.2718 | 18.3638 | 0.092
GEN-2018-027 | 04 SOUTHEAST | 509757 | WEKIWA-4 | 138 | 33.5181 | 33.5581 | 0.04
GEN-2018-027 | 04 SOUTHEAST | 509758 | PRATTV-4 | 138 | 21.1087 | 21.1456 | 0.0369
GEN-2018-027 | 04 SOUTHEAST | 509759 | JENKS--4 | 138 | 26.3348 | 26.3889 | 0.0541
GEN-2018-027 | 04 SOUTHEAST | 509760 | MINGO-N4 | 138 | 28.2762 | 28.3328 | 0.0566
GEN-2018-027 | 04 SOUTHEAST | 509761 | MINGO-S4 | 138 | 26.3889 | 26.4421 | 0.0532
GEN-2018-027 | 04 SOUTHEAST | 509762 | 53GARNT4 | 138 | 22.045 | 22.0803 | 0.0353
GEN-2018-027 | 04 SOUTHEAST | 509763 | 53GARST4 | 138 | 21.0526 | 21.0827 | 0.0301
GEN-2018-027 | 04 SOUTHEAST | 509764 | WRNMEDT4 | 138 | 26.2976 | 26.3484 | 0.0508
GEN-2018-027 | 04 SOUTHEAST | 509765 | 77MEMTP4 | 138 | 18.7721 | 18.7952 | 0.0231
GEN-2018-027 | 04 SOUTHEAST | 509766 | 77MEM-W4 | 138 | 23.8474 | 23.8876 | 0.0402
GEN-2018-027 | 04 SOUTHEAST | 509767 | B111---4 | 138 | 16.5148 | 16.5248 | 0.01
GEN-2018-027 | 04 SOUTHEAST | 509772 | FORD---4 | 138 | 18.7806 | 18.8012 | 0.0206
GEN-2018-027 | 04 SOUTHEAST | 509773 | RSS T1 4 | 138 | 52.3037 | 52.4342 | 0.1305
GEN-2018-027 | 04 SOUTHEAST | 509774 | 53GARNS4 | 138 | 18.5608 | 18.5843 | 0.0235
GEN-2018-027 | 04 SOUTHEAST | 509775 | 136YALE4 | 138 | 24.3837 | 24.4111 | 0.0274
GEN-2018-027 | 04 SOUTHEAST | 509776 | 52DELTP4 | 138 | 34.107 | 34.2864 | 0.1794
GEN-2018-027 | 04 SOUTHEAST | 509777 | KENSH-W4 | 138 | 15.4084 | 15.4737 | 0.0653
GEN-2018-027 | 04 SOUTHEAST | 509780 | MAYO--S4 | 138 | 21.9808 | 22.0138 | 0.033
GEN-2018-027 | 04 SOUTHEAST | 509783 | R.S.S.-4 | 138 | 63.0032 | 63.2128 | 0.2096
GEN-2018-027 | 04 SOUTHEAST | 509788 | T.P.S.-4 | 138 | 40.3076 | 40.7573 | 0.4497
GEN-2018-027 | 04 SOUTHEAST | 509800 | 36LEWIS4 | 138 | 34.3622 | 34.5885 | 0.2263
GEN-2018-027 | 04 SOUTHEAST | 509808 | S21ST--4 | 138 | 21.1117 | 21.1454 | 0.0337
GEN-2018-027 | 04 SOUTHEAST | 509809 | 81YALTP4 | 138 | 26.1526 | 26.1994 | 0.0468
GEN-2018-027 | 04 SOUTHEAST | 509810 | 81YALES4 | 138 | 20.7835 | 20.8097 | 0.0262
GEN-2018-027 | 04 SOUTHEAST | 509811 | T.S.E.-4 | 138 | 40.0637 | 40.2038 | 0.1401
GEN-2018-027 | 04 SOUTHEAST | 509812 | SHEFFD-4 | 138 | 26.7417 | 26.8036 | 0.0619
GEN-2018-027 | 04 SOUTHEAST | 509813 | SHILETP4 | 138 | 28.8529 | 28.9052 | 0.0523
GEN-2018-027 | 04 SOUTHEAST | 509814 | 52DELWT4 | 138 | 23.6396 | 23.7014 | 0.0618
GEN-2018-027 | 04 SOUTHEAST | 509815 | S.S.---4 | 138 | 29.5729 | 29.6551 | 0.0822
GEN-2018-027 | 04 SOUTHEAST | 509821 | HWY20-T4 | 138 | 4.0999 | 4.1015 | 0.0016
GEN-2018-027 | 04 SOUTHEAST | 509823 | WED-TAP4 | 138 | 19.8025 | 19.8315 | 0.029
GEN-2018-027 | 04 SOUTHEAST | 509824 | YARCH-S4 | 138 | 15.0293 | 15.0491 | 0.0198
GEN-2018-027 | 04 SOUTHEAST | 509826 | ZUNIS-S4 | 138 | 16.5222 | 16.5647 | 0.0425
GEN-2018-027 | 04 SOUTHEAST | 509828 | 21STTAP4 | 138 | 30.7767 | 30.8483 | 0.0716
GEN-2018-027 | 04 SOUTHEAST | 509829 | FULTONW4 | 138 | 17.6664 | 17.6937 | 0.0273
GEN-2018-027 | 04 SOUTHEAST | 509830 | KENSH-E-TP4 | 138 | 20.9212 | 20.9595 | 0.0383
GEN-2018-027 | 04 SOUTHEAST | 509831 | E.61ST-4 | 138 | 25.2987 | 25.3473 | 0.0486
GEN-2018-027 | 04 SOUTHEAST | 509833 | S.HUD.-4 | 138 | 29.6738 | 29.7443 | 0.0705
GEN-2018-027 | 04 SOUTHEAST | 509845 | KIMCLRK4 | 138 | 23.1407 | 23.165 | 0.0243
GEN-2018-027 | 04 SOUTHEAST | 509846 | OAKS--E4 | 138 | 14.1132 | 14.1542 | 0.041
GEN-2018-027 | 04 SOUTHEAST | 509847 | 96YALE-4 | 138 | 28.4584 | 28.5075 | 0.0491
GEN-2018-027 | 04 SOUTHEAST | 509848 | OAKSWTP4 | 138 | 25.7279 | 25.8679 | 0.14
GEN-2018-027 | 04 SOUTHEAST | 509849 | ORU ETP4 | 138 | 35.2865 | 35.3576 | 0.0711
GEN-2018-027 | 04 SOUTHEAST | 509850 | OAKSETP4 | 138 | 27.8345 | 27.9926 | 0.1581
GEN-2018-027 | 04 SOUTHEAST | 509853 | ORU-WTP4 | 138 | 30.8949 | 30.953 | 0.0581
GEN-2018-027 | 04 SOUTHEAST | 509856 | 52DEL-W4 | 138 | 12.4884 | 12.5058 | 0.0174
GEN-2018-027 | 04 SOUTHEAST | 509858 | WARNTAP4 | 138 | 29.7675 | 29.8204 | 0.0529
GEN-2018-027 | 04 SOUTHEAST | 509859 | S HILLW4 | 138 | 17.3667 | 17.4002 | 0.0335
GEN-2018-027 | 04 SOUTHEAST | 509865 | CARSONT4 | 138 | 12.3886 | 12.4 | 0.0114
GEN-2018-027 | 04 SOUTHEAST | 509871 | SAPLPRD4 | 138 | 34.1583 | 34.295 | 0.1367
GEN-2018-027 | 04 SOUTHEAST | 509875 | RSS T2 4 | 138 | 53.2324 | 53.369 | 0.1366
GEN-2018-027 | 04 SOUTHEAST | 509888 | 72ELWOD4 | 138 | 24.1259 | 24.2444 | 0.1185
GEN-2018-027 | 04 SOUTHEAST | 509896 | DENV_WTAP4 | 138 | 28.8353 | 28.9139 | 0.0786
GEN-2018-027 | 04 SOUTHEAST | 509897 | WLDCT_HIL4 | 138 | 4.0918 | 4.0934 | 0.0016
GEN-2018-027 | 04 SOUTHEAST | 510892 | HENRYET4 | 138 | 8.9411 | 8.9422 | 0.0011
GEN-2018-027 | 04 SOUTHEAST | 510898 | OKMULGE4 | 138 | 11.8561 | 11.8595 | 0.0034
GEN-2018-027 | 04 SOUTHEAST | 510902 | WELETK4 | 138 | 15.4341 | 15.4358 | 0.0017
GEN-2018-027 | 04 SOUTHEAST | 510904 | EXP_OKM4 | 138 | 10.2965 | 10.2995 | 0.003
GEN-2018-027 | 04 SOUTHEAST | 510923 | EC.HEN-4 | 138 | 8.9964 | 8.9975 | 0.0011
GEN-2018-027 | 04 SOUTHEAST | 510931 | KELCO 4 | 138 | 10.5977 | 10.6002 | 0.0025
GEN-2018-027 | 04 SOUTHEAST | 515237 | TIBBENS4 | 138 | 18.1492 | 18.1663 | 0.0171
GEN-2018-027 | 04 SOUTHEAST | 515242 | BLUEBEL4 | 138 | 17.7174 | 17.7345 | 0.0171
GEN-2018-027 | 04 SOUTHEAST | 515245 | LONESTR4 | 138 | 13.7931 | 13.8032 | 0.0101
GEN-2018-027 | 04 SOUTHEAST | 515247 | BEELINE4 | 138 | 22.9388 | 22.966 | 0.0272
GEN-2018-027 | 04 SOUTHEAST | 515248 | EXPLGLN4 | 138 | 24.8454 | 24.8775 | 0.0321
GEN-2018-027 | 04 SOUTHEAST | 515473 | EXPGLNT4 | 138 | 25.294 | 25.3273 | 0.0333
GEN-2018-027 | 04 SOUTHEAST | 762625 | GEN-2018-027 | 138 | 34.5714 | 35.0225 | 0.4511
GEN-2018-027 | 04 SOUTHEAST | 509718 | BAWATAP2 | 69 | 2.7875 | 2.7876 | 0.0001
GEN-2018-027 | 04 SOUTHEAST | 509750 | WILLPIP2 | 69 | 5.5191 | 5.5234 | 0.0043
GEN-2018-027 | 04 SOUTHEAST | 509751 | OGMARTN2 | 69 | 5.4862 | 5.4905 | 0.0043
GEN-2018-027 | 04 SOUTHEAST | 509789 | T.P.S.-2 | 69 | 9.195 | 9.2068 | 0.0118
GEN-2018-027 | 04 SOUTHEAST | 509795 | DX----E2 | 69 | 5.3104 | 5.3144 | 0.004
GEN-2018-027 | 04 SOUTHEAST | 509796 | DX----W2 | 69 | 3.8512 | 3.8519 | 0.0007
GEN-2018-027 | 04 SOUTHEAST | 509816 | S.S.---2 | 69 | 6.4281 | 6.43 | 0.0019
GEN-2018-027 | 04 SOUTHEAST | 509820 | T.S.E.-2 | 69 | 6.3449 | 6.3464 | 0.0015
GEN-2018-027 | 04 SOUTHEAST | 515246 | BEELINE2 | 69 | 12.2263 | 12.2297 | 0.0034
GEN-2018-028 | 04 SOUTHEAST | 300739 | 7BLACKBERRY | 345 | 15.5541 | 15.5559 | 0.0018
GEN-2018-028 | 04 SOUTHEAST | 300740 | 7SPORTSMAN | 345 | 24.9618 | 24.9759 | 0.0141
GEN-2018-028 | 04 SOUTHEAST | 506945 | CHAMSPR7 | 345 | 10.6394 | 10.6404 | 0.001
GEN-2018-028 | 04 SOUTHEAST | 509745 | CLARKSV7 | 345 | 20.8845 | 20.892 | 0.0075
GEN-2018-028 | 04 SOUTHEAST | 509755 | WEKIWA-7 | 345 | 23.2102 | 23.2689 | 0.0587
GEN-2018-028 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 33.0511 | 33.0851 | 0.034
GEN-2018-028 | 04 SOUTHEAST | 509807 | ONETA--7 | 345 | 30.5122 | 30.5423 | 0.0301
GEN-2018-028 | 04 SOUTHEAST | 509834 | COGENT 7 | 345 | 30.6817 | 30.7104 | 0.0287
GEN-2018-028 | 04 SOUTHEAST | 509836 | OEC 7 | 345 | 30.2183 | 30.2476 | 0.0293
GEN-2018-028 | 04 SOUTHEAST | 509852 | T.NO.--7 | 345 | 24.8758 | 25.0254 | 0.1496
GEN-2018-028 | 04 SOUTHEAST | 509870 | SAPLPRD7 | 345 | 23.606 | 23.6381 | 0.0321
GEN-2018-028 | 04 SOUTHEAST | 510380 | DELWARE7 | 345 | 12.1028 | 12.1099 | 0.0071
GEN-2018-028 | 04 SOUTHEAST | 510406 | N.E.S.-7 | 345 | 19.6964 | 19.7286 | 0.0322
GEN-2018-028 | 04 SOUTHEAST | 512650 | GRDA1 7 | 345 | 27.4882 | 27.5068 | 0.0186
GEN-2018-028 | 04 SOUTHEAST | 512694 | CLEVLND7 | 345 | 15.6325 | 15.6576 | 0.0251
GEN-2018-028 | 04 SOUTHEAST | 512750 | TONECE7 | 345 | 15.6415 | 15.6441 | 0.0026
GEN-2018-028 | 04 SOUTHEAST | 512865 | GREC TAP5 | 345 | 26.2477 | 26.2658 | 0.0181
GEN-2018-028 | 04 SOUTHEAST | 513596 | IGLOOV 7 | 345 | 20.7862 | 20.8023 | 0.0161
GEN-2018-028 | 04 SOUTHEAST | 514715 | WOODRNG7 | 345 | 20.8409 | 20.8426 | 0.0017
GEN-2018-028 | 04 SOUTHEAST | 514803 | SOONER 7 | 345 | 30.1159 | 30.1337 | 0.0178
GEN-2018-028 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 24.8744 | 24.8759 | 0.0015
GEN-2018-028 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 26.9171 | 26.9184 | 0.0013
GEN-2018-028 | 04 SOUTHEAST | 515224 | MUSKOGE7 | 345 | 28.1231 | 28.1299 | 0.0068
GEN-2018-028 | 04 SOUTHEAST | 515235 | PECANCK7 | 345 | 22.4321 | 22.4382 | 0.0061
GEN-2018-028 | 04 SOUTHEAST | 515576 | RANCHRD7 | 345 | 15.4577 | 15.4597 | 0.002
GEN-2018-028 | 04 SOUTHEAST | 515621 | OPENSKY7 | 345 | 13.6684 | 13.6697 | 0.0013
GEN-2018-028 | 04 SOUTHEAST | 515688 | FRNTWND7 | 345 | 12.4937 | 12.495 | 0.0013
GEN-2018-028 | 04 SOUTHEAST | 515894 | THUNDER7 | 345 | 12.1304 | 12.1329 | 0.0025
GEN-2018-028 | 04 SOUTHEAST | 516010 | PINTAIL7 | 345 | 17.9034 | 17.9062 | 0.0028
GEN-2018-028 | 04 SOUTHEAST | 516019 | KINGWD 7 | 345 | 17.8398 | 17.8426 | 0.0028
GEN-2018-028 | 04 SOUTHEAST | 516066 | FRNT2WD7 | 345 | 12.0921 | 12.0933 | 0.0012
GEN-2018-028 | 04 SOUTHEAST | 529200 | OMCDLEC7 | 345 | 15.4272 | 15.4292 | 0.002
GEN-2018-028 | 04 SOUTHEAST | 532777 | G17-009-TAP | 345 | 11.8287 | 11.8299 | 0.0012
GEN-2018-028 | 04 SOUTHEAST | 532793 | NEOSHO 7 | 345 | 17.8925 | 17.8962 | 0.0037
GEN-2018-028 | 04 SOUTHEAST | 560056 | G15-066T | 345 | 20.1284 | 20.1428 | 0.0144
GEN-2018-028 | 04 SOUTHEAST | 585040 | GEN-2015-066 | 345 | 19.9306 | 19.9447 | 0.0141
GEN-2018-028 | 04 SOUTHEAST | 587804 | G16-119-TAP | 345 | 16.7801 | 16.7826 | 0.0025
GEN-2018-028 | 04 SOUTHEAST | 587950 | GEN-2016-119 | 345 | 10.404 | 10.4048 | 0.0008
GEN-2018-028 | 04 SOUTHEAST | 588039 | G16133G16146 | 345 | 33.0511 | 33.0851 | 0.034
GEN-2018-028 | 04 SOUTHEAST | 760389 | GEN-2017-140 | 345 | 1.7037 | 1.7038 | 0.0001
GEN-2018-028 | 04 SOUTHEAST | 760921 | G17-209-TAP | 345 | 19.4746 | 19.4749 | 0.0003
GEN-2018-028 | 04 SOUTHEAST | 762680 | GEN-2018-032 | 345 | 11.8438 | 11.8454 | 0.0016
GEN-2018-028 | 04 SOUTHEAST | 505609 | KEYSTON5 | 161 | 7.406 | 7.4094 | 0.0034
GEN-2018-028 | 04 SOUTHEAST | 512638 | CATSAGR5 | 161 | 24.7671 | 24.8214 | 0.0543
GEN-2018-028 | 04 SOUTHEAST | 512651 | CLARMR 5 | 161 | 13.4231 | 13.4321 | 0.009
GEN-2018-028 | 04 SOUTHEAST | 512656 | GRDA1 5 | 161 | 45.6602 | 45.6909 | 0.0307
GEN-2018-028 | 04 SOUTHEAST | 513590 | CUSTDAY1 5 | 161 | 16.976 | 16.9808 | 0.0048
GEN-2018-028 | 04 SOUTHEAST | 513591 | HERRON 5 | 161 | 17.3968 | 17.402 | 0.0052
GEN-2018-028 | 04 SOUTHEAST | 513593 | IGLOOV1 5 | 161 | 17.5871 | 17.5923 | 0.0052
GEN-2018-028 | 04 SOUTHEAST | 513595 | IGLOOV2 5 | 161 | 17.5871 | 17.5923 | 0.0052
GEN-2018-028 | 04 SOUTHEAST | 532937 | NEOSHO 5 | 161 | 22.4632 | 22.4657 | 0.0025
GEN-2018-028 | 04 SOUTHEAST | 300131 | 4FISHERTP | 138 | 15.525 | 15.5373 | 0.0123
GEN-2018-028 | 04 SOUTHEAST | 300138 | 4CLEVLND | 138 | 17.4832 | 17.4942 | 0.011
GEN-2018-028 | 04 SOUTHEAST | 300140 | 4SILVCTY | 138 | 16.5441 | 16.5541 | 0.01
GEN-2018-028 | 04 SOUTHEAST | 300996 | 4JAVINE | 138 | 6.8851 | 6.8872 | 0.0021
GEN-2018-028 | 04 SOUTHEAST | 505610 | KEYSTON4 | 138 | 23.3374 | 23.3685 | 0.0311
GEN-2018-028 | 04 SOUTHEAST | 509714 | CIP 4 | 138 | 14.0903 | 14.1839 | 0.0936
GEN-2018-028 | 04 SOUTHEAST | 509715 | CDC 4 | 138 | 14.0806 | 14.1741 | 0.0935
GEN-2018-028 | 04 SOUTHEAST | 509722 | SPNKY CK4 | 138 | 31.3322 | 31.4491 | 0.1169
GEN-2018-028 | 04 SOUTHEAST | 509726 | OWASO1_4 | 138 | 14.549 | 14.6302 | 0.0812
GEN-2018-028 | 04 SOUTHEAST | 509743 | DENVR-E4 | 138 | 8.3189 | 8.3648 | 0.0459
GEN-2018-028 | 04 SOUTHEAST | 509746 | DENVTAP4 | 138 | 9.7559 | 9.819 | 0.0631
GEN-2018-028 | 04 SOUTHEAST | 509752 | INOLATP4 | 138 | 9.8315 | 9.8386 | 0.0071
GEN-2018-028 | 04 SOUTHEAST | 509757 | WEKIWA-4 | 138 | 33.4899 | 33.5581 | 0.0682
GEN-2018-028 | 04 SOUTHEAST | 509759 | JENKS--4 | 138 | 26.3776 | 26.3889 | 0.0113
GEN-2018-028 | 04 SOUTHEAST | 509768 | BA101ST4 | 138 | 19.3538 | 19.3603 | 0.0065
GEN-2018-028 | 04 SOUTHEAST | 509769 | BA101-N4 | 138 | 20.2061 | 20.2145 | 0.0084
GEN-2018-028 | 04 SOUTHEAST | 509771 | LLAN ET4 | 138 | 25.2546 | 25.3066 | 0.052
GEN-2018-028 | 04 SOUTHEAST | 509773 | RSS T1 4 | 138 | 52.3989 | 52.4342 | 0.0353
GEN-2018-028 | 04 SOUTHEAST | 509784 | A.A.---4 | 138 | 17.4344 | 17.538 | 0.1036
GEN-2018-028 | 04 SOUTHEAST | 509786 | BA.N-ST4 | 138 | 24.6148 | 24.6388 | 0.024
GEN-2018-028 | 04 SOUTHEAST | 509787 | DAWSN-N4 | 138 | 18.2997 | 18.3813 | 0.0816
GEN-2018-028 | 04 SOUTHEAST | 509790 | CATOOSA4 | 138 | 37.0668 | 37.2117 | 0.1449
GEN-2018-028 | 04 SOUTHEAST | 509801 | MOHAWK 4 | 138 | 11.4334 | 11.4838 | 0.0504
GEN-2018-028 | 04 SOUTHEAST | 509802 | MINGORD4 | 138 | 17.4547 | 17.5465 | 0.0918
GEN-2018-028 | 04 SOUTHEAST | 509804 | LLANETP4 | 138 | 28.1932 | 28.2643 | 0.0711
GEN-2018-028 | 04 SOUTHEAST | 509805 | PP----W4 | 138 | 8.704 | 8.7232 | 0.0192
GEN-2018-028 | 04 SOUTHEAST | 509806 | ONETA--4 | 138 | 50.2893 | 50.3382 | 0.0489
GEN-2018-028 | 04 SOUTHEAST | 509812 | SHEFFD-4 | 138 | 26.7784 | 26.8036 | 0.0252
GEN-2018-028 | 04 SOUTHEAST | 509815 | S.S.---4 | 138 | 29.6264 | 29.6551 | 0.0287
GEN-2018-028 | 04 SOUTHEAST | 509817 | T.NO.--4 | 138 | 36.064 | 36.9384 | 0.8744
GEN-2018-028 | 04 SOUTHEAST | 509818 | PP----E4 | 138 | 8.127 | 8.1532 | 0.0262
GEN-2018-028 | 04 SOUTHEAST | 509822 | W.ED.-E4 | 138 | 8.1531 | 8.1971 | 0.044
GEN-2018-028 | 04 SOUTHEAST | 509823 | WED-TAP4 | 138 | 19.8157 | 19.8315 | 0.0158
GEN-2018-028 | 04 SOUTHEAST | 509825 | YARCH-N4 | 138 | 7.0176 | 7.0372 | 0.0196
GEN-2018-028 | 04 SOUTHEAST | 509835 | TERNITP4 | 138 | 16.5683 | 16.5955 | 0.0272
GEN-2018-028 | 04 SOUTHEAST | 509837 | 46ST--E4 | 138 | 3.0611 | 3.0649 | 0.0038
GEN-2018-028 | 04 SOUTHEAST | 509839 | CDC-ET 4 | 138 | 19.5449 | 19.7262 | 0.1813
GEN-2018-028 | 04 SOUTHEAST | 509840 | WHIRLPO4 | 138 | 19.1937 | 19.3914 | 0.1977
GEN-2018-028 | 04 SOUTHEAST | 509841 | PCATSAT4 | 138 | 18.517 | 18.5515 | 0.0345
GEN-2018-028 | 04 SOUTHEAST | 509842 | CDC-WT 4 | 138 | 20.2704 | 20.491 | 0.2206
GEN-2018-028 | 04 SOUTHEAST | 509843 | OWASO2_4 | 138 | 14.5874 | 14.6077 | 0.0203
GEN-2018-028 | 04 SOUTHEAST | 509844 | OWASOTP4 | 138 | 15.6506 | 15.7446 | 0.094
GEN-2018-028 | 04 SOUTHEAST | 509848 | OAKSWTP4 | 138 | 25.8547 | 25.8679 | 0.0132
GEN-2018-028 | 04 SOUTHEAST | 509851 | P&P WTP4 | 138 | 15.7723 | 15.8354 | 0.0631
GEN-2018-028 | 04 SOUTHEAST | 509854 | VERDIGS4 | 138 | 14.2858 | 14.305 | 0.0192
GEN-2018-028 | 04 SOUTHEAST | 509860 | OWAS1094 | 138 | 15.0459 | 15.1152 | 0.0693
GEN-2018-028 | 04 SOUTHEAST | 509862 | YARCHT 4 | 138 | 9.1657 | 9.1991 | 0.0334
GEN-2018-028 | 04 SOUTHEAST | 509863 | PPTAP 4 | 138 | 10.8319 | 10.8784 | 0.0465
GEN-2018-028 | 04 SOUTHEAST | 509864 | CLARTOK4 | 138 | 14.2807 | 14.2999 | 0.0192
GEN-2018-028 | 04 SOUTHEAST | 509865 | CARSONT4 | 138 | 12.3938 | 12.4 | 0.0062
GEN-2018-028 | 04 SOUTHEAST | 509869 | 121LYNN4 | 138 | 18.2812 | 18.288 | 0.0068
GEN-2018-028 | 04 SOUTHEAST | 509871 | SAPLPRD4 | 138 | 34.2703 | 34.295 | 0.0247
GEN-2018-028 | 04 SOUTHEAST | 509875 | RSS T2 4 | 138 | 53.3324 | 53.369 | 0.0366
GEN-2018-028 | 04 SOUTHEAST | 509884 | SKIATOK4 | 138 | 10.95 | 11.0113 | 0.0613
GEN-2018-028 | 04 SOUTHEAST | 509887 | OWAS88_4 | 138 | 17.4126 | 17.5273 | 0.1147
GEN-2018-028 | 04 SOUTHEAST | 509888 | 72ELWOD4 | 138 | 24.2327 | 24.2444 | 0.0117
GEN-2018-028 | 04 SOUTHEAST | 509891 | BA_71ST4 | 138 | 23.9314 | 23.9429 | 0.0115
GEN-2018-028 | 04 SOUTHEAST | 509895 | T.NO.2-4 | 138 | 36.0064 | 36.9018 | 0.8954
GEN-2018-028 | 04 SOUTHEAST | 509896 | DENV_WTAP4 | 138 | 28.8867 | 28.9139 | 0.0272
GEN-2018-028 | 04 SOUTHEAST | 509899 | BIRDCREE-4 | 138 | 17.9308 | 17.9631 | 0.0323
GEN-2018-028 | 04 SOUTHEAST | 509900 | 46ST-TP-4 | 138 | 10.03 | 10.0721 | 0.0421
GEN-2018-028 | 04 SOUTHEAST | 510379 | DELWARE4 | 138 | 11.288 | 11.2906 | 0.0026
GEN-2018-028 | 04 SOUTHEAST | 510384 | WATOVA 4 | 138 | 9.4291 | 9.4364 | 0.0073
GEN-2018-028 | 04 SOUTHEAST | 510385 | RICE CK4 | 138 | 11.7148 | 11.7261 | 0.0113
GEN-2018-028 | 04 SOUTHEAST | 510386 | NBVILLE4 | 138 | 9.729 | 9.7345 | 0.0055
GEN-2018-028 | 04 SOUTHEAST | 510388 | BARNSAL4 | 138 | 6.9349 | 6.9489 | 0.014
GEN-2018-028 | 04 SOUTHEAST | 510390 | BV-COM-4 | 138 | 10.5962 | 10.6069 | 0.0107
GEN-2018-028 | 04 SOUTHEAST | 510391 | BV-SE--4 | 138 | 12.5654 | 12.5784 | 0.013
GEN-2018-028 | 04 SOUTHEAST | 510394 | BLUESTM4 | 138 | 8.6872 | 8.694 | 0.0068
GEN-2018-028 | 04 SOUTHEAST | 510395 | MOUNDRD4 | 138 | 9.6008 | 9.6112 | 0.0104
GEN-2018-028 | 04 SOUTHEAST | 510396 | N.E.S.-4 | 138 | 36.8918 | 37.0037 | 0.1119
GEN-2018-028 | 04 SOUTHEAST | 510397 | NOWATA-4 | 138 | 8.755 | 8.7613 | 0.0063
GEN-2018-028 | 04 SOUTHEAST | 510410 | CHELSA4 | 138 | 6.2843 | 6.2863 | 0.002
GEN-2018-028 | 04 SOUTHEAST | 510413 | HAWTHRN4 | 138 | 21.0884 | 21.1233 | 0.0349
GEN-2018-028 | 04 SOUTHEAST | 510429 | ALWUETP4 | 138 | 6.0134 | 6.0152 | 0.0018
GEN-2018-028 | 04 SOUTHEAST | 510433 | BARNPMP4 | 138 | 6.8963 | 6.9081 | 0.0118
GEN-2018-028 | 04 SOUTHEAST | 512707 | CLARMR 4 | 138 | 13.9469 | 13.9584 | 0.0115
GEN-2018-028 | 04 SOUTHEAST | 512726 | SILVCTYGR4 | 138 | 16.3821 | 16.3919 | 0.0098
GEN-2018-028 | 04 SOUTHEAST | 512729 | CLEVLND 4 | 138 | 17.4833 | 17.4942 | 0.0109
GEN-2018-028 | 04 SOUTHEAST | 512734 | FARML 4 | 138 | 8.5755 | 8.5771 | 0.0016
GEN-2018-028 | 04 SOUTHEAST | 512749 | PAWNSW4 | 138 | 10.4576 | 10.46 | 0.0024
GEN-2018-028 | 04 SOUTHEAST | 513124 | OOLOGAHKM 4 | 138 | 21.388 | 21.4222 | 0.0342
GEN-2018-028 | 04 SOUTHEAST | 514704 | MILLERT4 | 138 | 21.5393 | 21.5407 | 0.0014
GEN-2018-028 | 04 SOUTHEAST | 514707 | PERRY 4 | 138 | 11.9116 | 11.912 | 0.0004
GEN-2018-028 | 04 SOUTHEAST | 514798 | SNRPMPT4 | 138 | 21.5843 | 21.5857 | 0.0014
GEN-2018-028 | 04 SOUTHEAST | 514802 | SOONER 4 | 138 | 33.431 | 33.4343 | 0.0033
GEN-2018-028 | 04 SOUTHEAST | 515447 | MORISNT4 | 138 | 14.7675 | 14.7684 | 0.0009
GEN-2018-028 | 04 SOUTHEAST | 533021 | NEOSHO 4 | 138 | 25.3469 | 25.3498 | 0.0029
GEN-2018-028 | 04 SOUTHEAST | 560389 | GEN-2010-055 | 138 | 33.4899 | 33.5581 | 0.0682
GEN-2018-028 | 04 SOUTHEAST | 762636 | GEN-2018-028 | 138 | 35.9897 | 36.8851 | 0.8954
GEN-2018-028 | 04 SOUTHEAST | 300927 | 2CLEVLND | 69 | 10.1954 | 10.1973 | 0.0019
GEN-2018-028 | 04 SOUTHEAST | 509799 | CATOOSA2 | 69 | 10.6067 | 10.6121 | 0.0054
GEN-2018-029 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 33.0838 | 33.0851 | 0.0013
GEN-2018-029 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 14.765 | 14.7659 | 0.0009
GEN-2018-029 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 35.2893 | 35.3073 | 0.018
GEN-2018-029 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 24.8689 | 24.8759 | 0.007
GEN-2018-029 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 37.892 | 37.909 | 0.017
GEN-2018-029 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 27.7895 | 27.8065 | 0.017
GEN-2018-029 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 26.9043 | 26.9184 | 0.0141
GEN-2018-029 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 26.8024 | 26.8166 | 0.0142
GEN-2018-029 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 29.4706 | 29.4803 | 0.0097
GEN-2018-029 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 35.7071 | 35.7199 | 0.0128
GEN-2018-029 | 04 SOUTHEAST | 516096 | NORMHLL7 | 345 | 27.8104 | 27.8237 | 0.0133
GEN-2018-029 | 04 SOUTHEAST | 588839 | FIREWHL-TAP | 345 | 18.6413 | 18.642 | 0.0007
GEN-2018-029 | 04 SOUTHEAST | 760032 | GEN-2017-133 | 345 | 5.6944 | 5.6949 | 0.0005
GEN-2018-029 | 04 SOUTHEAST | 300135 | 4LUTHER | 138 | 8.5235 | 8.5289 | 0.0054
GEN-2018-029 | 04 SOUTHEAST | 300136 | 4MEMORALT | 138 | 21.1879 | 21.2296 | 0.0417
GEN-2018-029 | 04 SOUTHEAST | 300915 | 4WARWICK | 138 | 4.671 | 4.6723 | 0.0013
GEN-2018-029 | 04 SOUTHEAST | 301372 | 4LUTHERD | 138 | 8.513 | 8.5183 | 0.0053
GEN-2018-029 | 04 SOUTHEAST | 301541 | 4MEMORAL | 138 | 20.9807 | 21.0215 | 0.0408
GEN-2018-029 | 04 SOUTHEAST | 514501 | KELLYAV4 | 138 | 27.0481 | 27.0797 | 0.0316
GEN-2018-029 | 04 SOUTHEAST | 514510 | BURGETT4 | 138 | 23.4469 | 23.463 | 0.0161
GEN-2018-029 | 04 SOUTHEAST | 514714 | WOODRNG4 | 138 | 22.0443 | 22.0451 | 0.0008
GEN-2018-029 | 04 SOUTHEAST | 514733 | MARSHL 4 | 138 | 8.4813 | 8.4816 | 0.0003
GEN-2018-029 | 04 SOUTHEAST | 514827 | CTNWOOD4 | 138 | 19.0861 | 19.0914 | 0.0053
GEN-2018-029 | 04 SOUTHEAST | 514829 | PINE ST4 | 138 | 12.9391 | 12.9414 | 0.0023
GEN-2018-029 | 04 SOUTHEAST | 514830 | FITZGRD4 | 138 | 9.6095 | 9.6105 | 0.001
GEN-2018-029 | 04 SOUTHEAST | 514831 | WATRLOO4 | 138 | 15.2584 | 15.263 | 0.0046
GEN-2018-029 | 04 SOUTHEAST | 514832 | EASTERN4 | 138 | 25.2531 | 25.2763 | 0.0232
GEN-2018-029 | 04 SOUTHEAST | 514833 | DANFRTH4 | 138 | 27.4413 | 27.4637 | 0.0224
GEN-2018-029 | 04 SOUTHEAST | 514835 | MEMRIAL4 | 138 | 37.7559 | 37.8167 | 0.0608
GEN-2018-029 | 04 SOUTHEAST | 514837 | TENESTP4 | 138 | 32.2418 | 32.2826 | 0.0408
GEN-2018-029 | 04 SOUTHEAST | 514839 | BRYANT 4 | 138 | 30.5994 | 30.654 | 0.0546
GEN-2018-029 | 04 SOUTHEAST | 514842 | CHTWOOD4 | 138 | 21.7521 | 21.7964 | 0.0443
GEN-2018-029 | 04 SOUTHEAST | 514850 | SKYLINE4 | 138 | 33.9226 | 33.9632 | 0.0406
GEN-2018-029 | 04 SOUTHEAST | 514875 | OUMED 4 | 138 | 23.1182 | 23.1465 | 0.0283
GEN-2018-029 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 46.3602 | 46.3893 | 0.0291
GEN-2018-029 | 04 SOUTHEAST | 514884 | DUNJEE 4 | 138 | 22.029 | 22.0999 | 0.0709
GEN-2018-029 | 04 SOUTHEAST | 514906 | JNSKAMO4 | 138 | 21.3476 | 21.39 | 0.0424
GEN-2018-029 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 42.7374 | 42.7907 | 0.0533
GEN-2018-029 | 04 SOUTHEAST | 514923 | LIGHTCK4 | 138 | 25.9875 | 26.0157 | 0.0282
GEN-2018-029 | 04 SOUTHEAST | 514930 | OAKTRET4 | 138 | 21.4624 | 21.4687 | 0.0063
GEN-2018-029 | 04 SOUTHEAST | 514933 | DRAPER 4 | 138 | 41.9819 | 42.0123 | 0.0304
GEN-2018-029 | 04 SOUTHEAST | 514941 | HSL 4 | 138 | 42.9381 | 43.396 | 0.4579
GEN-2018-029 | 04 SOUTHEAST | 514946 | MIDWEST4 | 138 | 31.1217 | 31.1376 | 0.0159
GEN-2018-029 | 04 SOUTHEAST | 514948 | CEDARLN4 | 138 | 24.2039 | 24.2112 | 0.0073
GEN-2018-029 | 04 SOUTHEAST | 514949 | SOONRTP4 | 138 | 22.9967 | 23.0037 | 0.007
GEN-2018-029 | 04 SOUTHEAST | 514953 | HOLLYWD4 | 138 | 25.0134 | 25.0246 | 0.0112
GEN-2018-029 | 04 SOUTHEAST | 514959 | FOSTER 4 | 138 | 26.6816 | 26.7096 | 0.028
GEN-2018-029 | 04 SOUTHEAST | 514961 | GM 4 | 138 | 20.4338 | 20.4434 | 0.0096
GEN-2018-029 | 04 SOUTHEAST | 514963 | TROSPER4 | 138 | 29.3521 | 29.3978 | 0.0457
GEN-2018-029 | 04 SOUTHEAST | 514964 | NE10TH 4 | 138 | 18.9234 | 18.9643 | 0.0409
GEN-2018-029 | 04 SOUTHEAST | 514966 | MIDWAY 4 | 138 | 19.0391 | 19.1054 | 0.0663
GEN-2018-029 | 04 SOUTHEAST | 514973 | RENO 4 | 138 | 29.023 | 29.094 | 0.071
GEN-2018-029 | 04 SOUTHEAST | 514986 | GLENDAL4 | 138 | 14.0393 | 14.0537 | 0.0144
GEN-2018-029 | 04 SOUTHEAST | 514987 | DALE 4 | 138 | 14.5213 | 14.5504 | 0.0291
GEN-2018-029 | 04 SOUTHEAST | 514993 | SE15TH 4 | 138 | 16.0247 | 16.0446 | 0.0199
GEN-2018-029 | 04 SOUTHEAST | 514994 | TINKER54 | 138 | 14.6437 | 14.6578 | 0.0141
GEN-2018-029 | 04 SOUTHEAST | 515003 | BARNES 4 | 138 | 16.8459 | 16.8637 | 0.0178
GEN-2018-029 | 04 SOUTHEAST | 515044 | SEMINOL4 | 138 | 41.6977 | 41.7083 | 0.0106
GEN-2018-029 | 04 SOUTHEAST | 515046 | HAMMTAP4 | 138 | 17.4838 | 17.5326 | 0.0488
GEN-2018-029 | 04 SOUTHEAST | 515047 | WARWICK4 | 138 | 10.6869 | 10.6933 | 0.0064
GEN-2018-029 | 04 SOUTHEAST | 515051 | JACKTWN4 | 138 | 10.1532 | 10.1633 | 0.0101
GEN-2018-029 | 04 SOUTHEAST | 515055 | MAUD 4 | 138 | 21.0083 | 21.0169 | 0.0086
GEN-2018-029 | 04 SOUTHEAST | 515056 | WOLVERN4 | 138 | 8.8094 | 8.8166 | 0.0072
GEN-2018-029 | 04 SOUTHEAST | 515057 | MOBIL 4 | 138 | 8.8872 | 8.8945 | 0.0073
GEN-2018-029 | 04 SOUTHEAST | 515059 | SQUIRCK4 | 138 | 14.6217 | 14.6402 | 0.0185
GEN-2018-029 | 04 SOUTHEAST | 515060 | INGLEWD4 | 138 | 10.7426 | 10.7527 | 0.0101
GEN-2018-029 | 04 SOUTHEAST | 515061 | STGREG 4 | 138 | 9.5412 | 9.5493 | 0.0081
GEN-2018-029 | 04 SOUTHEAST | 515062 | NE45TAP4 | 138 | 9.2344 | 9.2421 | 0.0077
GEN-2018-029 | 04 SOUTHEAST | 515075 | FRSTHIL4 | 138 | 14.5108 | 14.5245 | 0.0137
GEN-2018-029 | 04 SOUTHEAST | 515156 | WASHPRK4 | 138 | 22.23 | 22.2629 | 0.0329
GEN-2018-029 | 04 SOUTHEAST | 515286 | STRLGTP4 | 138 | 14.4563 | 14.4729 | 0.0166
GEN-2018-029 | 04 SOUTHEAST | 515366 | WFROSST4 | 138 | 12.7841 | 12.7981 | 0.014
GEN-2018-029 | 04 SOUTHEAST | 515369 | BELLCOW4 | 138 | 6.8507 | 6.8526 | 0.0019
GEN-2018-029 | 04 SOUTHEAST | 515373 | LBRTYLK4 | 138 | 14.8476 | 14.8515 | 0.0039
GEN-2018-029 | 04 SOUTHEAST | 515377 | CRESENT4 | 138 | 11.1856 | 11.1865 | 0.0009
GEN-2018-029 | 04 SOUTHEAST | 515387 | NEWDOMI4 | 138 | 27.529 | 27.5651 | 0.0361
GEN-2018-029 | 04 SOUTHEAST | 515442 | LINCOLN4 | 138 | 15.5843 | 15.6093 | 0.025
GEN-2018-029 | 04 SOUTHEAST | 515457 | AIRDEPT4 | 138 | 20.8267 | 20.837 | 0.0103
GEN-2018-029 | 04 SOUTHEAST | 515459 | ACORN 4 | 138 | 27.5359 | 27.5992 | 0.0633
GEN-2018-029 | 04 SOUTHEAST | 515461 | RNDBARN4 | 138 | 40.6896 | 40.7379 | 0.0483
GEN-2018-029 | 04 SOUTHEAST | 515465 | LGARBER4 | 138 | 22.0357 | 22.0612 | 0.0255
GEN-2018-029 | 04 SOUTHEAST | 515480 | JONESSB4 | 138 | 30.0078 | 30.1171 | 0.1093
GEN-2018-029 | 04 SOUTHEAST | 515532 | WOLVRNT4 | 138 | 8.8832 | 8.8905 | 0.0073
GEN-2018-029 | 04 SOUTHEAST | 515675 | TRYON 4 | 138 | 9.317 | 9.3192 | 0.0022
GEN-2018-029 | 04 SOUTHEAST | 515806 | TINKER64 | 138 | 14.1926 | 14.2061 | 0.0135
GEN-2018-029 | 04 SOUTHEAST | 515851 | CROSTWN4 | 138 | 26.5033 | 26.5309 | 0.0276
GEN-2018-029 | 04 SOUTHEAST | 515959 | TINKER74 | 138 | 13.7649 | 13.7782 | 0.0133
GEN-2018-029 | 04 SOUTHEAST | 515963 | GATEWAY4 | 138 | 22.0078 | 22.0364 | 0.0286
GEN-2018-029 | 04 SOUTHEAST | 520449 | STERLNG4 | 138 | 11.742 | 11.753 | 0.011
GEN-2018-029 | 04 SOUTHEAST | 520464 | MEEKER 4 | 138 | 9.3017 | 9.3078 | 0.0061
GEN-2018-029 | 04 SOUTHEAST | 520526 | GRDGVTP4 | 138 | 7.2465 | 7.2492 | 0.0027
GEN-2018-029 | 04 SOUTHEAST | 520917 | FRNKLNS4 | 138 | 28.1011 | 28.1134 | 0.0123
GEN-2018-029 | 04 SOUTHEAST | 520951 | HAMMETT4 | 138 | 13.0411 | 13.0684 | 0.0273
GEN-2018-029 | 04 SOUTHEAST | 520994 | MEEKRSW4 | 138 | 8.5423 | 8.5465 | 0.0042
GEN-2018-029 | 04 SOUTHEAST | 521006 | MARSHAL4 | 138 | 8.4813 | 8.4816 | 0.0003
GEN-2018-029 | 04 SOUTHEAST | 521073 | TWNLKSW4 | 138 | 10.4751 | 10.4757 | 0.0006
GEN-2018-029 | 04 SOUTHEAST | 521097 | WREDHIL4 | 138 | 7.4285 | 7.4313 | 0.0028
GEN-2018-029 | 04 SOUTHEAST | 521107 | RSSVILE4 | 138 | 12.7841 | 12.7981 | 0.014
GEN-2018-029 | 04 SOUTHEAST | 587210 | GEN-2016-032 | 138 | 8.1877 | 8.1881 | 0.0004
GEN-2018-029 | 04 SOUTHEAST | 762647 | GEN-2018-029 | 138 | 42.9246 | 43.3825 | 0.4579
GEN-2018-029 | 04 SOUTHEAST | 300834 | 2CARNEY | 69 | 5.0858 | 5.0861 | 0.0003
GEN-2018-029 | 04 SOUTHEAST | 300839 | 2MERIDAN | 69 | 5.3295 | 5.33 | 0.0005
GEN-2018-029 | 04 SOUTHEAST | 300856 | 2LUTHER | 69 | 6.7291 | 6.7301 | 0.001
GEN-2018-029 | 04 SOUTHEAST | 514927 | HSLEAST2 | 69 | 11.7722 | 11.7834 | 0.0112
GEN-2018-029 | 04 SOUTHEAST | 514937 | HSLWEST2 | 69 | 12.4204 | 12.4334 | 0.013
GEN-2018-029 | 04 SOUTHEAST | 514951 | LITTLAX2 | 69 | 3.4829 | 3.4834 | 0.0005
GEN-2018-029 | 04 SOUTHEAST | 514956 | MACOCTP2 | 69 | 3.4366 | 3.4371 | 0.0005
GEN-2018-029 | 04 SOUTHEAST | 514969 | NE30TH 2 | 69 | 9.2764 | 9.2798 | 0.0034
GEN-2018-029 | 04 SOUTHEAST | 514970 | DEEPFKT2 | 69 | 7.9459 | 7.9486 | 0.0027
GEN-2018-029 | 04 SOUTHEAST | 514971 | GRNPAST2 | 69 | 6.0353 | 6.0374 | 0.0021
GEN-2018-029 | 04 SOUTHEAST | 514972 | RENO 2 | 69 | 14.4993 | 14.5065 | 0.0072
GEN-2018-029 | 04 SOUTHEAST | 514974 | DEEPFRK2 | 69 | 6.687 | 6.6889 | 0.0019
GEN-2018-029 | 04 SOUTHEAST | 514979 | 44&SUNL2 | 69 | 12.0085 | 12.0124 | 0.0039
GEN-2018-029 | 04 SOUTHEAST | 514980 | SUNNYLN2 | 69 | 12.3196 | 12.324 | 0.0044
GEN-2018-029 | 04 SOUTHEAST | 514981 | TINKER32 | 69 | 9.3024 | 9.305 | 0.0026
GEN-2018-029 | 04 SOUTHEAST | 514983 | LTLRLKT2 | 69 | 2.913 | 2.9135 | 0.0005
GEN-2018-029 | 04 SOUTHEAST | 514985 | TXSTELA2 | 69 | 4.0973 | 4.0982 | 0.0009
GEN-2018-029 | 04 SOUTHEAST | 514989 | TXPLSTE2 | 69 | 3.1525 | 3.153 | 0.0005
GEN-2018-029 | 04 SOUTHEAST | 515065 | MCLOUD 2 | 69 | 5.087 | 5.0887 | 0.0017
GEN-2018-029 | 04 SOUTHEAST | 515068 | SHAWNEE2 | 69 | 8.3951 | 8.3978 | 0.0027
GEN-2018-029 | 04 SOUTHEAST | 515072 | SINCPAN2 | 69 | 6.0825 | 6.0841 | 0.0016
GEN-2018-029 | 04 SOUTHEAST | 515074 | FRSTHIL2 | 69 | 11.8071 | 11.8111 | 0.004
GEN-2018-029 | 04 SOUTHEAST | 515502 | LITLAXT2 | 69 | 3.4879 | 3.4884 | 0.0005
GEN-2018-029 | 04 SOUTHEAST | 515504 | MCLOUDT2 | 69 | 5.1112 | 5.1129 | 0.0017
GEN-2018-029 | 04 SOUTHEAST | 515516 | TXPLSTP2 | 69 | 3.1565 | 3.157 | 0.0005
GEN-2018-029 | 04 SOUTHEAST | 515642 | SINCPNT2 | 69 | 6.1174 | 6.119 | 0.0016
GEN-2018-048 | 04 SOUTHEAST | 588041 | G16133_765GS | 765 | 6.5805 | 6.5891 | 0.0086
GEN-2018-048 | 04 SOUTHEAST | 588043 | G16133_765MP | 765 | 4.0348 | 4.037 | 0.0022
GEN-2018-048 | 04 SOUTHEAST | 337811 | 8HAPPYVALY% | 500 | 25.7304 | 25.7311 | 0.0007
GEN-2018-048 | 04 SOUTHEAST | 337909 | 8ANO% | 500 | 18.2501 | 18.2518 | 0.0017
GEN-2018-048 | 04 SOUTHEAST | 337922 | 8P.HILL% | 500 | 15.8963 | 15.8971 | 0.0008
GEN-2018-048 | 04 SOUTHEAST | 515305 | FTSMITH8 | 500 | 8.7354 | 8.7399 | 0.0045
GEN-2018-048 | 04 SOUTHEAST | 506945 | CHAMSPR7 | 345 | 10.6353 | 10.6404 | 0.0051
GEN-2018-048 | 04 SOUTHEAST | 506959 | TONTITN7 | 345 | 9.5831 | 9.5866 | 0.0035
GEN-2018-048 | 04 SOUTHEAST | 509745 | CLARKSV7 | 345 | 20.8073 | 20.892 | 0.0847
GEN-2018-048 | 04 SOUTHEAST | 509755 | WEKIWA-7 | 345 | 23.2471 | 23.2689 | 0.0218
GEN-2018-048 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 32.9578 | 33.0851 | 0.1273
GEN-2018-048 | 04 SOUTHEAST | 509807 | ONETA--7 | 345 | 30.4699 | 30.5423 | 0.0724
GEN-2018-048 | 04 SOUTHEAST | 509834 | COGENT 7 | 345 | 30.6026 | 30.7104 | 0.1078
GEN-2018-048 | 04 SOUTHEAST | 509836 | OEC 7 | 345 | 30.1771 | 30.2476 | 0.0705
GEN-2018-048 | 04 SOUTHEAST | 509852 | T.NO.--7 | 345 | 25.0113 | 25.0254 | 0.0141
GEN-2018-048 | 04 SOUTHEAST | 509870 | SAPLPRD7 | 345 | 23.5953 | 23.6381 | 0.0428
GEN-2018-048 | 04 SOUTHEAST | 510380 | DELWARE7 | 345 | 12.1079 | 12.1099 | 0.002
GEN-2018-048 | 04 SOUTHEAST | 510406 | N.E.S.-7 | 345 | 19.7189 | 19.7286 | 0.0097
GEN-2018-048 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 14.7582 | 14.7659 | 0.0077
GEN-2018-048 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 13.6798 | 13.6809 | 0.0011
GEN-2018-048 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 14.4909 | 14.4983 | 0.0074
GEN-2018-048 | 04 SOUTHEAST | 512694 | CLEVLND7 | 345 | 15.6544 | 15.6576 | 0.0032
GEN-2018-048 | 04 SOUTHEAST | 513596 | IGLOOV 7 | 345 | 20.7987 | 20.8023 | 0.0036
GEN-2018-048 | 04 SOUTHEAST | 514803 | SOONER 7 | 345 | 30.1293 | 30.1337 | 0.0044
GEN-2018-048 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 11.1919 | 11.1932 | 0.0013
GEN-2018-048 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 35.304 | 35.3073 | 0.0033
GEN-2018-048 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 24.8743 | 24.8759 | 0.0016
GEN-2018-048 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 37.9057 | 37.909 | 0.0033
GEN-2018-048 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 27.8022 | 27.8065 | 0.0043
GEN-2018-048 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 26.9141 | 26.9184 | 0.0043
GEN-2018-048 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 26.8121 | 26.8166 | 0.0045
GEN-2018-048 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 29.4682 | 29.4803 | 0.0121
GEN-2018-048 | 04 SOUTHEAST | 515224 | MUSKOGE7 | 345 | 27.7615 | 28.1299 | 0.3684
GEN-2018-048 | 04 SOUTHEAST | 515235 | PECANCK7 | 345 | 21.8684 | 22.4382 | 0.5698
GEN-2018-048 | 04 SOUTHEAST | 515302 | FTSMITH7 | 345 | 10.4568 | 10.4652 | 0.0084
GEN-2018-048 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 11.5345 | 11.5494 | 0.0149
GEN-2018-048 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 35.7173 | 35.7199 | 0.0026
GEN-2018-048 | 04 SOUTHEAST | 515576 | RANCHRD7 | 345 | 15.4592 | 15.4597 | 0.0005
GEN-2018-048 | 04 SOUTHEAST | 515894 | THUNDER7 | 345 | 12.1323 | 12.1329 | 0.0006
GEN-2018-048 | 04 SOUTHEAST | 516010 | PINTAIL7 | 345 | 17.9054 | 17.9062 | 0.0008
GEN-2018-048 | 04 SOUTHEAST | 516096 | NORMHLL7 | 345 | 27.8202 | 27.8237 | 0.0035
GEN-2018-048 | 04 SOUTHEAST | 532793 | NEOSHO 7 | 345 | 17.8952 | 17.8962 | 0.001
GEN-2018-048 | 04 SOUTHEAST | 560056 | G15-066T | 345 | 20.1401 | 20.1428 | 0.0027
GEN-2018-048 | 04 SOUTHEAST | 587804 | G16-119-TAP | 345 | 16.7816 | 16.7826 | 0.001
GEN-2018-048 | 04 SOUTHEAST | 588039 | G16133G16146 | 345 | 32.9578 | 33.0851 | 0.1273
GEN-2018-048 | 04 SOUTHEAST | 588040 | G16133_345GS | 345 | 18.0832 | 18.1172 | 0.034
GEN-2018-048 | 04 SOUTHEAST | 588810 | GEN-2017-040 | 345 | 18.1392 | 18.2318 | 0.0926
GEN-2018-048 | 04 SOUTHEAST | 588838 | G17-092-SWYD | 345 | 18.5451 | 18.642 | 0.0969
GEN-2018-048 | 04 SOUTHEAST | 588839 | FIREWHL-TAP | 345 | 18.5451 | 18.642 | 0.0969
GEN-2018-048 | 04 SOUTHEAST | 589300 | GEN-2017-092 | 345 | 15.1577 | 15.2219 | 0.0642
GEN-2018-048 | 04 SOUTHEAST | 760032 | GEN-2017-133 | 345 | 5.6948 | 5.6949 | 0.0001
GEN-2018-048 | 04 SOUTHEAST | 760389 | GEN-2017-140 | 345 | 1.7034 | 1.7038 | 0.0004
GEN-2018-048 | 04 SOUTHEAST | 760393 | G17-140-BUS | 345 | 1.6927 | 1.6931 | 0.0004
GEN-2018-048 | 04 SOUTHEAST | 762592 | GEN-2018-024 | 345 | 18.0039 | 18.0953 | 0.0914
GEN-2018-048 | 04 SOUTHEAST | 762823 | GEN-2018-048 | 345 | 15.6881 | 16.2633 | 0.5752
GEN-2018-048 | 04 SOUTHEAST | 337912 | 5ANO% | 161 | 17.9076 | 17.9081 | 0.0005
GEN-2018-048 | 04 SOUTHEAST | 504202 | SILOAMSP 5 | 161 | 20.3685 | 20.3717 | 0.0032
GEN-2018-048 | 04 SOUTHEAST | 506944 | CHAMSPR5 | 161 | 24.3738 | 24.3805 | 0.0067
GEN-2018-048 | 04 SOUTHEAST | 506948 | SILOAM 5 | 161 | 22.8006 | 22.8043 | 0.0037
GEN-2018-048 | 04 SOUTHEAST | 506957 | TONTITN5 | 161 | 23.8185 | 23.8242 | 0.0057
GEN-2018-048 | 04 SOUTHEAST | 506992 | WEDINGTON | 161 | 16.9516 | 16.9547 | 0.0031
GEN-2018-048 | 04 SOUTHEAST | 515184 | MSKPORT5 | 161 | 13.2129 | 13.2454 | 0.0325
GEN-2018-048 | 04 SOUTHEAST | 515222 | MUSKOGE5 | 161 | 16.7623 | 16.8127 | 0.0504
GEN-2018-048 | 04 SOUTHEAST | 515228 | 5TRIBES5 | 161 | 16.0062 | 16.0797 | 0.0735
GEN-2018-048 | 04 SOUTHEAST | 515230 | AGENCY 5 | 161 | 14.5763 | 14.6312 | 0.0549
GEN-2018-048 | 04 SOUTHEAST | 515232 | MSKPTAP5 | 161 | 16.0447 | 16.0927 | 0.048
GEN-2018-048 | 04 SOUTHEAST | 515234 | PECANCK5 | 161 | 21.5363 | 21.6982 | 0.1619
GEN-2018-048 | 04 SOUTHEAST | 515250 | HANCOK-5 | 161 | 14.6891 | 14.7431 | 0.054
GEN-2018-048 | 04 SOUTHEAST | 515251 | EUCLID 5 | 161 | 14.2878 | 14.3335 | 0.0457
GEN-2018-048 | 04 SOUTHEAST | 515299 | BEVYTAP5 | 161 | 21.2187 | 21.2272 | 0.0085
GEN-2018-048 | 04 SOUTHEAST | 515300 | FTSMTHE5 | 161 | 24.0052 | 24.0164 | 0.0112
GEN-2018-048 | 04 SOUTHEAST | 515301 | FTSMTHW5 | 161 | 23.8684 | 23.8796 | 0.0112
GEN-2018-048 | 04 SOUTHEAST | 515306 | ARKOMA 5 | 161 | 16.7817 | 16.7871 | 0.0054
GEN-2018-048 | 04 SOUTHEAST | 515308 | 3RDST 5 | 161 | 16.1601 | 16.1651 | 0.005
GEN-2018-048 | 04 SOUTHEAST | 515310 | QUANXTP5 | 161 | 18.4304 | 18.4369 | 0.0065
GEN-2018-048 | 04 SOUTHEAST | 515345 | COLONY 5 | 161 | 19.0811 | 19.0881 | 0.007
GEN-2018-048 | 04 SOUTHEAST | 515640 | THRERVR5 | 161 | 15.2457 | 15.2925 | 0.0468
GEN-2018-048 | 04 SOUTHEAST | 589140 | GEN-2017-076 | 161 | 21.6827 | 21.688 | 0.0053
GEN-2018-048 | 04 SOUTHEAST | 505610 | KEYSTON4 | 138 | 23.3607 | 23.3685 | 0.0078
GEN-2018-048 | 04 SOUTHEAST | 509721 | BA.NO-S4 | 138 | 12.6595 | 12.6629 | 0.0034
GEN-2018-048 | 04 SOUTHEAST | 509727 | OAKS W4 | 138 | 16.188 | 16.1935 | 0.0055
GEN-2018-048 | 04 SOUTHEAST | 509732 | ORU W4 | 138 | 24.1716 | 24.1853 | 0.0137
GEN-2018-048 | 04 SOUTHEAST | 509737 | BA101 S4 | 138 | 18.6514 | 18.6607 | 0.0093
GEN-2018-048 | 04 SOUTHEAST | 509738 | ORU E4 | 138 | 25.5631 | 25.5786 | 0.0155
GEN-2018-048 | 04 SOUTHEAST | 509747 | BA81---4 | 138 | 18.6197 | 18.6282 | 0.0085
GEN-2018-048 | 04 SOUTHEAST | 509748 | DENVR-W4 | 138 | 9.9138 | 9.9157 | 0.0019
GEN-2018-048 | 04 SOUTHEAST | 509753 | 116JENK4 | 138 | 44.2273 | 44.2743 | 0.047
GEN-2018-048 | 04 SOUTHEAST | 509757 | WEKIWA-4 | 138 | 33.5412 | 33.5581 | 0.0169
GEN-2018-048 | 04 SOUTHEAST | 509759 | JENKS--4 | 138 | 26.3725 | 26.3889 | 0.0164
GEN-2018-048 | 04 SOUTHEAST | 509767 | B111---4 | 138 | 16.5178 | 16.5248 | 0.007
GEN-2018-048 | 04 SOUTHEAST | 509768 | BA101ST4 | 138 | 19.3503 | 19.3603 | 0.01
GEN-2018-048 | 04 SOUTHEAST | 509769 | BA101-N4 | 138 | 20.2041 | 20.2145 | 0.0104
GEN-2018-048 | 04 SOUTHEAST | 509773 | RSS T1 4 | 138 | 52.3609 | 52.4342 | 0.0733
GEN-2018-048 | 04 SOUTHEAST | 509775 | 136YALE4 | 138 | 24.3966 | 24.4111 | 0.0145
GEN-2018-048 | 04 SOUTHEAST | 509783 | R.S.S.-4 | 138 | 63.1167 | 63.2128 | 0.0961
GEN-2018-048 | 04 SOUTHEAST | 509785 | BANNTAP4 | 138 | 19.2643 | 19.273 | 0.0087
GEN-2018-048 | 04 SOUTHEAST | 509786 | BA.N-ST4 | 138 | 24.6261 | 24.6388 | 0.0127
GEN-2018-048 | 04 SOUTHEAST | 509788 | T.P.S.-4 | 138 | 40.7247 | 40.7573 | 0.0326
GEN-2018-048 | 04 SOUTHEAST | 509804 | LLANETP4 | 138 | 28.2552 | 28.2643 | 0.0091
GEN-2018-048 | 04 SOUTHEAST | 509806 | ONETA--4 | 138 | 50.2678 | 50.3382 | 0.0704
GEN-2018-048 | 04 SOUTHEAST | 509812 | SHEFFD-4 | 138 | 26.7902 | 26.8036 | 0.0134
GEN-2018-048 | 04 SOUTHEAST | 509813 | SHILETP4 | 138 | 28.8859 | 28.9052 | 0.0193
GEN-2018-048 | 04 SOUTHEAST | 509814 | 52DELWT4 | 138 | 23.6888 | 23.7014 | 0.0126
GEN-2018-048 | 04 SOUTHEAST | 509815 | S.S.---4 | 138 | 29.6383 | 29.6551 | 0.0168
GEN-2018-048 | 04 SOUTHEAST | 509823 | WED-TAP4 | 138 | 19.8245 | 19.8315 | 0.007
GEN-2018-048 | 04 SOUTHEAST | 509845 | KIMCLRK4 | 138 | 23.1519 | 23.165 | 0.0131
GEN-2018-048 | 04 SOUTHEAST | 509846 | OAKS--E4 | 138 | 14.15 | 14.1542 | 0.0042
GEN-2018-048 | 04 SOUTHEAST | 509848 | OAKSWTP4 | 138 | 25.8541 | 25.8679 | 0.0138
GEN-2018-048 | 04 SOUTHEAST | 509849 | ORU ETP4 | 138 | 35.3282 | 35.3576 | 0.0294
GEN-2018-048 | 04 SOUTHEAST | 509850 | OAKSETP4 | 138 | 27.9765 | 27.9926 | 0.0161
GEN-2018-048 | 04 SOUTHEAST | 509851 | P&P WTP4 | 138 | 15.8325 | 15.8354 | 0.0029
GEN-2018-048 | 04 SOUTHEAST | 509853 | ORU-WTP4 | 138 | 30.9308 | 30.953 | 0.0222
GEN-2018-048 | 04 SOUTHEAST | 509858 | WARNTAP4 | 138 | 29.7998 | 29.8204 | 0.0206
GEN-2018-048 | 04 SOUTHEAST | 509859 | S HILLW4 | 138 | 17.3934 | 17.4002 | 0.0068
GEN-2018-048 | 04 SOUTHEAST | 509869 | 121LYNN4 | 138 | 18.2796 | 18.288 | 0.0084
GEN-2018-048 | 04 SOUTHEAST | 509871 | SAPLPRD4 | 138 | 34.2682 | 34.295 | 0.0268
GEN-2018-048 | 04 SOUTHEAST | 509875 | RSS T2 4 | 138 | 53.2938 | 53.369 | 0.0752
GEN-2018-048 | 04 SOUTHEAST | 509888 | 72ELWOD4 | 138 | 24.2321 | 24.2444 | 0.0123
GEN-2018-048 | 04 SOUTHEAST | 509889 | E_121ST4 | 138 | 16.3524 | 16.3588 | 0.0064
GEN-2018-048 | 04 SOUTHEAST | 509891 | BA_71ST4 | 138 | 23.928 | 23.9429 | 0.0149
GEN-2018-048 | 04 SOUTHEAST | 509895 | T.NO.2-4 | 138 | 36.8913 | 36.9018 | 0.0105
GEN-2018-048 | 04 SOUTHEAST | 509896 | DENV_WTAP4 | 138 | 28.8978 | 28.9139 | 0.0161
GEN-2018-048 | 04 SOUTHEAST | 510379 | DELWARE4 | 138 | 11.29 | 11.2906 | 0.0006
GEN-2018-048 | 04 SOUTHEAST | 510898 | OKMULGE4 | 138 | 11.8568 | 11.8595 | 0.0027
GEN-2018-048 | 04 SOUTHEAST | 510904 | EXP_OKM4 | 138 | 10.2974 | 10.2995 | 0.0021
GEN-2018-048 | 04 SOUTHEAST | 510923 | EC.HEN-4 | 138 | 8.9962 | 8.9975 | 0.0013
GEN-2018-048 | 04 SOUTHEAST | 510931 | KELCO 4 | 138 | 10.5982 | 10.6002 | 0.002
GEN-2018-048 | 04 SOUTHEAST | 510946 | C-RIVER4 | 138 | 14.0253 | 14.0325 | 0.0072
GEN-2018-048 | 04 SOUTHEAST | 510951 | TALAWANDA 4 | 138 | 10.1189 | 10.1215 | 0.0026
GEN-2018-048 | 04 SOUTHEAST | 512726 | SILVCTYGR4 | 138 | 16.3892 | 16.3919 | 0.0027
GEN-2018-048 | 04 SOUTHEAST | 514802 | SOONER 4 | 138 | 33.4333 | 33.4343 | 0.001
GEN-2018-048 | 04 SOUTHEAST | 514827 | CTNWOOD4 | 138 | 19.0908 | 19.0914 | 0.0006
GEN-2018-048 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 46.3869 | 46.3893 | 0.0024
GEN-2018-048 | 04 SOUTHEAST | 514906 | JNSKAMO4 | 138 | 21.3891 | 21.39 | 0.0009
GEN-2018-048 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 42.7872 | 42.7907 | 0.0035
GEN-2018-048 | 04 SOUTHEAST | 514933 | DRAPER 4 | 138 | 42.0087 | 42.0123 | 0.0036
GEN-2018-048 | 04 SOUTHEAST | 515035 | BRISTOW4 | 138 | 10.5798 | 10.583 | 0.0032
GEN-2018-048 | 04 SOUTHEAST | 515044 | SEMINOL4 | 138 | 41.7026 | 41.7083 | 0.0057
GEN-2018-048 | 04 SOUTHEAST | 515048 | KEYWEST4 | 138 | 6.1037 | 6.1044 | 0.0007
GEN-2018-048 | 04 SOUTHEAST | 515055 | MAUD 4 | 138 | 21.0154 | 21.0169 | 0.0015
GEN-2018-048 | 04 SOUTHEAST | 515100 | PAOLI- 4 | 138 | 10.8314 | 10.8317 | 0.0003
GEN-2018-048 | 04 SOUTHEAST | 515233 | PECANCK4 | 138 | 9.9766 | 10.0007 | 0.0241
GEN-2018-048 | 04 SOUTHEAST | 515242 | BLUEBEL4 | 138 | 17.7271 | 17.7345 | 0.0074
GEN-2018-048 | 04 SOUTHEAST | 515247 | BEELINE4 | 138 | 22.9529 | 22.966 | 0.0131
GEN-2018-048 | 04 SOUTHEAST | 515248 | EXPLGLN4 | 138 | 24.8622 | 24.8775 | 0.0153
GEN-2018-048 | 04 SOUTHEAST | 515249 | BEGGS 4 | 138 | 5.7846 | 5.7872 | 0.0026
GEN-2018-048 | 04 SOUTHEAST | 515417 | GRNWOOD4 | 138 | 8.8598 | 8.8608 | 0.001
GEN-2018-048 | 04 SOUTHEAST | 515461 | RNDBARN4 | 138 | 40.7348 | 40.7379 | 0.0031
GEN-2018-048 | 04 SOUTHEAST | 515465 | LGARBER4 | 138 | 22.0604 | 22.0612 | 0.0008
GEN-2018-048 | 04 SOUTHEAST | 515473 | EXPGLNT4 | 138 | 25.3114 | 25.3273 | 0.0159
GEN-2018-048 | 04 SOUTHEAST | 515531 | VANOSTP4 | 138 | 13.8879 | 13.8884 | 0.0005
GEN-2018-048 | 04 SOUTHEAST | 515977 | LKKONWA4 | 138 | 40.7729 | 40.7783 | 0.0054
GEN-2018-048 | 04 SOUTHEAST | 560389 | GEN-2010-055 | 138 | 33.5412 | 33.5581 | 0.0169
GEN-2018-048 | 04 SOUTHEAST | 515034 | BRISTOW2 | 69 | 6.1295 | 6.13 | 0.0005
GEN-2018-048 | 04 SOUTHEAST | 515201 | CHECOTA2 | 69 | 3.5078 | 3.5088 | 0.001
GEN-2018-048 | 04 SOUTHEAST | 515202 | WELLS 2 | 69 | 3.3653 | 3.3661 | 0.0008
GEN-2018-048 | 04 SOUTHEAST | 515216 | HONORHT2 | 69 | 13.1911 | 13.2088 | 0.0177
GEN-2018-048 | 04 SOUTHEAST | 515217 | TENYSON2 | 69 | 12.2834 | 12.2994 | 0.016
GEN-2018-048 | 04 SOUTHEAST | 515227 | 5TRIBES2 | 69 | 13.1413 | 13.1599 | 0.0186
GEN-2018-048 | 04 SOUTHEAST | 515229 | AGENCY 2 | 69 | 13.4991 | 13.5175 | 0.0184
GEN-2018-048 | 04 SOUTHEAST | 515239 | BIXBY 2 | 69 | 6.0104 | 6.0114 | 0.001
GEN-2018-048 | 04 SOUTHEAST | 515240 | JAMESVL2 | 69 | 4.5451 | 4.5463 | 0.0012
GEN-2018-050 | 04 SOUTHEAST | 337368 | 8MT_OLIVE% | 500 | 12.0746 | 12.0746 | 0
GEN-2018-050 | 04 SOUTHEAST | 337413 | 8STERLING2% | 500 | 20.0692 | 20.0692 | 0
GEN-2018-050 | 04 SOUTHEAST | 337420 | 8STERLING% | 500 | 20.0692 | 20.0692 | 0
GEN-2018-050 | 04 SOUTHEAST | 337427 | 8PERRYVILLE% | 500 | 19.7589 | 19.7589 | 0
GEN-2018-050 | 04 SOUTHEAST | 337515 | 8MCNEIL% | 500 | 14.5174 | 14.5174 | 0
GEN-2018-050 | 04 SOUTHEAST | 337561 | 8EL DORADO% | 500 | 27.783 | 27.783 | 0
GEN-2018-050 | 04 SOUTHEAST | 337643 | 8SHERIDAN% | 500 | 27.987 | 27.987 | 0
GEN-2018-050 | 04 SOUTHEAST | 337651 | 8WHT BLUFF% | 500 | 27.817 | 27.817 | 0
GEN-2018-050 | 04 SOUTHEAST | 337754 | 8ETTA% | 500 | 19.0609 | 19.0609 | 0
GEN-2018-050 | 04 SOUTHEAST | 337763 | 8MAGNETCOVE% | 500 | 22.5798 | 22.5798 | 0
GEN-2018-050 | 04 SOUTHEAST | 337808 | 8MABELVALE% | 500 | 27.678 | 27.678 | 0
GEN-2018-050 | 04 SOUTHEAST | 338440 | 8PANDA% | 500 | 27.7163 | 27.7163 | 0
GEN-2018-050 | 04 SOUTHEAST | 509366 | LAYFLD8 | 500 | 10.4585 | 10.4585 | 0
GEN-2018-050 | 04 SOUTHEAST | 5917 | SPPMAINBUS | 345 | 21.3538 | 21.3538 | 0
GEN-2018-050 | 04 SOUTHEAST | 5918 | DCEAST | 345 | 4.511 | 4.511 | 0
GEN-2018-050 | 04 SOUTHEAST | 5919 | WELSHDC1 | 345 | 21.3538 | 21.3538 | 0
GEN-2018-050 | 04 SOUTHEAST | 5921 | SPP-CAP1 | 345 | 21.3538 | 21.3538 | 0
GEN-2018-050 | 04 SOUTHEAST | 5922 | SPP-CAP2 | 345 | 21.3538 | 21.3538 | 0
GEN-2018-050 | 04 SOUTHEAST | 5923 | SPP-CAP3 | 345 | 21.3538 | 21.3538 | 0
GEN-2018-050 | 04 SOUTHEAST | 5924 | SPP-REAC1 | 345 | 21.3538 | 21.3538 | 0
GEN-2018-050 | 04 SOUTHEAST | 337376 | 7SAREPTA% | 345 | 10.0887 | 10.0887 | 0
GEN-2018-050 | 04 SOUTHEAST | 337562 | 7EL DORADO | 345 | 14.2485 | 14.2485 | 0
GEN-2018-050 | 04 SOUTHEAST | 500250 | DOLHILL7 | 345 | 12.6464 | 12.6464 | 0
GEN-2018-050 | 04 SOUTHEAST | 507455 | TURK 7 | 345 | 9.405 | 9.405 | 0
GEN-2018-050 | 04 SOUTHEAST | 507760 | SW SHV 7 | 345 | 16.1717 | 16.1717 | 0
GEN-2018-050 | 04 SOUTHEAST | 508072 | NWTXARK7 | 345 | 13.7572 | 13.7572 | 0
GEN-2018-050 | 04 SOUTHEAST | 508298 | LYDIA 7 | 345 | 13.0796 | 13.0796 | 0
GEN-2018-050 | 04 SOUTHEAST | 508359 | WELSH 7 | 345 | 21.3538 | 21.3538 | 0
GEN-2018-050 | 04 SOUTHEAST | 508563 | PIRKEY 7 | 345 | 17.7687 | 17.7687 | 0
GEN-2018-050 | 04 SOUTHEAST | 508572 | LEBROCK7 | 345 | 16.5563 | 16.5563 | 0
GEN-2018-050 | 04 SOUTHEAST | 508585 | TENRUSK7 | 345 | 8.0728 | 8.0728 | 0
GEN-2018-050 | 04 SOUTHEAST | 508809 | LONGWD 7 | 345 | 15.9321 | 15.9322 | 0.0001
GEN-2018-050 | 04 SOUTHEAST | 508832 | DIANA 7 | 345 | 19.6098 | 19.6098 | 0
GEN-2018-050 | 04 SOUTHEAST | 508841 | WILKES 7 | 345 | 15.696 | 15.696 | 0
GEN-2018-050 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 14.7659 | 14.7659 | 0
GEN-2018-050 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 13.6809 | 13.6809 | 0
GEN-2018-050 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 11.4594 | 11.4594 | 0
GEN-2018-050 | 04 SOUTHEAST | 762845 | GEN-2018-050 | 345 | 15.5901 | 15.5901 | 0
GEN-2018-050 | 04 SOUTHEAST | 337369 | 6MT_OLIVE% | 230 | 14.3559 | 14.3559 | 0
GEN-2018-050 | 04 SOUTHEAST | 500140 | CARROLL6 | 230 | 13.8507 | 13.8507 | 0
GEN-2018-050 | 04 SOUTHEAST | 500255 | REDBAYOU_6 | 230 | 10.7664 | 10.7664 | 0
GEN-2018-050 | 04 SOUTHEAST | 500260 | DOLHILL6 | 230 | 15.4618 | 15.4618 | 0
GEN-2018-050 | 04 SOUTHEAST | 500465 | 6LAYFLD | 230 | 16.1197 | 16.1197 | 0
GEN-2018-050 | 04 SOUTHEAST | 500525 | MANCOMP 6 | 230 | 8.7619 | 8.7619 | 0
GEN-2018-050 | 04 SOUTHEAST | 500150 | CARROLL4 | 138 | 13.4967 | 13.4967 | 0
GEN-2018-050 | 04 SOUTHEAST | 500430 | IPAPER 4 | 138 | 5.7076 | 5.7076 | 0
GEN-2018-050 | 04 SOUTHEAST | 507431 | PATTERS4 | 138 | 13.7109 | 13.7109 | 0
GEN-2018-050 | 04 SOUTHEAST | 507454 | TURK 4 | 138 | 25.11 | 25.11 | 0
GEN-2018-050 | 04 SOUTHEAST | 507711 | ARSHILL4 | 138 | 26.0168 | 26.0168 | 0
GEN-2018-050 | 04 SOUTHEAST | 507727 | FLOURNY4 | 138 | 17.3052 | 17.3052 | 0
GEN-2018-050 | 04 SOUTHEAST | 507731 | FTHUMBG4 | 138 | 20.1511 | 20.1511 | 0
GEN-2018-050 | 04 SOUTHEAST | 507732 | GENMOTR4 | 138 | 18.5482 | 18.5483 | 0.0001
GEN-2018-050 | 04 SOUTHEAST | 507735 | HARTSIS4 | 138 | 16.9918 | 16.9918 | 0
GEN-2018-050 | 04 SOUTHEAST | 507738 | LINWOOD4 | 138 | 23.35 | 23.35 | 0
GEN-2018-050 | 04 SOUTHEAST | 507742 | MCWILLI4 | 138 | 22.0863 | 22.0863 | 0
GEN-2018-050 | 04 SOUTHEAST | 507746 | PIERMNT4 | 138 | 17.0324 | 17.0324 | 0
GEN-2018-050 | 04 SOUTHEAST | 507748 | POWELL 4 | 138 | 20.2845 | 20.2845 | 0
GEN-2018-050 | 04 SOUTHEAST | 507749 | RAINES 4 | 138 | 16.898 | 16.898 | 0
GEN-2018-050 | 04 SOUTHEAST | 507755 | S SHV 4 | 138 | 24.1819 | 24.182 | 0.0001
GEN-2018-050 | 04 SOUTHEAST | 507757 | SPRIDGE4 | 138 | 11.758 | 11.758 | 0
GEN-2018-050 | 04 SOUTHEAST | 507759 | SW SHV 4 | 138 | 32.3569 | 32.3569 | 0
GEN-2018-050 | 04 SOUTHEAST | 507763 | TRICHEL4 | 138 | 16.8905 | 16.8905 | 0
GEN-2018-050 | 04 SOUTHEAST | 507765 | WALLAKE4 | 138 | 11.2263 | 11.2263 | 0
GEN-2018-050 | 04 SOUTHEAST | 507767 | WESTELC4 | 138 | 21.4418 | 21.4418 | 0
GEN-2018-050 | 04 SOUTHEAST | 507771 | CEDARGR4 | 138 | 23.2245 | 23.2245 | 0
GEN-2018-050 | 04 SOUTHEAST | 507774 | NORAM 4 | 138 | 17.6484 | 17.6484 | 0
GEN-2018-050 | 04 SOUTHEAST | 507782 | PROBSON4 | 138 | 9.0382 | 9.0382 | 0
GEN-2018-050 | 04 SOUTHEAST | 507789 | STLGENS4 | 138 | 25.6169 | 25.6169 | 0
GEN-2018-050 | 04 SOUTHEAST | 507793 | LEASIDE 4 | 138 | 23.2956 | 23.2956 | 0
GEN-2018-050 | 04 SOUTHEAST | 508049 | NASH 4 | 138 | 20.3557 | 20.3557 | 0
GEN-2018-050 | 04 SOUTHEAST | 508050 | ANDRSNC4 | 138 | 7.9719 | 7.9719 | 0
GEN-2018-050 | 04 SOUTHEAST | 508056 | BRYANML4 | 138 | 7.4708 | 7.4708 | 0
GEN-2018-050 | 04 SOUTHEAST | 508059 | IPC T 4 | 138 | 8.4646 | 8.4646 | 0
GEN-2018-050 | 04 SOUTHEAST | 508064 | MUNZCTY4 | 138 | 7.584 | 7.584 | 0
GEN-2018-050 | 04 SOUTHEAST | 508070 | NWT-BNT4 | 138 | 25.0419 | 25.0419 | 0
GEN-2018-050 | 04 SOUTHEAST | 508071 | NWTXARK4 | 138 | 26.0698 | 26.0698 | 0
GEN-2018-050 | 04 SOUTHEAST | 508080 | SUGARHL4 | 138 | 12.6068 | 12.6068 | 0
GEN-2018-050 | 04 SOUTHEAST | 508090 | WATLANT4 | 138 | 7.8238 | 7.8238 | 0
GEN-2018-050 | 04 SOUTHEAST | 508106 | CASSTP4 | 138 | 7.8007 | 7.8007 | 0
GEN-2018-050 | 04 SOUTHEAST | 508286 | CAMPCOR4 | 138 | 8.5692 | 8.5692 | 0
GEN-2018-050 | 04 SOUTHEAST | 508297 | LSSOUTH4 | 138 | 18.1148 | 18.1148 | 0
GEN-2018-050 | 04 SOUTHEAST | 508310 | PETTY 4 | 138 | 8.3807 | 8.3807 | 0
GEN-2018-050 | 04 SOUTHEAST | 508313 | PITTSB_4 | 138 | 9.3651 | 9.3651 | 0
GEN-2018-050 | 04 SOUTHEAST | 508337 | CHAPELH4 | 138 | 7.8525 | 7.8525 | 0
GEN-2018-050 | 04 SOUTHEAST | 508351 | PERDUE 4 | 138 | 11.0247 | 11.0247 | 0
GEN-2018-050 | 04 SOUTHEAST | 508355 | WELSHRE4 | 138 | 7.8281 | 7.8281 | 0
GEN-2018-050 | 04 SOUTHEAST | 508368 | SCROGNSSW4 | 138 | 6.0765 | 6.0765 | 0
GEN-2018-050 | 04 SOUTHEAST | 508369 | EXXONM 4 | 138 | 6.942 | 6.942 | 0
GEN-2018-050 | 04 SOUTHEAST | 508552 | LLAMOND4 | 138 | 7.3393 | 7.3393 | 0
GEN-2018-050 | 04 SOUTHEAST | 508557 | MARSHL-4 | 138 | 17.3359 | 17.3359 | 0
GEN-2018-050 | 04 SOUTHEAST | 508560 | NEWGLAD4 | 138 | 9.8845 | 9.8845 | 0
GEN-2018-050 | 04 SOUTHEAST | 508562 | PIRKEY 4 | 138 | 42.794 | 42.794 | 0
GEN-2018-050 | 04 SOUTHEAST | 508564 | PLILER 4 | 138 | 12.7067 | 12.7067 | 0
GEN-2018-050 | 04 SOUTHEAST | 508566 | SABMINT4 | 138 | 34.974 | 34.974 | 0
GEN-2018-050 | 04 SOUTHEAST | 508567 | SCOTTSV4 | 138 | 12.5656 | 12.5656 | 0
GEN-2018-050 | 04 SOUTHEAST | 508569 | SEMRSHL4 | 138 | 13.9368 | 13.9368 | 0
GEN-2018-050 | 04 SOUTHEAST | 508571 | SPRHILL4 | 138 | 8.6597 | 8.6597 | 0
GEN-2018-050 | 04 SOUTHEAST | 508577 | SABINEM4 | 138 | 23.1228 | 23.1228 | 0
GEN-2018-050 | 04 SOUTHEAST | 508595 | HALLSVLS4 | 138 | 19.4604 | 19.4604 | 0
GEN-2018-050 | 04 SOUTHEAST | 508806 | LIEBERM4 | 138 | 17.3733 | 17.3733 | 0
GEN-2018-050 | 04 SOUTHEAST | 508807 | LINTNRD4 | 138 | 9.2785 | 9.2785 | 0
GEN-2018-050 | 04 SOUTHEAST | 508808 | LONGWD 4 | 138 | 25.2497 | 25.2497 | 0
GEN-2018-050 | 04 SOUTHEAST | 508811 | NBENTON4 | 138 | 9.6016 | 9.6016 | 0
GEN-2018-050 | 04 SOUTHEAST | 508816 | OAKPH 4 | 138 | 19.8974 | 19.8974 | 0
GEN-2018-050 | 04 SOUTHEAST | 508827 | NGPL 4 | 138 | 10.4979 | 10.4979 | 0
GEN-2018-050 | 04 SOUTHEAST | 508831 | DIANA 4 | 138 | 29.69 | 29.69 | 0
GEN-2018-050 | 04 SOUTHEAST | 508833 | IPCJEFF4 | 138 | 12.6872 | 12.6872 | 0
GEN-2018-050 | 04 SOUTHEAST | 508835 | JEFFRSN4 | 138 | 14.0065 | 14.0065 | 0
GEN-2018-050 | 04 SOUTHEAST | 508837 | NGPLTAP4 | 138 | 13.9003 | 13.9003 | 0
GEN-2018-050 | 04 SOUTHEAST | 508840 | WILKES 4 | 138 | 31.2995 | 31.2995 | 0
GEN-2018-050 | 04 SOUTHEAST | 509050 | KEATCHI4 | 138 | 8.2552 | 8.2552 | 0
GEN-2018-050 | 04 SOUTHEAST | 509052 | STONWAL4 | 138 | 10.8199 | 10.8199 | 0
GEN-2018-050 | 04 SOUTHEAST | 509083 | ROKHILL4 | 138 | 11.8759 | 11.8759 | 0
GEN-2018-050 | 04 SOUTHEAST | 509092 | EASTON 4 | 138 | 25.2517 | 25.2517 | 0
GEN-2018-050 | 04 SOUTHEAST | 509103 | WLNTSPRINGS4 | 138 | 9.4096 | 9.4096 | 0
GEN-2018-050 | 04 SOUTHEAST | 509603 | BIGSAND4 | 138 | 7.4666 | 7.4666 | 0
GEN-2018-050 | 04 SOUTHEAST | 509607 | DIAN 4 | 138 | 11.9798 | 11.9798 | 0
GEN-2018-050 | 04 SOUTHEAST | 509624 | LAKEPIN4 | 138 | 7.73 | 7.73 | 0
GEN-2018-050 | 04 SOUTHEAST | 509628 | NOONDAY4 | 138 | 6.065 | 6.065 | 0
GEN-2018-050 | 04 SOUTHEAST | 509639 | DIANASW4 | 138 | 12.4662 | 12.4662 | 0
GEN-2018-050 | 04 SOUTHEAST | 509664 | CHAPLHL4 | 138 | 7.5984 | 7.5984 | 0
GEN-2018-050 | 04 SOUTHEAST | 509666 | DUGLASV4 | 138 | 5.2992 | 5.2992 | 0
GEN-2018-050 | 04 SOUTHEAST | 510918 | VALIANT4 | 138 | 15.1296 | 15.1296 | 0
GEN-2018-050 | 04 SOUTHEAST | 588400 | GEN-2016-167 | 138 | 10.1861 | 10.1861 | 0
GEN-2018-050 | 04 SOUTHEAST | 588404 | G16-167-TAP | 138 | 10.2907 | 10.2907 | 0
GEN-2018-050 | 04 SOUTHEAST | 303302 | 3MINDEN_LG | 115 | 5.75 | 5.75 | 0
GEN-2018-050 | 04 SOUTHEAST | 337351 | 3SAILES! | 115 | 6.1543 | 6.1543 | 0
GEN-2018-050 | 04 SOUTHEAST | 337360 | 3ADA_LA | 115 | 5.663 | 5.663 | 0
GEN-2018-050 | 04 SOUTHEAST | 337361 | 3MINDEN_LA! | 115 | 7.0086 | 7.0086 | 0
GEN-2018-050 | 04 SOUTHEAST | 337362 | 3LA_ORD_PLNT | 115 | 4.565 | 4.565 | 0
GEN-2018-050 | 04 SOUTHEAST | 337363 | 3SAREPTA! | 115 | 20.2769 | 20.2769 | 0
GEN-2018-050 | 04 SOUTHEAST | 337364 | 3CULLEN | 115 | 8.6475 | 8.6475 | 0
GEN-2018-050 | 04 SOUTHEAST | 337365 | 3SPRINGHILL | 115 | 9.9852 | 9.9852 | 0
GEN-2018-050 | 04 SOUTHEAST | 337366 | 3HAYNESVILLE | 115 | 6.0614 | 6.0614 | 0
GEN-2018-050 | 04 SOUTHEAST | 337367 | 3ARCADIA | 115 | 5.5884 | 5.5884 | 0
GEN-2018-050 | 04 SOUTHEAST | 337415 | 3STERLING% | 115 | 37.0036 | 37.0036 | 0
GEN-2018-050 | 04 SOUTHEAST | 337500 | 3TAYLOR | 115 | 7.3022 | 7.3022 | 0
GEN-2018-050 | 04 SOUTHEAST | 337514 | 3MACEDONA | 115 | 6.5942 | 6.5942 | 0
GEN-2018-050 | 04 SOUTHEAST | 337516 | 3MCNEIL! | 115 | 25.1987 | 25.1987 | 0
GEN-2018-050 | 04 SOUTHEAST | 337524 | 3KERLIN+ | 115 | 7.3754 | 7.3754 | 0
GEN-2018-050 | 04 SOUTHEAST | 337526 | 3EMERSON! | 115 | 6.0114 | 6.0114 | 0
GEN-2018-050 | 04 SOUTHEAST | 337537 | 3SMACKOVER+ | 115 | 9.5328 | 9.5328 | 0
GEN-2018-050 | 04 SOUTHEAST | 337539 | 3EL DORADO! | 115 | 29.344 | 29.344 | 0
GEN-2018-050 | 04 SOUTHEAST | 337540 | 3ELD DONAN | 115 | 15.1667 | 15.1667 | 0
GEN-2018-050 | 04 SOUTHEAST | 337553 | 3ELDORADO.E! | 115 | 13.8666 | 13.8666 | 0
GEN-2018-050 | 04 SOUTHEAST | 337560 | 3ELD QUINN | 115 | 28.5694 | 28.5694 | 0
GEN-2018-050 | 04 SOUTHEAST | 507788 | MINDEN-3 | 115 | 5.6692 | 5.6692 | 0
GEN-2018-050 | 04 SOUTHEAST | 507710 | ARSHILL2 | 69 | 28.6232 | 28.6232 | 0
GEN-2018-050 | 04 SOUTHEAST | 507717 | BROOKS 2 | 69 | 20.8298 | 20.8298 | 0
GEN-2018-050 | 04 SOUTHEAST | 507726 | FLOURNY2 | 69 | 14.3311 | 14.3311 | 0
GEN-2018-050 | 04 SOUTHEAST | 507728 | FORBNGT2 | 69 | 17.837 | 17.837 | 0
GEN-2018-050 | 04 SOUTHEAST | 507730 | FTHUMBG2 | 69 | 18.362 | 18.362 | 0
GEN-2018-050 | 04 SOUTHEAST | 507745 | NMARKET2 | 69 | 16.4584 | 16.4584 | 0
GEN-2018-050 | 04 SOUTHEAST | 507747 | PINESRD2 | 69 | 10.9511 | 10.9511 | 0
GEN-2018-050 | 04 SOUTHEAST | 507754 | S SHV 2 | 69 | 18.6062 | 18.6062 | 0
GEN-2018-050 | 04 SOUTHEAST | 507756 | SHEDRD 2 | 69 | 17.6687 | 17.6687 | 0
GEN-2018-050 | 04 SOUTHEAST | 507758 | SUMMERG2 | 69 | 11.6051 | 11.6051 | 0
GEN-2018-050 | 04 SOUTHEAST | 507762 | T70THST2 | 69 | 12.9899 | 12.9899 | 0
GEN-2018-050 | 04 SOUTHEAST | 507764 | WALLAKE2 | 69 | 8.9046 | 8.9046 | 0
GEN-2018-050 | 04 SOUTHEAST | 507766 | WATERWK2 | 69 | 17.2224 | 17.2224 | 0
GEN-2018-050 | 04 SOUTHEAST | 507770 | WOOLWTP2 | 69 | 11.9696 | 11.9696 | 0
GEN-2018-050 | 04 SOUTHEAST | 507794 | LEASIDE 2 | 69 | 13.4352 | 13.4352 | 0
GEN-2018-050 | 04 SOUTHEAST | 508052 | ATLANTA2 | 69 | 5.5468 | 5.5468 | 0
GEN-2018-050 | 04 SOUTHEAST | 508062 | LINDEN 2 | 69 | 5.8836 | 5.8836 | 0
GEN-2018-050 | 04 SOUTHEAST | 508089 | WATLANT2 | 69 | 8.0629 | 8.0629 | 0
GEN-2018-050 | 04 SOUTHEAST | 508295 | LSREC 2 | 69 | 7.653 | 7.653 | 0
GEN-2018-050 | 04 SOUTHEAST | 508296 | LSSOUTH2 | 69 | 9.7968 | 9.7968 | 0
GEN-2018-050 | 04 SOUTHEAST | 508312 | PITTSB_2 | 69 | 8.6858 | 8.6858 | 0
GEN-2018-050 | 04 SOUTHEAST | 508320 | LONSTAR2 | 69 | 8.2302 | 8.2302 | 0
GEN-2018-050 | 04 SOUTHEAST | 508350 | PERDUE 2 | 69 | 13.5513 | 13.5513 | 0
GEN-2018-050 | 04 SOUTHEAST | 508576 | MARAUTO2 | 69 | 18.154 | 18.154 | 0
GEN-2018-050 | 04 SOUTHEAST | 508801 | BLANCH-2 | 69 | 7.0592 | 7.0592 | 0
GEN-2018-050 | 04 SOUTHEAST | 508802 | BLANCHR2 | 69 | 7.9151 | 7.9151 | 0
GEN-2018-050 | 04 SOUTHEAST | 508805 | LIEBERM2 | 69 | 9.3477 | 9.3477 | 0
GEN-2018-050 | 04 SOUTHEAST | 508810 | NBENTON2 | 69 | 4.1999 | 4.1999 | 0
GEN-2018-050 | 04 SOUTHEAST | 508812 | OILCITY2 | 69 | 7.4954 | 7.4954 | 0
GEN-2018-050 | 04 SOUTHEAST | 508815 | SUPEROR2 | 69 | 6.9413 | 6.9413 | 0
GEN-2018-050 | 04 SOUTHEAST | 508839 | WASKOM 2 | 69 | 4.6521 | 4.6521 | 0
GEN-2018-050 | 04 SOUTHEAST | 509623 | LAKEPIN2 | 69 | 7.6762 | 7.6762 | 0
GEN-2018-050 | 04 SOUTHEAST | 509645 | DUGLASV2 | 69 | 6.6049 | 6.6049 | 0
GEN-2018-050 | 04 SOUTHEAST | 509668 | ROACH 2 | 69 | 6.1907 | 6.1907 | 0
GEN-2018-055 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 14.7442 | 14.7659 | 0.0217
GEN-2018-055 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 13.6676 | 13.6809 | 0.0133
GEN-2018-055 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 14.4774 | 14.4983 | 0.0209
GEN-2018-055 | 04 SOUTHEAST | 511456 | O.K.U.-7 | 345 | 5.5535 | 5.5754 | 0.0219
GEN-2018-055 | 04 SOUTHEAST | 511468 | L.E.S.-7 | 345 | 13.8386 | 14.0954 | 0.2568
GEN-2018-055 | 04 SOUTHEAST | 511565 | OKLAUN HVDC7 | 345 | 5.5376 | 5.5593 | 0.0217
GEN-2018-055 | 04 SOUTHEAST | 511568 | TERRYRD7 | 345 | 9.7785 | 10.2508 | 0.4723
GEN-2018-055 | 04 SOUTHEAST | 511571 | RUSHSPR7 | 345 | 6.0411 | 6.5263 | 0.4852
GEN-2018-055 | 04 SOUTHEAST | 511979 | RSHSPR1_MPT1 | 345 | 5.8996 | 6.0926 | 0.193
GEN-2018-055 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 11.1294 | 11.1932 | 0.0638
GEN-2018-055 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 29.4615 | 29.4803 | 0.0188
GEN-2018-055 | 04 SOUTHEAST | 515136 | SUNNYSD7 | 345 | 11.382 | 11.5368 | 0.1548
GEN-2018-055 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 11.5434 | 11.5494 | 0.006
GEN-2018-055 | 04 SOUTHEAST | 515800 | GRACMNT7 | 345 | 20.0557 | 20.1401 | 0.0844
GEN-2018-055 | 04 SOUTHEAST | 516006 | DMNDSPG7 | 345 | 8.0118 | 8.0416 | 0.0298
GEN-2018-055 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 11.4451 | 11.4594 | 0.0143
GEN-2018-055 | 04 SOUTHEAST | 560088 | G17-075-TAP | 345 | 7.3385 | 7.3701 | 0.0316
GEN-2018-055 | 04 SOUTHEAST | 587740 | GEN-2016-091 | 345 | 11.2947 | 11.3436 | 0.0489
GEN-2018-055 | 04 SOUTHEAST | 587744 | G16-091-TAP | 345 | 16.3326 | 16.4383 | 0.1057
GEN-2018-055 | 04 SOUTHEAST | 587770 | GEN-2016-095 | 345 | 11.7737 | 11.8266 | 0.0529
GEN-2018-055 | 04 SOUTHEAST | 588760 | GEN-2017-033 | 345 | 3.9216 | 3.9326 | 0.011
GEN-2018-055 | 04 SOUTHEAST | 589130 | GEN-2017-075 | 345 | 7.3294 | 7.3609 | 0.0315
GEN-2018-055 | 04 SOUTHEAST | 760830 | GEN-2017-149 | 345 | 4.1466 | 4.1534 | 0.0068
GEN-2018-055 | 04 SOUTHEAST | 760851 | GEN-2017-154 | 345 | 3.7819 | 3.7875 | 0.0056
GEN-2018-055 | 04 SOUTHEAST | 760938 | G17-171-TAP | 345 | 11.0743 | 11.4205 | 0.3462
GEN-2018-055 | 04 SOUTHEAST | 760939 | GEN-2017-171 | 345 | 11.0743 | 11.4205 | 0.3462
GEN-2018-055 | 04 SOUTHEAST | 761859 | GEN-2017-167 | 345 | 6.8004 | 6.855 | 0.0546
GEN-2018-055 | 04 SOUTHEAST | 762216 | G17-151TAP | 345 | 7.9672 | 7.9709 | 0.0037
GEN-2018-055 | 04 SOUTHEAST | 762467 | G18-015-TAP | 345 | 5.1729 | 5.1814 | 0.0085
GEN-2018-055 | 04 SOUTHEAST | 762900 | GEN-2018-055 | 345 | 5.6193 | 6.1072 | 0.4879
GEN-2018-055 | 04 SOUTHEAST | 511423 | FLE TAP4 | 138 | 9.2904 | 9.3002 | 0.0098
GEN-2018-055 | 04 SOUTHEAST | 511437 | COMANC-4 | 138 | 19.1177 | 19.2039 | 0.0862
GEN-2018-055 | 04 SOUTHEAST | 511439 | LWSTAP 4 | 138 | 12.1914 | 12.2268 | 0.0354
GEN-2018-055 | 04 SOUTHEAST | 511467 | L.E.S.-4 | 138 | 26.1059 | 26.2964 | 0.1905
GEN-2018-055 | 04 SOUTHEAST | 511474 | SHERID4 | 138 | 12.9836 | 13.0261 | 0.0425
GEN-2018-055 | 04 SOUTHEAST | 511486 | ELGINJT4 | 138 | 10.5412 | 10.5566 | 0.0154
GEN-2018-055 | 04 SOUTHEAST | 511494 | COMMTAP4 | 138 | 22.7786 | 22.9169 | 0.1383
GEN-2018-055 | 04 SOUTHEAST | 514808 | JOHNCO 4 | 138 | 16.0772 | 16.1174 | 0.0402
GEN-2018-055 | 04 SOUTHEAST | 515120 | RUSSET-4 | 138 | 11.8594 | 11.8801 | 0.0207
GEN-2018-055 | 04 SOUTHEAST | 515122 | SXMLCKT4 | 138 | 11.6114 | 11.6288 | 0.0174
GEN-2018-055 | 04 SOUTHEAST | 515129 | RATLIFF4 | 138 | 6.6525 | 6.6596 | 0.0071
GEN-2018-055 | 04 SOUTHEAST | 515130 | POOLVIL4 | 138 | 8.4017 | 8.4149 | 0.0132
GEN-2018-055 | 04 SOUTHEAST | 515135 | SUNNYSD4 | 138 | 19.3706 | 19.4887 | 0.1181
GEN-2018-055 | 04 SOUTHEAST | 515137 | UNIROY 4 | 138 | 13.1855 | 13.2286 | 0.0431
GEN-2018-055 | 04 SOUTHEAST | 515144 | LONEGRV4 | 138 | 13.8577 | 13.9162 | 0.0585
GEN-2018-055 | 04 SOUTHEAST | 515150 | CANEYCK4 | 138 | 9.5282 | 9.5407 | 0.0125
GEN-2018-055 | 04 SOUTHEAST | 515160 | MRIETA 2 | 138 | 7.7463 | 7.7565 | 0.0102
GEN-2018-055 | 04 SOUTHEAST | 515164 | ROCKYPT4 | 138 | 12.2928 | 12.3265 | 0.0337
GEN-2018-055 | 04 SOUTHEAST | 515172 | SPRNDAL4 | 138 | 12.294 | 12.3233 | 0.0293
GEN-2018-055 | 04 SOUTHEAST | 515372 | ARDWEST4 | 138 | 13.0095 | 13.0503 | 0.0408
GEN-2018-055 | 04 SOUTHEAST | 515415 | CHEEKTP4 | 138 | 12.5117 | 12.5587 | 0.047
GEN-2018-055 | 04 SOUTHEAST | 515561 | CARTRCO4 | 138 | 8.5827 | 8.5964 | 0.0137
GEN-2018-055 | 04 SOUTHEAST | 515563 | ORIGINW4 | 138 | 3.7896 | 3.7923 | 0.0027
GEN-2018-055 | 04 SOUTHEAST | 520560 | HUGOITC4 | 138 | 22.859 | 22.8727 | 0.0137
GEN-2018-055 | 04 SOUTHEAST | 588710 | GEN-2017-027 | 138 | 8.5482 | 8.5618 | 0.0136
GEN-2018-055 | 04 SOUTHEAST | 511466 | L.E.S.-2 | 69 | 16.7467 | 16.7766 | 0.0299
GEN-2018-055 | 04 SOUTHEAST | 515163 | ROCKYPT2 | 69 | 8.2253 | 8.2322 | 0.0069
GEN-2018-004 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 9.8164 | 9.8222 | 0.0058
GEN-2018-004 | 05 SOUTHWEST | 527656 | CROSSROADS 7 | 345 | 11.3308 | 11.3374 | 0.0066
GEN-2018-004 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 11.8194 | 11.8374 | 0.018
GEN-2018-004 | 05 SOUTHWEST | 527965 | KIOWA 7 | 345 | 8.9599 | 8.9716 | 0.0117
GEN-2018-004 | 05 SOUTHWEST | 528027 | RDRUNNER 7 | 345 | 8.7559 | 8.7666 | 0.0107
GEN-2018-004 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 19.2518 | 19.2662 | 0.0144
GEN-2018-004 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 11.5302 | 11.5411 | 0.0109
GEN-2018-004 | 05 SOUTHWEST | 527799 | EDDY_NORTH 6 | 230 | 9.6981 | 9.7068 | 0.0087
GEN-2018-004 | 05 SOUTHWEST | 527865 | CUNNIGHM_N 6 | 230 | 17.9652 | 18.0175 | 0.0523
GEN-2018-004 | 05 SOUTHWEST | 527867 | CUNNIGHM_S 6 | 230 | 17.9652 | 18.0175 | 0.0523
GEN-2018-004 | 05 SOUTHWEST | 527894 | HOBBS_INT 6 | 230 | 19.8841 | 19.9528 | 0.0687
GEN-2018-004 | 05 SOUTHWEST | 527963 | POTASH_JCT 6 | 230 | 7.9127 | 7.9206 | 0.0079
GEN-2018-004 | 05 SOUTHWEST | 528604 | ANDREWS 6 | 230 | 6.3 | 6.3093 | 0.0093
GEN-2018-004 | 05 SOUTHWEST | 527027 | INK_BASIN 3 | 115 | 13.8809 | 13.8907 | 0.0098
GEN-2018-004 | 05 SOUTHWEST | 527284 | RUSSELL 3 | 115 | 9.6192 | 9.6321 | 0.0129
GEN-2018-004 | 05 SOUTHWEST | 527286 | HIGGEAST 3 | 115 | 10.613 | 10.6277 | 0.0147
GEN-2018-004 | 05 SOUTHWEST | 527362 | JOHNSON_DRW3 | 115 | 11.3391 | 11.3644 | 0.0253
GEN-2018-004 | 05 SOUTHWEST | 527363 | HIGG 3 | 115 | 10.7999 | 10.8163 | 0.0164
GEN-2018-004 | 05 SOUTHWEST | 527864 | CUNNINHAM 3 | 115 | 27.9451 | 28.2095 | 0.2644
GEN-2018-004 | 05 SOUTHWEST | 527891 | HOBBS_INT 3 | 115 | 31.7227 | 32.049 | 0.3263
GEN-2018-004 | 05 SOUTHWEST | 527930 | PCA 3 | 115 | 12.5065 | 12.5205 | 0.014
GEN-2018-004 | 05 SOUTHWEST | 528317 | ENRON_TP 3 | 115 | 7.1757 | 7.1875 | 0.0118
GEN-2018-004 | 05 SOUTHWEST | 528318 | ENRON 3 | 115 | 6.2426 | 6.2514 | 0.0088
GEN-2018-004 | 05 SOUTHWEST | 528325 | LE-WAITS 3 | 115 | 9.5119 | 9.5185 | 0.0066
GEN-2018-004 | 05 SOUTHWEST | 528333 | LE-WEST_SUB3 | 115 | 9.5229 | 9.5359 | 0.013
GEN-2018-004 | 05 SOUTHWEST | 528334 | LE-NRTH_INT3 | 115 | 9.4593 | 9.4719 | 0.0126
GEN-2018-004 | 05 SOUTHWEST | 528341 | LE-SANANDRS3 | 115 | 6.7409 | 6.7543 | 0.0134
GEN-2018-004 | 05 SOUTHWEST | 528348 | BUCKEYE_TP 3 | 115 | 8.614 | 8.6368 | 0.0228
GEN-2018-004 | 05 SOUTHWEST | 528353 | MADDOXG23 3 | 115 | 26.5957 | 27.0095 | 0.4138
GEN-2018-004 | 05 SOUTHWEST | 528355 | MADDOX 3 | 115 | 26.5957 | 27.0095 | 0.4138
GEN-2018-004 | 05 SOUTHWEST | 528385 | BUCKEYE 3 | 115 | 7.7493 | 7.7678 | 0.0185
GEN-2018-004 | 05 SOUTHWEST | 528392 | PEARLE 3 | 115 | 6.636 | 6.6536 | 0.0176
GEN-2018-004 | 05 SOUTHWEST | 528394 | QUAHADA 3 | 115 | 8.5478 | 8.5624 | 0.0146
GEN-2018-004 | 05 SOUTHWEST | 528396 | XTO_BIGEDDY3 | 115 | 9.3416 | 9.3532 | 0.0116
GEN-2018-004 | 05 SOUTHWEST | 528399 | LEA_NATIONL3 | 115 | 7.2187 | 7.2304 | 0.0117
GEN-2018-004 | 05 SOUTHWEST | 528404 | SUMMIT_3 | 115 | 5.9797 | 5.9878 | 0.0081
GEN-2018-004 | 05 SOUTHWEST | 528413 | TAYLOR 3 | 115 | 14.9797 | 15.0751 | 0.0954
GEN-2018-004 | 05 SOUTHWEST | 528420 | ZIA 3 | 115 | 6.9396 | 6.9491 | 0.0095
GEN-2018-004 | 05 SOUTHWEST | 528422 | DCP_ZIA TP 3 | 115 | 7.4227 | 7.4336 | 0.0109
GEN-2018-004 | 05 SOUTHWEST | 528423 | DCP_ZIA 3 | 115 | 7.0399 | 7.0497 | 0.0098
GEN-2018-004 | 05 SOUTHWEST | 528433 | BENSING 3 | 115 | 8.3568 | 8.3724 | 0.0156
GEN-2018-004 | 05 SOUTHWEST | 528434 | MILLEN_TPW 3 | 115 | 12.0734 | 12.1294 | 0.056
GEN-2018-004 | 05 SOUTHWEST | 528435 | MILLEN 3 | 115 | 12.0734 | 12.1294 | 0.056
GEN-2018-004 | 05 SOUTHWEST | 528436 | MILLEN_TPE 3 | 115 | 12.0734 | 12.1294 | 0.056
GEN-2018-004 | 05 SOUTHWEST | 528442 | NE_HOBBS 3 | 115 | 12.3518 | 12.4126 | 0.0608
GEN-2018-004 | 05 SOUTHWEST | 528449 | W_BENDER 3 | 115 | 15.2133 | 15.3598 | 0.1465
GEN-2018-004 | 05 SOUTHWEST | 528456 | N_HOBBS 3 | 115 | 9.3641 | 9.4195 | 0.0554
GEN-2018-004 | 05 SOUTHWEST | 528463 | SANGER_SW 3 | 115 | 16.3141 | 16.4946 | 0.1805
GEN-2018-004 | 05 SOUTHWEST | 528470 | E_SANGER 3 | 115 | 13.0843 | 13.157 | 0.0727
GEN-2018-004 | 05 SOUTHWEST | 528477 | S_HOBBS 3 | 115 | 10.7495 | 10.7987 | 0.0492
GEN-2018-004 | 05 SOUTHWEST | 528480 | OXY_S_HOBBS3 | 115 | 10.8608 | 10.9112 | 0.0504
GEN-2018-004 | 05 SOUTHWEST | 528484 | SW_4J44 3 | 115 | 11.4146 | 11.4706 | 0.056
GEN-2018-004 | 05 SOUTHWEST | 528491 | MONUMENT 3 | 115 | 15.6925 | 15.8217 | 0.1292
GEN-2018-004 | 05 SOUTHWEST | 528498 | W_HOBBS 3 | 115 | 11.9419 | 12.0034 | 0.0615
GEN-2018-004 | 05 SOUTHWEST | 528512 | EUNICE 3 | 115 | 5.933 | 5.9427 | 0.0097
GEN-2018-004 | 05 SOUTHWEST | 528533 | DRINKARD_TP3 | 115 | 7.5916 | 7.6072 | 0.0156
GEN-2018-004 | 05 SOUTHWEST | 528554 | COOPER_RNCH3 | 115 | 6.8478 | 6.8587 | 0.0109
GEN-2018-004 | 05 SOUTHWEST | 528568 | MONUMNT_TP 3 | 115 | 10.6002 | 10.6328 | 0.0326
GEN-2018-004 | 05 SOUTHWEST | 528574 | OXY_NHU_RCF3 | 115 | 15.5247 | 15.6806 | 0.1559
GEN-2018-004 | 05 SOUTHWEST | 528575 | OXYPERMIAN 3 | 115 | 15.7143 | 15.876 | 0.1617
GEN-2018-004 | 05 SOUTHWEST | 528581 | BYRD_TP 3 | 115 | 8.2821 | 8.3001 | 0.018
GEN-2018-004 | 05 SOUTHWEST | 528582 | BYRD 3 | 115 | 7.6636 | 7.6791 | 0.0155
GEN-2018-004 | 05 SOUTHWEST | 528589 | DRINKARD 3 | 115 | 7.6897 | 7.7041 | 0.0144
GEN-2018-004 | 05 SOUTHWEST | 528602 | ANDREWS 3 | 115 | 9.8012 | 9.8161 | 0.0149
GEN-2018-004 | 05 SOUTHWEST | 528627 | LE-TXACO_TP3 | 115 | 7.4792 | 7.496 | 0.0168
GEN-2018-004 | 05 SOUTHWEST | 528792 | LE-TEXACO 3 | 115 | 6.776 | 6.7898 | 0.0138
GEN-2018-004 | 05 SOUTHWEST | 762438 | GEN-2018-004 | 115 | 22.5615 | 22.9848 | 0.4233
GEN-2018-004 | 05 SOUTHWEST | 762442 | G18-004-TAP | 115 | 22.9069 | 23.3304 | 0.4235
GEN-2018-004 | 05 SOUTHWEST | 528618 | LE-LOVINTON2 | 69 | 6.5991 | 6.6034 | 0.0043
GEN-2018-015 | 05 SOUTHWEST | 511456 | O.K.U.-7 | 345 | 5.4958 | 5.7206 | 0.2248
GEN-2018-015 | 05 SOUTHWEST | 511468 | L.E.S.-7 | 345 | 13.1187 | 13.2384 | 0.1197
GEN-2018-015 | 05 SOUTHWEST | 511553 | CHISHOLM7 | 345 | 10.5114 | 10.5209 | 0.0095
GEN-2018-015 | 05 SOUTHWEST | 511565 | OKLAUN HVDC7 | 345 | 5.4799 | 5.7033 | 0.2234
GEN-2018-015 | 05 SOUTHWEST | 511568 | TERRYRD7 | 345 | 9.7014 | 9.7372 | 0.0358
GEN-2018-015 | 05 SOUTHWEST | 511571 | RUSHSPR7 | 345 | 6.3115 | 6.3258 | 0.0143
GEN-2018-015 | 05 SOUTHWEST | 511979 | RSHSPR1_MPT1 | 345 | 5.8953 | 5.9084 | 0.0131
GEN-2018-015 | 05 SOUTHWEST | 514801 | MINCO 7 | 345 | 21.1507 | 21.1722 | 0.0215
GEN-2018-015 | 05 SOUTHWEST | 515136 | SUNNYSD7 | 345 | 10.3365 | 10.349 | 0.0125
GEN-2018-015 | 05 SOUTHWEST | 515375 | WWRDEHV7 | 345 | 20.602 | 20.6057 | 0.0037
GEN-2018-015 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 7.5438 | 7.5509 | 0.0071
GEN-2018-015 | 05 SOUTHWEST | 515800 | GRACMNT7 | 345 | 17.3457 | 17.3917 | 0.046
GEN-2018-015 | 05 SOUTHWEST | 516059 | BECKHAM7 | 345 | 10.4997 | 10.5092 | 0.0095
GEN-2018-015 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 13.3167 | 13.3197 | 0.003
GEN-2018-015 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 13.088 | 13.2455 | 0.1575
GEN-2018-015 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 12.9827 | 13.1374 | 0.1547
GEN-2018-015 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 9.8117 | 9.8222 | 0.0105
GEN-2018-015 | 05 SOUTHWEST | 527656 | CROSSROADS 7 | 345 | 11.3356 | 11.3374 | 0.0018
GEN-2018-015 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 11.8344 | 11.8374 | 0.003
GEN-2018-015 | 05 SOUTHWEST | 527965 | KIOWA 7 | 345 | 8.9705 | 8.9716 | 0.0011
GEN-2018-015 | 05 SOUTHWEST | 528027 | RDRUNNER 7 | 345 | 8.7656 | 8.7666 | 0.001
GEN-2018-015 | 05 SOUTHWEST | 560078 | G16-037-TAP | 345 | 9.0188 | 9.028 | 0.0092
GEN-2018-015 | 05 SOUTHWEST | 563269 | GEN-2015-093 | 345 | 9.7942 | 9.8088 | 0.0146
GEN-2018-015 | 05 SOUTHWEST | 587740 | GEN-2016-091 | 345 | 9.9652 | 9.9911 | 0.0259
GEN-2018-015 | 05 SOUTHWEST | 587744 | G16-091-TAP | 345 | 14.1707 | 14.223 | 0.0523
GEN-2018-015 | 05 SOUTHWEST | 587770 | GEN-2016-095 | 345 | 10.3092 | 10.3369 | 0.0277
GEN-2018-015 | 05 SOUTHWEST | 588760 | GEN-2017-033 | 345 | 4.0828 | 4.199 | 0.1162
GEN-2018-015 | 05 SOUTHWEST | 599891 | OKLAUN 7 | 345 | 4.2384 | 4.2384 | 0
GEN-2018-015 | 05 SOUTHWEST | 760938 | G17-171-TAP | 345 | 10.7896 | 10.8495 | 0.0599
GEN-2018-015 | 05 SOUTHWEST | 760939 | GEN-2017-171 | 345 | 10.7896 | 10.8495 | 0.0599
GEN-2018-015 | 05 SOUTHWEST | 762216 | G17-151TAP | 345 | 7.8487 | 8.0514 | 0.2027
GEN-2018-015 | 05 SOUTHWEST | 762217 | GEN-2017-151 | 345 | 5.8736 | 5.9819 | 0.1083
GEN-2018-015 | 05 SOUTHWEST | 762460 | GEN-2018-015 | 345 | 4.748 | 5.2323 | 0.4843
GEN-2018-015 | 05 SOUTHWEST | 762467 | G18-015-TAP | 345 | 4.7573 | 5.2415 | 0.4842
GEN-2018-015 | 05 SOUTHWEST | 524415 | AMA_SOUTH 6 | 230 | 14.2472 | 14.2488 | 0.0016
GEN-2018-015 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 9.3409 | 9.3418 | 0.0009
GEN-2018-015 | 05 SOUTHWEST | 525213 | SWISHER 6 | 230 | 10.7847 | 10.7919 | 0.0072
GEN-2018-015 | 05 SOUTHWEST | 525461 | NEWHART 6 | 230 | 11.1214 | 11.1254 | 0.004
GEN-2018-015 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 23.8128 | 23.8215 | 0.0087
GEN-2018-015 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 30.0588 | 30.0716 | 0.0128
GEN-2018-015 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.1531 | 11.155 | 0.0019
GEN-2018-015 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 5.838 | 5.8386 | 0.0006
GEN-2018-015 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 22.6345 | 22.7673 | 0.1328
GEN-2018-015 | 05 SOUTHWEST | 525840 | ANTELOPE_1 6 | 230 | 22.446 | 22.5765 | 0.1305
GEN-2018-015 | 05 SOUTHWEST | 525957 | HALE_WNDCL16 | 230 | 12.1972 | 12.2261 | 0.0289
GEN-2018-015 | 05 SOUTHWEST | 526161 | CARLISLE 6 | 230 | 11.0087 | 11.023 | 0.0143
GEN-2018-015 | 05 SOUTHWEST | 526269 | LUBBCK_STH 6 | 230 | 16.2653 | 16.2817 | 0.0164
GEN-2018-015 | 05 SOUTHWEST | 526299 | LUBBCK_EST 6 | 230 | 11.9667 | 11.9754 | 0.0087
GEN-2018-015 | 05 SOUTHWEST | 526337 | JONES 6 | 230 | 18.2278 | 18.2472 | 0.0194
GEN-2018-015 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 10.2011 | 10.2049 | 0.0038
GEN-2018-015 | 05 SOUTHWEST | 526525 | WOLFFORTH 6 | 230 | 13.2769 | 13.2903 | 0.0134
GEN-2018-015 | 05 SOUTHWEST | 526677 | GRASSLAND 6 | 230 | 6.5183 | 6.5207 | 0.0024
GEN-2018-015 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 19.2568 | 19.2662 | 0.0094
GEN-2018-015 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 15.2375 | 15.2424 | 0.0049
GEN-2018-015 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 11.539 | 11.5411 | 0.0021
GEN-2018-015 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 16.4975 | 16.5017 | 0.0042
GEN-2018-015 | 05 SOUTHWEST | 527894 | HOBBS_INT 6 | 230 | 19.9501 | 19.9528 | 0.0027
GEN-2018-015 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 13.1824 | 13.1847 | 0.0023
GEN-2018-015 | 05 SOUTHWEST | 511422 | FLETCHR4 | 138 | 8.1747 | 8.1792 | 0.0045
GEN-2018-015 | 05 SOUTHWEST | 511423 | FLE TAP4 | 138 | 8.9298 | 8.9351 | 0.0053
GEN-2018-015 | 05 SOUTHWEST | 511431 | LWS S4 | 138 | 11.5225 | 11.5395 | 0.017
GEN-2018-015 | 05 SOUTHWEST | 511437 | COMANC-4 | 138 | 18.6968 | 18.7409 | 0.0441
GEN-2018-015 | 05 SOUTHWEST | 511439 | LWSTAP 4 | 138 | 12.0104 | 12.0289 | 0.0185
GEN-2018-015 | 05 SOUTHWEST | 511467 | L.E.S.-4 | 138 | 25.2181 | 25.3129 | 0.0948
GEN-2018-015 | 05 SOUTHWEST | 511474 | SHERID4 | 138 | 12.7721 | 12.7942 | 0.0221
GEN-2018-015 | 05 SOUTHWEST | 511486 | ELGINJT4 | 138 | 10.4017 | 10.41 | 0.0083
GEN-2018-015 | 05 SOUTHWEST | 511488 | 112GORE4 | 138 | 13.2077 | 13.2292 | 0.0215
GEN-2018-015 | 05 SOUTHWEST | 511494 | COMMTAP4 | 138 | 22.1001 | 22.1697 | 0.0696
GEN-2018-015 | 05 SOUTHWEST | 511512 | RPPAPER4 | 138 | 12.4498 | 12.4692 | 0.0194
GEN-2018-015 | 05 SOUTHWEST | 511537 | ARTVLTP4 | 138 | 12.1466 | 12.1661 | 0.0195
GEN-2018-015 | 05 SOUTHWEST | 511563 | ELSWORTH 4 | 138 | 10.3266 | 10.3346 | 0.008
GEN-2018-015 | 05 SOUTHWEST | 515802 | GRACMNT4 | 138 | 33.5204 | 33.545 | 0.0246
GEN-2018-015 | 05 SOUTHWEST | 529304 | OMDUNCN4 | 138 | 6.9424 | 6.9464 | 0.004
GEN-2018-015 | 05 SOUTHWEST | 587794 | G16-097-TAP | 138 | 11.1732 | 11.1781 | 0.0049
GEN-2018-015 | 05 SOUTHWEST | 590001 | OKLEHV24 | 138 | 5.1704 | 5.1704 | 0
GEN-2018-015 | 05 SOUTHWEST | 590003 | OKLEHV14 | 138 | 5.2556 | 5.2556 | 0
GEN-2018-015 | 05 SOUTHWEST | 525212 | SWISHER 3 | 115 | 11.788 | 11.7915 | 0.0035
GEN-2018-015 | 05 SOUTHWEST | 525454 | HALE_CNTY 3 | 115 | 10.6382 | 10.6417 | 0.0035
GEN-2018-015 | 05 SOUTHWEST | 525780 | FLOYD_CNTY 3 | 115 | 6.9984 | 7.0005 | 0.0021
GEN-2018-015 | 05 SOUTHWEST | 525828 | TUCO_INT 3 | 115 | 20.3456 | 20.38 | 0.0344
GEN-2018-015 | 05 SOUTHWEST | 526076 | STANTON_W 3 | 115 | 9.6662 | 9.6716 | 0.0054
GEN-2018-015 | 05 SOUTHWEST | 526160 | CARLISLE 3 | 115 | 14.3925 | 14.4027 | 0.0102
GEN-2018-015 | 05 SOUTHWEST | 526298 | LUBBCK_EST 3 | 115 | 15.3834 | 15.3928 | 0.0094
GEN-2018-015 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 18.7497 | 18.7535 | 0.0038
GEN-2018-015 | 05 SOUTHWEST | 511436 | COMANC-2 | 69 | 9.9573 | 9.9608 | 0.0035
GEN-2018-015 | 05 SOUTHWEST | 511466 | L.E.S.-2 | 69 | 16.5847 | 16.6004 | 0.0157
GEN-2018-015 | 05 SOUTHWEST | 511469 | LGORE-N2 | 69 | 8.2121 | 8.2158 | 0.0037
GEN-2018-015 | 05 SOUTHWEST | 511470 | LGORE-S2 | 69 | 7.1886 | 7.1916 | 0.003
GEN-2018-015 | 05 SOUTHWEST | 511487 | ELGINJT2 | 69 | 8.9043 | 8.9072 | 0.0029
GEN-2018-015 | 05 SOUTHWEST | 525816 | TUCO_INT2 2 | 69 | 4.7907 | 4.7918 | 0.0011
GEN-2018-015 | 05 SOUTHWEST | 525826 | TUCO_INT 2 | 69 | 8.1118 | 8.1149 | 0.0031
GEN-2018-052 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 7.5509 | 7.5509 | 0
GEN-2018-052 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 9.8548 | 9.8548 | 0
GEN-2018-052 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 13.32 | 13.3197 | -0.0003
GEN-2018-052 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 13.2456 | 13.2455 | -0.0001
GEN-2018-052 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 13.1375 | 13.1374 | -0.0001
GEN-2018-052 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 9.8227 | 9.8222 | -0.0005
GEN-2018-052 | 05 SOUTHWEST | 527599 | SAGA_SDCOL 7 | 345 | 10.1478 | 10.1471 | -0.0007
GEN-2018-052 | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 10.1478 | 10.1471 | -0.0007
GEN-2018-052 | 05 SOUTHWEST | 527654 | RSVLT_CC_W 7 | 345 | 8.7224 | 8.7219 | -0.0005
GEN-2018-052 | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 9.9029 | 9.9022 | -0.0007
GEN-2018-052 | 05 SOUTHWEST | 527656 | CROSSROADS 7 | 345 | 11.3383 | 11.3374 | -0.0009
GEN-2018-052 | 05 SOUTHWEST | 527802 | EDDY_CNTY 7 | 345 | 7.4691 | 7.4683 | -0.0008
GEN-2018-052 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 11.8405 | 11.8374 | -0.0031
GEN-2018-052 | 05 SOUTHWEST | 527965 | KIOWA 7 | 345 | 8.9731 | 8.9716 | -0.0015
GEN-2018-052 | 05 SOUTHWEST | 528015 | PHANTOM 7 | 345 | 6.052 | 6.0519 | -0.0001
GEN-2018-052 | 05 SOUTHWEST | 528027 | RDRUNNER 7 | 345 | 8.7705 | 8.7666 | -0.0039
GEN-2018-052 | 05 SOUTHWEST | 528185 | N_LOVING 7 | 345 | 6.8823 | 6.8823 | 0
GEN-2018-052 | 05 SOUTHWEST | 528223 | CHINA_DRAW 7 | 345 | 6.1489 | 6.1495 | 0.0006
GEN-2018-052 | 05 SOUTHWEST | 762216 | G17-151TAP | 345 | 8.0515 | 8.0514 | -0.0001
GEN-2018-052 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 30.072 | 30.0716 | -0.0004
GEN-2018-052 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.1551 | 11.155 | -0.0001
GEN-2018-052 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 22.7674 | 22.7673 | -0.0001
GEN-2018-052 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 10.2049 | 10.2049 | 0
GEN-2018-052 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 19.2668 | 19.2662 | -0.0006
GEN-2018-052 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 15.2427 | 15.2424 | -0.0003
GEN-2018-052 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 11.5414 | 11.5411 | -0.0003
GEN-2018-052 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 16.502 | 16.5017 | -0.0003
GEN-2018-052 | 05 SOUTHWEST | 527483 | CHAVES_CNTY6 | 230 | 4.3393 | 4.3393 | 0
GEN-2018-052 | 05 SOUTHWEST | 527799 | EDDY_NORTH 6 | 230 | 9.7075 | 9.7068 | -0.0007
GEN-2018-052 | 05 SOUTHWEST | 527865 | CUNNIGHM_N 6 | 230 | 18.0192 | 18.0175 | -0.0017
GEN-2018-052 | 05 SOUTHWEST | 527867 | CUNNIGHM_S 6 | 230 | 18.0192 | 18.0175 | -0.0017
GEN-2018-052 | 05 SOUTHWEST | 527894 | HOBBS_INT 6 | 230 | 19.9551 | 19.9528 | -0.0023
GEN-2018-052 | 05 SOUTHWEST | 527963 | POTASH_JCT 6 | 230 | 7.921 | 7.9206 | -0.0004
GEN-2018-052 | 05 SOUTHWEST | 528095 | 7-RIVERS 6 | 230 | 6.6816 | 6.6813 | -0.0003
GEN-2018-052 | 05 SOUTHWEST | 528604 | ANDREWS 6 | 230 | 6.3097 | 6.3093 | -0.0004
GEN-2018-052 | 05 SOUTHWEST | 599960 | EPTNP-D6 | 230 | 9.7075 | 9.7068 | -0.0007
GEN-2018-052 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 18.7538 | 18.7535 | -0.0003
GEN-2018-052 | 05 SOUTHWEST | 527027 | INK_BASIN 3 | 115 | 13.8909 | 13.8907 | -0.0002
GEN-2018-052 | 05 SOUTHWEST | 527793 | EDDY_STH 3 | 115 | 12.1817 | 12.1812 | -0.0005
GEN-2018-052 | 05 SOUTHWEST | 527798 | EDDY_NTH 3 | 115 | 12.1817 | 12.1812 | -0.0005
GEN-2018-052 | 05 SOUTHWEST | 527864 | CUNNINHAM 3 | 115 | 28.2113 | 28.2095 | -0.0018
GEN-2018-052 | 05 SOUTHWEST | 527891 | HOBBS_INT 3 | 115 | 32.051 | 32.049 | -0.002
GEN-2018-052 | 05 SOUTHWEST | 527930 | PCA 3 | 115 | 12.5213 | 12.5205 | -0.0008
GEN-2018-052 | 05 SOUTHWEST | 527953 | LIVSTNRIDGE3 | 115 | 8.0103 | 8.0092 | -0.0011
GEN-2018-052 | 05 SOUTHWEST | 527954 | MEDANOS 3 | 115 | 5.8073 | 5.8068 | -0.0005
GEN-2018-052 | 05 SOUTHWEST | 527962 | POTASH_JCT 3 | 115 | 17.7196 | 17.7178 | -0.0018
GEN-2018-052 | 05 SOUTHWEST | 527966 | KIOWA 3 | 115 | 17.729 | 17.7272 | -0.0018
GEN-2018-052 | 05 SOUTHWEST | 527999 | INTREPDW_TP3 | 115 | 14.4672 | 14.4658 | -0.0014
GEN-2018-052 | 05 SOUTHWEST | 528009 | WIPP 3 | 115 | 7.5939 | 7.5928 | -0.0011
GEN-2018-052 | 05 SOUTHWEST | 528013 | PHANTOM 3 | 115 | 13.3536 | 13.353 | -0.0006
GEN-2018-052 | 05 SOUTHWEST | 528016 | SAND_DUNES 3 | 115 | 7.7378 | 7.7363 | -0.0015
GEN-2018-052 | 05 SOUTHWEST | 528018 | RED_BLUFF 3 | 115 | 10.5149 | 10.511 | -0.0039
GEN-2018-052 | 05 SOUTHWEST | 528020 | BOPCO_PKRLK3 | 115 | 13.1608 | 13.1601 | -0.0007
GEN-2018-052 | 05 SOUTHWEST | 528024 | RR_SVC_HV 3 | 115 | 13.8255 | 13.8046 | -0.0209
GEN-2018-052 | 05 SOUTHWEST | 528025 | RDRUNNER 3 | 115 | 13.8255 | 13.8046 | -0.0209
GEN-2018-052 | 05 SOUTHWEST | 528040 | BATTLE_AXE 3 | 115 | 3.4322 | 3.431 | -0.0012
GEN-2018-052 | 05 SOUTHWEST | 528064 | XTO_DI9_TP 3 | 115 | 8.4641 | 8.4632 | -0.0009
GEN-2018-052 | 05 SOUTHWEST | 528160 | CARLSBAD 3 | 115 | 11.8003 | 11.7997 | -0.0006
GEN-2018-052 | 05 SOUTHWEST | 528182 | NORTH_LOVNG3 | 115 | 12.5667 | 12.5677 | 0.001
GEN-2018-052 | 05 SOUTHWEST | 528192 | SOUTH_LOVNG3 | 115 | 9.598 | 9.5984 | 0.0004
GEN-2018-052 | 05 SOUTHWEST | 528193 | BLACKRIVER 3 | 115 | 10.6204 | 10.6216 | 0.0012
GEN-2018-052 | 05 SOUTHWEST | 528194 | MALAGABEND 3 | 115 | 8.152 | 8.152 | 0
GEN-2018-052 | 05 SOUTHWEST | 528195 | AGAVE_PDURO3 | 115 | 8.2488 | 8.2492 | 0.0004
GEN-2018-052 | 05 SOUTHWEST | 528206 | BLCKRVR_DST3 | 115 | 8.4325 | 8.4346 | 0.0021
GEN-2018-052 | 05 SOUTHWEST | 528222 | CHINA_DRAW 3 | 115 | 11.5514 | 11.559 | 0.0076
GEN-2018-052 | 05 SOUTHWEST | 528225 | CD_SVC_HV 3 | 115 | 11.5514 | 11.559 | 0.0076
GEN-2018-052 | 05 SOUTHWEST | 528226 | HOPI_SUB 3 | 115 | 7.5725 | 7.5725 | 0
GEN-2018-052 | 05 SOUTHWEST | 528228 | WOOD_DRAW 3 | 115 | 8.5135 | 8.5147 | 0.0012
GEN-2018-052 | 05 SOUTHWEST | 528230 | AGAVE_RHILL3 | 115 | 12.439 | 12.4221 | -0.0169
GEN-2018-052 | 05 SOUTHWEST | 528231 | AGAVE_RHIL23 | 115 | 11.7992 | 11.7841 | -0.0151
GEN-2018-052 | 05 SOUTHWEST | 528232 | OCHOA 3 | 115 | 11.7783 | 11.7631 | -0.0152
GEN-2018-052 | 05 SOUTHWEST | 528235 | WOLFCAMP_TP3 | 115 | 12.4868 | 12.4857 | -0.0011
GEN-2018-052 | 05 SOUTHWEST | 528236 | WOLFCAMP 3 | 115 | 11.5709 | 11.57 | -0.0009
GEN-2018-052 | 05 SOUTHWEST | 528239 | CUSTERMTN 3 | 115 | 7.921 | 7.9176 | -0.0034
GEN-2018-052 | 05 SOUTHWEST | 528240 | PONDEROSA 3 | 115 | 4.2309 | 4.2299 | -0.001
GEN-2018-052 | 05 SOUTHWEST | 528252 | CHVRN_EDDYS3 | 115 | 7.68 | 7.6833 | 0.0033
GEN-2018-052 | 05 SOUTHWEST | 528333 | LE-WEST_SUB3 | 115 | 9.536 | 9.5359 | -0.0001
GEN-2018-052 | 05 SOUTHWEST | 528355 | MADDOX 3 | 115 | 27.011 | 27.0095 | -0.0015
GEN-2018-052 | 05 SOUTHWEST | 528433 | BENSING 3 | 115 | 8.3725 | 8.3724 | -0.0001
GEN-2018-052 | 05 SOUTHWEST | 528434 | MILLEN_TPW 3 | 115 | 12.1297 | 12.1294 | -0.0003
GEN-2018-052 | 05 SOUTHWEST | 528505 | LEA_ROAD 3 | 115 | 6.0583 | 6.0577 | -0.0006
GEN-2018-052 | 05 SOUTHWEST | 528519 | WARD 3 | 115 | 5.9918 | 5.9909 | -0.0009
GEN-2018-052 | 05 SOUTHWEST | 528526 | TEAGUE 3 | 115 | 6.6168 | 6.616 | -0.0008
GEN-2018-052 | 05 SOUTHWEST | 528540 | WHITTEN 3 | 115 | 7.8804 | 7.8779 | -0.0025
GEN-2018-052 | 05 SOUTHWEST | 528547 | S_JAL 3 | 115 | 6.766 | 6.7647 | -0.0013
GEN-2018-052 | 05 SOUTHWEST | 528552 | OIL_CENTER 3 | 115 | 6.3188 | 6.3182 | -0.0006
GEN-2018-052 | 05 SOUTHWEST | 528561 | DOLLARHIDE 3 | 115 | 5.2014 | 5.2006 | -0.0008
GEN-2018-052 | 05 SOUTHWEST | 528596 | CARDINAL 3 | 115 | 7.8703 | 7.8695 | -0.0008
GEN-2018-052 | 05 SOUTHWEST | 528602 | ANDREWS 3 | 115 | 9.8168 | 9.8161 | -0.0007
GEN-2018-052 | 05 SOUTHWEST | 587990 | GEN-2016-121 | 115 | 12.7822 | 12.7642 | -0.018
GEN-2018-052 | 05 SOUTHWEST | 762866 | GEN-2018-052 | 115 | 13.6056 | 13.5853 | -0.0203
GEN-2018-052 | 05 SOUTHWEST | 527961 | POTASH_JCT 2 | 69 | 9.8376 | 9.8372 | -0.0004

## SCRCCT
Study Name | Group | Season | Gen Number | POI | Contingency | SCR | Critical_Clearing_Time | Stability_Margin | Pg_out | Pg_rated | SCR PASS/FAIL | CCT PASS/FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | Base | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [7FAIRPT 345.00] TO [ST JOE 7 345.00] CKT 1 | 7.3902 | 0.1949 | 94.9078 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [7FAIRPT 345.00] TO [COOPER 3 345.00] CKT 1 | 7.3899 | 0.1949 | 94.9057 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [5HOLDENB2 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9053 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [2CLINTN 69.000] CKT 1 | 7.3899 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [2CLINTN 69.000] CKT 3 | 7.3899 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [5OSCEOKCTP 161.00] CKT 1 | 7.3898 | 0.1949 | 94.9045 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [TRUMAN 5 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9058 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [WINDSR 5 161.00] CKT 1 | 7.39 | 0.1949 | 94.9067 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [CLINTON5 161.00] CKT Z1 | 7.39 | 0.1949 | 94.9063 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [N MADRD5 161.00] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [SIKETAP5 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9059 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [7BLACKBERRY 345.00] TO [7SPORTSMAN 345.00] CKT 1 | 7.3897 | 0.1949 | 94.9041 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [7BLACKBERRY 345.00] TO [7JASPER 345.00] CKT 1 | 7.3906 | 0.1949 | 94.9119 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [7BLACKBERRY 345.00] TO [WOLFCRK7 345.00] CKT 1 | 7.3884 | 0.1949 | 94.894 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5MINER 1 161.00] TO [SIKESTN5 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9059 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [N MADRD5 161.00] TO [KENNETT5 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9055 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [N MADRD5 161.00] TO [N MADRD2 69.000] TO [NMA X1 1 13.800] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [N MADRD5 161.00] TO [N MADRD2 69.000] TO [NMA X2 1 13.800] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SIKETAP5 161.00] TO [SIKESTN5 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9059 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SIKESTN5 161.00] TO [SIKGEN 1 13.800] CKT 1 | 7.3902 | 0.1949 | 94.9084 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SIKESTN5 161.00] TO [IDALIA 5 161.00] CKT 1 | 7.39 | 0.1949 | 94.9063 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SIKESTN5 161.00] TO [SIKESTN2 69.000] TO [SIK X1 1 13.800] CKT 1 | 7.3899 | 0.1949 | 94.9053 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [DELAWAR1 13.800] TO [DELWARE4 138.00] TO [DELWARE7 345.00] CKT 1 | 7.39 | 0.1949 | 94.9065 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [DELWARE7 345.00] TO [N.E.S.-7 345.00] CKT 1 | 7.3893 | 0.1949 | 94.9014 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [DGRASSE7 345.00] CKT 1 | 7.3857 | 0.1949 | 94.8741 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [DGRASSE7 345.00] CKT 2 | 7.3857 | 0.1949 | 94.8741 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [DGRASSE7 345.00] TO [DGRASSE4 138.00] TO [DGRASSE1 13.800] CKT 1 | 7.386 | 0.1949 | 94.911 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WALKMYR1 13.800] TO [WALKMYR2 69.000] TO [WALKMYR3 115.00] CKT 1 | 7.3881 | 0.1949 | 94.9235 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WALKMYR3 115.00] TO [HUGOTON3 115.00] CKT 1 | 7.344 | 0.1952 | 95.157 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WALKMYR3 115.00] TO [HARBNGR3 115.00] CKT 1 | 5.7482 | 0.1982 | 98.2371 | 150 | 168 | FAIL | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SEWARD-3 115.00] TO [N-CIMRN3 115.00] CKT 1 | 5.4664 | 0.2004 | 100.4147 | 150 | 168 | FAIL | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [CLARKCOUNTY7345.00] CKT 1 | 7.3801 | 0.1949 | 94.9077 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NSES 2X1 13.200] TO [NEOSHO 4 138.00] TO [NEOSHOS2 69.000] CKT 1 | 7.3899 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EEC GT1 13.800] TO [EVANS S4 138.00] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EEC GT2 13.800] TO [EVANS S4 138.00] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EEC GT3 18.000] TO [EVANS S4 138.00] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [SWISVAL7 345.00] CKT 1 | 7.3894 | 0.1949 | 94.905 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EXPEDITION7 345.00] CKT 1 | 7.3867 | 0.1949 | 94.902 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [RENO 7 345.00] TO [WICHITA7 345.00] CKT 1 | 7.389 | 0.1949 | 94.8977 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUMMIT 7 345.00] TO [G17-004-TAP 345.00] CKT 1 | 7.3894 | 0.1949 | 94.9016 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SWISVAL7 345.00] TO [SWISVAL6 230.00] TO [SWISV1X1 14.400] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SWISVAL7 345.00] TO [SWISVAL6 230.00] TO [SWISV2X2 14.400] CKT 2 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [87TH 7 345.00] TO [CRAIG 7 345.00] CKT 1 | 7.3893 | 0.1949 | 94.9011 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [G17-009-TAP 345.00] TO [GEN-2017-009345.00] CKT 1 | 7.39 | 0.1949 | 94.906 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [G17-009-TAP 345.00] TO [CANEYRV7 345.00] CKT 1 | 7.3891 | 0.1949 | 94.905 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [KINGMAN7 345.00] TO [NINN1WF7 345.00] CKT 1 | 7.3907 | 0.1949 | 94.911 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [KINGMAN7 345.00] TO [K1 LV 1 34.500] TO [K1 WFTX1 13.800] CKT 1 | 7.3902 | 0.1949 | 94.9076 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [KINGMAN7 345.00] TO [K2 LV 1 34.500] TO [K2 WFTX1 13.800] CKT 1 | 7.3902 | 0.1949 | 94.9073 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BENTON 7 345.00] TO [WICHITA7 345.00] CKT 1 | 7.383 | 0.1949 | 94.895 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BENTON 7 345.00] TO [WOLFCRK7 345.00] CKT 1 | 7.3889 | 0.1949 | 94.9053 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [VIOLA 7 345.00] CKT 1 | 7.3874 | 0.1949 | 94.8885 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [EXPEDITION7 345.00] CKT 1 | 7.3862 | 0.1949 | 94.8965 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WOLFCRK7 345.00] TO [WAVERLY7 345.00] CKT 1 | 7.3898 | 0.1949 | 94.9068 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [VIOLA 7 345.00] TO [VIOLA 4 138.00] TO [VIOLA1X1 13.800] CKT 1 | 7.39 | 0.1949 | 94.9065 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [VIOLA 7 345.00] TO [VIOLA 4 138.00] TO [SCJ1X1 13.800] CKT 2 | 7.39 | 0.1949 | 94.9067 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WAVERLY7 345.00] TO [LACYGNE7 345.00] CKT 1 | 7.39 | 0.1949 | 94.9081 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NMANHT6 230.00] TO [ELMCREK6 230.00] CKT 1 | 7.3896 | 0.1949 | 94.9073 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LITCH 5 161.00] TO [FRANKLIN5 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9053 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LITCH 5 161.00] TO [LITCH S2 69.000] TO [LITCH1 1 13.200] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LITCH 5 161.00] TO [LITCH N2 69.000] TO [LITCH2 1 13.200] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [MARMTNW5 161.00] TO [NEOSHO 5 161.00] CKT 1 | 7.39 | 0.1949 | 94.9063 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEOSHO 5 161.00] TO [RIV4525 161.00] CKT 1 | 7.3898 | 0.1949 | 94.9049 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEOSHO 5 161.00] TO [NEOSHO 4 138.00] TO [NEOSH4 1 13.200] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEOSHO 5 161.00] TO [NEOSHOS4 138.00] TO [NEOSH5 1 13.200] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRESWLN4 138.00] TO [OXFORD 4 138.00] CKT 1 | 7.3895 | 0.1949 | 94.9042 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [TCROCK 4 138.00] TO [TIMBJCT4 138.00] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [TIMBJCT4 138.00] TO [TIMBJCT2 69.000] TO [TIMBJCT1 13.200] CKT 1 | 7.3898 | 0.1949 | 94.906 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [TIOGA 4 138.00] TO [ALTOONA4 138.00] CKT 1 | 7.39 | 0.1949 | 94.9063 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [OTTRCRK4 138.00] TO [ALTOONA4 138.00] CKT 1 | 7.3898 | 0.1949 | 94.9055 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ALTOONA4 138.00] TO [TAYLOR 4 138.00] CKT 1 | 7.3898 | 0.1949 | 94.9048 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ALTOONA4 138.00] TO [ALTOO W2 69.000] TO [ALTOO1 1 13.200] CKT 1 | 7.3899 | 0.1949 | 94.906 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ALTOONA4 138.00] TO [ALTOO E2 69.000] TO [ALTOO3 1 13.200] CKT 1 | 7.3899 | 0.1949 | 94.906 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEPARSN4 138.00] TO [NEOSHON4 138.00] CKT 1 | 7.39 | 0.1949 | 94.9063 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BENTLEY4 138.00] TO [SG12COL4 138.00] CKT 1 | 7.3897 | 0.1949 | 94.9068 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEOSHOS4 138.00] TO [NEOSHO 4 138.00] CKT Z1 | 7.3899 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEOSHO 4 138.00] TO [NEOSHON4 138.00] CKT Z1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CHISHLM4 138.00] TO [MAIZE 4 138.00] CKT 1 | 7.3894 | 0.1949 | 94.9034 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CLEARWT4 138.00] TO [GILL 4 138.00] CKT 1 | 7.3899 | 0.1949 | 94.9067 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CLEARWT4 138.00] TO [VIOLA 4 138.00] CKT 1 | 7.3897 | 0.1949 | 94.9065 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EVANS S4 138.00] TO [LAKERDG4 138.00] CKT 1 | 7.3893 | 0.1949 | 94.902 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EVANS S4 138.00] TO [45TH ST4 138.00] CKT 1 | 7.3893 | 0.1949 | 94.9022 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [FARBER 4 138.00] TO [SC10BEL4 138.00] CKT 1 | 7.3899 | 0.1949 | 94.9059 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GILL 4 138.00] TO [VIOLA 4 138.00] CKT 1 | 7.3899 | 0.1949 | 94.9065 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [VIOLA 4 138.00] TO [MILAN_GOAB 138.00] CKT 1 | 7.3896 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [VIOLA 4 138.00] TO [CONWAY 138.00] CKT 1 | 7.3887 | 0.1949 | 94.9063 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [AEC 3 115.00] TO [EABILEN3 115.00] CKT 1 | 7.3896 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [AEC 3 115.00] TO [AEC E1 34.500] CKT 2 | 7.3898 | 0.1949 | 94.9055 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [AEC 3 115.00] TO [AEC W1 34.500] CKT 1 | 7.3896 | 0.1949 | 94.9046 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NORTHST3 115.00] TO [NORTHVW3 115.00] CKT 1 | 7.3901 | 0.1949 | 94.9071 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NORTHVW3 115.00] TO [SUMMIT 3 115.00] CKT 1 | 7.39 | 0.1949 | 94.907 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LITCH N2 69.000] TO [LITCH S2 69.000] CKT Z1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [MRWYP16 230.00] TO [ELMCREK6 230.00] CKT 1 | 7.3904 | 0.1949 | 94.9099 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [FLATRDG4 138.00] TO [THISTLE4 138.00] CKT 1 | 7.3905 | 0.1949 | 94.9131 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ELMCREK6 230.00] TO [CONCRD6 230.00] CKT 1 | 7.3904 | 0.1949 | 94.9102 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAYNE3 115.00] TO [NLIB 3 115.00] CKT 1 | 7.2316 | 0.1957 | 95.6559 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [KISMET 3 115.00] TO [CMRIVTP3 115.00] CKT 1 | 6.0963 | 0.1996 | 99.6474 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CMRIVTP3 115.00] TO [E-LIBER3 115.00] CKT 1 | 7.3476 | 0.1951 | 95.1071 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CIM-PLT1 13.800] TO [CIM-PLT 13.800] CKT Z1 | 7.4061 | 0.1953 | 95.3056 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [N-CIMRN3 115.00] TO [N-CMRN 1 34.500] TO [N-CMRN-T 13.800] CKT 1 | 7.3793 | 0.1952 | 95.1664 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [TRANSFORMER 345.00] CKT 1 | 7.3934 | 0.1949 | 94.9371 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [GEN-2011-008345.00] CKT 1 | 7.3943 | 0.1949 | 94.9382 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [G16-046-TAP 345.00] CKT 1 | 7.3834 | 0.1949 | 94.9076 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [MULLNCR7 345.00] TO [MC REAC1 345.00] CKT Z1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [MULLNCR7 345.00] TO [MC REAC2 345.00] CKT Z1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [MULLNCR7 345.00] TO [MC REAC3 345.00] CKT Z1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [MULLNCR7 345.00] TO [KETCHEM7 345.00] CKT 1 | 7.3897 | 0.1949 | 94.9042 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [PECULR 7 345.00] TO [STILWEL7 345.00] CKT 1 | 7.3902 | 0.1949 | 94.9086 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ST JOE 7 345.00] TO [EASTOWN7 345.00] CKT 1 | 7.3903 | 0.1949 | 94.9087 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ST JOE 7 345.00] TO [COOPER 3 345.00] CKT 1 | 7.3901 | 0.1949 | 94.9073 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ST JOE 7 345.00] TO [ST JOE 5 161.00] TO [STJOE 1T 13.800] CKT 22 | 7.3899 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ST JOE 7 345.00] TO [ST JOE 5 161.00] TO [STJOE 2T 13.800] CKT 33 | 7.3899 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ARCHIE 5 161.00] TO [HSNVL 5 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9059 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ARCHIE 5 161.00] TO [ADRIAN 5 161.00] CKT 1 | 7.3897 | 0.1949 | 94.9039 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ARCHIE 5 161.00] TO [S.HARP 5 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9057 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [STILWEL5 161.00] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EASTOWN7 345.00] TO [IATAN 7 345.00] CKT 1 | 7.3908 | 0.1949 | 94.9123 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ROCKCK_TR1_113.200] TO [ROCKCK7 345.00] TO [ROCKCK_T1_1 34.500] CKT 1 | 7.3902 | 0.1949 | 94.9076 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ROCKCK_TR2_113.200] TO [ROCKCK7 345.00] TO [ROCKCK_T2_1 34.500] CKT 1 | 7.3903 | 0.1949 | 94.908 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ROCKCK7 345.00] TO [OUTLAW 345.00] CKT 1 | 7.3904 | 0.1949 | 94.9096 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LAC G1 1 22.000] TO [LACYGNE7 345.00] CKT 1 | 7.3928 | 0.1949 | 94.9302 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LAC G2 1 24.000] TO [LACYGNE7 345.00] CKT 1 | 7.3926 | 0.1949 | 94.9284 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [CEDRCRK5 161.00] CKT 1 | 7.39 | 0.1949 | 94.9067 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [CEDARNL5 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9058 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [PLSTVAL5 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9058 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [BULLCRK5 161.00] CKT 1 | 7.3915 | 0.1949 | 94.9188 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [BNSF 5 161.00] CKT 1 | 7.39 | 0.1949 | 94.9066 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [WGARDNR1 34.500] CKT 7 | 7.3899 | 0.1949 | 94.9053 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [STILWEL7 345.00] TO [LACYGNE7 345.00] CKT 1 | 7.3915 | 0.1949 | 94.9191 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [STILWEL7 345.00] TO [STILWEL5 161.00] TO [STIL T11 13.800] CKT 11 | 7.39 | 0.1949 | 94.9065 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [STILWEL7 345.00] TO [STILWEL5 161.00] TO [STIL T22 13.800] CKT 22 | 7.39 | 0.1949 | 94.9065 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [HICKMAN5 161.00] CKT 1 | 7.39 | 0.1949 | 94.9068 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [ANTIOCH5 161.00] CKT 1 | 7.39 | 0.1949 | 94.9069 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [REDEL 5 161.00] CKT 1 | 7.39 | 0.1949 | 94.9067 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [BUCYRUS5 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9057 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [LACKMAN5 161.00] CKT 1 | 7.39 | 0.1949 | 94.9063 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTH 7 345.00] TO [NASHUA 7 345.00] CKT 1 | 7.3895 | 0.1949 | 94.9026 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [SUB M-161 161.00] CKT 1 | 7.3899 | 0.1949 | 94.906 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRAIG 7 345.00] TO [CRAIG 5 161.00] TO [CRAI T11 13.800] CKT 11 | 7.3899 | 0.1949 | 94.906 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRAIG 7 345.00] TO [CRAIG 5 161.00] TO [CRAI T22 13.800] CKT 22 | 7.3899 | 0.1949 | 94.906 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRAIG 7 345.00] TO [CRAIG 5 161.00] TO [CRAI T33 13.800] CKT 33 | 7.3899 | 0.1949 | 94.906 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [CEDRCRK5 161.00] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NASHUA 7 345.00] TO [IATAN 7 345.00] CKT 1 | 7.3898 | 0.1949 | 94.9045 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NASHUA 7 345.00] TO [NASHUA-5 161.00] TO [NASH T11 13.800] CKT 11 | 7.3899 | 0.1949 | 94.9056 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NASHUA 7 345.00] TO [NASHUA-5 161.00] TO [NASH T12 13.800] CKT 12 | 7.3899 | 0.1949 | 94.9056 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [LACYGNE11_7 345.00] CKT 1 | 7.3897 | 0.1949 | 94.905 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [LACYGNE22_7 345.00] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [LAC3_STAR7 345.00] CKT H | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [LAC8_STAR7 345.00] CKT H | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [LACYGNE2 69.000] TO [LACYGN7_TER16.9000] CKT 7 | 7.3899 | 0.1949 | 94.9057 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BLUMILS5 161.00] TO [ECKLES-161 161.00] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BLUMILS5 161.00] TO [BLUEMLS2 69.000] TO [BLUMILS_TER112.500] CKT 3 | 7.3899 | 0.1949 | 94.9058 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LAKCTYJ2 69.000] TO [BLUVLY 69.000] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CJ 366 5 161.00] TO [FIR417 5 161.00] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CAR395 5 161.00] TO [PUR421 5 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9059 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB K 69.000] TO [BLUVLY 69.000] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB H 69.000] TO [BLUVLY 69.000] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB H 69.000] TO [SUB M 69.000] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BLUVLY 13.8 13.800] TO [BLUVLY 69.000] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [SUB B 69.000] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [SUB J 69.000] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [SUB P 69.000] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB B 69.000] TO [SUB J 69.000] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB J 69.000] TO [SUB M 69.000] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB M-161 161.00] TO [SUB M 69.000] CKT 1 | 7.3899 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GEN-2017-004345.00] TO [G17-004-TAP 345.00] CKT 1 | 7.3906 | 0.1949 | 94.9116 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GEN-2017-018345.00] TO [G17-018XFMR134.500] CKT 1 | 7.3905 | 0.1949 | 94.9107 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GEN-2017-018345.00] TO [G17-018XFMR234.500] CKT 1 | 7.3905 | 0.1949 | 94.9107 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GEN-2017-068138.00] TO [G17-068XFMR134.500] CKT 1 | 7.3903 | 0.1949 | 94.9087 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GEN-2017-082161.00] TO [G17-082XFMR134.500] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [S3458 3 345.00] CKT 1 | 7.39 | 0.1949 | 94.9067 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEBCTY1G 18.000] TO [S3458 3 345.00] CKT 1 | 7.396 | 0.195 | 94.9548 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEBCTY2G 23.000] TO [S3458 3 345.00] CKT 1 | 7.3963 | 0.195 | 94.9572 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S3456 3 345.00] TO [S3458 3 345.00] CKT 1 | 7.3901 | 0.1949 | 94.9076 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S3458 3 345.00] TO [S3740 3 345.00] CKT 1 | 7.3902 | 0.1949 | 94.908 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S3458 3 345.00] TO [103&ROKEBY3 345.00] CKT 1 | 7.3907 | 0.1949 | 94.9127 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [7FAIRPT 345.00] TO [5FAIRPTXF3 161.00] CKT 3 | 7.3897 | 0.1949 | 94.9042 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [G17-108-TAP 161.00] CKT 1 | 7.3897 | 0.1949 | 94.904 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5GIBSON 161.00] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M0 161.00] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M1 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9053 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M2 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9053 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M3 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9053 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5NEWMADCP 161.00] CKT Z1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5NEWMADXF12 161.00] CKT Z1 | 7.3899 | 0.1949 | 94.906 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5NEWMADGSU1 161.00] CKT 1 | 7.3905 | 0.1949 | 94.9107 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5NMDSU100HS 161.00] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5NMDSU200HS 161.00] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5PORTAGEVLE 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9058 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5TIPTONVL TN161.00] CKT 1 | 7.3897 | 0.1949 | 94.9044 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5HOLDENB2 161.00] TO [1HOLDNG11 13.800] CKT 11 | 7.3905 | 0.1949 | 94.9105 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5HOLDENB2 161.00] TO [1HOLDNG12 13.800] CKT 12 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5HOLDENB2 161.00] TO [2HOLDEN 69.000] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5HOLDENB2 161.00] TO [5HOLDENB1 161.00] CKT Z1 | 7.39 | 0.1949 | 94.9064 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [2CLINTN 69.000] TO [2LINCLN 69.000] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [2CLINTN 69.000] TO [2GAINES 69.000] CKT 1 | 7.3899 | 0.1949 | 94.906 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [2CLINTN 69.000] TO [2LEETON 69.000] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [2CLINTN 69.000] TO [2PIPER 69.000] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [2CLINTN 69.000] TO [2CLINTNLD 69.000] CKT 1 | 7.3899 | 0.1949 | 94.9059 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [7BLACKBERRY 345.00] TO [NEOSHO 7 345.00] CKT 1 | 7.3899 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [7SPORTSMAN 345.00] TO [5SPORTSMAN 161.00] CKT 1 | 7.39 | 0.1949 | 94.9064 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [7SPORTSMAN 345.00] TO [5SPORTSMAN 161.00] CKT 2 | 7.39 | 0.1949 | 94.9064 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [7SPORTSMAN 345.00] TO [GRDA1 7 345.00] CKT 1 | 7.3893 | 0.1949 | 94.9011 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [7JASPER 345.00] TO [7MORGAN 345.00] CKT 1 | 7.3902 | 0.1949 | 94.9085 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [7JASPER 345.00] TO [5JASPER 161.00] CKT 1 | 7.3901 | 0.1949 | 94.9075 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5OSCEOKCTP 161.00] TO [5OSCEOLTP 161.00] CKT 1 | 7.3898 | 0.1949 | 94.9049 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5OSCEOKCTP 161.00] TO [5OSCEOKC 161.00] CKT 1 | 7.3899 | 0.1949 | 94.906 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5MINER 1 161.00] TO [5CHARLSTN 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9059 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5MINER 1 161.00] TO [5BULLION 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9057 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5MINER 1 161.00] TO [5MINER 2 161.00] CKT Z | 7.3899 | 0.1949 | 94.906 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [N MADRD5 161.00] TO [G17-202-TAP 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9056 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [N MADRD2 69.000] TO [2STJUDEW 69.000] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [N MADRD2 69.000] TO [2LILBRN 69.000] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [N MADRD2 69.000] TO [MALDEN 2 69.000] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [KENNETT5 161.00] TO [PARAGLD5 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9056 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [KENNETT5 161.00] TO [KENNETT2 69.000] TO [KEN X1 1 13.800] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [KENNETT5 161.00] TO [KENNETT2 69.000] TO [KEN X2 1 13.800] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SIKETAP5 161.00] TO [SIKE SW5 161.00] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SIKESTN5 161.00] TO [G17-202-TAP 161.00] CKT 1 | 7.3899 | 0.1949 | 94.906 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [IDALIA 5 161.00] TO [5ESSEX 161.00] CKT 1 | 7.3899 | 0.1949 | 94.906 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [IDALIA 5 161.00] TO [2IDALIA 69.000] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [IDALIA 5 161.00] TO [2IDALIA 69.000] CKT 2 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [IDALIA 5 161.00] TO [ASHRVL5 161.00] CKT 1 | 7.3899 | 0.1949 | 94.906 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [TRUMAN 5 161.00] TO [5LOSTVALY 161.00] CKT 1 | 7.3898 | 0.1949 | 94.9044 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [TRUMAN 5 161.00] TO [TRU123 1 13.800] CKT 1 | 7.3903 | 0.1949 | 94.9087 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [TRUMAN 5 161.00] TO [TRU456 1 13.800] CKT 1 | 7.3903 | 0.1949 | 94.9087 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [DELWARE4 138.00] TO [FARML 4 138.00] CKT 1 | 7.39 | 0.1949 | 94.9065 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [DELWARE7 345.00] TO [NEOSHO 7 345.00] CKT 1 | 7.3888 | 0.1949 | 94.8972 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [N.E.S.-7 345.00] TO [ONETA--7 345.00] CKT 1 | 7.3894 | 0.1949 | 94.9019 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [N.E.S.-7 345.00] TO [T.NO.--7 345.00] CKT 1 | 7.3895 | 0.1949 | 94.9027 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [N.E.S.-7 345.00] TO [NES3-1 22.000] CKT 1 | 7.3888 | 0.1949 | 94.8967 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [TATONGA7 345.00] CKT 1 | 7.3846 | 0.1949 | 94.9103 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [TATONGA7 345.00] CKT 2 | 7.3845 | 0.1949 | 94.9105 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [G07621119-20345.00] CKT 1 | 7.39 | 0.1949 | 94.9044 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [GUTHRIE7 345.00] CKT 1 | 7.39 | 0.1949 | 94.9056 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [BECKHAM7 345.00] CKT 1 | 7.3781 | 0.1949 | 94.8948 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [G16-003-TAP 345.00] CKT 1 | 7.3783 | 0.1949 | 94.9156 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [G16-003-TAP 345.00] CKT 2 | 7.3783 | 0.1949 | 94.9155 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [WWRDEHV4 138.00] TO [WWDEHV31 13.800] CKT 1 | 7.3893 | 0.1949 | 94.9083 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [WWRDEHV4 138.00] TO [WWDEHV21 13.800] CKT 2 | 7.3893 | 0.1949 | 94.9103 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [DGRASSE7 345.00] TO [THISTLE7 345.00] CKT 1 | 7.384 | 0.1949 | 94.8626 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [DGRASSE7 345.00] TO [THISTLE7 345.00] CKT 2 | 7.384 | 0.1949 | 94.8626 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [DGRASSE4 138.00] TO [KNOBHIL4 138.00] CKT 1 | 7.3897 | 0.1949 | 94.9064 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [DGRASSE4 138.00] TO [ROSEVLY4 138.00] CKT 1 | 7.3897 | 0.1949 | 94.9065 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [DGRASSE4 138.00] TO [MOORLND4 138.00] CKT 1 | 7.3888 | 0.1949 | 94.9055 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WALKMYR2 69.000] TO [NORTH6T2 69.000] CKT 1 | 7.3904 | 0.195 | 94.9515 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WALKMYR2 69.000] TO [WOODS 2 69.000] CKT 1 | 7.3906 | 0.1949 | 94.9497 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WALKMYR3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 4.853 | 0.202 | 102.0008 | 150 | 168 | FAIL | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SEWARD-3 115.00] TO [HASKELL3 115.00] CKT 1 | 5.4759 | 0.2 | 99.9695 | 150 | 168 | FAIL | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SEWARD-3 115.00] TO [CMSSWRD2 69.000] TO [SEWARD 1 13.800] CKT 1 | 7.3856 | 0.1951 | 95.0574 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [POSTROCK7 345.00] CKT 1 | 7.355 | 0.1949 | 94.9107 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [BUCKNER7 345.00] CKT 1 | 7.3509 | 0.1949 | 94.9297 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [IRONWOOD7 345.00] CKT 1 | 7.3808 | 0.1949 | 94.9369 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [SPRVL 3 115.00] TO [SPRVL-T 13.800] CKT 1 | 7.2825 | 0.195 | 94.9926 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [SPEARVL6 230.00] TO [SPERTER1 13.800] CKT 1 | 7.378 | 0.1949 | 94.9182 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HUGOTON3 115.00] TO [GRANTTP3 115.00] CKT 1 | 7.3392 | 0.195 | 95.0041 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HUGOTON3 115.00] TO [ABBK 2 115.00] CKT 1 | 7.3899 | 0.1949 | 94.9409 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HUGOTON3 115.00] TO [HUGOTON2 69.000] TO [HUGOTON1 13.800] CKT 1 | 7.3912 | 0.195 | 95.0191 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HARBNGR3 115.00] TO [HARBNGR7 345.00] TO [HARBNGR-T 13.800] CKT 1 | 5.7481 | 0.1982 | 98.2412 | 150 | 168 | FAIL | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EEC GT1 13.800] TO [DG TIE 1 4.1600] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EEC GT2 13.800] TO [EEC DG 1 4.1600] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC121 13.800] CKT 1 | 7.3902 | 0.1949 | 94.9092 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC341 13.800] CKT 1 | 7.3902 | 0.1949 | 94.9092 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC5 1 18.000] CKT 1 | 7.3904 | 0.1949 | 94.9116 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC6 1 18.000] CKT 1 | 7.3907 | 0.1949 | 94.9137 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC7 1 18.000] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [LANG 7 345.00] CKT 1 | 7.3899 | 0.1949 | 94.9056 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [MORRIS 7 345.00] CKT 1 | 7.3894 | 0.1949 | 94.9031 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [READWF 7 345.00] CKT 1 | 7.3903 | 0.1949 | 94.9093 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [RENO 7 345.00] TO [G16-111-TAP 345.00] CKT 1 | 7.3875 | 0.1949 | 94.8889 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [RENO 7 345.00] TO [RENO 3 115.00] TO [RENO 1X1 14.400] CKT 1 | 7.3902 | 0.1949 | 94.9092 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [RENO 7 345.00] TO [RENO 3 115.00] TO [RENO 2X1 14.400] CKT 1 | 7.3902 | 0.1949 | 94.9093 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUMMIT 7 345.00] TO [GEARY 7 345.00] CKT 1 | 7.3886 | 0.1949 | 94.9112 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUMMIT 7 345.00] TO [G16-111-TAP 345.00] CKT 1 | 7.3882 | 0.1949 | 94.8969 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUMMIT 7 345.00] TO [SUMMIT 6 230.00] TO [SUMMIT 1 14.400] CKT 1 | 7.3899 | 0.1949 | 94.9107 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SWISVAL7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 7.3891 | 0.1949 | 94.9015 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [87TH 7 345.00] TO [STRANGR7 345.00] CKT 1 | 7.3891 | 0.1949 | 94.8992 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [87TH 7 345.00] TO [87TH 3 115.00] TO [87TH 1X1 13.800] CKT 1 | 7.39 | 0.1949 | 94.9065 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [G17-009-TAP 345.00] TO [NEOSHO 7 345.00] CKT 1 | 7.3893 | 0.1949 | 94.9068 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GEN-2017-009345.00] TO [G17-009XFMR134.500] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GEN-2017-009345.00] TO [G17-009XFMR234.500] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CANEYRV7 345.00] TO [CANEYWF7 345.00] CKT 1 | 7.39 | 0.1949 | 94.9066 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CANEYRV7 345.00] TO [LATHAMS7 345.00] CKT 1 | 7.3892 | 0.1949 | 94.9054 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [KINGMAN7 345.00] TO [BUFFALO7 345.00] CKT 1 | 7.3907 | 0.1949 | 94.9103 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NINN1WF7 345.00] TO [PRATTWF7 345.00] CKT 1 | 7.3905 | 0.1949 | 94.91 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NINN1WF7 345.00] TO [N1 LV 1 34.500] TO [N1 WFTX1 13.800] CKT 1 | 7.3902 | 0.1949 | 94.9084 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BENTON 7 345.00] TO [ROSEHIL7 345.00] CKT 1 | 7.3873 | 0.1949 | 94.8993 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BENTON 7 345.00] TO [BENTON 4 138.00] TO [BENTN1 1 13.800] CKT 1 | 7.3896 | 0.1949 | 94.9055 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BENTON 7 345.00] TO [BENTON 4 138.00] TO [BENTN2 1 13.800] CKT 1 | 7.3896 | 0.1949 | 94.9055 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 1 | 7.3879 | 0.1949 | 94.9074 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 2 | 7.3879 | 0.1949 | 94.9074 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [EVANS N4 138.00] TO [WICH11 1 13.800] CKT 1 | 7.3898 | 0.1949 | 94.9076 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [EVANS N4 138.00] TO [WICH12 1 13.800] CKT 1 | 7.3898 | 0.1949 | 94.9079 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WOLFCRK7 345.00] TO [WCGS U1 25.000] CKT 1 | 7.3934 | 0.1949 | 94.9396 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WOLFCRK7 345.00] TO [ROSEHIL7 345.00] CKT 1 | 7.389 | 0.1949 | 94.9018 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WOLFCRK7 345.00] TO [WOLFCRK2 69.000] TO [WOLFCRK1 17.000] CKT 1 | 7.3898 | 0.1949 | 94.9052 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [VIOLA 7 345.00] TO [RENFROW7 345.00] CKT 1 | 7.3838 | 0.1949 | 94.8634 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [VIOLA 7 345.00] TO [G16-153-TAP 345.00] CKT 1 | 7.3902 | 0.1949 | 94.9066 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WAVERLY7 345.00] TO [WAVERTX7 345.00] CKT 1 | 7.3901 | 0.1949 | 94.9076 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EXPEDITION7 345.00] TO [GEN-2014-001345.00] CKT 1 | 7.3903 | 0.1949 | 94.9086 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [N345 1 1 13.800] TO [NEOSHO 7 345.00] TO [NEOSHO 4 138.00] CKT 1 | 7.3899 | 0.1949 | 94.9058 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [N345 2 1 13.800] TO [NEOSHO 7 345.00] TO [NEOSHO 5 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9058 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SWISVAL6 230.00] TO [AUBURN 6 230.00] CKT 1 | 7.3898 | 0.1949 | 94.9053 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SWISVAL6 230.00] TO [LAWHILL6 230.00] CKT 1 | 7.3898 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SWISVAL6 230.00] TO [TECHILL6 230.00] CKT 1 | 7.39 | 0.1949 | 94.9066 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SWISVAL6 230.00] TO [MORRIS 6 230.00] CKT 1 | 7.3896 | 0.1949 | 94.9056 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NMANHT6 230.00] TO [EMANHAT6 230.00] CKT 1 | 7.3899 | 0.1949 | 94.9079 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NMANHT6 230.00] TO [NMANHT3 115.00] TO [NMANHX1 14.400] CKT 1 | 7.3898 | 0.1949 | 94.906 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LITCH 5 161.00] TO [ASB349 5 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9055 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [MARMTNW5 161.00] TO [MARMTNE5 161.00] CKT Z1 | 7.3899 | 0.1949 | 94.9055 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [MARMTNW5 161.00] TO [MARMATN2 69.000] TO [MARMATN1 13.200] CKT 1 | 7.3898 | 0.1949 | 94.9058 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [FRANKLIN5 161.00] TO [G17-005-TAP 161.00] CKT 1 | 7.3897 | 0.1949 | 94.9042 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [FRANKLIN5 161.00] TO [FRANKLIN2 69.000] TO [FRANKLIN1 12.470] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRESWLN4 138.00] TO [MIDLTNT4 138.00] CKT 1 | 7.3898 | 0.1949 | 94.9052 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRESWLN4 138.00] TO [SLATECRK4 138.00] CKT 1 | 7.3898 | 0.1949 | 94.9059 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRESWLN4 138.00] TO [CRESWLN2 69.000] TO [CRESW1 1 13.200] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRESWLN4 138.00] TO [CRESWLS2 69.000] TO [CRESW2 1 13.200] CKT 1 | 7.39 | 0.1949 | 94.9063 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [OXFORD 4 138.00] TO [SUMNER 4 138.00] CKT 1 | 7.3895 | 0.1949 | 94.9041 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [TIMBJCT4 138.00] TO [SUMNER 4 138.00] CKT 1 | 7.3899 | 0.1949 | 94.906 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [TIOGA 4 138.00] TO [TIOGA 2 69.000] TO [TIOGA 1 13.200] CKT 1 | 7.39 | 0.1949 | 94.9063 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [OTTRCRK4 138.00] TO [BUTLER 4 138.00] CKT 1 | 7.3897 | 0.1949 | 94.9058 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [OTTRCRK4 138.00] TO [OTTRCRK3 115.00] TO [OTTRX1 1 13.800] CKT 1 | 7.3897 | 0.1949 | 94.9047 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ALTOONA4 138.00] TO [G17-022-TAP 138.00] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEPARSN4 138.00] TO [G17-022-TAP 138.00] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [TAYLOR 4 138.00] TO [MONTGOM4 138.00] CKT 1 | 7.3898 | 0.1949 | 94.905 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BENTLEY4 138.00] TO [HALSTD 4 138.00] CKT 1 | 7.3897 | 0.1949 | 94.9068 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BENTLEY4 138.00] TO [WWUPLNT4 138.00] CKT 1 | 7.3899 | 0.1949 | 94.906 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEOSHOS4 138.00] TO [TV1MNDV4 138.00] CKT 1 | 7.3898 | 0.1949 | 94.905 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEOSHON4 138.00] TO [NEOSHON2 69.000] TO [NEC U3 12.000] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CHISHLM4 138.00] TO [PARKCTY4 138.00] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CHISHLM4 138.00] TO [17TH 4 138.00] CKT 1 | 7.3895 | 0.1949 | 94.9051 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CHISHLM4 138.00] TO [CHISHLM2 69.000] TO [CHISOLM1 13.200] CKT 1 | 7.3896 | 0.1949 | 94.9057 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EVANS S4 138.00] TO [EVANS N4 138.00] CKT Z1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EVANS S4 138.00] TO [EVANS N4 138.00] CKT Z2 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [FARBER 4 138.00] TO [ELPASOE4 138.00] CKT 1 | 7.3899 | 0.1949 | 94.9057 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GILL 4 138.00] TO [GILL W 4 138.00] CKT Z1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GILL 4 138.00] TO [GILL S 4 138.00] CKT Z1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LAKERDG4 138.00] TO [HOOVERN4 138.00] CKT 1 | 7.3894 | 0.1949 | 94.9029 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [MAIZE 4 138.00] TO [EVANS N4 138.00] CKT 1 | 7.3893 | 0.1949 | 94.9029 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SC10BEL4 138.00] TO [SUMNER 4 138.00] CKT 1 | 7.3899 | 0.1949 | 94.9059 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SG12COL4 138.00] TO [EVANS N4 138.00] CKT 1 | 7.3896 | 0.1949 | 94.9068 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [45TH ST4 138.00] TO [COWSKIN4 138.00] CKT 1 | 7.3894 | 0.1949 | 94.9023 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [VIOLA 4 138.00] TO [SUMNER 4 138.00] CKT 1 | 7.3897 | 0.1949 | 94.9058 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [AEC 3 115.00] TO [G17-120-TAP 115.00] CKT 1 | 7.3894 | 0.1949 | 94.9047 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EABILEN3 115.00] TO [CHAPMAN3 115.00] CKT 1 | 7.3896 | 0.1949 | 94.9065 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NORTHST3 115.00] TO [SALINA 3 115.00] CKT 1 | 7.3895 | 0.1949 | 94.9056 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NORTHVW3 115.00] TO [G17-120-TAP 115.00] CKT 1 | 7.3902 | 0.1949 | 94.9093 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUMMIT 3 115.00] TO [MENTOR 3 115.00] CKT 1 | 7.3901 | 0.1949 | 94.9073 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUMMIT 3 115.00] TO [SO GATE3 115.00] CKT 1 | 7.3898 | 0.1949 | 94.9059 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUMMIT 3 115.00] TO [SUMMIT 6 230.00] TO [SUMIT2 1 13.800] CKT 1 | 7.3899 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUMMIT 3 115.00] TO [SUMMIT 6 230.00] TO [SUMIT3 1 13.800] CKT 1 | 7.3899 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [TIMBJCT2 69.000] TO [AKRON 2 69.000] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [TIMBJCT2 69.000] TO [UDALL 2 69.000] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [TIMBJCT2 69.000] TO [WINFLD 2 69.000] CKT 1 | 7.3899 | 0.1949 | 94.9056 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ALTOO E2 69.000] TO [NEODJCT2 69.000] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ALTOO E2 69.000] TO [RA5HIPR2 69.000] CKT Z1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ALTOO W2 69.000] TO [STUDBKR2 69.000] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LITCH N2 69.000] TO [AQUARS 2 69.000] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LITCH N2 69.000] TO [PITNAC 2 69.000] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LITCH S2 69.000] TO [ROUSE 2 69.000] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LITCH S2 69.000] TO [SOPITT 2 69.000] CKT 1 | 7.3899 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEOSHOS2 69.000] TO [BAKER 2 69.000] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEOSHOS2 69.000] TO [ORDNJCT2 69.000] CKT 1 | 7.3899 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEOSHOS2 69.000] TO [CRAWFOR2 69.000] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEOSHOS2 69.000] TO [NEOSHON2 69.000] CKT Z1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [K1 LV 1 34.500] TO [K1 CLCT1 34.500] CKT 1 | 7.3901 | 0.1949 | 94.9076 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [K2 LV 1 34.500] TO [K2 CLCT1 34.500] CKT 1 | 7.3903 | 0.1949 | 94.9073 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [MILAN_GOAB 138.00] TO [CLDWELL4 138.00] CKT 1 | 7.3895 | 0.1949 | 94.906 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [MILAN_GOAB 138.00] TO [MILAN 4 138.00] CKT 1 | 7.3899 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CONWAY 138.00] TO [MILANTP4 138.00] CKT 1 | 7.3887 | 0.1949 | 94.9065 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [MRWYP16 230.00] TO [MRWYP26 230.00] CKT 1 | 7.3903 | 0.1949 | 94.9078 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [MRWYP16 230.00] TO [MRWYG11 34.500] TO [MRWYP1T1 13.800] CKT 1 | 7.3903 | 0.1949 | 94.9085 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [FLATRDG4 138.00] TO [FLATRWD4 138.00] CKT 1 | 7.3889 | 0.1949 | 94.9072 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [FLATRDG4 138.00] TO [HARPER 4 138.00] CKT 1 | 7.3867 | 0.1949 | 94.9047 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [FLATRDG4 138.00] TO [BARBER 4 138.00] CKT 1 | 7.3805 | 0.1949 | 94.9183 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ELMCREK6 230.00] TO [ELMCREEK7 345.00] TO [ELMCREEK1 13.800] CKT 1 | 7.3898 | 0.1949 | 94.9063 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAYNE3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 7.2212 | 0.1959 | 95.9122 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [KISMET 3 115.00] TO [CUDAHY 3 115.00] CKT 1 | 6.1038 | 0.1993 | 99.3456 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CMRIVTP3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 6.7171 | 0.1979 | 97.9447 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CONCRD6 230.00] TO [CONCORD3 115.00] TO [CONCOD-T 13.800] CKT 1 | 7.3904 | 0.1949 | 94.9103 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [E-LIBER3 115.00] TO [TXPHSF 3115.00] CKT 1 | 6.3681 | 0.1968 | 96.7817 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [E-LIBER3 115.00] TO [E-PINE 3 115.00] CKT 1 | 7.3758 | 0.1954 | 95.3893 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [E-LIBER3 115.00] TO [NATBEEF3 115.00] CKT 1 | 7.2678 | 0.1946 | 94.6377 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [E-LIBER3 115.00] TO [E-LIBER1 34.500] TO [ELIB-T 2.4000] CKT 1 | 7.3862 | 0.1954 | 95.3932 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NLIB 3 115.00] TO [W-LIBER3 115.00] CKT 1 | 7.3818 | 0.1954 | 95.4011 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NLIB 3 115.00] TO [NATBEEF3 115.00] CKT 1 | 7.2444 | 0.1952 | 95.1651 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NLIB 3 115.00] TO [NLIB 1 34.500] TO [N-LIB-T 13.800] CKT 1 | 7.3641 | 0.1956 | 95.6085 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [N-CIMRN3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 5.4537 | 0.2009 | 100.8838 | 150 | 168 | FAIL | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CIM-PLT 13.800] TO [CIM-PLT3 115.00] CKT 1 | 7.3278 | 0.1973 | 97.2595 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [THISTLE7 345.00] CKT 1 | 7.3682 | 0.1949 | 94.8669 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [THISTLE7 345.00] CKT 2 | 7.3682 | 0.1949 | 94.8669 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [THISTLE T1 13.800] TO [THISTLE7 345.00] TO [THISTLE4 138.00] CKT 1 | 7.3905 | 0.1949 | 94.9132 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [TRANSFORMER 345.00] TO [SUB34.5KVB 34.500] TO [TERTIARYBUS 19.900] CKT 1 | 7.3934 | 0.1949 | 94.9371 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GEN-2011-008345.00] TO [G-2011-008-1345.00] CKT 1 | 7.3913 | 0.1949 | 94.9209 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GEN-2011-008345.00] TO [G-2011-008-2345.00] CKT 1 | 7.3907 | 0.1949 | 94.9142 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GEN-2011-008345.00] TO [G-2011-008-3345.00] CKT 1 | 7.3925 | 0.1949 | 94.9156 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [MULLNCR7 345.00] TO [HOLT 7 345.00] CKT 1 | 7.3897 | 0.1949 | 94.9042 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [PECULR 7 345.00] TO [PHILL 7 345.00] CKT 1 | 7.3902 | 0.1949 | 94.9078 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [PECULR 7 345.00] TO [PECULR 5 161.00] TO [PECULRT 13.800] CKT 11 | 7.3899 | 0.1949 | 94.906 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ST JOE 7 345.00] TO [G17-183-TAP 345.00] CKT 1 | 7.39 | 0.1949 | 94.9067 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ARCHIE 5 161.00] TO [G17-108-TAP 161.00] CKT 1 | 7.3899 | 0.1949 | 94.906 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WINDSR 5 161.00] TO [5SEDALA 161.00] CKT 1 | 7.39 | 0.1949 | 94.9067 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HSNVL 5 161.00] TO [5SHARSNV 161.00] CKT 1 | 7.3899 | 0.1949 | 94.906 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HSNVL 5 161.00] TO [PHILL 5 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9053 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HSNVL 5 161.00] TO [HSNVL 2 69.000] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HSNVL 5 161.00] TO [HSNVL 2 69.000] CKT 2 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ADRIAN 5 161.00] TO [5BUTLER 161.00] CKT 1 | 7.3897 | 0.1949 | 94.9042 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CLINTON5 161.00] TO [CLNTN N2 69.000] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CLINTON5 161.00] TO [CLNTN S2 69.000] CKT 2 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ST JOE 5 161.00] TO [ST JOE_CAP5 161.00] CKT R | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ST JOE 5 161.00] TO [COOK 5 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ST JOE 5 161.00] TO [WOODBIN5 161.00] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ST JOE 5 161.00] TO [AVENUECTY 5 161.00] CKT 1 | 7.39 | 0.1949 | 94.9065 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP#1 13.800] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP#2 13.800] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP#3 13.800] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP 2 69.000] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [PECULRS5 161.00] CKT 1 | 7.3899 | 0.1949 | 94.906 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EASTOWN7 345.00] TO [EASTOWN5 161.00] TO [EASTOWN1 13.800] CKT 11 | 7.3899 | 0.1949 | 94.9065 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [KETCHEM7 345.00] TO [SIBLEY 7 345.00] CKT 1 | 7.3893 | 0.1949 | 94.9012 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [KETCHEM7 345.00] TO [OSBORN7 345.00] CKT 1 | 7.3905 | 0.1949 | 94.9107 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ROCKCK7 345.00] TO [HOLT 7 345.00] CKT 1 | 7.3908 | 0.1949 | 94.913 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ROCKCK_T1_1 34.500] TO [ROCKCK_P1_1 34.500] CKT 1 | 7.3902 | 0.1949 | 94.9077 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ROCKCK_T2_1 34.500] TO [ROCKCK_P2_1 34.500] CKT 1 | 7.3902 | 0.1949 | 94.9081 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HOLT_REACT7 345.00] TO [HOLT 7 345.00] CKT Z1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [OUTLAW 345.00] TO [OUTLAW_T2_1 34.500] TO [OUTLAW_TR2_113.800] CKT 1 | 7.3902 | 0.1949 | 94.9082 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [OUTLAW 345.00] TO [OUTLAW_T1_1 34.500] TO [OUTLAW_TR1_113.800] CKT 1 | 7.3901 | 0.1949 | 94.9076 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [W.GRDNR7 345.00] TO [WGAR T11 13.800] CKT 11 | 7.39 | 0.1949 | 94.9063 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [STILWEL7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 7.3897 | 0.1949 | 94.9043 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [G17-108-TAP 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9059 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTH 7 345.00] TO [SIBLEY 7 345.00] CKT 1 | 7.3899 | 0.1949 | 94.906 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTH 7 345.00] TO [HAWTHN5 161.00] TO [HAWT T20 13.800] CKT 20 | 7.3899 | 0.1949 | 94.9057 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTH 7 345.00] TO [HAWTHN5 161.00] TO [HAWT T22 13.800] CKT 22 | 7.3899 | 0.1949 | 94.9059 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAW G9 1 13.800] CKT 1 | 7.3906 | 0.1949 | 94.9111 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [LEEDS 5 161.00] CKT 1 | 7.3899 | 0.1949 | 94.906 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [LEEDS 5 161.00] CKT 2 | 7.3899 | 0.1949 | 94.906 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTH_B2_1 13.200] CKT 1 | 7.3898 | 0.1949 | 94.905 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [BRMGHAM5 161.00] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHS_G65 161.00] CKT Z1 | 7.3905 | 0.1949 | 94.9109 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHS_XF5 161.00] CKT Z2 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHN5 161.00] CKT @1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHN5 161.00] CKT @2 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRAIG 7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 7.3905 | 0.1949 | 94.9105 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [CRAIG_CAP 5 161.00] CKT R | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [PFLUMM 5 161.00] CKT 1 | 7.39 | 0.1949 | 94.9063 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [LENEXA 5 161.00] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [LENEXA 5 161.00] CKT 2 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [COLLEGE5 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9058 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NASHUA 7 345.00] TO [G17-183-TAP 345.00] CKT 1 | 7.3895 | 0.1949 | 94.9026 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 7.3908 | 0.1949 | 94.9132 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [G17-209-TAP 345.00] CKT 1 | 7.3888 | 0.1949 | 94.8967 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [STRANGR7 345.00] CKT 1 | 7.3899 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [STRANGR7 345.00] CKT 2 | 7.3899 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [IAT G1 1 24.000] CKT 1 | 7.3947 | 0.1949 | 94.9446 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [IAT G2 1 24.500] CKT 1 | 7.3949 | 0.1949 | 94.9466 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [IATAN5 161.00] TO [IATAN 11 14.400] CKT 11 | 7.3899 | 0.1949 | 94.9055 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HICKMAN5 161.00] TO [STHTOWN5 161.00] CKT 1 | 7.39 | 0.1949 | 94.9065 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BLUMILS5 161.00] TO [BLUVLY-161 161.00] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NASHUA-5 161.00] TO [NASHUA 5 161.00] CKT Z1 | 7.3899 | 0.1949 | 94.906 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NASHUA-5 161.00] TO [RNRIDGE5 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9058 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NASHUA-5 161.00] TO [SHOLCRK5 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9057 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CEDRCRK5 161.00] TO [SHWNMSN5 161.00] CKT 1 | 7.39 | 0.1949 | 94.9063 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ANTIOCH5 161.00] TO [OXFORD 5 161.00] CKT 1 | 7.39 | 0.1949 | 94.9067 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [REDEL 5 161.00] TO [MARTCIT5 161.00] CKT 1 | 7.39 | 0.1949 | 94.9066 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BUCYRUS5 161.00] TO [NLOUISB5 161.00] CKT 1 | 7.3898 | 0.1949 | 94.9056 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BUCYRUS5 161.00] TO [WAGSTAF5 161.00] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [PLSTVAL5 161.00] TO [SEOTTWA5 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9055 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [PLSTVAL5 161.00] TO [ASG-2018-010161.00] CKT 1 | 7.3901 | 0.1949 | 94.9076 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [PLSTVAL5 161.00] TO [PLSTVAL1 34.500] TO [PLSTVL2_TER17.6210] CKT 2 | 7.3899 | 0.1949 | 94.9058 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LAKCTYJ2 69.000] TO [LAKCTY 2 69.000] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 1 13.800] CKT 1 | 7.3903 | 0.1949 | 94.9091 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 2 13.800] CKT 1 | 7.3903 | 0.1949 | 94.9091 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 3 13.800] CKT 1 | 7.3903 | 0.1949 | 94.9091 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 4 13.800] CKT 1 | 7.3903 | 0.1949 | 94.9091 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LACKMAN5 161.00] TO [SPRGHL 5 161.00] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BNSF 5 161.00] TO [MOONLT 5 161.00] CKT 1 | 7.39 | 0.1949 | 94.9066 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WGARDNR1 34.500] TO [BALDWINCTY1 34.500] CKT 1 | 7.39 | 0.1949 | 94.9064 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LACYGNE11_7 345.00] TO [LAC11_AQC1 13.800] TO [LAC11_TER1 13.800] CKT 11 | 7.3897 | 0.1949 | 94.905 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LACYGNE22_7 345.00] TO [LAC22_AQC1 13.800] TO [LAC22_TER1 13.800] CKT 22 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LACYGNE2 69.000] TO [LAC_LAKE_2 69.000] CKT 1 | 7.3899 | 0.1949 | 94.9057 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LAC3_STAR7 345.00] TO [LAC3_X1 6.9000] CKT X | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LAC3_STAR7 345.00] TO [LAC3_Y1 6.9000] CKT Y | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LAC3_STAR7 345.00] TO [LAC3_Z1 3.9800] CKT Z | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LAC8_STAR7 345.00] TO [LAC8_X1 6.9000] CKT X | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LAC8_STAR7 345.00] TO [LAC8_Y1 6.9000] CKT Y | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LAC8_STAR7 345.00] TO [LAC8_Z1 4.0000] CKT Z | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [RIV4525 161.00] TO [ORO110 5 161.00] CKT 1 | 7.39 | 0.1949 | 94.9064 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [RIV4525 161.00] TO [STL439 5 161.00] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [RIV4525 161.00] TO [RIV452T 5 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9059 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [RIV4525 161.00] TO [BAX488 5 161.00] CKT 1 | 7.3898 | 0.1949 | 94.9046 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [RIV4525 161.00] TO [RIV167 2 69.000] TO [RIV452 1 12.500] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CJ 366 5 161.00] TO [ASB349 5 161.00] CKT 1 | 7.3899 | 0.1949 | 94.906 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CAR395 5 161.00] TO [CARTHAG5 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9059 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [FIR417 5 161.00] TO [ORO110 5 161.00] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [PUR421 5 161.00] TO [ASB349 5 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9059 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [A1G349 1 13.800] TO [ASB349 5 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [A2G349 1 13.800] TO [ASB349 5 161.00] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB K 69.000] TO [SUB R 69.000] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB H 69.000] TO [COURTNY2 69.000] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB H 69.000] TO [SUGRCK_TP_E269.000] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB H 69.000] TO [SUB H-13B1 13.800] CKT H1 | 7.3899 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB H 69.000] TO [SUB H-13B2 13.800] CKT H2 | 7.39 | 0.1949 | 94.9063 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [BLUVLY-161 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [BLUVLY-161 161.00] CKT 2 | 7.3899 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ECKLES-161 161.00] TO [5LEVASY 161.00] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ECKLES-161 161.00] TO [5MOCITYB1 161.00] CKT 1 | 7.39 | 0.1949 | 94.9064 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ECKLES-161 161.00] TO [SIBLEYPL 161.00] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB J 69.000] TO [SUB J-13B1 13.800] CKT J1 | 7.39 | 0.1949 | 94.9063 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB J 69.000] TO [SUB J-13B2 13.800] CKT J2 | 7.3899 | 0.1949 | 94.9058 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB M-161 161.00] TO [BLUVLY-161 161.00] CKT 1 | 7.3899 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB M 69.000] TO [SHRNKRD 69.000] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB P 69.000] TO [SUB I 69.000] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [G16-046-TAP 345.00] TO [IRONWOOD7 345.00] CKT 1 | 7.3782 | 0.1949 | 94.9141 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [G16-046-TAP 345.00] TO [GEN-2016-046345.00] CKT 1 | 7.3809 | 0.1949 | 94.9279 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GEN-2017-004345.00] TO [G17-004XFMR134.500] CKT 1 | 7.3906 | 0.1949 | 94.9117 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [G17-004-TAP 345.00] TO [ELMCREEK7 345.00] CKT 1 | 7.3895 | 0.1949 | 94.9032 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GEN-2017-018345.00] TO [THISTLE7 345.00] CKT 1 | 7.3913 | 0.1949 | 94.9164 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [G17-018XFMR134.500] TO [G17-018-GSU134.500] CKT 1 | 7.3905 | 0.1949 | 94.9107 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [G17-018XFMR234.500] TO [G17-018-GSU234.500] CKT 1 | 7.3905 | 0.1949 | 94.9107 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GEN-2017-068138.00] TO [EVANS N4 138.00] CKT 1 | 7.3903 | 0.1949 | 94.9087 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [G17-068XFMR134.500] TO [G17-068-GSU134.500] CKT 1 | 7.3903 | 0.1949 | 94.9087 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GEN-2017-082161.00] TO [ASB349 5 161.00] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [G17-082XFMR134.500] TO [G17-082-GSU134.500] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [ATCHSN 3 345.00] CKT 1 | 7.3899 | 0.1949 | 94.9055 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [COOPER1G 22.000] CKT 1 | 7.3976 | 0.195 | 94.9683 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [MONOLITH 3 345.00] CKT 1 | 7.3909 | 0.1949 | 94.9145 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [COOPER 5 161.00] TO [COOPER T2 913.800] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [COOPER 5 161.00] TO [COOPER T5 913.800] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEBCTY1G 18.000] TO [NC1GA1X9 4.2000] TO [NC1GA1Y9 4.2000] CKT 1 | 7.3897 | 0.1949 | 94.9048 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEBCTY1G 18.000] TO [NC1GA2X9 4.2000] TO [NC1GA2Y9 4.2000] CKT 1 | 7.3897 | 0.1949 | 94.9048 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEBCTY2G 23.000] TO [NC2GA1X9 4.2000] TO [NC2GA1Y9 4.2000] CKT 1 | 7.3899 | 0.1949 | 94.9055 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEBCTY2G 23.000] TO [NC2GA2X9 13.800] TO [NC2GA2Y9 13.800] CKT 1 | 7.3895 | 0.1949 | 94.9025 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S3456 3 345.00] TO [CBLUFFS3 345.00] CKT 1 | 7.3901 | 0.1949 | 94.9077 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S3456 3 345.00] TO [S3455 3 345.00] CKT 1 | 7.39 | 0.1949 | 94.9065 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S3456 3 345.00] TO [S3459 3 345.00] CKT 1 | 7.39 | 0.1949 | 94.9067 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S3456 3 345.00] TO [S1206 5 161.00] TO [S3456T49 13.800] CKT 1 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S3458 3 345.00] TO [HOLT 7 345.00] CKT 1 | 7.3904 | 0.1949 | 94.9099 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S3740 3 345.00] TO [CASS 1G 15.000] CKT 1 | 7.3914 | 0.1949 | 94.9182 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S3740 3 345.00] TO [CASS 2G 15.000] CKT 1 | 7.3914 | 0.1949 | 94.9181 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S3740 3 345.00] TO [S3454 3 345.00] CKT 1 | 7.39 | 0.1949 | 94.9068 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S3740 3 345.00] TO [S3455 3 345.00] CKT 1 | 7.39 | 0.1949 | 94.9064 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S3740 3 345.00] TO [GEN-2018-033345.00] CKT 1 | 7.39 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [103&ROKEBY3 345.00] TO [MOORE 3 345.00] CKT 1 | 7.3898 | 0.1949 | 94.9061 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [103&ROKEBY3 345.00] TO [WAGENER 3 345.00] CKT 1 | 7.3899 | 0.1949 | 94.9057 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [7SPORTSMAN 345.00] TO [5SPORTSMAN 161.00] CKT 2 | 7.3901 | 0.1949 | 94.9075 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [IDALIA 5 161.00] TO [2IDALIA 69.000] CKT 2 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [TATONGA7 345.00] CKT 2 | 7.3634 | 0.1949 | 94.9354 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [G16-003-TAP 345.00] CKT 2 | 7.2465 | 0.195 | 94.9511 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [DGRASSE7 345.00] TO [THISTLE7 345.00] CKT 2 | 7.3496 | 0.1946 | 94.5967 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 2 | 7.3496 | 0.1949 | 94.8967 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EVANS S4 138.00] TO [EVANS N4 138.00] CKT Z2 | 7.3882 | 0.1949 | 94.8932 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [THISTLE7 345.00] CKT 2 | 7.2932 | 0.1947 | 94.691 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HSNVL 5 161.00] TO [HSNVL 2 69.000] CKT 2 | 7.39 | 0.1949 | 94.9063 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [LEEDS 5 161.00] CKT 2 | 7.3899 | 0.1949 | 94.9054 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHN5 161.00] CKT @2 | 7.3898 | 0.1949 | 94.9051 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [LENEXA 5 161.00] CKT 2 | 7.39 | 0.1949 | 94.9065 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [STRANGR7 345.00] CKT 2 | 7.3898 | 0.1949 | 94.906 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [BLUVLY-161 161.00] CKT 2 | 7.39 | 0.1949 | 94.9062 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | Base | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [7FAIRPT 345.00] TO [ST JOE 7 345.00] CKT 1 | 7.2299 | 0.1963 | 96.2855 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [7FAIRPT 345.00] TO [COOPER 3 345.00] CKT 1 | 7.2296 | 0.1963 | 96.2829 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [5HOLDENB2 161.00] CKT 1 | 7.2297 | 0.1963 | 96.284 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [2CLINTN 69.000] CKT 1 | 7.2299 | 0.1963 | 96.2855 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [2CLINTN 69.000] CKT 3 | 7.2299 | 0.1963 | 96.2855 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [5OSCEOKCTP 161.00] CKT 1 | 7.2297 | 0.1963 | 96.2836 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [TRUMAN 5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2848 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [WINDSR 5 161.00] CKT 1 | 7.23 | 0.1963 | 96.2862 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [CLINTON5 161.00] CKT Z1 | 7.2299 | 0.1963 | 96.2857 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [N MADRD5 161.00] CKT 1 | 7.23 | 0.1963 | 96.2857 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [SIKETAP5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2853 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [7BLACKBERRY 345.00] TO [7SPORTSMAN 345.00] CKT 1 | 7.2298 | 0.1963 | 96.2849 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [7BLACKBERRY 345.00] TO [7JASPER 345.00] CKT 1 | 7.2312 | 0.1963 | 96.2967 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [7BLACKBERRY 345.00] TO [WOLFCRK7 345.00] CKT 1 | 7.2277 | 0.1963 | 96.269 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5MINER 1 161.00] TO [SIKESTN5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2852 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [N MADRD5 161.00] TO [KENNETT5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2848 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [N MADRD5 161.00] TO [N MADRD2 69.000] TO [NMA X1 1 13.800] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [N MADRD5 161.00] TO [N MADRD2 69.000] TO [NMA X2 1 13.800] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SIKETAP5 161.00] TO [SIKESTN5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2853 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SIKESTN5 161.00] TO [SIKGEN 1 13.800] CKT 1 | 7.2303 | 0.1963 | 96.2886 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SIKESTN5 161.00] TO [IDALIA 5 161.00] CKT 1 | 7.23 | 0.1963 | 96.2857 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SIKESTN5 161.00] TO [SIKESTN2 69.000] TO [SIK X1 1 13.800] CKT 1 | 7.2298 | 0.1963 | 96.2845 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [DELAWAR1 13.800] TO [DELWARE4 138.00] TO [DELWARE7 345.00] CKT 1 | 7.23 | 0.1963 | 96.2859 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [DELWARE7 345.00] TO [N.E.S.-7 345.00] CKT 1 | 7.2293 | 0.1963 | 96.2807 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [DGRASSE7 345.00] CKT 1 | 7.2244 | 0.1962 | 96.2455 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [DGRASSE7 345.00] CKT 2 | 7.2244 | 0.1962 | 96.2455 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [DGRASSE7 345.00] TO [DGRASSE4 138.00] TO [DGRASSE1 13.800] CKT 1 | 7.2252 | 0.1963 | 96.2913 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WALKMYR1 13.800] TO [WALKMYR2 69.000] TO [WALKMYR3 115.00] CKT 1 | 7.2277 | 0.1963 | 96.27 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WALKMYR3 115.00] TO [HUGOTON3 115.00] CKT 1 | 7.2053 | 0.1965 | 96.4525 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WALKMYR3 115.00] TO [HARBNGR3 115.00] CKT 1 | 5.5341 | 0.2012 | 101.1647 | 150 | 168 | FAIL | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SEWARD-3 115.00] TO [N-CIMRN3 115.00] CKT 1 | 5.4559 | 0.2022 | 102.2205 | 150 | 168 | FAIL | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [CLARKCOUNTY7345.00] CKT 1 | 7.2179 | 0.1963 | 96.2902 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NSES 2X1 13.200] TO [NEOSHO 4 138.00] TO [NEOSHOS2 69.000] CKT 1 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EEC GT1 13.800] TO [EVANS S4 138.00] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EEC GT2 13.800] TO [EVANS S4 138.00] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EEC GT3 18.000] TO [EVANS S4 138.00] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [SWISVAL7 345.00] CKT 1 | 7.2294 | 0.1963 | 96.2852 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EXPEDITION7 345.00] CKT 1 | 7.2268 | 0.1963 | 96.2874 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [RENO 7 345.00] TO [WICHITA7 345.00] CKT 1 | 7.2301 | 0.1963 | 96.2852 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUMMIT 7 345.00] TO [G17-004-TAP 345.00] CKT 1 | 7.2296 | 0.1963 | 96.2836 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SWISVAL7 345.00] TO [SWISVAL6 230.00] TO [SWISV1X1 14.400] CKT 1 | 7.2299 | 0.1963 | 96.2857 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SWISVAL7 345.00] TO [SWISVAL6 230.00] TO [SWISV2X2 14.400] CKT 2 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [87TH 7 345.00] TO [CRAIG 7 345.00] CKT 1 | 7.2291 | 0.1963 | 96.279 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [G17-009-TAP 345.00] TO [GEN-2017-009345.00] CKT 1 | 7.23 | 0.1963 | 96.2855 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [G17-009-TAP 345.00] TO [CANEYRV7 345.00] CKT 1 | 7.2284 | 0.1963 | 96.2825 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [KINGMAN7 345.00] TO [NINN1WF7 345.00] CKT 1 | 7.231 | 0.1963 | 96.2934 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [KINGMAN7 345.00] TO [K1 LV 1 34.500] TO [K1 WFTX1 13.800] CKT 1 | 7.2302 | 0.1963 | 96.2879 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [KINGMAN7 345.00] TO [K2 LV 1 34.500] TO [K2 WFTX1 13.800] CKT 1 | 7.2302 | 0.1963 | 96.2878 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BENTON 7 345.00] TO [WICHITA7 345.00] CKT 1 | 7.221 | 0.1963 | 96.2763 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BENTON 7 345.00] TO [WOLFCRK7 345.00] CKT 1 | 7.2283 | 0.1963 | 96.285 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [VIOLA 7 345.00] CKT 1 | 7.2274 | 0.1963 | 96.2703 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [EXPEDITION7 345.00] CKT 1 | 7.2263 | 0.1963 | 96.2826 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WOLFCRK7 345.00] TO [WAVERLY7 345.00] CKT 1 | 7.2303 | 0.1963 | 96.2904 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [VIOLA 7 345.00] TO [VIOLA 4 138.00] TO [VIOLA1X1 13.800] CKT 1 | 7.23 | 0.1963 | 96.286 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [VIOLA 7 345.00] TO [VIOLA 4 138.00] TO [SCJ1X1 13.800] CKT 2 | 7.23 | 0.1963 | 96.2861 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WAVERLY7 345.00] TO [LACYGNE7 345.00] CKT 1 | 7.2307 | 0.1963 | 96.2933 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NMANHT6 230.00] TO [ELMCREK6 230.00] CKT 1 | 7.2292 | 0.1963 | 96.2838 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LITCH 5 161.00] TO [FRANKLIN5 161.00] CKT 1 | 7.2298 | 0.1963 | 96.2842 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LITCH 5 161.00] TO [LITCH S2 69.000] TO [LITCH1 1 13.200] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LITCH 5 161.00] TO [LITCH N2 69.000] TO [LITCH2 1 13.200] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [MARMTNW5 161.00] TO [NEOSHO 5 161.00] CKT 1 | 7.23 | 0.1963 | 96.2859 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEOSHO 5 161.00] TO [RIV4525 161.00] CKT 1 | 7.2296 | 0.1963 | 96.2833 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEOSHO 5 161.00] TO [NEOSHO 4 138.00] TO [NEOSH4 1 13.200] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEOSHO 5 161.00] TO [NEOSHOS4 138.00] TO [NEOSH5 1 13.200] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRESWLN4 138.00] TO [OXFORD 4 138.00] CKT 1 | 7.2294 | 0.1963 | 96.2833 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [TCROCK 4 138.00] TO [TIMBJCT4 138.00] CKT 1 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [TIMBJCT4 138.00] TO [TIMBJCT2 69.000] TO [TIMBJCT1 13.200] CKT 1 | 7.2297 | 0.1963 | 96.2854 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [TIOGA 4 138.00] TO [ALTOONA4 138.00] CKT 1 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [OTTRCRK4 138.00] TO [ALTOONA4 138.00] CKT 1 | 7.2296 | 0.1963 | 96.2844 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ALTOONA4 138.00] TO [TAYLOR 4 138.00] CKT 1 | 7.2297 | 0.1963 | 96.284 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ALTOONA4 138.00] TO [ALTOO W2 69.000] TO [ALTOO1 1 13.200] CKT 1 | 7.2299 | 0.1963 | 96.2855 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ALTOONA4 138.00] TO [ALTOO E2 69.000] TO [ALTOO3 1 13.200] CKT 1 | 7.2299 | 0.1963 | 96.2855 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEPARSN4 138.00] TO [NEOSHON4 138.00] CKT 1 | 7.2299 | 0.1963 | 96.2857 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BENTLEY4 138.00] TO [SG12COL4 138.00] CKT 1 | 7.2299 | 0.1963 | 96.2875 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEOSHOS4 138.00] TO [NEOSHO 4 138.00] CKT Z1 | 7.2299 | 0.1963 | 96.2855 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEOSHO 4 138.00] TO [NEOSHON4 138.00] CKT Z1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CHISHLM4 138.00] TO [MAIZE 4 138.00] CKT 1 | 7.2293 | 0.1963 | 96.283 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CLEARWT4 138.00] TO [GILL 4 138.00] CKT 1 | 7.23 | 0.1963 | 96.2862 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CLEARWT4 138.00] TO [VIOLA 4 138.00] CKT 1 | 7.2298 | 0.1963 | 96.2861 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EVANS S4 138.00] TO [LAKERDG4 138.00] CKT 1 | 7.2294 | 0.1963 | 96.2825 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EVANS S4 138.00] TO [45TH ST4 138.00] CKT 1 | 7.2294 | 0.1963 | 96.2825 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [FARBER 4 138.00] TO [SC10BEL4 138.00] CKT 1 | 7.2299 | 0.1963 | 96.2855 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GILL 4 138.00] TO [VIOLA 4 138.00] CKT 1 | 7.2299 | 0.1963 | 96.286 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [VIOLA 4 138.00] TO [MILAN_GOAB 138.00] CKT 1 | 7.2295 | 0.1963 | 96.2857 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [VIOLA 4 138.00] TO [CONWAY 138.00] CKT 1 | 7.2286 | 0.1963 | 96.2863 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [AEC 3 115.00] TO [EABILEN3 115.00] CKT 1 | 7.2291 | 0.1963 | 96.2809 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [AEC 3 115.00] TO [AEC E1 34.500] CKT 2 | 7.2298 | 0.1963 | 96.2852 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [AEC 3 115.00] TO [AEC W1 34.500] CKT 1 | 7.2296 | 0.1963 | 96.2841 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NORTHST3 115.00] TO [NORTHVW3 115.00] CKT 1 | 7.2297 | 0.1963 | 96.2857 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NORTHVW3 115.00] TO [SUMMIT 3 115.00] CKT 1 | 7.2299 | 0.1963 | 96.2862 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LITCH N2 69.000] TO [LITCH S2 69.000] CKT Z1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [MRWYP16 230.00] TO [ELMCREK6 230.00] CKT 1 | 7.2308 | 0.1963 | 96.2921 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [FLATRDG4 138.00] TO [THISTLE4 138.00] CKT 1 | 7.2301 | 0.1963 | 96.2882 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ELMCREK6 230.00] TO [CONCRD6 230.00] CKT 1 | 7.2305 | 0.1963 | 96.2908 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAYNE3 115.00] TO [NLIB 3 115.00] CKT 1 | 7.0651 | 0.197 | 96.9908 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [KISMET 3 115.00] TO [CMRIVTP3 115.00] CKT 1 | 5.9667 | 0.2015 | 101.4834 | 150 | 168 | FAIL | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CMRIVTP3 115.00] TO [E-LIBER3 115.00] CKT 1 | 7.1819 | 0.1965 | 96.5177 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CIM-PLT1 13.800] TO [CIM-PLT 13.800] CKT Z1 | 7.2338 | 0.1969 | 96.8771 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [N-CIMRN3 115.00] TO [N-CMRN 1 34.500] TO [N-CMRN-T 13.800] CKT 1 | 7.2233 | 0.1965 | 96.4577 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [TRANSFORMER 345.00] CKT 1 | 7.232 | 0.1963 | 96.3046 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [GEN-2011-008345.00] CKT 1 | 7.2354 | 0.1963 | 96.3312 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [G16-046-TAP 345.00] CKT 1 | 7.2207 | 0.1963 | 96.2775 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [MULLNCR7 345.00] TO [MC REAC1 345.00] CKT Z1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [MULLNCR7 345.00] TO [MC REAC2 345.00] CKT Z1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [MULLNCR7 345.00] TO [MC REAC3 345.00] CKT Z1 | 7.23 | 0.1963 | 96.2857 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [MULLNCR7 345.00] TO [KETCHEM7 345.00] CKT 1 | 7.2285 | 0.1963 | 96.2737 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [PECULR 7 345.00] TO [STILWEL7 345.00] CKT 1 | 7.2304 | 0.1963 | 96.2894 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ST JOE 7 345.00] TO [EASTOWN7 345.00] CKT 1 | 7.2302 | 0.1963 | 96.2877 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ST JOE 7 345.00] TO [COOPER 3 345.00] CKT 1 | 7.2295 | 0.1963 | 96.2818 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ST JOE 7 345.00] TO [ST JOE 5 161.00] TO [STJOE 1T 13.800] CKT 22 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ST JOE 7 345.00] TO [ST JOE 5 161.00] TO [STJOE 2T 13.800] CKT 33 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ARCHIE 5 161.00] TO [HSNVL 5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2851 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ARCHIE 5 161.00] TO [ADRIAN 5 161.00] CKT 1 | 7.2296 | 0.1963 | 96.2828 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ARCHIE 5 161.00] TO [S.HARP 5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2848 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [STILWEL5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2855 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EASTOWN7 345.00] TO [IATAN 7 345.00] CKT 1 | 7.2308 | 0.1963 | 96.292 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ROCKCK_TR1_113.200] TO [ROCKCK7 345.00] TO [ROCKCK_T1_1 34.500] CKT 1 | 7.2309 | 0.1963 | 96.2931 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ROCKCK_TR2_113.200] TO [ROCKCK7 345.00] TO [ROCKCK_T2_1 34.500] CKT 1 | 7.2309 | 0.1963 | 96.2929 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ROCKCK7 345.00] TO [OUTLAW 345.00] CKT 1 | 7.2315 | 0.1963 | 96.2979 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LAC G1 1 22.000] TO [LACYGNE7 345.00] CKT 1 | 7.2332 | 0.1963 | 96.3116 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LAC G2 1 24.000] TO [LACYGNE7 345.00] CKT 1 | 7.2329 | 0.1963 | 96.3092 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [CEDRCRK5 161.00] CKT 1 | 7.23 | 0.1963 | 96.286 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [CEDARNL5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2852 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [PLSTVAL5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2854 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [BULLCRK5 161.00] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [BNSF 5 161.00] CKT 1 | 7.23 | 0.1963 | 96.2861 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [WGARDNR1 34.500] CKT 7 | 7.2298 | 0.1963 | 96.2847 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [STILWEL7 345.00] TO [LACYGNE7 345.00] CKT 1 | 7.2323 | 0.1963 | 96.3037 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [STILWEL7 345.00] TO [STILWEL5 161.00] TO [STIL T11 13.800] CKT 11 | 7.23 | 0.1963 | 96.286 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [STILWEL7 345.00] TO [STILWEL5 161.00] TO [STIL T22 13.800] CKT 22 | 7.23 | 0.1963 | 96.286 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [HICKMAN5 161.00] CKT 1 | 7.23 | 0.1963 | 96.2864 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [ANTIOCH5 161.00] CKT 1 | 7.23 | 0.1963 | 96.2863 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [REDEL 5 161.00] CKT 1 | 7.23 | 0.1963 | 96.2863 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [BUCYRUS5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2848 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [LACKMAN5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2855 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTH 7 345.00] TO [NASHUA 7 345.00] CKT 1 | 7.2293 | 0.1963 | 96.2805 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [SUB M-161 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2855 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRAIG 7 345.00] TO [CRAIG 5 161.00] TO [CRAI T11 13.800] CKT 11 | 7.2299 | 0.1963 | 96.2854 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRAIG 7 345.00] TO [CRAIG 5 161.00] TO [CRAI T22 13.800] CKT 22 | 7.2299 | 0.1963 | 96.2854 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRAIG 7 345.00] TO [CRAIG 5 161.00] TO [CRAI T33 13.800] CKT 33 | 7.2299 | 0.1963 | 96.2855 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [CEDRCRK5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2855 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NASHUA 7 345.00] TO [IATAN 7 345.00] CKT 1 | 7.2298 | 0.1963 | 96.2842 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NASHUA 7 345.00] TO [NASHUA-5 161.00] TO [NASH T11 13.800] CKT 11 | 7.2299 | 0.1963 | 96.2849 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NASHUA 7 345.00] TO [NASHUA-5 161.00] TO [NASH T12 13.800] CKT 12 | 7.2299 | 0.1963 | 96.2848 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [LACYGNE11_7 345.00] CKT 1 | 7.2298 | 0.1963 | 96.2842 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [LACYGNE22_7 345.00] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [LAC3_STAR7 345.00] CKT H | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [LAC8_STAR7 345.00] CKT H | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [LACYGNE2 69.000] TO [LACYGN7_TER16.9000] CKT 7 | 7.2299 | 0.1963 | 96.2851 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BLUMILS5 161.00] TO [ECKLES-161 161.00] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BLUMILS5 161.00] TO [BLUEMLS2 69.000] TO [BLUMILS_TER112.500] CKT 3 | 7.2299 | 0.1963 | 96.2851 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LAKCTYJ2 69.000] TO [BLUVLY 69.000] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CJ 366 5 161.00] TO [FIR417 5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2855 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CAR395 5 161.00] TO [PUR421 5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2852 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB K 69.000] TO [BLUVLY 69.000] CKT 1 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB H 69.000] TO [BLUVLY 69.000] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB H 69.000] TO [SUB M 69.000] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BLUVLY 13.8 13.800] TO [BLUVLY 69.000] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [SUB B 69.000] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [SUB J 69.000] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [SUB P 69.000] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB B 69.000] TO [SUB J 69.000] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB J 69.000] TO [SUB M 69.000] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB M-161 161.00] TO [SUB M 69.000] CKT 1 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GEN-2017-004345.00] TO [G17-004-TAP 345.00] CKT 1 | 7.2309 | 0.1963 | 96.2929 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GEN-2017-018345.00] TO [G17-018XFMR134.500] CKT 1 | 7.2306 | 0.1963 | 96.2907 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GEN-2017-018345.00] TO [G17-018XFMR234.500] CKT 1 | 7.2306 | 0.1963 | 96.2907 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GEN-2017-068138.00] TO [G17-068XFMR134.500] CKT 1 | 7.2303 | 0.1963 | 96.2889 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GEN-2017-082161.00] TO [G17-082XFMR134.500] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [S3458 3 345.00] CKT 1 | 7.2298 | 0.1963 | 96.2846 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEBCTY1G 18.000] TO [S3458 3 345.00] CKT 1 | 7.2368 | 0.1963 | 96.3391 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEBCTY2G 23.000] TO [S3458 3 345.00] CKT 1 | 7.2371 | 0.1963 | 96.3418 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S3456 3 345.00] TO [S3458 3 345.00] CKT 1 | 7.2302 | 0.1963 | 96.2877 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S3458 3 345.00] TO [S3740 3 345.00] CKT 1 | 7.2303 | 0.1963 | 96.2881 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S3458 3 345.00] TO [103&ROKEBY3 345.00] CKT 1 | 7.2308 | 0.1963 | 96.2932 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [7FAIRPT 345.00] TO [5FAIRPTXF3 161.00] CKT 3 | 7.2298 | 0.1963 | 96.2843 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [G17-108-TAP 161.00] CKT 1 | 7.2297 | 0.1963 | 96.2833 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5GIBSON 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2855 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M0 161.00] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M1 161.00] CKT 1 | 7.2298 | 0.1963 | 96.2845 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M2 161.00] CKT 1 | 7.2298 | 0.1963 | 96.2845 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M3 161.00] CKT 1 | 7.2298 | 0.1963 | 96.2845 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5NEWMADCP 161.00] CKT Z1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5NEWMADXF12 161.00] CKT Z1 | 7.2299 | 0.1963 | 96.2854 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5NEWMADGSU1 161.00] CKT 1 | 7.2307 | 0.1963 | 96.2917 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5NMDSU100HS 161.00] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5NMDSU200HS 161.00] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5PORTAGEVLE 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2852 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5TIPTONVL TN161.00] CKT 1 | 7.2297 | 0.1963 | 96.2833 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5HOLDENB2 161.00] TO [1HOLDNG11 13.800] CKT 11 | 7.2307 | 0.1963 | 96.2911 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5HOLDENB2 161.00] TO [1HOLDNG12 13.800] CKT 12 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5HOLDENB2 161.00] TO [2HOLDEN 69.000] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5HOLDENB2 161.00] TO [5HOLDENB1 161.00] CKT Z1 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [2CLINTN 69.000] TO [2LINCLN 69.000] CKT 1 | 7.2299 | 0.1963 | 96.2857 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [2CLINTN 69.000] TO [2GAINES 69.000] CKT 1 | 7.2299 | 0.1963 | 96.2853 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [2CLINTN 69.000] TO [2LEETON 69.000] CKT 1 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [2CLINTN 69.000] TO [2PIPER 69.000] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [2CLINTN 69.000] TO [2CLINTNLD 69.000] CKT 1 | 7.2299 | 0.1963 | 96.2853 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [7BLACKBERRY 345.00] TO [NEOSHO 7 345.00] CKT 1 | 7.2299 | 0.1963 | 96.2858 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [7SPORTSMAN 345.00] TO [5SPORTSMAN 161.00] CKT 1 | 7.23 | 0.1963 | 96.2859 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [7SPORTSMAN 345.00] TO [5SPORTSMAN 161.00] CKT 2 | 7.23 | 0.1963 | 96.2859 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [7SPORTSMAN 345.00] TO [GRDA1 7 345.00] CKT 1 | 7.2292 | 0.1963 | 96.2795 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [7JASPER 345.00] TO [7MORGAN 345.00] CKT 1 | 7.2305 | 0.1963 | 96.2907 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [7JASPER 345.00] TO [5JASPER 161.00] CKT 1 | 7.2302 | 0.1963 | 96.2877 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5OSCEOKCTP 161.00] TO [5OSCEOLTP 161.00] CKT 1 | 7.2298 | 0.1963 | 96.2842 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5OSCEOKCTP 161.00] TO [5OSCEOKC 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2853 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5MINER 1 161.00] TO [5CHARLSTN 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2854 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5MINER 1 161.00] TO [5BULLION 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2849 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [5MINER 1 161.00] TO [5MINER 2 161.00] CKT Z | 7.2299 | 0.1963 | 96.2854 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [N MADRD5 161.00] TO [G17-202-TAP 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2851 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [N MADRD2 69.000] TO [2STJUDEW 69.000] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [N MADRD2 69.000] TO [2LILBRN 69.000] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [N MADRD2 69.000] TO [MALDEN 2 69.000] CKT 1 | 7.2299 | 0.1963 | 96.2855 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [KENNETT5 161.00] TO [PARAGLD5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.285 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [KENNETT5 161.00] TO [KENNETT2 69.000] TO [KEN X1 1 13.800] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [KENNETT5 161.00] TO [KENNETT2 69.000] TO [KEN X2 1 13.800] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SIKETAP5 161.00] TO [SIKE SW5 161.00] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SIKESTN5 161.00] TO [G17-202-TAP 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2852 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [IDALIA 5 161.00] TO [5ESSEX 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2853 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [IDALIA 5 161.00] TO [2IDALIA 69.000] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [IDALIA 5 161.00] TO [2IDALIA 69.000] CKT 2 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [IDALIA 5 161.00] TO [ASHRVL5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2853 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [TRUMAN 5 161.00] TO [5LOSTVALY 161.00] CKT 1 | 7.2297 | 0.1963 | 96.2834 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [TRUMAN 5 161.00] TO [TRU123 1 13.800] CKT 1 | 7.2303 | 0.1963 | 96.2886 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [TRUMAN 5 161.00] TO [TRU456 1 13.800] CKT 1 | 7.2303 | 0.1963 | 96.2886 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [DELWARE4 138.00] TO [FARML 4 138.00] CKT 1 | 7.23 | 0.1963 | 96.2859 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [DELWARE7 345.00] TO [NEOSHO 7 345.00] CKT 1 | 7.2287 | 0.1963 | 96.2759 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [N.E.S.-7 345.00] TO [ONETA--7 345.00] CKT 1 | 7.2291 | 0.1963 | 96.2791 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [N.E.S.-7 345.00] TO [T.NO.--7 345.00] CKT 1 | 7.2296 | 0.1963 | 96.2826 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [N.E.S.-7 345.00] TO [NES3-1 22.000] CKT 1 | 7.2284 | 0.1963 | 96.2735 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [TATONGA7 345.00] CKT 1 | 7.2237 | 0.1963 | 96.2906 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [TATONGA7 345.00] CKT 2 | 7.2236 | 0.1963 | 96.2909 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [G07621119-20345.00] CKT 1 | 7.2298 | 0.1963 | 96.2812 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [GUTHRIE7 345.00] CKT 1 | 7.2299 | 0.1963 | 96.2844 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [BECKHAM7 345.00] CKT 1 | 7.2169 | 0.1963 | 96.2756 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [G16-003-TAP 345.00] CKT 1 | 7.2184 | 0.1963 | 96.3084 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [G16-003-TAP 345.00] CKT 2 | 7.2184 | 0.1963 | 96.3084 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [WWRDEHV4 138.00] TO [WWDEHV31 13.800] CKT 1 | 7.2292 | 0.1963 | 96.2888 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [WWRDEHV4 138.00] TO [WWDEHV21 13.800] CKT 2 | 7.2291 | 0.1963 | 96.2903 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [DGRASSE7 345.00] TO [THISTLE7 345.00] CKT 1 | 7.2217 | 0.1962 | 96.2271 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [DGRASSE7 345.00] TO [THISTLE7 345.00] CKT 2 | 7.2217 | 0.1962 | 96.2271 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [DGRASSE4 138.00] TO [KNOBHIL4 138.00] CKT 1 | 7.2297 | 0.1963 | 96.2859 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [DGRASSE4 138.00] TO [ROSEVLY4 138.00] CKT 1 | 7.2297 | 0.1963 | 96.286 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [DGRASSE4 138.00] TO [MOORLND4 138.00] CKT 1 | 7.2284 | 0.1963 | 96.2848 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WALKMYR2 69.000] TO [NORTH6T2 69.000] CKT 1 | 7.2303 | 0.1963 | 96.3167 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WALKMYR2 69.000] TO [WOODS 2 69.000] CKT 1 | 7.2304 | 0.1963 | 96.316 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WALKMYR3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 4.7591 | 0.2048 | 104.793 | 150 | 168 | FAIL | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SEWARD-3 115.00] TO [HASKELL3 115.00] CKT 1 | 5.4615 | 0.2019 | 101.9172 | 150 | 168 | FAIL | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SEWARD-3 115.00] TO [CMSSWRD2 69.000] TO [SEWARD 1 13.800] CKT 1 | 7.2268 | 0.1964 | 96.403 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [POSTROCK7 345.00] CKT 1 | 7.1908 | 0.1963 | 96.3003 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [BUCKNER7 345.00] CKT 1 | 7.1709 | 0.1963 | 96.2829 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [IRONWOOD7 345.00] CKT 1 | 7.2194 | 0.1963 | 96.3311 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [SPRVL 3 115.00] TO [SPRVL-T 13.800] CKT 1 | 7.119 | 0.1965 | 96.486 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [SPEARVL6 230.00] TO [SPERTER1 13.800] CKT 1 | 7.2163 | 0.1963 | 96.3002 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HUGOTON3 115.00] TO [GRANTTP3 115.00] CKT 1 | 7.203 | 0.1964 | 96.382 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HUGOTON3 115.00] TO [ABBK 2 115.00] CKT 1 | 7.2298 | 0.1963 | 96.3067 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HUGOTON3 115.00] TO [HUGOTON2 69.000] TO [HUGOTON1 13.800] CKT 1 | 7.2312 | 0.1964 | 96.3688 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HARBNGR3 115.00] TO [HARBNGR7 345.00] TO [HARBNGR-T 13.800] CKT 1 | 5.534 | 0.2012 | 101.1693 | 150 | 168 | FAIL | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EEC GT1 13.800] TO [DG TIE 1 4.1600] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EEC GT2 13.800] TO [EEC DG 1 4.1600] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC121 13.800] CKT 1 | 7.2303 | 0.1963 | 96.29 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC341 13.800] CKT 1 | 7.2303 | 0.1963 | 96.29 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC5 1 18.000] CKT 1 | 7.2305 | 0.1963 | 96.294 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC6 1 18.000] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC7 1 18.000] CKT 1 | 7.2305 | 0.1963 | 96.2932 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [LANG 7 345.00] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [MORRIS 7 345.00] CKT 1 | 7.2302 | 0.1963 | 96.2881 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [READWF 7 345.00] CKT 1 | 7.2304 | 0.1963 | 96.2891 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [RENO 7 345.00] TO [G16-111-TAP 345.00] CKT 1 | 7.2287 | 0.1963 | 96.2789 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [RENO 7 345.00] TO [RENO 3 115.00] TO [RENO 1X1 14.400] CKT 1 | 7.23 | 0.1963 | 96.288 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [RENO 7 345.00] TO [RENO 3 115.00] TO [RENO 2X1 14.400] CKT 1 | 7.23 | 0.1963 | 96.288 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUMMIT 7 345.00] TO [GEARY 7 345.00] CKT 1 | 7.2275 | 0.1963 | 96.2837 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUMMIT 7 345.00] TO [G16-111-TAP 345.00] CKT 1 | 7.2295 | 0.1963 | 96.2851 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUMMIT 7 345.00] TO [SUMMIT 6 230.00] TO [SUMMIT 1 14.400] CKT 1 | 7.2289 | 0.1963 | 96.2855 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SWISVAL7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 7.2285 | 0.1963 | 96.2808 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [87TH 7 345.00] TO [STRANGR7 345.00] CKT 1 | 7.2289 | 0.1963 | 96.2777 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [87TH 7 345.00] TO [87TH 3 115.00] TO [87TH 1X1 13.800] CKT 1 | 7.23 | 0.1963 | 96.2858 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [G17-009-TAP 345.00] TO [NEOSHO 7 345.00] CKT 1 | 7.2285 | 0.1963 | 96.2832 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GEN-2017-009345.00] TO [G17-009XFMR134.500] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GEN-2017-009345.00] TO [G17-009XFMR234.500] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CANEYRV7 345.00] TO [CANEYWF7 345.00] CKT 1 | 7.2301 | 0.1963 | 96.2865 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CANEYRV7 345.00] TO [LATHAMS7 345.00] CKT 1 | 7.2286 | 0.1963 | 96.2835 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [KINGMAN7 345.00] TO [BUFFALO7 345.00] CKT 1 | 7.2313 | 0.1963 | 96.2949 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NINN1WF7 345.00] TO [PRATTWF7 345.00] CKT 1 | 7.2305 | 0.1963 | 96.2901 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NINN1WF7 345.00] TO [N1 LV 1 34.500] TO [N1 WFTX1 13.800] CKT 1 | 7.2304 | 0.1963 | 96.2898 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BENTON 7 345.00] TO [ROSEHIL7 345.00] CKT 1 | 7.2263 | 0.1963 | 96.2777 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BENTON 7 345.00] TO [BENTON 4 138.00] TO [BENTN1 1 13.800] CKT 1 | 7.2299 | 0.1963 | 96.2854 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BENTON 7 345.00] TO [BENTON 4 138.00] TO [BENTN2 1 13.800] CKT 1 | 7.2299 | 0.1963 | 96.2854 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 1 | 7.2274 | 0.1963 | 96.2867 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 2 | 7.2274 | 0.1963 | 96.2867 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [EVANS N4 138.00] TO [WICH11 1 13.800] CKT 1 | 7.2298 | 0.1963 | 96.2869 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [EVANS N4 138.00] TO [WICH12 1 13.800] CKT 1 | 7.2298 | 0.1963 | 96.2872 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WOLFCRK7 345.00] TO [WCGS U1 25.000] CKT 1 | 7.2327 | 0.1963 | 96.3147 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WOLFCRK7 345.00] TO [ROSEHIL7 345.00] CKT 1 | 7.2287 | 0.1963 | 96.282 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WOLFCRK7 345.00] TO [WOLFCRK2 69.000] TO [WOLFCRK1 17.000] CKT 1 | 7.2298 | 0.1963 | 96.2847 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [VIOLA 7 345.00] TO [RENFROW7 345.00] CKT 1 | 7.2201 | 0.1962 | 96.2207 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [VIOLA 7 345.00] TO [G16-153-TAP 345.00] CKT 1 | 7.2305 | 0.1963 | 96.2886 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WAVERLY7 345.00] TO [WAVERTX7 345.00] CKT 1 | 7.2303 | 0.1963 | 96.2883 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EXPEDITION7 345.00] TO [GEN-2014-001345.00] CKT 1 | 7.2304 | 0.1963 | 96.2891 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [N345 1 1 13.800] TO [NEOSHO 7 345.00] TO [NEOSHO 4 138.00] CKT 1 | 7.2299 | 0.1963 | 96.2854 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [N345 2 1 13.800] TO [NEOSHO 7 345.00] TO [NEOSHO 5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.285 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SWISVAL6 230.00] TO [AUBURN 6 230.00] CKT 1 | 7.23 | 0.1963 | 96.2861 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SWISVAL6 230.00] TO [LAWHILL6 230.00] CKT 1 | 7.2298 | 0.1963 | 96.2855 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SWISVAL6 230.00] TO [TECHILL6 230.00] CKT 1 | 7.23 | 0.1963 | 96.2861 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SWISVAL6 230.00] TO [MORRIS 6 230.00] CKT 1 | 7.2296 | 0.1963 | 96.2851 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NMANHT6 230.00] TO [EMANHAT6 230.00] CKT 1 | 7.2297 | 0.1963 | 96.2854 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NMANHT6 230.00] TO [NMANHT3 115.00] TO [NMANHX1 14.400] CKT 1 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LITCH 5 161.00] TO [ASB349 5 161.00] CKT 1 | 7.2297 | 0.1963 | 96.2834 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [MARMTNW5 161.00] TO [MARMTNE5 161.00] CKT Z1 | 7.2299 | 0.1963 | 96.2854 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [MARMTNW5 161.00] TO [MARMATN2 69.000] TO [MARMATN1 13.200] CKT 1 | 7.2299 | 0.1963 | 96.2854 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [FRANKLIN5 161.00] TO [G17-005-TAP 161.00] CKT 1 | 7.2296 | 0.1963 | 96.2829 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [FRANKLIN5 161.00] TO [FRANKLIN2 69.000] TO [FRANKLIN1 12.470] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRESWLN4 138.00] TO [MIDLTNT4 138.00] CKT 1 | 7.2295 | 0.1963 | 96.2823 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRESWLN4 138.00] TO [SLATECRK4 138.00] CKT 1 | 7.2298 | 0.1963 | 96.2848 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRESWLN4 138.00] TO [CRESWLN2 69.000] TO [CRESW1 1 13.200] CKT 1 | 7.23 | 0.1963 | 96.2857 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRESWLN4 138.00] TO [CRESWLS2 69.000] TO [CRESW2 1 13.200] CKT 1 | 7.23 | 0.1963 | 96.2857 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [OXFORD 4 138.00] TO [SUMNER 4 138.00] CKT 1 | 7.2294 | 0.1963 | 96.2833 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [TIMBJCT4 138.00] TO [SUMNER 4 138.00] CKT 1 | 7.2299 | 0.1963 | 96.2853 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [TIOGA 4 138.00] TO [TIOGA 2 69.000] TO [TIOGA 1 13.200] CKT 1 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [OTTRCRK4 138.00] TO [BUTLER 4 138.00] CKT 1 | 7.2297 | 0.1963 | 96.2855 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [OTTRCRK4 138.00] TO [OTTRCRK3 115.00] TO [OTTRX1 1 13.800] CKT 1 | 7.2297 | 0.1963 | 96.2847 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ALTOONA4 138.00] TO [G17-022-TAP 138.00] CKT 1 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEPARSN4 138.00] TO [G17-022-TAP 138.00] CKT 1 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [TAYLOR 4 138.00] TO [MONTGOM4 138.00] CKT 1 | 7.2298 | 0.1963 | 96.2842 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BENTLEY4 138.00] TO [HALSTD 4 138.00] CKT 1 | 7.23 | 0.1963 | 96.2873 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BENTLEY4 138.00] TO [WWUPLNT4 138.00] CKT 1 | 7.2299 | 0.1963 | 96.2854 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEOSHOS4 138.00] TO [TV1MNDV4 138.00] CKT 1 | 7.2298 | 0.1963 | 96.2845 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEOSHON4 138.00] TO [NEOSHON2 69.000] TO [NEC U3 12.000] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CHISHLM4 138.00] TO [PARKCTY4 138.00] CKT 1 | 7.2299 | 0.1963 | 96.2855 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CHISHLM4 138.00] TO [17TH 4 138.00] CKT 1 | 7.2297 | 0.1963 | 96.2848 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CHISHLM4 138.00] TO [CHISHLM2 69.000] TO [CHISOLM1 13.200] CKT 1 | 7.2298 | 0.1963 | 96.2854 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EVANS S4 138.00] TO [EVANS N4 138.00] CKT Z1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EVANS S4 138.00] TO [EVANS N4 138.00] CKT Z2 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [FARBER 4 138.00] TO [ELPASOE4 138.00] CKT 1 | 7.2299 | 0.1963 | 96.2853 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GILL 4 138.00] TO [GILL W 4 138.00] CKT Z1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GILL 4 138.00] TO [GILL S 4 138.00] CKT Z1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LAKERDG4 138.00] TO [HOOVERN4 138.00] CKT 1 | 7.2295 | 0.1963 | 96.283 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [MAIZE 4 138.00] TO [EVANS N4 138.00] CKT 1 | 7.2292 | 0.1963 | 96.2827 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SC10BEL4 138.00] TO [SUMNER 4 138.00] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SG12COL4 138.00] TO [EVANS N4 138.00] CKT 1 | 7.2299 | 0.1963 | 96.2875 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [45TH ST4 138.00] TO [COWSKIN4 138.00] CKT 1 | 7.2294 | 0.1963 | 96.2825 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [VIOLA 4 138.00] TO [SUMNER 4 138.00] CKT 1 | 7.2296 | 0.1963 | 96.2853 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [AEC 3 115.00] TO [G17-120-TAP 115.00] CKT 1 | 7.2291 | 0.1963 | 96.281 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EABILEN3 115.00] TO [CHAPMAN3 115.00] CKT 1 | 7.2292 | 0.1963 | 96.2811 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NORTHST3 115.00] TO [SALINA 3 115.00] CKT 1 | 7.2298 | 0.1963 | 96.2857 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NORTHVW3 115.00] TO [G17-120-TAP 115.00] CKT 1 | 7.2302 | 0.1963 | 96.2895 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUMMIT 3 115.00] TO [MENTOR 3 115.00] CKT 1 | 7.2299 | 0.1963 | 96.2855 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUMMIT 3 115.00] TO [SO GATE3 115.00] CKT 1 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUMMIT 3 115.00] TO [SUMMIT 6 230.00] TO [SUMIT2 1 13.800] CKT 1 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUMMIT 3 115.00] TO [SUMMIT 6 230.00] TO [SUMIT3 1 13.800] CKT 1 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [TIMBJCT2 69.000] TO [AKRON 2 69.000] CKT 1 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [TIMBJCT2 69.000] TO [UDALL 2 69.000] CKT 1 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [TIMBJCT2 69.000] TO [WINFLD 2 69.000] CKT 1 | 7.2298 | 0.1963 | 96.2845 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ALTOO E2 69.000] TO [NEODJCT2 69.000] CKT 1 | 7.2299 | 0.1963 | 96.2855 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ALTOO E2 69.000] TO [RA5HIPR2 69.000] CKT Z1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ALTOO W2 69.000] TO [STUDBKR2 69.000] CKT 1 | 7.2299 | 0.1963 | 96.2855 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LITCH N2 69.000] TO [AQUARS 2 69.000] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LITCH N2 69.000] TO [PITNAC 2 69.000] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LITCH S2 69.000] TO [ROUSE 2 69.000] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LITCH S2 69.000] TO [SOPITT 2 69.000] CKT 1 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEOSHOS2 69.000] TO [BAKER 2 69.000] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEOSHOS2 69.000] TO [ORDNJCT2 69.000] CKT 1 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEOSHOS2 69.000] TO [CRAWFOR2 69.000] CKT 1 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEOSHOS2 69.000] TO [NEOSHON2 69.000] CKT Z1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [K1 LV 1 34.500] TO [K1 CLCT1 34.500] CKT 1 | 7.2302 | 0.1963 | 96.2879 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [K2 LV 1 34.500] TO [K2 CLCT1 34.500] CKT 1 | 7.2302 | 0.1963 | 96.2878 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [MILAN_GOAB 138.00] TO [CLDWELL4 138.00] CKT 1 | 7.2294 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [MILAN_GOAB 138.00] TO [MILAN 4 138.00] CKT 1 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CONWAY 138.00] TO [MILANTP4 138.00] CKT 1 | 7.2285 | 0.1963 | 96.2863 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [MRWYP16 230.00] TO [MRWYP26 230.00] CKT 1 | 7.2303 | 0.1963 | 96.2885 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [MRWYP16 230.00] TO [MRWYG11 34.500] TO [MRWYP1T1 13.800] CKT 1 | 7.2304 | 0.1963 | 96.2893 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [FLATRDG4 138.00] TO [FLATRWD4 138.00] CKT 1 | 7.2287 | 0.1963 | 96.2888 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [FLATRDG4 138.00] TO [HARPER 4 138.00] CKT 1 | 7.2263 | 0.1963 | 96.2852 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [FLATRDG4 138.00] TO [BARBER 4 138.00] CKT 1 | 7.2186 | 0.1963 | 96.3039 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ELMCREK6 230.00] TO [ELMCREEK7 345.00] TO [ELMCREEK1 13.800] CKT 1 | 7.23 | 0.1963 | 96.2865 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAYNE3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 7.0561 | 0.1972 | 97.2057 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [KISMET 3 115.00] TO [CUDAHY 3 115.00] CKT 1 | 5.9708 | 0.2013 | 101.281 | 150 | 168 | FAIL | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CMRIVTP3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 6.5538 | 0.1994 | 99.3584 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CONCRD6 230.00] TO [CONCORD3 115.00] TO [CONCOD-T 13.800] CKT 1 | 7.2305 | 0.1963 | 96.2909 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [E-LIBER3 115.00] TO [TXPHSF 3115.00] CKT 1 | 6.2244 | 0.1987 | 98.7056 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [E-LIBER3 115.00] TO [E-PINE 3 115.00] CKT 1 | 7.2254 | 0.1965 | 96.5365 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [E-LIBER3 115.00] TO [NATBEEF3 115.00] CKT 1 | 7.093 | 0.1961 | 96.1417 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [E-LIBER3 115.00] TO [E-LIBER1 34.500] TO [ELIB-T 2.4000] CKT 1 | 7.1943 | 0.1964 | 96.4456 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NLIB 3 115.00] TO [W-LIBER3 115.00] CKT 1 | 7.2331 | 0.1965 | 96.4887 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NLIB 3 115.00] TO [NATBEEF3 115.00] CKT 1 | 7.0702 | 0.1967 | 96.6895 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NLIB 3 115.00] TO [NLIB 1 34.500] TO [N-LIB-T 13.800] CKT 1 | 7.2144 | 0.1967 | 96.7377 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [N-CIMRN3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 5.4481 | 0.2025 | 102.5209 | 150 | 168 | FAIL | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CIM-PLT 13.800] TO [CIM-PLT3 115.00] CKT 1 | 7.1575 | 0.1989 | 98.8901 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [THISTLE7 345.00] CKT 1 | 7.2027 | 0.1962 | 96.2339 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [THISTLE7 345.00] CKT 2 | 7.2027 | 0.1962 | 96.2339 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [THISTLE T1 13.800] TO [THISTLE7 345.00] TO [THISTLE4 138.00] CKT 1 | 7.2301 | 0.1963 | 96.2882 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [TRANSFORMER 345.00] TO [SUB34.5KVB 34.500] TO [TERTIARYBUS 19.900] CKT 1 | 7.232 | 0.1963 | 96.3046 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GEN-2011-008345.00] TO [G-2011-008-1345.00] CKT 1 | 7.2315 | 0.1963 | 96.3042 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GEN-2011-008345.00] TO [G-2011-008-2345.00] CKT 1 | 7.2312 | 0.1963 | 96.3002 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GEN-2011-008345.00] TO [G-2011-008-3345.00] CKT 1 | 7.2327 | 0.1963 | 96.2978 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [MULLNCR7 345.00] TO [HOLT 7 345.00] CKT 1 | 7.2284 | 0.1963 | 96.2737 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [PECULR 7 345.00] TO [PHILL 7 345.00] CKT 1 | 7.2302 | 0.1963 | 96.2882 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [PECULR 7 345.00] TO [PECULR 5 161.00] TO [PECULRT 13.800] CKT 11 | 7.2299 | 0.1963 | 96.2854 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ST JOE 7 345.00] TO [G17-183-TAP 345.00] CKT 1 | 7.2297 | 0.1963 | 96.2833 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ARCHIE 5 161.00] TO [G17-108-TAP 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2851 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WINDSR 5 161.00] TO [5SEDALA 161.00] CKT 1 | 7.23 | 0.1963 | 96.2861 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HSNVL 5 161.00] TO [5SHARSNV 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2854 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HSNVL 5 161.00] TO [PHILL 5 161.00] CKT 1 | 7.2298 | 0.1963 | 96.2844 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HSNVL 5 161.00] TO [HSNVL 2 69.000] CKT 1 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HSNVL 5 161.00] TO [HSNVL 2 69.000] CKT 2 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ADRIAN 5 161.00] TO [5BUTLER 161.00] CKT 1 | 7.2296 | 0.1963 | 96.283 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CLINTON5 161.00] TO [CLNTN N2 69.000] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CLINTON5 161.00] TO [CLNTN S2 69.000] CKT 2 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ST JOE 5 161.00] TO [ST JOE_CAP5 161.00] CKT R | 7.2299 | 0.1963 | 96.2855 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ST JOE 5 161.00] TO [COOK 5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2855 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ST JOE 5 161.00] TO [WOODBIN5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2855 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ST JOE 5 161.00] TO [AVENUECTY 5 161.00] CKT 1 | 7.23 | 0.1963 | 96.2857 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP#1 13.800] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP#2 13.800] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP#3 13.800] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP 2 69.000] CKT 1 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [PECULRS5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2853 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EASTOWN7 345.00] TO [EASTOWN5 161.00] TO [EASTOWN1 13.800] CKT 11 | 7.23 | 0.1963 | 96.2861 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [KETCHEM7 345.00] TO [SIBLEY 7 345.00] CKT 1 | 7.2279 | 0.1963 | 96.2692 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [KETCHEM7 345.00] TO [OSBORN7 345.00] CKT 1 | 7.2307 | 0.1963 | 96.2917 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ROCKCK7 345.00] TO [HOLT 7 345.00] CKT 1 | 7.2334 | 0.1963 | 96.3123 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ROCKCK_T1_1 34.500] TO [ROCKCK_P1_1 34.500] CKT 1 | 7.2309 | 0.1963 | 96.2931 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ROCKCK_T2_1 34.500] TO [ROCKCK_P2_1 34.500] CKT 1 | 7.2309 | 0.1963 | 96.2929 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HOLT_REACT7 345.00] TO [HOLT 7 345.00] CKT Z1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [OUTLAW 345.00] TO [OUTLAW_T2_1 34.500] TO [OUTLAW_TR2_113.800] CKT 1 | 7.2306 | 0.1963 | 96.2906 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [OUTLAW 345.00] TO [OUTLAW_T1_1 34.500] TO [OUTLAW_TR1_113.800] CKT 1 | 7.2309 | 0.1963 | 96.293 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [W.GRDNR7 345.00] TO [WGAR T11 13.800] CKT 11 | 7.23 | 0.1963 | 96.2861 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [STILWEL7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 7.2297 | 0.1963 | 96.2841 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [G17-108-TAP 161.00] CKT 1 | 7.2299 | 0.1963 | 96.285 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTH 7 345.00] TO [SIBLEY 7 345.00] CKT 1 | 7.2299 | 0.1963 | 96.2855 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTH 7 345.00] TO [HAWTHN5 161.00] TO [HAWT T20 13.800] CKT 20 | 7.2299 | 0.1963 | 96.2849 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTH 7 345.00] TO [HAWTHN5 161.00] TO [HAWT T22 13.800] CKT 22 | 7.2299 | 0.1963 | 96.2851 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAW G9 1 13.800] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [LEEDS 5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2854 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [LEEDS 5 161.00] CKT 2 | 7.2299 | 0.1963 | 96.2854 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTH_B2_1 13.200] CKT 1 | 7.2298 | 0.1963 | 96.2842 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [BRMGHAM5 161.00] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHS_G65 161.00] CKT Z1 | 7.2299 | 0.1963 | 96.2853 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHS_XF5 161.00] CKT Z2 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHN5 161.00] CKT @1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHN5 161.00] CKT @2 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRAIG 7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 7.2305 | 0.1963 | 96.2902 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [CRAIG_CAP 5 161.00] CKT R | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [PFLUMM 5 161.00] CKT 1 | 7.23 | 0.1963 | 96.2857 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [LENEXA 5 161.00] CKT 1 | 7.23 | 0.1963 | 96.2857 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [LENEXA 5 161.00] CKT 2 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [COLLEGE5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2852 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NASHUA 7 345.00] TO [G17-183-TAP 345.00] CKT 1 | 7.2292 | 0.1963 | 96.2796 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 7.2314 | 0.1963 | 96.2965 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [G17-209-TAP 345.00] CKT 1 | 7.2283 | 0.1963 | 96.2729 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [STRANGR7 345.00] CKT 1 | 7.2298 | 0.1963 | 96.2853 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [STRANGR7 345.00] CKT 2 | 7.2299 | 0.1963 | 96.2853 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [IAT G1 1 24.000] CKT 1 | 7.2351 | 0.1963 | 96.3256 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [IAT G2 1 24.500] CKT 1 | 7.2352 | 0.1963 | 96.3268 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [IATAN5 161.00] TO [IATAN 11 14.400] CKT 11 | 7.2299 | 0.1963 | 96.2849 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HICKMAN5 161.00] TO [STHTOWN5 161.00] CKT 1 | 7.23 | 0.1963 | 96.2861 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BLUMILS5 161.00] TO [BLUVLY-161 161.00] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NASHUA-5 161.00] TO [NASHUA 5 161.00] CKT Z1 | 7.2299 | 0.1963 | 96.2854 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NASHUA-5 161.00] TO [RNRIDGE5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2851 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NASHUA-5 161.00] TO [SHOLCRK5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2849 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CEDRCRK5 161.00] TO [SHWNMSN5 161.00] CKT 1 | 7.23 | 0.1963 | 96.2857 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ANTIOCH5 161.00] TO [OXFORD 5 161.00] CKT 1 | 7.23 | 0.1963 | 96.2862 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [REDEL 5 161.00] TO [MARTCIT5 161.00] CKT 1 | 7.23 | 0.1963 | 96.2861 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BUCYRUS5 161.00] TO [NLOUISB5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.285 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BUCYRUS5 161.00] TO [WAGSTAF5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2851 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [PLSTVAL5 161.00] TO [SEOTTWA5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2851 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [PLSTVAL5 161.00] TO [ASG-2018-010161.00] CKT 1 | 7.2302 | 0.1963 | 96.2872 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [PLSTVAL5 161.00] TO [PLSTVAL1 34.500] TO [PLSTVL2_TER17.6210] CKT 2 | 7.2299 | 0.1963 | 96.2852 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LAKCTYJ2 69.000] TO [LAKCTY 2 69.000] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 1 13.800] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 2 13.800] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 3 13.800] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 4 13.800] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LACKMAN5 161.00] TO [SPRGHL 5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2855 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BNSF 5 161.00] TO [MOONLT 5 161.00] CKT 1 | 7.23 | 0.1963 | 96.286 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WGARDNR1 34.500] TO [BALDWINCTY1 34.500] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LACYGNE11_7 345.00] TO [LAC11_AQC1 13.800] TO [LAC11_TER1 13.800] CKT 11 | 7.2298 | 0.1963 | 96.2842 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LACYGNE22_7 345.00] TO [LAC22_AQC1 13.800] TO [LAC22_TER1 13.800] CKT 22 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LACYGNE2 69.000] TO [LAC_LAKE_2 69.000] CKT 1 | 7.2299 | 0.1963 | 96.2851 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LAC3_STAR7 345.00] TO [LAC3_X1 6.9000] CKT X | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LAC3_STAR7 345.00] TO [LAC3_Y1 6.9000] CKT Y | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LAC3_STAR7 345.00] TO [LAC3_Z1 3.9800] CKT Z | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LAC8_STAR7 345.00] TO [LAC8_X1 6.9000] CKT X | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LAC8_STAR7 345.00] TO [LAC8_Y1 6.9000] CKT Y | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [LAC8_STAR7 345.00] TO [LAC8_Z1 4.0000] CKT Z | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [RIV4525 161.00] TO [ORO110 5 161.00] CKT 1 | 7.23 | 0.1963 | 96.286 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [RIV4525 161.00] TO [STL439 5 161.00] CKT 1 | 7.23 | 0.1963 | 96.2857 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [RIV4525 161.00] TO [RIV452T 5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2851 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [RIV4525 161.00] TO [BAX488 5 161.00] CKT 1 | 7.2298 | 0.1963 | 96.2846 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [RIV4525 161.00] TO [RIV167 2 69.000] TO [RIV452 1 12.500] CKT 1 | 7.2299 | 0.1963 | 96.2855 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CJ 366 5 161.00] TO [ASB349 5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2854 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CAR395 5 161.00] TO [CARTHAG5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2853 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [FIR417 5 161.00] TO [ORO110 5 161.00] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [PUR421 5 161.00] TO [ASB349 5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2852 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [A1G349 1 13.800] TO [ASB349 5 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [A2G349 1 13.800] TO [ASB349 5 161.00] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB K 69.000] TO [SUB R 69.000] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB H 69.000] TO [COURTNY2 69.000] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB H 69.000] TO [SUGRCK_TP_E269.000] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB H 69.000] TO [SUB H-13B1 13.800] CKT H1 | 7.2299 | 0.1963 | 96.2851 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB H 69.000] TO [SUB H-13B2 13.800] CKT H2 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [BLUVLY-161 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [BLUVLY-161 161.00] CKT 2 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ECKLES-161 161.00] TO [5LEVASY 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2851 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ECKLES-161 161.00] TO [5MOCITYB1 161.00] CKT 1 | 7.23 | 0.1963 | 96.2857 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [ECKLES-161 161.00] TO [SIBLEYPL 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB J 69.000] TO [SUB J-13B1 13.800] CKT J1 | 7.2299 | 0.1963 | 96.2852 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB J 69.000] TO [SUB J-13B2 13.800] CKT J2 | 7.2299 | 0.1963 | 96.285 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB M-161 161.00] TO [BLUVLY-161 161.00] CKT 1 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB M 69.000] TO [SHRNKRD 69.000] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [SUB P 69.000] TO [SUB I 69.000] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [G16-046-TAP 345.00] TO [IRONWOOD7 345.00] CKT 1 | 7.2155 | 0.1963 | 96.2983 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [G16-046-TAP 345.00] TO [GEN-2016-046345.00] CKT 1 | 7.2198 | 0.1963 | 96.324 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GEN-2017-004345.00] TO [G17-004XFMR134.500] CKT 1 | 7.2309 | 0.1963 | 96.2929 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [G17-004-TAP 345.00] TO [ELMCREEK7 345.00] CKT 1 | 7.2299 | 0.1963 | 96.2848 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GEN-2017-018345.00] TO [THISTLE7 345.00] CKT 1 | 7.2313 | 0.1963 | 96.2957 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [G17-018XFMR134.500] TO [G17-018-GSU134.500] CKT 1 | 7.2306 | 0.1963 | 96.2907 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [G17-018XFMR234.500] TO [G17-018-GSU234.500] CKT 1 | 7.2306 | 0.1963 | 96.2907 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GEN-2017-068138.00] TO [EVANS N4 138.00] CKT 1 | 7.2303 | 0.1963 | 96.2889 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [G17-068XFMR134.500] TO [G17-068-GSU134.500] CKT 1 | 7.2303 | 0.1963 | 96.2889 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [GEN-2017-082161.00] TO [ASB349 5 161.00] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [G17-082XFMR134.500] TO [G17-082-GSU134.500] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [ATCHSN 3 345.00] CKT 1 | 7.2299 | 0.1963 | 96.2851 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [COOPER1G 22.000] CKT 1 | 7.2385 | 0.1964 | 96.3521 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [MONOLITH 3 345.00] CKT 1 | 7.2307 | 0.1963 | 96.2927 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [COOPER 5 161.00] TO [COOPER T2 913.800] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [COOPER 5 161.00] TO [COOPER T5 913.800] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEBCTY1G 18.000] TO [NC1GA1X9 4.2000] TO [NC1GA1Y9 4.2000] CKT 1 | 7.2297 | 0.1963 | 96.2838 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEBCTY1G 18.000] TO [NC1GA2X9 4.2000] TO [NC1GA2Y9 4.2000] CKT 1 | 7.2297 | 0.1963 | 96.2838 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEBCTY2G 23.000] TO [NC2GA1X9 4.2000] TO [NC2GA1Y9 4.2000] CKT 1 | 7.2298 | 0.1963 | 96.2848 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [NEBCTY2G 23.000] TO [NC2GA2X9 13.800] TO [NC2GA2Y9 13.800] CKT 1 | 7.2294 | 0.1963 | 96.2811 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S3456 3 345.00] TO [CBLUFFS3 345.00] CKT 1 | 7.2301 | 0.1963 | 96.2866 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S3456 3 345.00] TO [S3455 3 345.00] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S3456 3 345.00] TO [S3459 3 345.00] CKT 1 | 7.2301 | 0.1963 | 96.2864 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S3456 3 345.00] TO [S1206 5 161.00] TO [S3456T49 13.800] CKT 1 | 7.23 | 0.1963 | 96.2857 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S3458 3 345.00] TO [HOLT 7 345.00] CKT 1 | 7.2309 | 0.1963 | 96.293 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S3740 3 345.00] TO [CASS 1G 15.000] CKT 1 | 7.2318 | 0.1963 | 96.3 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S3740 3 345.00] TO [CASS 2G 15.000] CKT 1 | 7.2318 | 0.1963 | 96.3 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S3740 3 345.00] TO [S3454 3 345.00] CKT 1 | 7.2301 | 0.1963 | 96.2864 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S3740 3 345.00] TO [S3455 3 345.00] CKT 1 | 7.23 | 0.1963 | 96.286 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [S3740 3 345.00] TO [GEN-2018-033345.00] CKT 1 | 7.23 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [103&ROKEBY3 345.00] TO [MOORE 3 345.00] CKT 1 | 7.2296 | 0.1963 | 96.2846 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [103&ROKEBY3 345.00] TO [WAGENER 3 345.00] CKT 1 | 7.2298 | 0.1963 | 96.285 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [7SPORTSMAN 345.00] TO [5SPORTSMAN 161.00] CKT 2 | 7.2302 | 0.1963 | 96.2873 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [IDALIA 5 161.00] TO [2IDALIA 69.000] CKT 2 | 7.23 | 0.1963 | 96.2857 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [TATONGA7 345.00] CKT 2 | 7.2007 | 0.1963 | 96.3367 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [G16-003-TAP 345.00] CKT 2 | 7.0868 | 0.1965 | 96.4831 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [DGRASSE7 345.00] TO [THISTLE7 345.00] CKT 2 | 7.1768 | 0.1959 | 95.8946 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 2 | 7.1826 | 0.1963 | 96.2735 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [EVANS S4 138.00] TO [EVANS N4 138.00] CKT Z2 | 7.2284 | 0.1963 | 96.2762 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [THISTLE7 345.00] CKT 2 | 7.1044 | 0.196 | 95.9743 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HSNVL 5 161.00] TO [HSNVL 2 69.000] CKT 2 | 7.23 | 0.1963 | 96.2857 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [LEEDS 5 161.00] CKT 2 | 7.2299 | 0.1963 | 96.2848 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHN5 161.00] CKT @2 | 7.2298 | 0.1963 | 96.2842 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [LENEXA 5 161.00] CKT 2 | 7.23 | 0.1963 | 96.2861 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [STRANGR7 345.00] CKT 2 | 7.2292 | 0.1963 | 96.2834 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-009 | Cimarron 115kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [BLUVLY-161 161.00] CKT 2 | 7.2299 | 0.1963 | 96.2856 | 150 | 168 | PASS | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | Base | 5.5918 | 7.619 | 7519.0088 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [MALLARD7 115.00] TO [LOGAN___-BE7115.00] CKT 1 | 5.5017 | 7.6168 | 7516.8493 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [GRE-STANTON4230.00] TO [LELAND_O-BE4230.00] CKT 1 | 5.5602 | 7.6172 | 7517.2476 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TWIN CH4 230.00] TO [SIOUXCY4 230.00] CKT 1 | 5.5918 | 7.619 | 7519.0093 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXC39 13.800] TO [SIOUXCY4 230.00] TO [SIOUXCY5 161.00] CKT 1 | 5.5917 | 7.619 | 7519.0082 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXC49 13.800] TO [SIOUXCY4 230.00] TO [SIOUXCY5 161.00] CKT 1 | 5.5917 | 7.619 | 7519.0082 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [VFODNES4 230.00] TO [SIOUXFL4 230.00] CKT 1 | 5.5918 | 7.619 | 7519.0084 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [VFODNES4 230.00] TO [VFODNES-ER8 69.000] CKT 1 | 5.5918 | 7.619 | 7519.0087 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [VFODNES4 230.00] TO [VFODNES-ER7 115.00] TO [VFODNES1-ER912.500] CKT 1 | 5.5918 | 7.619 | 7519.0064 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [GARRISN4 230.00] TO [LELAND_O-BE4230.00] CKT 1 | 5.5775 | 7.6182 | 7518.1955 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [WASHBRN4 230.00] TO [LELAND_O-BE4230.00] CKT 1 | 5.5714 | 7.6183 | 7518.2919 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [FTRANDL4 230.00] TO [UTICAJC4 230.00] CKT 1 | 5.5917 | 7.619 | 7519.0022 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [FTRANDL4 230.00] TO [SIOUXCY4 230.00] CKT 1 | 5.5917 | 7.619 | 7519.0002 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [UTICAJC4 230.00] TO [PRVLNG16 230.00] CKT 1 | 5.5917 | 7.619 | 7519.0108 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [UTICAJC4 230.00] TO [RASMUSN-ER4 230.00] CKT 1 | 5.5917 | 7.619 | 7519.0035 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [UTICAJC4 230.00] TO [UTICAJC7 115.00] TO [UTICAJC9 13.200] CKT 1 | 5.5917 | 7.619 | 7519.0093 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXCY2 230.00] TO [SIOUXCY4 230.00] CKT Z1 | 5.5918 | 7.619 | 7519.0098 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [DENISON5 161.00] TO [EXIRA 5 161.00] CKT 1 | 5.5918 | 7.619 | 7519.0087 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXCY4 230.00] TO [RASMUSN-ER4 230.00] CKT 1 | 5.5917 | 7.619 | 7519.0038 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [DENISON8 69.000] TO [MANNINGTAP 869.000] CKT 1 | 5.5918 | 7.619 | 7519.0088 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [DENISON8 69.000] TO [DENISONWEST869.000] CKT 1 | 5.5918 | 7.619 | 7519.0089 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [DENISON8 69.000] TO [DENSOUMAIN8 69.000] CKT 1 | 5.5918 | 7.619 | 7519.0088 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [DENISON8 69.000] TO [J6BOYER_-NI869.000] CKT 1 | 5.5918 | 7.619 | 7519.0086 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SW.MINOT-CP7115.00] TO [LOGAN___-BE7115.00] CKT 1 | 5.5761 | 7.6175 | 7517.46 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [HESS GAS-MW7115.00] TO [TIOGA.N_-MW7115.00] CKT Z | 5.5912 | 7.6189 | 7518.9275 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [HESS GAS-MW7115.00] TO [NESET___-BE7115.00] CKT 1 | 5.5903 | 7.6191 | 7519.1483 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [WHTEARTH-MW7115.00] TO [NESET___-BE7115.00] CKT 1 | 5.5858 | 7.6191 | 7519.1258 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [PWRSLKTP-MW7115.00] TO [NESET___-BE7115.00] CKT 1 | 5.5839 | 7.6155 | 7515.4877 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TIOGA.N_-MW7115.00] TO [NESET___-BE7115.00] CKT 1 | 5.59 | 7.6192 | 7519.1616 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [DENISONWEST869.000] TO [DENSOUMAIN8 69.000] CKT 1 | 5.5918 | 7.619 | 7519.0088 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [LELAND_O-BE3345.00] TO [LELAND_O-BE4230.00] TO [LO.KU1A_-BE913.800] CKT 1 | 5.5868 | 7.6184 | 7518.3714 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [LELAND_O-BE3345.00] TO [LELAND_O-BE4230.00] TO [LO.KVA2_-BE913.800] CKT 1 | 5.5873 | 7.6185 | 7518.5179 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [LELAND_O-BE4230.00] TO [LELAND_1-BEG22.000] CKT 1 | 5.5588 | 7.6167 | 7516.7408 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [LELAND_O-BE4230.00] TO [BASIN___-BE4230.00] CKT 1 | 5.5823 | 7.6187 | 7518.7118 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [NESET___-BE7115.00] TO [TIOGA4 7 115.00] CKT 1 | 5.5947 | 7.6184 | 7518.395 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [NRTSHORE-BE4230.00] TO [NRTSHORE-BE7115.00] TO [NRTSHORE-BE913.800] CKT 1 | 5.5009 | 7.6266 | 7526.577 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [BLAISDEL-BE4230.00] TO [TIOGA4 4 230.00] CKT 1 | 5.1096 | 7.6294 | 7529.3779 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [BLAISDEL-BE4230.00] TO [BLAISDEL-BE7115.00] TO [BLS.T1__-BE913.800] CKT 1 | 5.5682 | 7.6225 | 7522.4918 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TANDE___-BE3345.00] TO [TANDE___-BE4230.00] TO [TND.KU3A-BE913.800] CKT 1 | 4.1133 | 7.6086 | 7508.6482 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [WHEELOCK-BE4230.00] TO [TIOGA4 4 230.00] CKT 1 | 5.0498 | 7.6344 | 7534.4003 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TIOGA4 4 230.00] TO [BDV 4230.00] CKT 1 | 4.6371 | 7.5947 | 7494.6734 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TIOGA4 4 230.00] TO [TIOGA4 7 115.00] TO [TIOGA4 9 13.800] CKT 1 | 5.5329 | 7.6281 | 7528.1235 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [MALLARD7 115.00] TO [SOURIS 7 115.00] CKT 1 | 5.5344 | 7.6178 | 7517.7524 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [MALLARD7 115.00] TO [NELSON 7 115.00] CKT 1 | 5.5731 | 7.6167 | 7516.7136 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [MALLARD7 115.00] TO [RUGBY 7 115.00] CKT 1 | 5.5754 | 7.6183 | 7518.3063 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [MALLARD7 115.00] TO [MALLARD1-CP941.600] CKT 1 | 5.5913 | 7.6191 | 7519.1255 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [MALLARD7 115.00] TO [MALLARD2-CP941.600] CKT 1 | 5.5912 | 7.6192 | 7519.1568 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [MALLARD7 115.00] TO [E.RUTHVL-CP7115.00] CKT 1 | 5.5899 | 7.6188 | 7518.7912 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [GRE-STANTON4230.00] TO [GRE-COAL CR4230.00] CKT 1 | 5.5897 | 7.619 | 7518.9538 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [GRE-STANTON4230.00] TO [GRE-COAL TP4230.00] CKT 1 | 5.5914 | 7.619 | 7518.9973 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [GRE-STANTON4230.00] TO [SQBUTTE4 230.00] CKT 1 | 5.5883 | 7.6185 | 7518.5449 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TWIN CH4 230.00] TO [WAKEFIELD 4230.00] CKT 1 | 5.5918 | 7.619 | 7519.0087 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TWIN CH4 230.00] TO [TWIN CH7 115.00] TO [TWIN CH T4 913.800] CKT 1 | 5.5918 | 7.619 | 7519.0089 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TWIN CH4 230.00] TO [TWIN CH7 115.00] TO [TWIN CH T6 913.800] CKT 2 | 5.5918 | 7.619 | 7519.0088 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [VFODNES4 230.00] TO [G17-175TAP 230.00] CKT 1 | 5.5917 | 7.619 | 7519.0076 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [GARRISN4 230.00] TO [JAMESTN4 230.00] CKT 1 | 5.5865 | 7.619 | 7518.9879 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [GARRISN4 230.00] TO [GARISN1G 13.800] CKT 1 | 5.5851 | 7.6186 | 7518.5975 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [GARRISN4 230.00] TO [GARISN2G 13.800] CKT 1 | 5.5851 | 7.6186 | 7518.5979 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [GARRISN4 230.00] TO [GARISN3G 13.800] CKT 1 | 5.5851 | 7.6186 | 7518.598 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [GARRISN4 230.00] TO [HILKEN 4 230.00] CKT 1 | 5.5878 | 7.6189 | 7518.8955 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [GARRISN4 230.00] TO [GARRISN7 115.00] TO [GARRISON 9 13.800] CKT 1 | 5.5767 | 7.6182 | 7518.216 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [WASHBRN4 230.00] TO [WASHBRN9 41.800] CKT 1 | 5.5915 | 7.619 | 7519.04 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [WASHBRN4 230.00] TO [BISMARK4 230.00] CKT 1 | 5.572 | 7.6182 | 7518.2306 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [FTRANDL4 230.00] TO [MEADOWGROVE4230.00] CKT 1 | 5.5917 | 7.619 | 7518.9985 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [FTRANDL4 230.00] TO [FTTHOMP4 230.00] CKT 1 | 5.5913 | 7.619 | 7518.9851 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [FTRANDL4 230.00] TO [FTRANDL7 115.00] CKT 1 | 5.5918 | 7.619 | 7519.0086 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [FTRANDL4 230.00] TO [FTRANDL7 115.00] CKT 2 | 5.5918 | 7.619 | 7519.0086 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [FTRANDL4 230.00] TO [FTRDL34G 13.800] CKT 1 | 5.5917 | 7.619 | 7519.0105 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [FTRANDL4 230.00] TO [FTRDL56G 13.800] CKT 1 | 5.5917 | 7.619 | 7519.0106 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [FTRANDL4 230.00] TO [FTRDL78G 13.800] CKT 1 | 5.5917 | 7.619 | 7519.0093 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [FTRANDL4 230.00] TO [LAKPLAT-ER4 230.00] CKT 1 | 5.5913 | 7.619 | 7518.9855 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXFL4 230.00] TO [SPLT RK4 230.00] CKT 1 | 5.5917 | 7.619 | 7519.0064 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXFL4 230.00] TO [HANLON 4 230.00] CKT 1 | 5.5915 | 7.619 | 7518.9861 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXFL4 230.00] TO [LETCHER4 230.00] CKT 1 | 5.5915 | 7.619 | 7518.9869 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXFL4 230.00] TO [PAHOJA__-BE4230.00] CKT 1 | 5.5918 | 7.619 | 7519.0026 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXFL4 230.00] TO [SIOUXFL7 115.00] TO [SIOUXF19 13.200] CKT 1 | 5.5917 | 7.619 | 7519.008 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXFL4 230.00] TO [SIOUXFL7 115.00] TO [SIOUXF29 13.200] CKT 1 | 5.5917 | 7.619 | 7519.0079 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [UTICAJC4 230.00] TO [G17-175TAP 230.00] CKT 1 | 5.5918 | 7.619 | 7519.009 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXCY2 230.00] TO [EAGLE___-NI4230.00] CKT 1 | 5.5917 | 7.619 | 7519.0077 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXCY2 230.00] TO [SIOUXCY3 345.00] TO [SIOUXC19 13.800] CKT 1 | 5.5918 | 7.619 | 7519.0091 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXCY2 230.00] TO [SIOUXCY3 345.00] TO [SIOUXC29 13.800] CKT 1 | 5.5918 | 7.619 | 7519.0091 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [DENISON5 161.00] TO [DENISON4 230.00] TO [DENISON 9 13.800] CKT 1 | 5.5918 | 7.619 | 7519.0087 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXCY4 230.00] TO [DENISON4 230.00] CKT 1 | 5.5918 | 7.619 | 7519.0075 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXCY5 161.00] TO [PLYMOTH5 161.00] CKT 1 | 5.5918 | 7.619 | 7519.007 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXCY5 161.00] TO [SPENCER5 161.00] CKT 1 | 5.5918 | 7.619 | 7519.0085 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXCY5 161.00] TO [SIOUXCY8 69.000] CKT 1 | 5.5918 | 7.619 | 7519.0088 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [DENISON8 69.000] TO [DENISON4 230.00] CKT 1 | 5.5918 | 7.619 | 7519.0087 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [DENISON8 69.000] TO [DENISON4 230.00] CKT 2 | 5.5918 | 7.619 | 7519.0088 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [EXIRA 5 161.00] TO [ANTA TP5 161.00] CKT 1 | 5.5918 | 7.619 | 7519.0071 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [EXIRA 5 161.00] TO [EXIRA 1G 13.800] CKT 1 | 5.5918 | 7.619 | 7519.0091 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [EXIRA 5 161.00] TO [EXIRA 2G 13.800] CKT 1 | 5.5918 | 7.619 | 7519.009 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [EXIRA 5 161.00] TO [EXIRA 3G 13.800] CKT 1 | 5.5918 | 7.619 | 7519.0093 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [UTICAJC7 115.00] TO [FREEMAN-ER7 115.00] CKT 1 | 5.5917 | 7.619 | 7519.0086 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [UTICAJC7 115.00] TO [MENNO JCT 7115.00] CKT 1 | 5.5917 | 7.619 | 7519.0067 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [UTICAJC7 115.00] TO [NAPA JCT 7115.00] CKT 1 | 5.5918 | 7.619 | 7519.0071 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [PRVLNG16 230.00] TO [PRVLNG23 115.00] TO [PRVLNGT21 13.800] CKT 1 | 5.5917 | 7.619 | 7519.0108 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [VFODNES-ER7 115.00] TO [SXFCHCLR-ER7115.00] CKT 1 | 5.5917 | 7.619 | 7519.0086 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [VFODNES-ER7 115.00] TO [BUCKSNRT-ER7115.00] CKT 1 | 5.5917 | 7.619 | 7519.0085 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [VFODNES-ER7 115.00] TO [SW1109-ER7 115.00] CKT 1 | 5.5917 | 7.619 | 7519.0084 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [VFODNES-ER7 115.00] TO [DAYTON__-ER7115.00] CKT 1 | 5.5918 | 7.619 | 7519.0074 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [RASMUSN-ER4 230.00] TO [RASMUSN-ER8 69.000] CKT 1 | 5.5917 | 7.619 | 7519.0084 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SW.MINOT-CP7115.00] TO [SW.MNOT1-CP941.600] CKT 1 | 5.5915 | 7.6191 | 7519.0857 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SW.MINOT-CP7115.00] TO [SW.MNOT2-CP941.600] CKT 2 | 5.59 | 7.6194 | 7519.4023 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SW.MINOT-CP7115.00] TO [BERTHOLD-CP7115.00] CKT 1 | 5.5013 | 7.6149 | 7514.9495 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SW.MINOT-CP7115.00] TO [E.RUTHVL-CP7115.00] CKT 1 | 5.5824 | 7.6188 | 7518.8402 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [WHTEARTH-MW7115.00] TO [PLSNTV_T-MW7115.00] CKT 1 | 5.5866 | 7.6192 | 7519.175 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [PWRSLKTP-MW7115.00] TO [POWERSLK-MW7115.00] CKT 1 | 5.588 | 7.6202 | 7520.2005 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [PWRSLKTP-MW7115.00] TO [LIBERTY -MW7115.00] CKT 1 | 5.587 | 7.6139 | 7513.9263 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TIOGA.N_-MW7115.00] TO [W.BANK_T-MW7115.00] CKT 1 | 5.5512 | 7.6191 | 7519.1021 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [MANNINGTAP 869.000] TO [TEMPLTON8 69.000] CKT 1 | 5.5918 | 7.619 | 7519.0088 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [LELAND_O-BE3345.00] TO [GEN-2016-130345.00] CKT 1 | 5.5923 | 7.6184 | 7518.3523 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [LELAND_O-BE3345.00] TO [FINSTAD345 345.00] CKT 1 | 4.7858 | 7.574 | 7474.0019 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [LELAND_O-BE3345.00] TO [ANTELOPE-BE3345.00] CKT 1 | 5.5902 | 7.6193 | 7519.3236 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [LELAND_O-BE3345.00] TO [ANTELOPE-BE3345.00] CKT 2 | 5.5902 | 7.6193 | 7519.3238 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [LELAND_O-BE3345.00] TO [LELAND_2-BEG20.000] CKT 1 | 5.5347 | 7.6153 | 7515.342 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [LELAND_O-BE3345.00] TO [LO.LS-GR-BE3345.00] CKT Z | 5.565 | 7.6174 | 7517.444 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [LELAND_O-BE3345.00] TO [LO.LS-FT-BE3345.00] CKT Z | 5.5657 | 7.6176 | 7517.564 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [LELAND_O-BE4230.00] TO [LOGAN___-BE4230.00] CKT 1 | 5.4169 | 7.6158 | 7515.7607 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [NESET___-BE7115.00] TO [NESET___-BE4230.00] TO [NES.KV2A-BE913.800] CKT 1 | 5.533 | 7.6281 | 7528.1113 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [NRTSHORE-BE4230.00] TO [NESET___-BE4230.00] CKT 1 | 5.5062 | 7.6276 | 7527.6288 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [NRTSHORE-BE7115.00] TO [BROOKBNK-MW7115.00] CKT 1 | 5.5595 | 7.6198 | 7519.8054 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [NRTSHORE-BE7115.00] TO [ROSS -MW7115.00] CKT 1 | 5.5882 | 7.6206 | 7520.632 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [NRTSHORE-BE7115.00] TO [RATLAKE -MW7115.00] CKT 1 | 5.5917 | 7.6189 | 7518.852 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [NRTSHORE-BE7115.00] TO [SATTER -MW7115.00] CKT 1 | 5.5593 | 7.6183 | 7518.3191 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [BLAISDEL-BE4230.00] TO [LOGAN___-BE4230.00] CKT 1 | 5.1861 | 7.6142 | 7514.2476 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [BLAISDEL-BE7115.00] TO [BERTHOLD-CP7115.00] CKT 1 | 5.5618 | 7.6185 | 7518.4814 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [BLAISDEL-BE7115.00] TO [PALERMO -MW7115.00] CKT 1 | 5.5895 | 7.6174 | 7517.4005 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [BLAISDEL-BE7115.00] TO [BLAISDEL-MW7115.00] CKT 1 | 5.5835 | 7.6191 | 7519.0902 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [LOGAN___-BE7115.00] TO [LOGAN___-BE4230.00] TO [LGN.KW1A-BE913.800] CKT 1 | 5.5332 | 7.6209 | 7520.8877 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [BASIN___-BE4230.00] TO [GEN-2016-004230.00] CKT 1 | 5.5831 | 7.6185 | 7518.5279 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [BASIN___-BE4230.00] TO [BASIN___-BE7115.00] TO [BAL.KY1A-BE913.800] CKT 1 | 5.5905 | 7.6192 | 7519.1842 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TANDE___-BE3345.00] TO [FINSTAD345 345.00] CKT 1 | 5.078 | 7.6272 | 7527.2309 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TANDE___-BE3345.00] TO [BURKE___-PP3345.00] CKT 1 | 5.6113 | 7.6131 | 7513.0639 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TANDE___-BE3345.00] TO [TN.LS-JD-BE3345.00] CKT Z | 4.879 | 7.6161 | 7516.1017 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TANDE___-BE3345.00] TO [TRADEWND-UA3345.00] CKT 1 | 5.6159 | 7.6076 | 7507.5901 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TANDE___-BE4230.00] TO [NESET___-BE4230.00] CKT 1 | 4.1135 | 7.6086 | 7508.6112 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [WHEELOCK-BE4230.00] TO [WILISTN4 230.00] CKT 1 | 5.1558 | 7.6197 | 7519.7064 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [WHEELOCK-BE4230.00] TO [WHEELOCK-BE7115.00] TO [WEL.T1__-BE913.800] CKT 1 | 5.5743 | 7.6226 | 7522.599 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [J6BOYER_-NI869.000] TO [K335AMAI-NI869.000] CKT 1 | 5.5918 | 7.619 | 7519.0088 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [J6BOYER_-NI869.000] TO [K307DENI-NI869.000] CKT 1 | 5.5918 | 7.619 | 7519.0088 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [J6BOYER_-NI869.000] TO [K306SCHL-NI869.000] CKT 1 | 5.5918 | 7.619 | 7519.0087 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [J6BOYER_-NI869.000] TO [J12_____-NI869.000] CKT 1 | 5.5918 | 7.619 | 7519.0088 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TIOGA4 4 230.00] TO [NESET___-BE4230.00] CKT Z | 3.6962 | 7.685 | 7585.0258 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TIOGA4 7 115.00] TO [STANLEY7 115.00] CKT 1 | 5.5635 | 7.6206 | 7520.5917 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TIOGA4 7 115.00] TO [TIOGA7 7 115.00] CKT 1 | 5.4938 | 7.6225 | 7522.4575 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [BDV 4230.00] TO [BDX 4230.00] CKT 1 & 2 | 4.6259 | 7.5922 | 7492.2281 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [FTRANDL4 230.00] TO [FTRANDL7 115.00] CKT 1 & 2 | 5.5917 | 7.619 | 7519.009 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [DENISON8 69.000] TO [DENISON4 230.00] CKT 1 & 2 | 5.5918 | 7.619 | 7519.0083 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25SP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [LELAND_O-BE3345.00] TO [ANTELOPE-BE3345.00] CKT 1 & 2 | 5.5838 | 7.6204 | 7520.3702 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | Base | 5.6285 | 7.5597 | 7459.6716 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [MALLARD7 115.00] TO [LOGAN___-BE7115.00] CKT 1 | 5.5373 | 7.5564 | 7456.4465 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [GRE-STANTON4230.00] TO [LELAND_O-BE4230.00] CKT 1 | 5.5969 | 7.5574 | 7457.4267 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TWIN CH4 230.00] TO [SIOUXCY4 230.00] CKT 1 | 5.6285 | 7.5597 | 7459.672 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXC39 13.800] TO [SIOUXCY4 230.00] TO [SIOUXCY5 161.00] CKT 1 | 5.6285 | 7.5597 | 7459.6702 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXC49 13.800] TO [SIOUXCY4 230.00] TO [SIOUXCY5 161.00] CKT 1 | 5.6285 | 7.5597 | 7459.6702 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [VFODNES4 230.00] TO [SIOUXFL4 230.00] CKT 1 | 5.6285 | 7.5597 | 7459.6698 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [VFODNES4 230.00] TO [VFODNES-ER8 69.000] CKT 1 | 5.6285 | 7.5597 | 7459.6716 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [VFODNES4 230.00] TO [VFODNES-ER7 115.00] TO [VFODNES1-ER912.500] CKT 1 | 5.6285 | 7.5597 | 7459.6674 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [GARRISN4 230.00] TO [LELAND_O-BE4230.00] CKT 1 | 5.6149 | 7.5586 | 7458.6384 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [WASHBRN4 230.00] TO [LELAND_O-BE4230.00] CKT 1 | 5.608 | 7.5586 | 7458.601 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [FTRANDL4 230.00] TO [UTICAJC4 230.00] CKT 1 | 5.6284 | 7.5597 | 7459.6619 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [FTRANDL4 230.00] TO [SIOUXCY4 230.00] CKT 1 | 5.6284 | 7.5597 | 7459.6585 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [UTICAJC4 230.00] TO [PRVLNG16 230.00] CKT 1 | 5.6285 | 7.5597 | 7459.675 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [UTICAJC4 230.00] TO [RASMUSN-ER4 230.00] CKT 1 | 5.6284 | 7.5597 | 7459.6627 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [UTICAJC4 230.00] TO [UTICAJC7 115.00] TO [UTICAJC9 13.200] CKT 1 | 5.6285 | 7.5597 | 7459.6719 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXCY2 230.00] TO [SIOUXCY4 230.00] CKT Z1 | 5.6285 | 7.5597 | 7459.6727 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [DENISON5 161.00] TO [EXIRA 5 161.00] CKT 1 | 5.6285 | 7.5597 | 7459.6698 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXCY4 230.00] TO [RASMUSN-ER4 230.00] CKT 1 | 5.6283 | 7.5597 | 7459.6639 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [DENISON8 69.000] TO [MANNINGTAP 869.000] CKT 1 | 5.6285 | 7.5597 | 7459.6715 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [DENISON8 69.000] TO [DENISONWEST869.000] CKT 1 | 5.6285 | 7.5597 | 7459.6716 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [DENISON8 69.000] TO [DENSOUMAIN8 69.000] CKT 1 | 5.6285 | 7.5597 | 7459.6716 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [DENISON8 69.000] TO [J6BOYER_-NI869.000] CKT 1 | 5.6285 | 7.5597 | 7459.6712 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SW.MINOT-CP7115.00] TO [LOGAN___-BE7115.00] CKT 1 | 5.6136 | 7.5574 | 7457.4444 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [HESS GAS-MW7115.00] TO [TIOGA.N_-MW7115.00] CKT Z | 5.628 | 7.5596 | 7459.5884 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [HESS GAS-MW7115.00] TO [NESET___-BE7115.00] CKT 1 | 5.6268 | 7.5598 | 7459.8434 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [WHTEARTH-MW7115.00] TO [NESET___-BE7115.00] CKT 1 | 5.6225 | 7.56 | 7460.0235 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [PWRSLKTP-MW7115.00] TO [NESET___-BE7115.00] CKT 1 | 5.6081 | 7.5559 | 7455.8915 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TIOGA.N_-MW7115.00] TO [NESET___-BE7115.00] CKT 1 | 5.6265 | 7.5599 | 7459.861 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [DENISONWEST869.000] TO [DENSOUMAIN8 69.000] CKT 1 | 5.6285 | 7.5597 | 7459.6716 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [LELAND_O-BE3345.00] TO [LELAND_O-BE4230.00] TO [LO.KU1A_-BE913.800] CKT 1 | 5.6238 | 7.5589 | 7458.9438 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [LELAND_O-BE3345.00] TO [LELAND_O-BE4230.00] TO [LO.KVA2_-BE913.800] CKT 1 | 5.6246 | 7.5591 | 7459.1302 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [LELAND_O-BE4230.00] TO [LELAND_1-BEG22.000] CKT 1 | 5.5975 | 7.5572 | 7457.1691 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [LELAND_O-BE4230.00] TO [BASIN___-BE4230.00] CKT 1 | 5.6193 | 7.5593 | 7459.2688 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [NESET___-BE7115.00] TO [TIOGA4 7 115.00] CKT 1 | 5.637 | 7.5589 | 7458.9085 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [NRTSHORE-BE4230.00] TO [NRTSHORE-BE7115.00] TO [NRTSHORE-BE913.800] CKT 1 | 5.536 | 7.5691 | 7469.1252 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [BLAISDEL-BE4230.00] TO [TIOGA4 4 230.00] CKT 1 | 5.1436 | 7.5705 | 7470.4549 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [BLAISDEL-BE4230.00] TO [BLAISDEL-BE7115.00] TO [BLS.T1__-BE913.800] CKT 1 | 5.6045 | 7.5646 | 7464.5524 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TANDE___-BE3345.00] TO [TANDE___-BE4230.00] TO [TND.KU3A-BE913.800] CKT 1 | 4.1289 | 7.5523 | 7452.3482 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [WHEELOCK-BE4230.00] TO [TIOGA4 4 230.00] CKT 1 | 5.0696 | 7.5751 | 7475.0862 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TIOGA4 4 230.00] TO [BDV 4230.00] CKT 1 | 4.6885 | 7.5262 | 7426.2291 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TIOGA4 4 230.00] TO [TIOGA4 7 115.00] TO [TIOGA4 9 13.800] CKT 1 | 5.5689 | 7.5703 | 7470.339 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [MALLARD7 115.00] TO [SOURIS 7 115.00] CKT 1 | 5.5718 | 7.5573 | 7457.3385 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [MALLARD7 115.00] TO [NELSON 7 115.00] CKT 1 | 5.6096 | 7.5568 | 7456.7677 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [MALLARD7 115.00] TO [RUGBY 7 115.00] CKT 1 | 5.613 | 7.5587 | 7458.6963 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [MALLARD7 115.00] TO [MALLARD1-CP941.600] CKT 1 | 5.6274 | 7.5598 | 7459.8482 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [MALLARD7 115.00] TO [MALLARD2-CP941.600] CKT 1 | 5.6273 | 7.5599 | 7459.8963 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [MALLARD7 115.00] TO [E.RUTHVL-CP7115.00] CKT 1 | 5.6266 | 7.5593 | 7459.3222 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [GRE-STANTON4230.00] TO [GRE-COAL CR4230.00] CKT 1 | 5.6263 | 7.5596 | 7459.5882 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [GRE-STANTON4230.00] TO [GRE-COAL TP4230.00] CKT 1 | 5.6281 | 7.5597 | 7459.6544 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [GRE-STANTON4230.00] TO [SQBUTTE4 230.00] CKT 1 | 5.6252 | 7.5591 | 7459.1241 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TWIN CH4 230.00] TO [WAKEFIELD 4230.00] CKT 1 | 5.6285 | 7.5597 | 7459.6714 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TWIN CH4 230.00] TO [TWIN CH7 115.00] TO [TWIN CH T4 913.800] CKT 1 | 5.6285 | 7.5597 | 7459.6715 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TWIN CH4 230.00] TO [TWIN CH7 115.00] TO [TWIN CH T6 913.800] CKT 2 | 5.6285 | 7.5597 | 7459.6715 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [VFODNES4 230.00] TO [G17-175TAP 230.00] CKT 1 | 5.6285 | 7.5597 | 7459.6684 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [GARRISN4 230.00] TO [JAMESTN4 230.00] CKT 1 | 5.6236 | 7.5596 | 7459.5676 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [GARRISN4 230.00] TO [GARISN1G 13.800] CKT 1 | 5.622 | 7.5592 | 7459.1612 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [GARRISN4 230.00] TO [GARISN2G 13.800] CKT 1 | 5.622 | 7.5592 | 7459.1613 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [GARRISN4 230.00] TO [GARISN3G 13.800] CKT 1 | 5.622 | 7.5592 | 7459.1615 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [GARRISN4 230.00] TO [HILKEN 4 230.00] CKT 1 | 5.6252 | 7.5594 | 7459.4363 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [GARRISN4 230.00] TO [GARRISN7 115.00] TO [GARRISON 9 13.800] CKT 1 | 5.616 | 7.5586 | 7458.5547 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [WASHBRN4 230.00] TO [WASHBRN9 41.800] CKT 1 | 5.6283 | 7.5597 | 7459.6977 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [WASHBRN4 230.00] TO [BISMARK4 230.00] CKT 1 | 5.6082 | 7.5585 | 7458.5445 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [FTRANDL4 230.00] TO [MEADOWGROVE4230.00] CKT 1 | 5.6284 | 7.5597 | 7459.6595 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [FTRANDL4 230.00] TO [FTTHOMP4 230.00] CKT 1 | 5.6281 | 7.5596 | 7459.6428 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [FTRANDL4 230.00] TO [FTRANDL7 115.00] CKT 1 | 5.6285 | 7.5597 | 7459.6713 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [FTRANDL4 230.00] TO [FTRANDL7 115.00] CKT 2 | 5.6285 | 7.5597 | 7459.6713 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [FTRANDL4 230.00] TO [FTRDL34G 13.800] CKT 1 | 5.6284 | 7.5597 | 7459.6753 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [FTRANDL4 230.00] TO [FTRDL56G 13.800] CKT 1 | 5.6284 | 7.5597 | 7459.6754 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [FTRANDL4 230.00] TO [FTRDL78G 13.800] CKT 1 | 5.6285 | 7.5597 | 7459.6731 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [FTRANDL4 230.00] TO [LAKPLAT-ER4 230.00] CKT 1 | 5.6281 | 7.5596 | 7459.6434 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXFL4 230.00] TO [SPLT RK4 230.00] CKT 1 | 5.6285 | 7.5597 | 7459.6685 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXFL4 230.00] TO [HANLON 4 230.00] CKT 1 | 5.6283 | 7.5596 | 7459.6458 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXFL4 230.00] TO [LETCHER4 230.00] CKT 1 | 5.6283 | 7.5596 | 7459.6451 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXFL4 230.00] TO [PAHOJA__-BE4230.00] CKT 1 | 5.6284 | 7.5597 | 7459.6632 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXFL4 230.00] TO [SIOUXFL7 115.00] TO [SIOUXF19 13.200] CKT 1 | 5.6285 | 7.5597 | 7459.6704 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXFL4 230.00] TO [SIOUXFL7 115.00] TO [SIOUXF29 13.200] CKT 1 | 5.6285 | 7.5597 | 7459.6703 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [UTICAJC4 230.00] TO [G17-175TAP 230.00] CKT 1 | 5.6285 | 7.5597 | 7459.6714 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXCY2 230.00] TO [EAGLE___-NI4230.00] CKT 1 | 5.6285 | 7.5597 | 7459.6696 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXCY2 230.00] TO [SIOUXCY3 345.00] TO [SIOUXC19 13.800] CKT 1 | 5.6285 | 7.5597 | 7459.6721 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXCY2 230.00] TO [SIOUXCY3 345.00] TO [SIOUXC29 13.800] CKT 1 | 5.6285 | 7.5597 | 7459.672 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [DENISON5 161.00] TO [DENISON4 230.00] TO [DENISON 9 13.800] CKT 1 | 5.6285 | 7.5597 | 7459.6698 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXCY4 230.00] TO [DENISON4 230.00] CKT 1 | 5.6285 | 7.5597 | 7459.6689 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXCY5 161.00] TO [PLYMOTH5 161.00] CKT 1 | 5.6285 | 7.5597 | 7459.6693 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXCY5 161.00] TO [SPENCER5 161.00] CKT 1 | 5.6285 | 7.5597 | 7459.6711 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SIOUXCY5 161.00] TO [SIOUXCY8 69.000] CKT 1 | 5.6285 | 7.5597 | 7459.6714 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [DENISON8 69.000] TO [DENISON4 230.00] CKT 1 | 5.6285 | 7.5597 | 7459.6714 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [DENISON8 69.000] TO [DENISON4 230.00] CKT 2 | 5.6285 | 7.5597 | 7459.6713 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [EXIRA 5 161.00] TO [ANTA TP5 161.00] CKT 1 | 5.6285 | 7.5597 | 7459.6697 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [EXIRA 5 161.00] TO [EXIRA 1G 13.800] CKT 1 | 5.6285 | 7.5597 | 7459.6716 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [EXIRA 5 161.00] TO [EXIRA 2G 13.800] CKT 1 | 5.6285 | 7.5597 | 7459.6716 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [EXIRA 5 161.00] TO [EXIRA 3G 13.800] CKT 1 | 5.6285 | 7.5597 | 7459.6716 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [UTICAJC7 115.00] TO [FREEMAN-ER7 115.00] CKT 1 | 5.6285 | 7.5597 | 7459.6705 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [UTICAJC7 115.00] TO [MENNO JCT 7115.00] CKT 1 | 5.6285 | 7.5597 | 7459.6694 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [UTICAJC7 115.00] TO [NAPA JCT 7115.00] CKT 1 | 5.6284 | 7.5597 | 7459.6694 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [PRVLNG16 230.00] TO [PRVLNG23 115.00] TO [PRVLNGT21 13.800] CKT 1 | 5.6285 | 7.5597 | 7459.675 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [VFODNES-ER7 115.00] TO [SXFCHCLR-ER7115.00] CKT 1 | 5.6285 | 7.5597 | 7459.6713 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [VFODNES-ER7 115.00] TO [BUCKSNRT-ER7115.00] CKT 1 | 5.6285 | 7.5597 | 7459.6705 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [VFODNES-ER7 115.00] TO [SW1109-ER7 115.00] CKT 1 | 5.6285 | 7.5597 | 7459.6705 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [VFODNES-ER7 115.00] TO [DAYTON__-ER7115.00] CKT 1 | 5.6285 | 7.5597 | 7459.6694 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [RASMUSN-ER4 230.00] TO [RASMUSN-ER8 69.000] CKT 1 | 5.6285 | 7.5597 | 7459.6704 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SW.MINOT-CP7115.00] TO [SW.MNOT1-CP941.600] CKT 1 | 5.6279 | 7.5598 | 7459.821 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SW.MINOT-CP7115.00] TO [SW.MNOT2-CP941.600] CKT 2 | 5.6248 | 7.5603 | 7460.2506 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SW.MINOT-CP7115.00] TO [BERTHOLD-CP7115.00] CKT 1 | 5.5381 | 7.5538 | 7453.8387 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [SW.MINOT-CP7115.00] TO [E.RUTHVL-CP7115.00] CKT 1 | 5.619 | 7.5594 | 7459.379 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [WHTEARTH-MW7115.00] TO [PLSNTV_T-MW7115.00] CKT 1 | 5.6238 | 7.5601 | 7460.0682 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [PWRSLKTP-MW7115.00] TO [POWERSLK-MW7115.00] CKT 1 | 5.6214 | 7.5612 | 7461.177 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [PWRSLKTP-MW7115.00] TO [LIBERTY -MW7115.00] CKT 1 | 5.613 | 7.554 | 7453.9576 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TIOGA.N_-MW7115.00] TO [W.BANK_T-MW7115.00] CKT 1 | 5.5838 | 7.56 | 7460.0093 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [MANNINGTAP 869.000] TO [TEMPLTON8 69.000] CKT 1 | 5.6285 | 7.5597 | 7459.6715 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [LELAND_O-BE3345.00] TO [GEN-2016-130345.00] CKT 1 | 5.629 | 7.5589 | 7458.8719 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [LELAND_O-BE3345.00] TO [FINSTAD345 345.00] CKT 1 | 4.84 | 7.5017 | 7401.7405 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [LELAND_O-BE3345.00] TO [ANTELOPE-BE3345.00] CKT 1 | 5.6259 | 7.5601 | 7460.0647 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [LELAND_O-BE3345.00] TO [ANTELOPE-BE3345.00] CKT 2 | 5.6259 | 7.5601 | 7460.0648 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [LELAND_O-BE3345.00] TO [LELAND_2-BEG20.000] CKT 1 | 5.5755 | 7.5552 | 7455.2434 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [LELAND_O-BE3345.00] TO [LO.LS-GR-BE3345.00] CKT Z | 5.603 | 7.5577 | 7457.68 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [LELAND_O-BE3345.00] TO [LO.LS-FT-BE3345.00] CKT Z | 5.6039 | 7.5578 | 7457.8186 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [LELAND_O-BE4230.00] TO [LOGAN___-BE4230.00] CKT 1 | 5.4612 | 7.5539 | 7453.8579 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [NESET___-BE7115.00] TO [NESET___-BE4230.00] TO [NES.KV2A-BE913.800] CKT 1 | 5.5692 | 7.5703 | 7470.3291 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [NRTSHORE-BE4230.00] TO [NESET___-BE4230.00] CKT 1 | 5.5416 | 7.5703 | 7470.284 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [NRTSHORE-BE7115.00] TO [BROOKBNK-MW7115.00] CKT 1 | 5.5978 | 7.5612 | 7461.164 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [NRTSHORE-BE7115.00] TO [ROSS -MW7115.00] CKT 1 | 5.6212 | 7.5614 | 7461.3833 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [NRTSHORE-BE7115.00] TO [RATLAKE -MW7115.00] CKT 1 | 5.6318 | 7.5598 | 7459.8232 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [NRTSHORE-BE7115.00] TO [SATTER -MW7115.00] CKT 1 | 5.5972 | 7.5593 | 7459.2537 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [BLAISDEL-BE4230.00] TO [LOGAN___-BE4230.00] CKT 1 | 5.2228 | 7.5506 | 7450.5795 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [BLAISDEL-BE7115.00] TO [BERTHOLD-CP7115.00] CKT 1 | 5.5969 | 7.5591 | 7459.1101 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [BLAISDEL-BE7115.00] TO [PALERMO -MW7115.00] CKT 1 | 5.6283 | 7.5577 | 7457.7225 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [BLAISDEL-BE7115.00] TO [BLAISDEL-MW7115.00] CKT 1 | 5.6198 | 7.5595 | 7459.5431 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [LOGAN___-BE7115.00] TO [LOGAN___-BE4230.00] TO [LGN.KW1A-BE913.800] CKT 1 | 5.5659 | 7.5621 | 7462.1025 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [BASIN___-BE4230.00] TO [GEN-2016-004230.00] CKT 1 | 5.6203 | 7.5591 | 7459.0651 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [BASIN___-BE4230.00] TO [BASIN___-BE7115.00] TO [BAL.KY1A-BE913.800] CKT 1 | 5.6275 | 7.5599 | 7459.8654 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TANDE___-BE3345.00] TO [FINSTAD345 345.00] CKT 1 | 5.1169 | 7.5718 | 7471.8304 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TANDE___-BE3345.00] TO [BURKE___-PP3345.00] CKT 1 | 5.6475 | 7.5521 | 7452.0726 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TANDE___-BE3345.00] TO [TN.LS-JD-BE3345.00] CKT Z | 4.8938 | 7.5545 | 7454.5221 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TANDE___-BE3345.00] TO [TRADEWND-UA3345.00] CKT 1 | 5.6467 | 7.5459 | 7445.9247 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TANDE___-BE4230.00] TO [NESET___-BE4230.00] CKT 1 | 4.1291 | 7.5524 | 7452.4151 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [WHEELOCK-BE4230.00] TO [WILISTN4 230.00] CKT 1 | 5.1885 | 7.5578 | 7457.7858 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [WHEELOCK-BE4230.00] TO [WHEELOCK-BE7115.00] TO [WEL.T1__-BE913.800] CKT 1 | 5.6115 | 7.5642 | 7464.2482 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [J6BOYER_-NI869.000] TO [K335AMAI-NI869.000] CKT 1 | 5.6285 | 7.5597 | 7459.6714 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [J6BOYER_-NI869.000] TO [K307DENI-NI869.000] CKT 1 | 5.6285 | 7.5597 | 7459.6714 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [J6BOYER_-NI869.000] TO [K306SCHL-NI869.000] CKT 1 | 5.6285 | 7.5597 | 7459.6716 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [J6BOYER_-NI869.000] TO [J12_____-NI869.000] CKT 1 | 5.6285 | 7.5597 | 7459.6715 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TIOGA4 4 230.00] TO [NESET___-BE4230.00] CKT Z | 3.7072 | 7.6229 | 7522.934 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TIOGA4 7 115.00] TO [STANLEY7 115.00] CKT 1 | 5.6008 | 7.5618 | 7461.792 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [TIOGA4 7 115.00] TO [TIOGA7 7 115.00] CKT 1 | 5.5265 | 7.5627 | 7462.6654 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [BDV 4230.00] TO [BDX 4230.00] CKT 1 & 2 | 4.6766 | 7.5235 | 7423.4988 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [FTRANDL4 230.00] TO [FTRANDL7 115.00] CKT 1 & 2 | 5.6284 | 7.5597 | 7459.6713 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [DENISON8 69.000] TO [DENISON4 230.00] CKT 1 & 2 | 5.6285 | 7.5597 | 7459.6704 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 01 NORTH | 25WP | GEN-2018-010 | Neset 230kV Substation | OPEN LINE FROM [LELAND_O-BE3345.00] TO [ANTELOPE-BE3345.00] CKT 1 & 2 | 5.6082 | 7.5615 | 7461.5127 | 74.1 | 84 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | Base | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [7FAIRPT 345.00] TO [ST JOE 7 345.00] CKT 1 | 6.2511 | 0.1828 | 82.8045 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [7FAIRPT 345.00] TO [COOPER 3 345.00] CKT 1 | 6.2528 | 0.1827 | 82.723 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [5CLINTN 161.00] TO [5HOLDENB2 161.00] CKT 1 | 6.2529 | 0.1827 | 82.7212 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [5CLINTN 161.00] TO [2CLINTN 69.000] CKT 1 | 6.2528 | 0.1827 | 82.7222 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [5CLINTN 161.00] TO [2CLINTN 69.000] CKT 3 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [5CLINTN 161.00] TO [5OSCEOKCTP 161.00] CKT 1 | 6.2527 | 0.1827 | 82.7231 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [5CLINTN 161.00] TO [TRUMAN 5 161.00] CKT 1 | 6.2528 | 0.1827 | 82.7222 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [5CLINTN 161.00] TO [WINDSR 5 161.00] CKT 1 | 6.2528 | 0.1827 | 82.7223 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [5CLINTN 161.00] TO [CLINTON5 161.00] CKT Z1 | 6.2527 | 0.1827 | 82.7224 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [5NEWMAD 161.00] TO [N MADRD5 161.00] CKT 1 | 6.2528 | 0.1827 | 82.7239 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [5NEWMAD 161.00] TO [SIKETAP5 161.00] CKT 1 | 6.2527 | 0.1827 | 82.7227 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHAMSPR1 13.800] TO [CHAMSPR5 161.00] TO [CHAMSPR7 345.00] CKT 1 | 6.2527 | 0.1827 | 82.7246 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHAMSPR7 345.00] TO [TONTITN7 345.00] CKT 1 | 6.2528 | 0.1827 | 82.7245 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [BOONVIL2 69.000] TO [BRANCH 2 69.000] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NMAGZIN5 161.00] TO [WBOONVL5 161.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NMAGZIN5 161.00] TO [MAGZREC5 161.00] CKT 1 | 6.2528 | 0.1827 | 82.722 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SW SHV 4 138.00] TO [SW SHV 7 345.00] TO [SWSHV1-1 13.800] CKT 1 | 6.2528 | 0.1827 | 82.722 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SW SHV 4 138.00] TO [SW SHV 7 345.00] TO [SWSHV2-1 13.800] CKT 2 | 6.2528 | 0.1827 | 82.722 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SW SHV 7 345.00] TO [DIANA 7 345.00] CKT 1 | 6.2528 | 0.1827 | 82.724 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORAM 4 138.00] TO [LONGWD 4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WELSH 7 345.00] TO [DIANA 7 345.00] CKT 1 | 6.2528 | 0.1827 | 82.7236 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WELSH 7 345.00] TO [DIANA 7 345.00] CKT 2 | 6.2528 | 0.1827 | 82.7236 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WELSH 7 345.00] TO [WILKES 7 345.00] CKT 1 | 6.2528 | 0.1827 | 82.7246 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SCOTTSV4 138.00] TO [LONGWD 4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7223 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LIEBERM4 138.00] TO [LONGWD 4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.722 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LONGWD 4 138.00] TO [OAKPH 4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILKES-1 13.200] TO [WILKES 4 138.00] TO [WILKES 7 345.00] CKT 1 | 6.2528 | 0.1827 | 82.7218 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILKES 7 345.00] TO [WILKE3-1 22.000] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILKES 7 345.00] TO [WILKE3-1 22.000] CKT 2 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [36&OLY-4 138.00] TO [CARSN-T4 138.00] CKT 1 | 6.2526 | 0.1827 | 82.7223 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OAKS W4 138.00] TO [OAKSWTP4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7218 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DENVTAP4 138.00] TO [T.NO.--4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7212 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILLPIP2 69.000] TO [T.P.S.-2 69.000] CKT 1 | 6.2528 | 0.1827 | 82.722 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WEKIWA-7 345.00] TO [T.NO.--7 345.00] CKT 1 | 6.2525 | 0.1827 | 82.7272 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WEKIWA-7 345.00] TO [SAPLPRD7 345.00] CKT 1 | 6.2511 | 0.1827 | 82.7316 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WEKIWA-7 345.00] TO [SOONER 7 345.00] CKT 1 | 6.2477 | 0.1827 | 82.7255 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CARSN-S4 138.00] TO [KENSH-W4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7218 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RSS T1 4 138.00] TO [R.S.S.-4 138.00] CKT 1 | 6.2527 | 0.1827 | 82.7233 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RSS T1 4 138.00] TO [R.S.S.-7 345.00] TO [RSST1 T1 13.800] CKT 1 | 6.2527 | 0.1827 | 82.7233 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [52DELTP4 138.00] TO [36LEWIS4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7223 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-7 345.00] TO [ONETA--7 345.00] CKT 1 | 6.2523 | 0.1827 | 82.7266 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-7 345.00] TO [COGENT 7 345.00] CKT 1 | 6.2521 | 0.1827 | 82.7225 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-7 345.00] TO [SAPLPRD7 345.00] CKT 1 | 6.2517 | 0.1827 | 82.7328 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-7 345.00] TO [REDBUD 7 345.00] CKT 1 | 6.2482 | 0.1828 | 82.7614 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-7 345.00] TO [G16133G16146345.00] CKT 1 | 6.2522 | 0.1827 | 82.7316 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-7 345.00] TO [RSS T2 4 138.00] TO [RSST2 T1 13.800] CKT 1 | 6.2527 | 0.1827 | 82.7233 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-4 138.00] TO [52DELWT4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7225 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-4 138.00] TO [OAKSETP4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7226 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-4 138.00] TO [RSS T2 4 138.00] CKT 1 | 6.2527 | 0.1827 | 82.7233 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ONETA--4 138.00] TO [ONETA--7 345.00] TO [ONETA1-1 13.800] CKT 1 | 6.2528 | 0.1827 | 82.7226 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ONETA--4 138.00] TO [ONETA--7 345.00] TO [ONETA2-1 34.500] CKT 2 | 6.2528 | 0.1827 | 82.7226 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ONETA--4 138.00] TO [ONETA--7 345.00] TO [ONETA5-1 34.500] CKT 3 | 6.2528 | 0.1827 | 82.7227 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ONETA--7 345.00] TO [OEC 7 345.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ONETA--7 345.00] TO [OEC 7 345.00] CKT 2 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ONETA--7 345.00] TO [N.E.S.-7 345.00] CKT 1 | 6.2526 | 0.1827 | 82.728 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [52DELWT4 138.00] TO [S HILLW4 138.00] CKT 1 | 6.2527 | 0.1827 | 82.7218 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [T.NO.--4 138.00] TO [CDC-ET 4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.721 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [T.NO.--4 138.00] TO [CDC-WT 4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7215 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [T.NO.--4 138.00] TO [OWASOTP4 138.00] CKT 1 | 6.2527 | 0.1827 | 82.7218 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [T.NO.--4 138.00] TO [P&P WTP4 138.00] CKT 1 | 6.2527 | 0.1827 | 82.7208 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [T.NO.--4 138.00] TO [SKIATOK4 138.00] CKT 1 | 6.2527 | 0.1827 | 82.7261 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [T.NO.--4 138.00] TO [46ST-TP-4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.722 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [T.NO.--4 138.00] TO [N.E.S.-4 138.00] CKT 1 | 6.2527 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OAKS--E4 138.00] TO [OAKSETP4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7219 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OAKSWTP4 138.00] TO [SAPLPRD4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [T.NO.--7 345.00] TO [N.E.S.-7 345.00] CKT 1 | 6.2516 | 0.1827 | 82.7236 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [T.NO.--7 345.00] TO [CLEVLND7 345.00] CKT 1 | 6.2475 | 0.1827 | 82.7145 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [T.NO.--7 345.00] TO [IGLOOV 7 345.00] CKT 1 | 6.2514 | 0.1827 | 82.7202 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SAPLPRD4 138.00] TO [72ELWOD4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7222 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [PITTSB-7 345.00] TO [VALIANT7 345.00] CKT 1 | 6.2517 | 0.1827 | 82.7327 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [PITTSB-7 345.00] TO [KIOWA 7 345.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [PITTSB-7 345.00] TO [SEMINOL7 345.00] CKT 1 | 6.2517 | 0.1827 | 82.7331 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [PITTSB-7 345.00] TO [C-RIVER7 345.00] CKT 1 | 6.2526 | 0.1827 | 82.721 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VALIANT7 345.00] TO [HUGO 7 345.00] CKT 1 | 6.2526 | 0.1827 | 82.7303 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [C-RIVER4 138.00] TO [C-RIVER7 345.00] TO [C-RIVER1 13.800] CKT 1 | 6.2526 | 0.1827 | 82.7326 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LES#5-1 13.800] TO [L.E.S.-4 138.00] TO [L.E.S.-7 345.00] CKT 2 | 6.2528 | 0.1827 | 82.7181 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LES#4-1 13.800] TO [L.E.S.-4 138.00] TO [L.E.S.-7 345.00] CKT 1 | 6.2529 | 0.1827 | 82.7202 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [O.K.U.-7 345.00] TO [L.E.S.-7 345.00] CKT 1 | 6.2522 | 0.1827 | 82.7117 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [L.E.S.-7 345.00] TO [G16-091-TAP 345.00] CKT 1 | 6.2497 | 0.1827 | 82.7306 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CAN_GAS4 138.00] TO [JENSEN 4 138.00] CKT 1 | 6.2483 | 0.1825 | 82.5408 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHISHOLM7 345.00] TO [BECKHAM7 345.00] CKT 1 | 6.253 | 0.1827 | 82.7135 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHISHOLM7 345.00] TO [CHISHOLM6 230.00] TO [CHISHOLM1 13.200] CKT 1 | 6.2532 | 0.1827 | 82.7019 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RSHSPR1_TER113.800] TO [RSHSPR1_COL134.500] TO [RSHSPR1_MPT1345.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OTTER 4 138.00] TO [WOODRNG4 138.00] CKT 1 | 6.1783 | 0.1829 | 82.9391 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [FRMNTAP4 138.00] TO [WOODRNG4 138.00] CKT 1 | 6.238 | 0.1831 | 83.0842 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WAUKOMI4 138.00] TO [WAUKOTP4 138.00] CKT 1 | 4.0899 | 0.1883 | 88.2926 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WAUKOMI4 138.00] TO [HENESEY4 138.00] CKT 1 | 4.0861 | 0.1883 | 88.3375 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WAUKOTP4 138.00] TO [WOODRNG4 138.00] CKT 1 | 5.9828 | 0.1834 | 83.3911 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WOODRNG4 138.00] TO [MARSHL 4 138.00] CKT 1 | 6.2428 | 0.1827 | 82.7462 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MARSHL 4 138.00] TO [CTNWOOD4 138.00] CKT 1 | 6.2425 | 0.1828 | 82.762 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DOVERTP2 69.000] TO [DOVERSW2 69.000] CKT 1 | 5.9844 | 0.1837 | 83.7345 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HENESEY4 138.00] TO [BULFTTP4 138.00] CKT 1 | 6.0623 | 0.1831 | 83.066 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SOONER 7 345.00] TO [PINTAIL7 345.00] CKT 1 | 6.2053 | 0.1827 | 82.7194 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [JOHNCO 4 138.00] TO [RUSSET-4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.724 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [JOHNCO 4 138.00] TO [SXMLCKT4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7226 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [JOHNCO 4 138.00] TO [CANEYCK4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7234 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [YUKON 2 69.000] TO [MSTANG 2 69.000] CKT 1 | 6.2262 | 0.1829 | 82.8746 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [JENSENT4 138.00] TO [JENSEN 4 138.00] CKT 1 | 6.1795 | 0.1836 | 83.5674 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [JENSENT4 138.00] TO [CIMARON4 138.00] CKT 1 | 6.2205 | 0.1831 | 83.0963 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CTNWOOD4 138.00] TO [ARCADIA4 138.00] CKT 1 | 6.1087 | 0.1835 | 83.5456 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHTWOOD4 138.00] TO [LGARBER4 138.00] CKT 1 | 6.2519 | 0.1827 | 82.7145 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHTWOOD4 138.00] TO [JONESSB4 138.00] CKT 1 | 6.2519 | 0.1827 | 82.7172 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LAKESID4 138.00] TO [DVISION4 138.00] CKT 1 | 6.2526 | 0.1827 | 82.735 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SLVRLAK4 138.00] TO [DVISION4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7214 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DVISION4 138.00] TO [RICHRDS4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7208 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DVISION4 138.00] TO [HAYMAKR4 138.00] CKT 1 | 6.2521 | 0.1827 | 82.7225 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MSTANG 2 69.000] TO [WODLAWN2 69.000] CKT 1 | 6.2523 | 0.1828 | 82.7552 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MSTANG 2 69.000] TO [WILROGR2 69.000] CKT 1 | 6.2525 | 0.1827 | 82.7282 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MSTANG 2 69.000] TO [MCARTHR2 69.000] CKT 1 | 6.2524 | 0.1827 | 82.7427 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MSTANG 2 69.000] TO [MSTNG 6G 13.800] CKT 1 | 6.2512 | 0.1827 | 82.7041 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MSTANG 2 69.000] TO [MSTNG 7G 13.800] CKT 1 | 6.2512 | 0.1827 | 82.7041 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HAYMAKR4 138.00] TO [CIMARON4 138.00] CKT 1 | 6.2521 | 0.1827 | 82.7258 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [COUNCIL4 138.00] TO [WESTOAK4 138.00] CKT 1 | 6.2521 | 0.1828 | 82.7653 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORTWST4 138.00] TO [NORTWST7 345.00] TO [NORTWS21 13.800] CKT 1 | 6.252 | 0.1827 | 82.7464 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORTWST4 138.00] TO [NORTWST7 345.00] TO [NORTWS31 13.800] CKT 1 | 6.252 | 0.1827 | 82.7478 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORTWST4 138.00] TO [NORTWST7 345.00] TO [NORTWS41 13.800] CKT 1 | 6.252 | 0.1827 | 82.7477 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORTWST7 345.00] TO [SPRNGCK7 345.00] CKT 1 | 6.2487 | 0.1827 | 82.7192 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORTWST7 345.00] TO [CIMARON7 345.00] CKT 1 | 6.2526 | 0.1827 | 82.7274 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORTWST7 345.00] TO [MATHWSN7 345.00] CKT 1 | 6.2512 | 0.1827 | 82.7366 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DUNJEE 4 138.00] TO [RENO 4 138.00] CKT 1 | 6.2526 | 0.1827 | 82.7257 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [36&MER 4 138.00] TO [SW 5TH 4 138.00] CKT 1 | 6.2526 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [36&MER 4 138.00] TO [HOBBYLO4 138.00] CKT 1 | 6.2529 | 0.1827 | 82.7198 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SMITHCO4 138.00] TO [DAYTON 4 138.00] CKT 1 | 6.2511 | 0.1827 | 82.7153 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DAYTON 4 138.00] TO [HOBBYLO4 138.00] CKT 1 | 6.2527 | 0.1827 | 82.7282 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [XEROX 4 138.00] TO [MORGAN 4 138.00] CKT 1 | 6.2509 | 0.1827 | 82.6649 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CIMARON4 138.00] TO [CIMARON7 345.00] TO [CIMARO11 13.800] CKT 1 | 6.2476 | 0.1829 | 82.8902 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CIMARON4 138.00] TO [CIMARON7 345.00] TO [CIMARO21 13.800] CKT 2 | 6.2489 | 0.1828 | 82.8444 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDBUD1S 18.000] TO [REDBUD 7 345.00] TO [REDBUD1G 18.000] CKT 1 | 6.2485 | 0.1827 | 82.707 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDBUD2S 18.000] TO [REDBUD 7 345.00] TO [REDBUD2G 18.000] CKT 1 | 6.2485 | 0.1827 | 82.707 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CIMARON7 345.00] TO [MATHWSN7 345.00] CKT 1 | 6.252 | 0.1827 | 82.7342 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CIMARON7 345.00] TO [MATHWSN7 345.00] CKT 2 | 6.2521 | 0.1827 | 82.7342 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CIMARON7 345.00] TO [FSHRTAP7 345.00] CKT 1 | 6.2477 | 0.1827 | 82.743 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CIMARON7 345.00] TO [NORMHLL7 345.00] CKT 1 | 6.2495 | 0.1827 | 82.7167 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDBUD3S 18.000] TO [REDBUD 7 345.00] TO [REDBUD3G 18.000] CKT 1 | 6.2484 | 0.1827 | 82.7071 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [JNSKAMO4 138.00] TO [ARCADIA4 138.00] CKT 1 | 6.2512 | 0.1827 | 82.6846 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ARCADIA4 138.00] TO [RNDBARN4 138.00] CKT 1 | 6.2509 | 0.1828 | 82.809 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ARCADIA4 138.00] TO [LGARBER4 138.00] CKT 1 | 6.252 | 0.1827 | 82.7133 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDBUD 7 345.00] TO [REDBUD4S 18.000] TO [REDBUD4G 18.000] CKT 1 | 6.2484 | 0.1827 | 82.7071 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SW 5TH 2 69.000] TO [SW 5TH 4 138.00] TO [SW 5TH 1 13.800] CKT 1 | 6.2529 | 0.1827 | 82.7168 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SW 5TH 4 138.00] TO [CLASSEN4 138.00] CKT 1 | 6.2524 | 0.1827 | 82.7413 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HSLEAST2 69.000] TO [HSLWEST2 69.000] CKT 1 | 6.2528 | 0.1827 | 82.7257 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DRAPER 7 345.00] TO [SEMINOL7 345.00] CKT 1 | 6.2511 | 0.1827 | 82.7341 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DRAPER 7 345.00] TO [SEMINOL7 345.00] CKT 2 | 6.2511 | 0.1827 | 82.7341 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DRAPER 7 345.00] TO [SEMINOL7 345.00] CKT 3 | 6.2519 | 0.1827 | 82.7351 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DRAPER 7 345.00] TO [NORMHLL7 345.00] CKT 1 | 6.2521 | 0.1827 | 82.7263 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DRAPER 7 345.00] TO [NORMHLL7 345.00] CKT 2 | 6.2522 | 0.1827 | 82.7263 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NE10TH 4 138.00] TO [MIDWAY 4 138.00] CKT 1 | 6.2527 | 0.1827 | 82.7239 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NE10TH 4 138.00] TO [RENO 4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7174 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GLENDAL4 138.00] TO [SE15TH 4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7232 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DALE 4 138.00] TO [SQUIRCK4 138.00] CKT 1 | 6.2523 | 0.1827 | 82.7262 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SE15TH 4 138.00] TO [BARNES 4 138.00] CKT 1 | 6.2529 | 0.1827 | 82.7203 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SEMINL2G 17.100] TO [SEMINOL7 345.00] CKT 1 | 6.2506 | 0.1827 | 82.7054 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SEMINL3G 20.900] TO [SEMINOL7 345.00] CKT 1 | 6.2498 | 0.1827 | 82.7064 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRTPLNS4 138.00] TO [LNWOODT4 138.00] CKT 1 | 6.2527 | 0.1827 | 82.7247 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SEMINOL4 138.00] TO [SEMINOL7 345.00] TO [SEMINO11 14.400] CKT 1 | 6.2525 | 0.1827 | 82.7228 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SEMINOL4 138.00] TO [SEMINOL7 345.00] TO [SEMINO21 14.400] CKT 1 | 6.2525 | 0.1827 | 82.7229 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HAMMTAP4 138.00] TO [LINCOLN4 138.00] CKT 1 | 6.2521 | 0.1828 | 82.7552 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HAMMTAP4 138.00] TO [HAMMETT4 138.00] CKT 1 | 6.2529 | 0.1827 | 82.7222 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WARWICK4 138.00] TO [WFROSST4 138.00] CKT 1 | 6.2526 | 0.1827 | 82.7239 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WARWICK4 138.00] TO [BELLCOW4 138.00] CKT 1 | 6.2525 | 0.1827 | 82.7238 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RUSSET-4 138.00] TO [RUSSETT4 138.00] CKT 1 | 6.2527 | 0.1827 | 82.7239 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SUNNYSD4 138.00] TO [UNIROY 4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7245 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SUNNYSD4 138.00] TO [LONEGRV4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7233 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SUNNYSD4 138.00] TO [ROCKYPT4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7245 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SUNNYSD4 138.00] TO [CARTRCO4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7224 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [BROWNTP4 138.00] TO [STRRDTP4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [COLEMNT4 138.00] TO [STRRDTP4 138.00] CKT 1 | 6.2529 | 0.1827 | 82.7222 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MUSKOG4G 18.000] TO [MUSKOGE7 345.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MUSKOGE7 345.00] TO [MUSKOG5G 18.000] CKT 1 | 6.2524 | 0.1827 | 82.7207 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MUSKOGE7 345.00] TO [MUSKOG6G 24.000] CKT 1 | 6.2523 | 0.1827 | 82.7204 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MUSKOGE7 345.00] TO [FTSMITH7 345.00] CKT 1 | 6.2524 | 0.1827 | 82.7296 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [5TRIBES5 161.00] TO [PECANCK5 161.00] CKT 1 | 6.2528 | 0.1827 | 82.7244 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [AGENCY 5 161.00] TO [PECANCK5 161.00] CKT 1 | 6.2528 | 0.1827 | 82.7238 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [PECANCK4 138.00] TO [PECANCK5 161.00] TO [PECANC31 13.200] CKT 1 | 6.2523 | 0.1827 | 82.7245 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [BRANCH 2 69.000] TO [PENDER 2 69.000] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VBI 5 161.00] TO [GRNDPRT5 161.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SHORTMT5 161.00] TO [SUBIACT5 161.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WFROSST4 138.00] TO [LINCOLN4 138.00] CKT 1 | 6.2525 | 0.1827 | 82.7249 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LINWOOD4 138.00] TO [LNWOODT4 138.00] CKT 1 | 6.2529 | 0.1827 | 82.7145 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MNCOWND1 34.500] TO [MCNOWND7 345.00] CKT 1 | 6.253 | 0.1827 | 82.7158 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ACORN 4 138.00] TO [JONESSB4 138.00] CKT 1 | 6.2511 | 0.1827 | 82.7412 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HUNTERS7 345.00] TO [CHSHLMV7 345.00] CKT 1 | 6.2526 | 0.1828 | 82.7532 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MATHWSN7 345.00] TO [REDNGTN7 345.00] CKT 1 | 6.2229 | 0.1827 | 82.7456 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [KNIPE 4 138.00] TO [SPGVLLY4 138.00] CKT 1 | 6.2508 | 0.1827 | 82.7432 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RENFROW4 138.00] TO [GRANTCO4 138.00] CKT 1 | 6.2482 | 0.1828 | 82.8023 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RENFROW4 138.00] TO [MDFRDTP4 138.00] CKT 1 | 6.2523 | 0.1827 | 82.7312 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RENFROW4 138.00] TO [WFEC_RNFRO4 138.00] CKT 1 | 6.251 | 0.1827 | 82.7181 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MNCWND37 345.00] TO [MNCWND31 34.500] CKT 1 | 6.2529 | 0.1827 | 82.7178 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MNCWND37 345.00] TO [MNCWND47 345.00] CKT 1 | 6.253 | 0.1827 | 82.724 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRNTWD 7 345.00] TO [GRNTWD12 34.500] TO [GRNTWDT2 12.500] CKT 1 | 6.2523 | 0.1827 | 82.746 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRNTWD 7 345.00] TO [GRNTWD11 34.500] TO [GRNTWDT1 12.500] CKT 1 | 6.2523 | 0.1827 | 82.7459 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRACMNT7 345.00] TO [GEN-2015-093345.00] CKT 1 | 6.2532 | 0.1827 | 82.7092 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRACMNT7 345.00] TO [G16-091-TAP 345.00] CKT 1 | 6.25 | 0.1827 | 82.7219 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRACMNT7 345.00] TO [GRACMNT4 138.00] TO [GRCMNT11 13.800] CKT 1 | 6.2529 | 0.1827 | 82.7208 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDNGTN7 345.00] TO [REDDIRT7 345.00] CKT Z1 | 6.2531 | 0.1827 | 82.721 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [BULFOOT4 138.00] TO [BULFTTP4 138.00] CKT 1 | 6.2478 | 0.1826 | 82.5776 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SKELTON7 345.00] TO [GEN-2016-128345.00] CKT 1 | 6.2529 | 0.1827 | 82.7252 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SKELTON7 345.00] TO [SKELTL11 34.500] TO [SKELTT11 13.800] CKT 1 | 6.2519 | 0.1828 | 82.7794 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DMNDSL11 34.500] TO [DMNDSPG7 345.00] TO [DMNDST11 12.450] CKT 1 | 6.2529 | 0.1827 | 82.7183 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DMNDSL21 34.500] TO [DMNDSPG7 345.00] TO [DMNDST21 12.450] CKT 1 | 6.2529 | 0.1827 | 82.7179 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [PINTAIL7 345.00] TO [KINGWD 7 345.00] CKT Z1 | 6.2507 | 0.1828 | 82.825 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORMHLL7 345.00] TO [NORMHLL4 138.00] TO [NORMHL11 13.800] CKT 1 | 6.253 | 0.1827 | 82.7164 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORMHLL7 345.00] TO [NORMHLL4 138.00] TO [NORMHL21 13.800] CKT 2 | 6.253 | 0.1827 | 82.7164 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [KGFSJCT4 138.00] TO [NKNGFSH4 138.00] CKT 1 | 5.3511 | 0.1841 | 84.1432 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MUSTANG4 138.00] TO [SARA RD4 138.00] CKT 1 | 6.2338 | 0.1826 | 82.6459 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CANA 4 138.00] TO [SCOTTSW4 138.00] CKT 1 | 5.4709 | 0.1845 | 84.5445 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WATNGSW4 138.00] TO [OKEENE 4 138.00] CKT 1 | 6.2325 | 0.183 | 82.9753 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [TWNLAKE4 138.00] TO [DOVER 4 138.00] CKT 1 | 5.219 | 0.1851 | 85.0891 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDCNTP4 138.00] TO [SCOTTSW4 138.00] CKT 1 | 6.1483 | 0.1829 | 82.9076 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CDRDLTP4 138.00] TO [OKEENE 4 138.00] CKT 1 | 5.9014 | 0.1836 | 83.6037 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DOVERSW2 69.000] TO [HENESEY2 69.000] CKT 1 | 6.2503 | 0.1826 | 82.6432 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DOVERSW2 69.000] TO [LACEY 2 69.000] CKT 1 | 6.2492 | 0.1826 | 82.5762 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OKEENE 2 69.000] TO [OKEENE 4 138.00] TO [OKENTERT 13.800] CKT 1 | 6.1171 | 0.1829 | 82.9169 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HUGO 7 345.00] TO [G17-075-TAP 345.00] CKT 1 | 6.2518 | 0.1827 | 82.7379 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WICHITA7 345.00] TO [VIOLA 7 345.00] CKT 1 | 6.2446 | 0.1826 | 82.6316 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VIOLA 7 345.00] TO [G16-153-TAP 345.00] CKT 1 | 6.2519 | 0.1828 | 82.7881 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VIOLA 7 345.00] TO [VIOLA 4 138.00] TO [SCJ1X1 13.800] CKT 2 | 6.2525 | 0.1827 | 82.7166 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VIOLA 7 345.00] TO [VIOLA 4 138.00] TO [VIOLA1X1 13.800] CKT 1 | 6.2526 | 0.1827 | 82.7038 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [G17-075-TAP 345.00] TO [GEN-2017-075345.00] CKT 1 | 6.2529 | 0.1827 | 82.7176 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GEN-2016-118138.00] TO [G16-118XFMR134.500] CKT 1 | 6.307 | 0.1817 | 81.7309 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GEN-2016-118138.00] TO [G16-118XFMR234.500] CKT 1 | 6.3087 | 0.1817 | 81.7016 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [4MEMORALT 138.00] TO [4LUTHER 138.00] CKT 1 | 6.2513 | 0.1828 | 82.7944 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [4MEMORALT 138.00] TO [4MEMORAL 138.00] CKT 1 | 6.2529 | 0.1827 | 82.72 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [3SAREPTA! 115.00] TO [3MINDEN_LA! 115.00] CKT 1 | 6.2528 | 0.1827 | 82.7225 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [3SAREPTA! 115.00] TO [3CULLEN 115.00] CKT 1 | 6.2528 | 0.1827 | 82.7222 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [3SAREPTA! 115.00] TO [3SPRINGHILL 115.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [3SAREPTA! 115.00] TO [3HAYNESVILLE115.00] CKT 1 | 6.2528 | 0.1827 | 82.7222 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [7SAREPTA% 345.00] TO [LONGWD 7 345.00] CKT 1 | 6.2528 | 0.1827 | 82.7238 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [7EL DORADO 345.00] TO [8EL DORADO% 500.00] TO [1EL DORADO2 13.800] CKT 1 | 6.2528 | 0.1827 | 82.7212 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DOLHILL7 345.00] TO [DOLHILL6 230.00] CKT 1 | 6.2527 | 0.1827 | 82.7289 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DOLHILL7 345.00] TO [G1DOLHIL 24.000] CKT 1 | 6.253 | 0.1827 | 82.7147 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [TUPELO 4 138.00] TO [ALLEN 4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.723 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [TUPELO 4 138.00] TO [CENTRATAP4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7225 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [TUPELO 4 138.00] TO [ALLENGT4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7223 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [TUPELO 4 138.00] TO [TUPELO 4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7226 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [TUPELO 4 138.00] TO [STNWLSW4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7232 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [TUPELO 4 138.00] TO [BOGGY4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [S BROWN4 138.00] TO [BROWN 4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7225 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DENISON4 138.00] TO [DEN #1 1 13.800] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DENISON4 138.00] TO [DEN #2 1 13.800] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHAMSPR5 161.00] TO [SILOAMSP 5 161.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHAMSPR5 161.00] TO [SILOAM 5 161.00] CKT 1 | 6.2528 | 0.1827 | 82.722 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHAMSPR5 161.00] TO [TONTITN5 161.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHAMSPR5 161.00] TO [WEDINGTON 161.00] CKT 1 | 6.2528 | 0.1827 | 82.7222 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHAMSPR5 161.00] TO [GEN-2017-076161.00] CKT 1 | 6.2528 | 0.1827 | 82.7225 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHAMSPR7 345.00] TO [CLARKSV7 345.00] CKT 1 | 6.2522 | 0.1827 | 82.7441 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [TONTITN7 345.00] TO [TONTITN5 161.00] TO [TONTITN1 13.800] CKT 1 | 6.2527 | 0.1827 | 82.7245 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [BOONVIL2 69.000] TO [BOONEVIL 2 69.000] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NMAGZIN5 161.00] TO [BRANCH 5 161.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WBOONVL5 161.00] TO [NHUNTNT5 161.00] CKT 1 | 6.2528 | 0.1827 | 82.7222 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WBOONVL5 161.00] TO [WBOONVL2 69.000] TO [WBOONVL1 12.470] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MAGZREC5 161.00] TO [5DANVLE AR! 161.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SW SHV 4 138.00] TO [GENMOTR4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SW SHV 4 138.00] TO [POWELL 4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SW SHV 4 138.00] TO [S SHV 4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SW SHV 4 138.00] TO [SPRIDGE4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.722 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SW SHV 4 138.00] TO [LEASIDE 4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SW SHV 7 345.00] TO [LONGWD 7 345.00] CKT 1 | 6.2528 | 0.1827 | 82.7219 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORAM 4 138.00] TO [RAINES 4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WELSH 7 345.00] TOSPPMAINBUS 345.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WELSH 7 345.00] TO [NWTXARK7 345.00] CKT 1 | 6.2528 | 0.1827 | 82.7231 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WELSH 7 345.00] TO [LYDIA 7 345.00] CKT 1 | 6.2525 | 0.1827 | 82.7274 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WELSH 7 345.00] TO [WELSH1-1 18.000] CKT 1 | 6.253 | 0.1827 | 82.7137 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WELSH 7 345.00] TO [WELSH3-1 18.000] CKT 1 | 6.253 | 0.1827 | 82.7136 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SCOTTSV4 138.00] TO [SEMRSHL4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7224 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LIEBERM4 138.00] TO [ARSHILL4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7222 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LIEBERM4 138.00] TO [IPCJEFF4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7223 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LIEBERM4 138.00] TO [LIEBR2-1 13.800] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LIEBERM4 138.00] TO [LIEBR3-1 13.800] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LIEBERM4 138.00] TO [LIEBR3-1 13.800] CKT 2 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LIEBERM4 138.00] TO [LIEBR4-1 13.800] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LIEBERM4 138.00] TO [LIEBR4-1 13.800] CKT 2 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LIEBERM4 138.00] TO [G16-167-TAP 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LIEBERM4 138.00] TO [LIEBERM2 69.000] TO [LBMN1-1 13.200] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LIEBERM4 138.00] TO [LIEBERM2 69.000] TO [LBMN2-1 13.200] CKT 2 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LIEBERM4 138.00] TO [LIEBERM2 69.000] TO [LBMN3-1 13.200] CKT 3 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LONGWD 4 138.00] TO [LONGWD 7 345.00] TO [LONGW1-1 13.200] CKT 1 | 6.2528 | 0.1827 | 82.7217 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OAKPH 4 138.00] TO [FLOURNY4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DIANA 7 345.00] TO [PIRKEY 7 345.00] CKT 1 | 6.2528 | 0.1827 | 82.723 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DIANA 7 345.00] TO [DIANA 4 138.00] TO [DIANA-S1 13.800] CKT 1 | 6.2528 | 0.1827 | 82.7222 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DIANA 7 345.00] TO [DIANA 4 138.00] TO [DIANA-M1 13.800] CKT 2 | 6.2528 | 0.1827 | 82.7222 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DIANA 7 345.00] TO [DIANA 4 138.00] TO [DIANA-N1 13.800] CKT 3 | 6.2528 | 0.1827 | 82.7222 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILKES 4 138.00] TO [MUNZCTY4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7223 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILKES 4 138.00] TO [WATLANT4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILKES 4 138.00] TO [LSSOUTH4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.722 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILKES 4 138.00] TO [WELSHRE4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.722 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILKES 4 138.00] TO [JEFFRSN4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7224 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILKES 4 138.00] TO [WILKE1-1 20.000] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILKES 4 138.00] TO [WILKE1-1 20.000] CKT 2 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILKES 4 138.00] TO [WILKE2-1 22.000] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILKES 4 138.00] TO [WILKE2-1 22.000] CKT 2 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILKES 7 345.00] TO [LONGWD 7 345.00] CKT 1 | 6.2527 | 0.1827 | 82.7265 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [36&OLY-4 138.00] TO [T.P.S.-4 138.00] CKT 1 | 6.2525 | 0.1827 | 82.7282 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CARSN-T4 138.00] TO [UNIONAV4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7218 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CARSN-T4 138.00] TO [S.S.---4 138.00] CKT 1 | 6.2526 | 0.1827 | 82.7212 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DENVTAP4 138.00] TO [DENVR-E4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7217 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DENVTAP4 138.00] TO [W.ED.-E4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7215 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILLPIP2 69.000] TO [OGMARTN2 69.000] CKT 1 | 6.2528 | 0.1827 | 82.722 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WEKIWA-7 345.00] TO [WEKIWA-4 138.00] TO [WEKIW1-1 34.500] CKT 1 | 6.2522 | 0.1828 | 82.7531 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CARSN-S4 138.00] TO [T.P.S.-4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7215 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [52DELTP4 138.00] TO [S52DEL 4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7219 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [52DELTP4 138.00] TO [T.S.E.-4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7223 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [52DELTP4 138.00] TO [ZUNIS-S4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.722 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [KENSH-W4 138.00] TO [DENVR-C4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.722 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-7 345.00] TO [PECANCK7 345.00] CKT 1 | 6.2527 | 0.1827 | 82.7214 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-4 138.00] TO [116JENK4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7231 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-4 138.00] TO [136YALE4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7225 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-4 138.00] TO [ORU ETP4 138.00] CKT 1 | 6.2529 | 0.1827 | 82.7238 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-4 138.00] TO [ORU-WTP4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7235 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-4 138.00] TO [OKMULGE4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7233 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-4 138.00] TO [EXP_OKM4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.724 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-4 138.00] TO [RSS1-1 24.000] CKT 1 | 6.2523 | 0.1827 | 82.7246 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-4 138.00] TO [RSS2-1 22.000] CKT 1 | 6.2522 | 0.1827 | 82.7255 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-4 138.00] TO [EXPGLNT4 138.00] CKT 1 | 6.2522 | 0.1827 | 82.7364 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-4 138.00] TO [RSS NG3 13.800] TO [RSS NG4 13.800] CKT 1 | 6.2526 | 0.1827 | 82.7232 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [T.P.S.-2 69.000] TO [T.P.S.-4 138.00] TO [TPS5-1 13.800] CKT 1 | 6.2528 | 0.1827 | 82.7219 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [36LEWIS4 138.00] TO [T.P.S.-4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7226 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ONETA--4 138.00] TO [BA101ST4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.722 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ONETA--4 138.00] TO [BA101-N4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7224 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ONETA--4 138.00] TO [BA.N-ST4 138.00] CKT 1 | 6.2527 | 0.1827 | 82.7278 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ONETA--4 138.00] TO [121LYNN4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7224 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ONETA--4 138.00] TO [BA_71ST4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7224 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ONETA--7 345.00] TO [CLARKSV7 345.00] CKT 1 | 6.2529 | 0.1827 | 82.7203 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [52DELWT4 138.00] TO [T.P.S.-4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7223 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [T.NO.--4 138.00] TO [T.NO.2-4 138.00] CKT 1 | 6.2524 | 0.1827 | 82.7246 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [COGENT 7 345.00] TO [COGEN G1 18.000] TO [COGEN S1 13.800] CKT 1 | 6.2524 | 0.1827 | 82.7234 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [COGENT 7 345.00] TO [COGEN G2 18.000] TO [COGEN S2 13.800] CKT 1 | 6.2527 | 0.1827 | 82.7223 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [COGENT 7 345.00] TO [COGEN G3 18.000] TO [COGEN S3 13.800] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OEC 7 345.00] TO [OECSTM 1 18.000] CKT 1 | 6.2526 | 0.1827 | 82.7231 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OEC 7 345.00] TO [OECGT1-1 18.000] CKT 1 | 6.2526 | 0.1827 | 82.7233 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OEC 7 345.00] TO [OECGT1-2 18.000] CKT 1 | 6.2527 | 0.1827 | 82.7229 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OEC 7 345.00] TO [OECSTM 2 18.000] CKT 1 | 6.2526 | 0.1827 | 82.7231 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OEC 7 345.00] TO [OECGT2-1 18.000] CKT 1 | 6.2526 | 0.1827 | 82.7234 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OEC 7 345.00] TO [OECGT2-2 18.000] CKT 1 | 6.2528 | 0.1827 | 82.722 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CDC-ET 4 138.00] TO [CIP 4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7202 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CDC-ET 4 138.00] TO [OWAS88_4 138.00] CKT 1 | 6.2527 | 0.1827 | 82.7217 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CDC-WT 4 138.00] TO [A.A.---4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7217 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CDC-WT 4 138.00] TO [WHIRLPO4 138.00] CKT 1 | 6.2529 | 0.1827 | 82.7214 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OWASOTP4 138.00] TO [OWASO1_4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7214 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OWASOTP4 138.00] TO [OWAS1094 138.00] CKT 1 | 6.2527 | 0.1827 | 82.7218 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OAKSWTP4 138.00] TO [T.P.S.-4 138.00] CKT 1 | 6.2527 | 0.1827 | 82.7223 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OAKSETP4 138.00] TO [T.P.S.-4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7224 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [P&P WTP4 138.00] TO [WEKIWA-4 138.00] CKT 1 | 6.2527 | 0.1827 | 82.7207 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [P&P WTP4 138.00] TO [PP----W4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.721 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [T.NO.--7 345.00] TO [T.NO.2-4 138.00] TO [TNO2-1 34.500] CKT 1 | 6.2525 | 0.1827 | 82.7218 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [S HILLW4 138.00] TO [52DEL-W4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.722 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SAPLPRD7 345.00] TO [SAPLPRD4 138.00] TO [SAPLPRD1 13.800] CKT 1 | 6.2528 | 0.1827 | 82.7224 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SAPLPRD4 138.00] TO [JENKS--4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7223 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SAPLPRD4 138.00] TO [DENV_WTAP4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.722 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SKIATOK4 138.00] TO [BARNSAL4 138.00] CKT 1 | 6.2527 | 0.1827 | 82.7244 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [72ELWOD4 138.00] TO [T.P.S.-4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7222 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [46ST-TP-4 138.00] TO [46ST--E4 138.00] CKT 1 | 6.2529 | 0.1827 | 82.7212 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [46ST-TP-4 138.00] TO [PPTAP 4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [N.E.S.-4 138.00] TO [OWASO2_4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.722 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [N.E.S.-4 138.00] TO [OWAS1094 138.00] CKT 1 | 6.2526 | 0.1827 | 82.7223 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [N.E.S.-4 138.00] TO [CLARTOK4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7222 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [N.E.S.-4 138.00] TO [WATOVA 4 138.00] CKT 1 | 6.2527 | 0.1827 | 82.7242 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [N.E.S.-4 138.00] TO [RICE CK4 138.00] CKT 1 | 6.2526 | 0.1827 | 82.7272 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [N.E.S.-4 138.00] TO [HAWTHRN4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7223 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [N.E.S.-4 138.00] TO [NES1-1 14.400] CKT 1 | 6.2527 | 0.1827 | 82.7249 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [N.E.S.-4 138.00] TO [NES1-1A 18.000] CKT 1 | 6.2526 | 0.1827 | 82.7253 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [N.E.S.-4 138.00] TO [NES1-1B 18.000] CKT 1 | 6.2526 | 0.1827 | 82.7254 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [N.E.S.-4 138.00] TO [NES2-1 22.000] CKT 1 | 6.2522 | 0.1827 | 82.733 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [N.E.S.-4 138.00] TO [OOLOGAHKM 4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7259 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [N.E.S.-7 345.00] TO [DELWARE7 345.00] CKT 1 | 6.2525 | 0.1827 | 82.7348 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [N.E.S.-7 345.00] TO [NES3-1 22.000] CKT 1 | 6.2519 | 0.1827 | 82.7362 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [PITTSB-7 345.00] TO [JOHNCO 7 345.00] CKT 1 | 6.2528 | 0.1827 | 82.7261 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VALIANT7 345.00] TO [NWTXARK7 345.00] CKT 1 | 6.2525 | 0.1827 | 82.7262 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VALIANT7 345.00] TO [LYDIA 7 345.00] CKT 1 | 6.2522 | 0.1827 | 82.7308 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VALIANT7 345.00] TO [VALIANT4 138.00] TO [VALN2-1 13.800] CKT 2 | 6.2528 | 0.1827 | 82.7222 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VALIANT7 345.00] TO [VALIANT4 138.00] TO [VALN3-1 13.800] CKT 1 | 6.2528 | 0.1827 | 82.7222 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [KIOWA 7 345.00] TO [KIOWA G1 18.000] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [KIOWA 7 345.00] TO [KIOWA G2 18.000] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [KIOWA 7 345.00] TO [KIOWA S1 18.000] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [KIOWA 7 345.00] TO [KIOWA S2 18.000] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [KIOWA 7 345.00] TO [KIOWA G3 18.000] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [KIOWA 7 345.00] TO [KIOWA G4 18.000] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [C-RIVER4 138.00] TO [TALAWANDA 4138.00] CKT 1 | 6.2526 | 0.1827 | 82.7328 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [O.K.U.-7 345.00] TO [OKLAUN HVDC7345.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [O.K.U.-7 345.00] TO [GEN-2017-033345.00] CKT 1 | 6.2528 | 0.1827 | 82.7229 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [O.K.U.-7 345.00] TO [G18-015-TAP 345.00] CKT 1 | 6.2522 | 0.1827 | 82.71 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [L.E.S.-4 138.00] TO [FLE TAP4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7232 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [L.E.S.-4 138.00] TO [COMANC-4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [L.E.S.-4 138.00] TO [LWSTAP 4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7213 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [L.E.S.-4 138.00] TO [SHERID4 138.00] CKT 1 | 6.2529 | 0.1827 | 82.7207 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [L.E.S.-4 138.00] TO [ELGINJT4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7225 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [L.E.S.-4 138.00] TO [COMMTAP4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7219 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [L.E.S.-4 138.00] TO [L.E.S.-2 69.000] TO [LES#1-1 13.800] CKT 1 | 6.2528 | 0.1827 | 82.722 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [L.E.S.-4 138.00] TO [L.E.S.-2 69.000] TO [LES#2-1 13.800] CKT 2 | 6.2528 | 0.1827 | 82.722 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [L.E.S.-7 345.00] TO [G17-171-TAP 345.00] CKT 1 | 6.2524 | 0.1827 | 82.7066 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CAN_GAS4 138.00] TO [REDROCKRD4 138.00] CKT 1 | 6.2472 | 0.1826 | 82.6168 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CAN_GAS4 138.00] TO [TLBEART4 138.00] CKT 1 | 6.2542 | 0.1826 | 82.6435 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHISHOLM7 345.00] TO [G16-037-TAP 345.00] CKT 1 | 6.254 | 0.1827 | 82.6754 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHISHOLM6 230.00] TO [ELKCITY6 230.00] CKT 1 | 6.2517 | 0.1827 | 82.7343 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHISHOLM6 230.00] TO [SWEETWT6 230.00] CKT 1 | 6.2508 | 0.1827 | 82.7387 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RUSHSPR1-1 13.800] TO [RUSHSPR7 345.00] TO [RUSHSPRW1-1 34.500] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [TPS2-1 14.400] TO [T.P.S.-4 138.00] CKT 1 | 6.2526 | 0.1827 | 82.7224 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [TPS4-1 14.400] TO [T.P.S.-4 138.00] CKT 1 | 6.2526 | 0.1827 | 82.7226 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RUSHSPRW1-1 34.500] TO [RUSHSPRWD0 0.7000] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RUSHSPRW1-1 34.500] TO [RSHSPR1_GSU134.500] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RSHSPR1_COL134.500] TO [RSHSPR1_GSU134.500] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RSHSPR1_MPT1345.00] TO [TERRYRD7 345.00] CKT 1 | 6.2528 | 0.1827 | 82.7232 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CLEVLND7 345.00] TO [G15-066T 345.00] CKT 1 | 6.2477 | 0.1827 | 82.7468 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CLEVLND7 345.00] TO [CLEVLND 4 138.00] TO [CLEVLND1 13.800] CKT 1 | 6.2515 | 0.1828 | 82.7827 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [IGLOOV 7 345.00] TO [GREC TAP5 345.00] CKT 1 | 6.2514 | 0.1827 | 82.72 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [IGLOOV 7 345.00] TO [IGLOOV1 5 161.00] TO [IGLOTER1 1 13.200] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [IGLOOV 7 345.00] TO [IGLOOV2 5 161.00] TO [IGLOTER2 1 13.200] CKT 2 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OTTER 4 138.00] TO [WRVALLY4 138.00] CKT 1 | 6.1771 | 0.1828 | 82.7935 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OTTER 4 138.00] TO [ARMFTWD4 138.00] CKT 1 | 6.2509 | 0.1829 | 82.9353 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [FRMNTAP4 138.00] TO [FAIRMON4 138.00] CKT 1 | 6.2525 | 0.1828 | 82.8126 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [FRMNTAP4 138.00] TO [SO4TH 4 138.00] CKT 1 | 6.2381 | 0.1828 | 82.7939 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WAUKOTP4 138.00] TO [SO4TH 4 138.00] CKT 1 | 6.136 | 0.1828 | 82.8454 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WOODRNG4 138.00] TO [WOODRNG7 345.00] TO [WOODRNG1 13.800] CKT 1 | 5.797 | 0.184 | 84.0171 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MARSHL 4 138.00] TO [MARSHAL4 138.00] CKT Z1 | 6.2529 | 0.1827 | 82.7113 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DOVERTP2 69.000] TO [TURCRKT2 69.000] CKT 1 | 5.9747 | 0.183 | 82.9899 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DOVERTP2 69.000] TO [REDWING2 69.000] CKT 1 | 6.2574 | 0.1834 | 83.3665 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HENESEY4 138.00] TO [DOVERSW4 138.00] CKT 1 | 6.0479 | 0.1831 | 83.1227 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SOONER 7 345.00] TO [SOONER2G 20.000] CKT 1 | 6.2435 | 0.1827 | 82.7324 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SOONER 7 345.00] TO [RANCHRD7 345.00] CKT 1 | 6.2477 | 0.1827 | 82.7278 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SOONER 7 345.00] TO [THUNDER7 345.00] CKT 1 | 6.2528 | 0.1827 | 82.7279 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SOONER 7 345.00] TO [G15-066T 345.00] CKT 1 | 6.248 | 0.1827 | 82.735 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SOONER 7 345.00] TO [G16-119-TAP 345.00] CKT 1 | 6.2513 | 0.1828 | 82.7795 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SOONER 7 345.00] TO [SOONER 4 138.00] TO [SOONER 1 13.800] CKT 1 | 6.2505 | 0.1827 | 82.7301 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [JOHNCO 4 138.00] TO [JOHNCO 7 345.00] TO [JOHNCO11 13.800] CKT 1 | 6.2527 | 0.1827 | 82.729 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [YUKON 2 69.000] TO [SVCELRN2 69.000] CKT 1 | 6.228 | 0.1828 | 82.7621 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [JENSENT4 138.00] TO [EL-RENO4 138.00] CKT 1 | 6.2492 | 0.1828 | 82.7598 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [JENSEN 4 138.00] TO [EL RENO4 138.00] CKT 1 | 6.1299 | 0.1832 | 83.2257 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CTNWOOD4 138.00] TO [PINE ST4 138.00] CKT 1 | 6.219 | 0.1824 | 82.3774 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CTNWOOD4 138.00] TO [LBRTYLK4 138.00] CKT 1 | 6.167 | 0.1829 | 82.8532 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CTNWOOD4 138.00] TO [CRESENT4 138.00] CKT 1 | 5.4922 | 0.1843 | 84.2528 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LAKESID4 138.00] TO [HEFNER 4 138.00] CKT 1 | 6.2527 | 0.1827 | 82.731 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SLVRLAK4 138.00] TO [QUAILCK4 138.00] CKT 1 | 6.2525 | 0.1827 | 82.7368 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SLVRLAK4 138.00] TO [BRADEN 4 138.00] CKT 1 | 6.2529 | 0.1827 | 82.7223 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DVISION4 138.00] TO [MUSTANG4 138.00] CKT 1 | 6.2526 | 0.1827 | 82.6862 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MSTANG 2 69.000] TO [MUSTANG4 138.00] TO [MUSTANG1 13.200] CKT 1 | 6.2529 | 0.1827 | 82.7099 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RICHRDS4 138.00] TO [PIEDMNT4 138.00] CKT 1 | 6.2529 | 0.1827 | 82.72 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [COUNCIL4 138.00] TO [MUSTANG4 138.00] CKT 1 | 6.2517 | 0.1828 | 82.7769 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WESTOAK4 138.00] TO [MERIDAN4 138.00] CKT 1 | 6.2523 | 0.1828 | 82.7558 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORTWST4 138.00] TO [KETCHTP4 138.00] CKT 1 | 6.244 | 0.1829 | 82.921 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORTWST4 138.00] TO [BRADEN 4 138.00] CKT 1 | 6.2529 | 0.1827 | 82.7235 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORTWST4 138.00] TO [PIEDMNT4 138.00] CKT 1 | 6.2529 | 0.1827 | 82.7204 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORTWST4 138.00] TO [LNEOAK 4 138.00] CKT 1 | 6.2523 | 0.1828 | 82.7557 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORTWST7 345.00] TO [ARCADIA7 345.00] CKT 1 | 6.2501 | 0.1828 | 82.757 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SPRNGCK7 345.00] TO [SPGCK1&2 13.800] CKT 1 | 6.2499 | 0.1827 | 82.7055 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SPRNGCK7 345.00] TO [SPGCK3&4 13.800] CKT 1 | 6.2499 | 0.1827 | 82.7055 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SPRNGCK7 345.00] TO [G16-119-TAP 345.00] CKT 1 | 6.2518 | 0.1828 | 82.7649 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DUNJEE 4 138.00] TO [HSL 4 138.00] CKT 1 | 6.2526 | 0.1827 | 82.7279 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [36&MER 4 138.00] TO [WRAIRPT4 138.00] CKT 1 | 6.2526 | 0.1827 | 82.7212 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SMITHCO4 138.00] TO [SMITH 1G 13.800] TO [SMITH 1S 13.800] CKT 1 | 6.2511 | 0.1827 | 82.7153 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DAYTON 4 138.00] TO [MUSTANG4 138.00] CKT 1 | 6.2522 | 0.1827 | 82.7291 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [XEROX 4 138.00] TO [CZECHAL4 138.00] CKT 1 | 6.251 | 0.1827 | 82.6566 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MORGAN 4 138.00] TO [MUSTANG4 138.00] CKT 1 | 6.2506 | 0.1827 | 82.6822 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CIMARON4 138.00] TO [TUTCONT4 138.00] CKT 1 | 6.2524 | 0.1827 | 82.6616 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CIMARON4 138.00] TO [EL-RENO4 138.00] CKT 1 | 6.2257 | 0.1831 | 83.0745 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CIMARON4 138.00] TO [CZECHAL4 138.00] CKT 1 | 6.2512 | 0.1826 | 82.6388 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CIMARON4 138.00] TO [SARA 4 138.00] CKT 1 | 6.2505 | 0.1826 | 82.6437 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CIMARON7 345.00] TO [MINCO 7 345.00] CKT 1 | 6.2493 | 0.1828 | 82.7761 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [JNSKAMO4 138.00] TO [HSL 4 138.00] CKT 1 | 6.2507 | 0.1827 | 82.7059 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ARCADIA4 138.00] TO [ARCADIA7 345.00] TO [ARCADI21 13.800] CKT 1 | 6.2475 | 0.1828 | 82.7953 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ARCADIA4 138.00] TO [ARCADIA7 345.00] TO [ARCADI31 13.800] CKT 1 | 6.2478 | 0.1828 | 82.7909 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ARCADIA4 138.00] TO [ARCADIA7 345.00] TO [ARCADI41 13.800] CKT 1 | 6.2465 | 0.1828 | 82.8188 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDBUD 7 345.00] TO [ARCADIA7 345.00] CKT 1 | 6.2528 | 0.1827 | 82.6956 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDBUD 7 345.00] TO [ARCADIA7 345.00] CKT 2 | 6.2528 | 0.1827 | 82.6925 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDBUD 7 345.00] TO [ARCADIA7 345.00] CKT 3 | 6.2528 | 0.1827 | 82.6913 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WODLAWN2 69.000] TO [BETHANY2 69.000] CKT 1 | 6.2526 | 0.1827 | 82.738 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MCARTHR2 69.000] TO [SW 64TH2 69.000] CKT 1 | 6.2527 | 0.1827 | 82.7307 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SW 5TH 2 69.000] TO [MAY AVE2 69.000] CKT 1 | 6.2527 | 0.1827 | 82.725 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SW 5TH 2 69.000] TO [SW22ND 2 69.000] CKT 1 | 6.2527 | 0.1827 | 82.7198 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SW 5TH 4 138.00] TO [MUSTANG4 138.00] CKT 1 | 6.2524 | 0.1827 | 82.7403 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CLASSEN4 138.00] TO [DOUGLTP4 138.00] CKT 1 | 6.2526 | 0.1827 | 82.7186 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CLASSEN4 138.00] TO [CROSTWN4 138.00] CKT 1 | 6.2526 | 0.1827 | 82.7228 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HSLEAST2 69.000] TO [GRNPAST2 69.000] CKT 1 | 6.2528 | 0.1827 | 82.7219 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HSLEAST2 69.000] TO [TXSTELA2 69.000] CKT 1 | 6.2527 | 0.1827 | 82.7228 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HSLEAST2 69.000] TO [MCLOUDT2 69.000] CKT 1 | 6.2527 | 0.1827 | 82.7228 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DRAPER 7 345.00] TO [DRAPER 4 138.00] TO [DRAPER21 13.800] CKT 2 | 6.2526 | 0.1827 | 82.7331 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DRAPER 7 345.00] TO [DRAPER 4 138.00] TO [DRAPER31 13.800] CKT 3 | 6.2525 | 0.1827 | 82.7349 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DRAPER 7 345.00] TO [DRAPER 4 138.00] TO [DRAPER41 13.800] CKT 4 | 6.2525 | 0.1827 | 82.7349 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HSL 7S 20.900] TO [HSL 4 138.00] CKT 1 | 6.2498 | 0.1827 | 82.716 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HSLWEST2 69.000] TO [HSL 4 138.00] TO [HSL 1 13.800] CKT 1 | 6.2527 | 0.1827 | 82.7267 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HSL 8G 22.800] TO [HSL 4 138.00] CKT 1 | 6.2475 | 0.1827 | 82.7153 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HSL 9G 13.800] TO [HSL 4 138.00] CKT 1 | 6.2521 | 0.1827 | 82.7206 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HSL 10G 13.800] TO [HSL 4 138.00] CKT 1 | 6.2521 | 0.1827 | 82.7207 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MIDWAY 4 138.00] TO [HSL 4 138.00] CKT 1 | 6.2526 | 0.1827 | 82.7362 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RENO 4 138.00] TO [TROSPER4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7229 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RENO 4 138.00] TO [WASHPRK4 138.00] CKT 1 | 6.2519 | 0.1827 | 82.7489 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RENO 4 138.00] TO [RENO 2 69.000] TO [RENO 1 13.800] CKT 1 | 6.2526 | 0.1827 | 82.719 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GLENDAL4 138.00] TO [TINKER74 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7224 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DALE 4 138.00] TO [HSL 4 138.00] CKT 1 | 6.2523 | 0.1827 | 82.7267 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SE15TH 4 138.00] TO [HSL 4 138.00] CKT 1 | 6.2527 | 0.1827 | 82.7294 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [BARNES 4 138.00] TO [DRAPER 4 138.00] CKT 1 | 6.2533 | 0.1827 | 82.6986 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [BARNES 4 138.00] TO [TINKER54 138.00] CKT 1 | 6.2529 | 0.1827 | 82.721 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRTPLNS4 138.00] TO [GRNWOOD4 138.00] CKT 1 | 6.2526 | 0.1827 | 82.7276 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SEMINOL4 138.00] TO [SEMINL1G 20.900] CKT 1 | 6.25 | 0.1827 | 82.7058 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SEMINOL4 138.00] TO [MAUD 4 138.00] CKT 1 | 6.2527 | 0.1827 | 82.7251 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SEMINOL4 138.00] TO [MAUD 4 138.00] CKT 2 | 6.2528 | 0.1827 | 82.7227 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SEMINOL4 138.00] TO [PAOLI- 4 138.00] CKT 1 | 6.2527 | 0.1827 | 82.729 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SEMINOL4 138.00] TO [VANOSTP4 138.00] CKT 1 | 6.2527 | 0.1827 | 82.7224 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SEMINOL4 138.00] TO [LKKONWA4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7272 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SEMINOL7 345.00] TO [ARCADIA7 345.00] CKT 1 | 6.2503 | 0.1827 | 82.7388 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SEMINOL7 345.00] TO [FIREWHL-TAP 345.00] CKT 1 | 6.2516 | 0.1827 | 82.728 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HAMMTAP4 138.00] TO [HSL 4 138.00] CKT 1 | 6.2521 | 0.1828 | 82.7587 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WARWICK4 138.00] TO [TRYON 4 138.00] CKT 1 | 6.2519 | 0.1827 | 82.7209 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SQUIRCK4 138.00] TO [INGLEWD4 138.00] CKT 1 | 6.2526 | 0.1827 | 82.7309 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SQUIRCK4 138.00] TO [STRLGTP4 138.00] CKT 1 | 6.2522 | 0.1827 | 82.7228 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RUSSET-4 138.00] TO [GLASSES4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7225 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RUSSET-4 138.00] TO [STIRLNG4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7225 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SXMLCKT4 138.00] TO [MILLCKT4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7225 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SXMLCKT4 138.00] TO [HOWE 4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7222 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SUNNYSD4 138.00] TO [SUNNYSD7 345.00] TO [SUNYSD 1 13.800] CKT 1 | 6.2528 | 0.1827 | 82.7253 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SUNNYSD4 138.00] TO [SUNNYSD7 345.00] TO [SUNNYSD1 13.800] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [UNIROY 4 138.00] TO [ARDWEST4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7235 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LONEGRV4 138.00] TO [CHEEKTP4 138.00] CKT 1 | 6.2527 | 0.1827 | 82.7228 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CANEYCK4 138.00] TO [MADINDT4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.722 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CANEYCK4 138.00] TO [LTLCITY4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7228 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CANEYCK4 138.00] TO [TEXOMAJ4 138.00] CKT 1 | 6.2527 | 0.1827 | 82.7228 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [BROWNTP4 138.00] TO [LTLCITY4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7227 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [BROWNTP4 138.00] TO [BODLE 4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7223 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [COLEMNT4 138.00] TO [EXPLRPL4 138.00] CKT 1 | 6.2529 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [COLBRTP4 138.00] TO [BODLE 4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [COLBRTP4 138.00] TO [BUTRFLD4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7222 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ROCKYPT4 138.00] TO [MRIETA 2 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7243 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ROCKYPT4 138.00] TO [SPRNDAL4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7224 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ROCKYPT4 138.00] TO [ROCKYPT2 69.000] TO [ROCKYPT1 13.200] CKT 1 | 6.2528 | 0.1827 | 82.7222 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MUSKOGE7 345.00] TO [CLARKSV7 345.00] CKT 1 | 6.2525 | 0.1827 | 82.7369 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MUSKOGE7 345.00] TO [PECANCK7 345.00] CKT 1 | 6.2528 | 0.1827 | 82.7227 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MUSKOGE7 345.00] TO [PECANCK7 345.00] CKT 2 | 6.2528 | 0.1827 | 82.7232 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MUSKOGE7 345.00] TO [FIREWHL-TAP 345.00] CKT 1 | 6.2525 | 0.1827 | 82.7255 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MUSKOGE7 345.00] TO [FIREWHL-TAP 345.00] CKT 2 | 6.2524 | 0.1827 | 82.7265 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [5TRIBES5 161.00] TO [HANCOK-5 161.00] CKT 1 | 6.2528 | 0.1827 | 82.7238 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [5TRIBES5 161.00] TO [5TRIBES2 69.000] TO [5TRIBES1 13.200] CKT 1 | 6.2528 | 0.1827 | 82.7222 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [AGENCY 5 161.00] TO [EUCLID 5 161.00] CKT 1 | 6.2528 | 0.1827 | 82.7234 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [AGENCY 5 161.00] TO [AGENCY 2 69.000] TO [AGENCY 1 13.800] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [PECANCK4 138.00] TO [BEGGS 4 138.00] CKT 1 | 6.2523 | 0.1827 | 82.7263 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [PECANCK5 161.00] TO [PECANCK7 345.00] TO [PECANC11 13.800] CKT 1 | 6.2528 | 0.1827 | 82.7241 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [PECANCK5 161.00] TO [PECANCK7 345.00] TO [PECANC21 13.800] CKT 2 | 6.2528 | 0.1827 | 82.7255 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [FTSMITH7 345.00] TO [FTSMITH8 500.00] TO [FTSMTH11 13.800] CKT 1 | 6.2527 | 0.1827 | 82.7231 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [FTSMITH7 345.00] TO [FTSMTHW5 161.00] TO [FTSMTH51 13.800] CKT 5 | 6.2528 | 0.1827 | 82.7227 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [BRANCH 2 69.000] TO [BRANCH 5 161.00] TO [BRANCH21 13.200] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [PENDER 2 69.000] TO [HELBERG2 69.000] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HOBBYLO4 138.00] TO [CHEMTRN4 138.00] CKT 1 | 6.2527 | 0.1827 | 82.7226 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VBI 5 161.00] TO [VAN BUR5 161.00] CKT Z1 | 6.2528 | 0.1827 | 82.7215 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VBI 5 161.00] TO [OAKGROV5 161.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VBI 5 161.00] TO [TWNBRDG5 161.00] CKT 1 | 6.2528 | 0.1827 | 82.722 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VBI 5 161.00] TO [ADABELL5 161.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VBI 5 161.00] TO [HWY59TP5 161.00] CKT 1 | 6.2528 | 0.1827 | 82.722 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VBI 5 161.00] TO [VBI 2 69.000] TO [VBI 1 13.800] CKT 1 | 6.2528 | 0.1827 | 82.7224 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SHORTMT5 161.00] TO [BRANCH 5 161.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WFROSST4 138.00] TO [RSSVILE4 138.00] CKT Z1 | 6.2528 | 0.1827 | 82.7218 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [BELLCOW4 138.00] TO [KEYWEST4 138.00] CKT 1 | 6.2526 | 0.1827 | 82.7239 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [C-RIVER7 345.00] TO [FIREWHL-TAP 345.00] CKT 1 | 6.2528 | 0.1827 | 82.7148 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SUBIACT5 161.00] TO [RAZRBAK5 161.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SUBIACT5 161.00] TO [SUBIACO5 161.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LINCOLN4 138.00] TO [JACKTWN4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.718 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LINCOLN4 138.00] TO [MEEKER 4 138.00] CKT 1 | 6.2524 | 0.1827 | 82.7375 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MNCOWND1 34.500] TO [MNCOWNC1 34.500] CKT 1 | 6.253 | 0.1827 | 82.7158 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MCNOWND7 345.00] TO [MINCO 7 345.00] CKT 1 | 6.253 | 0.1827 | 82.7158 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LNWOODT4 138.00] TO [TRYON 4 138.00] CKT 1 | 6.2526 | 0.1827 | 82.7243 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ACORN 4 138.00] TO [BRYANT 4 138.00] CKT 1 | 6.2512 | 0.1827 | 82.7353 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RNDBARN4 138.00] TO [BURGETT4 138.00] CKT 1 | 6.2509 | 0.1828 | 82.8074 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HUNTERS7 345.00] TO [WOODRNG7 345.00] CKT 1 | 6.2417 | 0.1825 | 82.5245 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HUNTERS7 345.00] TO [RENFROW7 345.00] CKT 1 | 6.2416 | 0.1825 | 82.4871 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHSHLMV7 345.00] TO [CHSHMVE1 34.500] TO [CHSHMVET 13.200] CKT 1 | 6.2527 | 0.1827 | 82.7368 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHSHLMV7 345.00] TO [CHSHMVW1 34.500] TO [CHSHMVWT 13.200] CKT 1 | 6.2527 | 0.1827 | 82.7368 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [JONESSB4 138.00] TO [HSL 4 138.00] CKT 1 | 6.2495 | 0.1827 | 82.6863 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MATHWSN7 345.00] TO [TATONGA7 345.00] CKT 1 | 6.2524 | 0.1828 | 82.7503 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MATHWSN7 345.00] TO [TATONGA7 345.00] CKT 2 | 6.2524 | 0.1828 | 82.7502 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MATHWSN7 345.00] TO [TRAVERSE3 345.00] CKT 1 | 6.2528 | 0.1828 | 82.7543 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [KNIPE 4 138.00] TO [TRYON 4 138.00] CKT 1 | 6.2508 | 0.1827 | 82.7466 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRNDPRT5 161.00] TO [BRANCH 5 161.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RENFROW4 138.00] TO [RENFROW7 345.00] TO [RENFRO11 13.800] CKT 1 | 6.2511 | 0.1827 | 82.7041 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRANTCO4 138.00] TO [GRANTCO2 69.000] TO [GRANTC11 13.200] CKT 1 | 6.2491 | 0.1827 | 82.6936 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MNCWND37 345.00] TO [MINCO 7 345.00] CKT 1 | 6.253 | 0.1827 | 82.7251 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MNCWND31 34.500] TO [MINCO-CB3 34.500] CKT 1 | 6.2529 | 0.1827 | 82.7178 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CARTRCO4 138.00] TO [RATLIFF4 138.00] CKT 1 | 6.2524 | 0.1827 | 82.7257 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CARTRCO4 138.00] TO [POOLVIL4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7219 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CARTRCO4 138.00] TO [ORIGINW4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7224 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CARTRCO4 138.00] TO [GEN-2017-027138.00] CKT 1 | 6.2529 | 0.1827 | 82.7204 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MDFRDTP4 138.00] TO [RDRUNNR4 138.00] CKT 1 | 6.2522 | 0.1827 | 82.7322 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MDFRDTP4 138.00] TO [MEDFORD4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7217 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SPGVLLY4 138.00] TO [STILWTR4 138.00] CKT 1 | 6.2452 | 0.1828 | 82.802 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SPGVLLY4 138.00] TO [PAYNESB4 138.00] CKT 1 | 6.2508 | 0.1827 | 82.7469 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [FSHRTAP7 345.00] TO [KNGFSHR7 345.00] CKT 1 | 6.2477 | 0.1827 | 82.7303 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [FSHRTAP7 345.00] TO [CANADN7 345.00] CKT 1 | 6.2529 | 0.1827 | 82.7244 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRNTWD 7 345.00] TO [RENFROW7 345.00] CKT 1 | 6.2518 | 0.1828 | 82.7736 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRNTWD11 34.500] TO [GRNTWDC1 34.500] CKT 1 | 6.2523 | 0.1827 | 82.7461 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRNTWD12 34.500] TO [GRNTWDC2 34.500] CKT 1 | 6.2523 | 0.1827 | 82.7461 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MSTNG 8G 13.800] TO [MUSTANG4 138.00] TO [MSTNG 9G 13.800] CKT 1 | 6.2501 | 0.1827 | 82.7173 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MSTNG10G 13.800] TO [MUSTANG4 138.00] TO [MSTNG11G 13.800] CKT 1 | 6.2499 | 0.1827 | 82.7191 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MSTNG12G 13.800] TO [MUSTANG4 138.00] CKT 1 | 6.2515 | 0.1827 | 82.7179 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRACMNT7 345.00] TO [MINCO 7 345.00] CKT 1 | 6.2504 | 0.1827 | 82.7374 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRACMNT7 345.00] TO [G16-037-TAP 345.00] CKT 1 | 6.2528 | 0.1827 | 82.7305 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRACMNT4 138.00] TO [ANADARK4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7226 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRACMNT4 138.00] TO [ANADARK4 138.00] CKT 2 | 6.2528 | 0.1827 | 82.7226 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRACMNT4 138.00] TO [WASHITA4 138.00] CKT 1 | 6.2527 | 0.1827 | 82.7227 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRACMNT4 138.00] TO [WASHITA4 138.00] CKT 2 | 6.2527 | 0.1827 | 82.7226 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDNGTN7 345.00] TO [WOODRNG7 345.00] CKT 1 | 6.2221 | 0.1828 | 82.8272 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDDIRT7 345.00] TO [RDDIRT11 34.500] TO [RDDRTT11 12.500] CKT 1 | 6.2529 | 0.1827 | 82.7232 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDDIRT7 345.00] TO [RDDIRT21 34.500] TO [RDDRTT21 12.500] CKT 1 | 6.253 | 0.1827 | 82.7198 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MNCWND47 345.00] TO [MNCWND57 345.00] CKT 1 | 6.2529 | 0.1827 | 82.7231 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MNCWND47 345.00] TO [MNCO4L11 34.500] TO [MNCO4T11 13.800] CKT 1 | 6.2529 | 0.1827 | 82.7177 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [STRRDTP4 138.00] TO [BROWN 4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7221 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SKELTON7 345.00] TO [WOODRNG7 345.00] CKT 1 | 6.2514 | 0.1828 | 82.8165 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SKELTL11 34.500] TO [SKELTC11 34.500] CKT 1 | 6.2519 | 0.1828 | 82.78 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DMNDSL11 34.500] TO [DMNDSC11 34.500] CKT 1 | 6.2529 | 0.1827 | 82.7183 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DMNDSL21 34.500] TO [DMNDSC21 34.500] CKT 1 | 6.2529 | 0.1827 | 82.7179 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DMNDSPG7 345.00] TO [JOHNCO 7 345.00] CKT 1 | 6.253 | 0.1827 | 82.7145 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [PINTAIL7 345.00] TO [WOODRNG7 345.00] CKT 1 | 6.2032 | 0.1829 | 82.8539 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [KINGWD 7 345.00] TO [KNGWDL11 34.500] TO [KNGWDT11 13.200] CKT 1 | 6.2527 | 0.1827 | 82.7293 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [KINGWD 7 345.00] TO [KNGWDL21 34.500] TO [KNGWDT21 13.200] CKT 1 | 6.2527 | 0.1827 | 82.7293 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [BECKHAM7 345.00] TO [WWRDEHV7 345.00] CKT 1 | 6.252 | 0.1827 | 82.7141 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [BECKHAM7 345.00] TO [BORDER 7345.00] CKT 1 | 6.2504 | 0.1827 | 82.7432 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORMHLL7 345.00] TO [MINCO 7 345.00] CKT 1 | 6.2519 | 0.1828 | 82.757 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORMHLL4 138.00] TO [MCCLAIN4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7146 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORMHLL4 138.00] TO [CHERYCK4 138.00] CKT 1 | 6.2521 | 0.1828 | 82.7626 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORMHLL4 138.00] TO [TURNER 4 138.00] CKT 1 | 6.253 | 0.1827 | 82.7155 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [KGFSJCT4 138.00] TO [EKFSHTP4 138.00] CKT 1 | 5.3507 | 0.1841 | 84.1101 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WFEC_RNFRO4 138.00] TO [WAKTASW4 138.00] CKT 1 | 6.2509 | 0.1827 | 82.7244 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MUSTANG4 138.00] TO [EL RENO4 138.00] CKT 1 | 6.234 | 0.1826 | 82.6283 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CANA 4 138.00] TO [CALUMET4 138.00] CKT 1 | 5.4698 | 0.1845 | 84.4622 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [BULFTTP4 138.00] TO [DOVERSW4 138.00] CKT 1 | 6.0601 | 0.1831 | 83.065 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WATNGSW4 138.00] TO [CALUMET4 138.00] CKT 1 | 6.1477 | 0.183 | 83.0038 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WATNGSW4 138.00] TO [OMEGA 4 138.00] CKT 1 | 6.2085 | 0.1829 | 82.8889 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WATNGSW4 138.00] TO [WATONGA4 138.00] CKT 1 | 6.2518 | 0.1826 | 82.5567 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [TWNLAKE4 138.00] TO [TWNLKSW4 138.00] CKT Z1 | 5.2205 | 0.185 | 84.9931 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDCNTP4 138.00] TO [REDCORN4 138.00] CKT 1 | 6.2532 | 0.1827 | 82.6871 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDCNTP4 138.00] TO [COGAR 4 138.00] CKT 1 | 6.148 | 0.183 | 82.9662 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NKNGFSH4 138.00] TO [DOVERSW4 138.00] CKT 1 | 5.3489 | 0.1842 | 84.1926 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CDRDLTP4 138.00] TO [PIC4 138.00] CKT 1 | 5.9013 | 0.1834 | 83.3916 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CDRDLTP4 138.00] TO [CEDRDAL4 138.00] CKT 1 | 6.2527 | 0.1827 | 82.7271 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DOVER 4 138.00] TO [DOVERSW4 138.00] CKT 1 | 5.2068 | 0.1849 | 84.859 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DOVERSW2 69.000] TO [DOVERSW4 138.00] TO [DVRTERT 13.800] CKT 1 | 5.9774 | 0.1835 | 83.4948 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SCOTTSW4 138.00] TO [EL RENO4 138.00] CKT 1 | 6.0116 | 0.1833 | 83.3247 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [KIERSEY4 138.00] TO [COLBERT4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7222 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SARA RD4 138.00] TO [SUNSHIN4 138.00] CKT 1 | 6.2328 | 0.1827 | 82.7327 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OKEENE 2 69.000] TO [CANTON-2 69.000] CKT 1 | 6.1884 | 0.1828 | 82.8302 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OKEENE 2 69.000] TO [FAIRVEW2 69.000] CKT 1 | 6.2152 | 0.1828 | 82.759 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OKEENE 4 138.00] TO [DOVERSW4 138.00] CKT 1 | 5.5385 | 0.1845 | 84.4721 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RUSSETT4 138.00] TO [REAGAN 4 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7223 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SCLMNJC4 138.00] TO [SCOLEMN4 138.00] CKT 1 | 6.2529 | 0.1827 | 82.7223 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SCLMNJC4 138.00] TO [DURANTP4 138.00] CKT 1 | 6.2527 | 0.1827 | 82.7228 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HUGO 7 345.00] TO [HUGOITC4 138.00] TO [HUGO TERTA 13.800] CKT 1 | 6.2527 | 0.1827 | 82.7213 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WICHITA7 345.00] TO [RENO 7 345.00] CKT 1 | 6.2511 | 0.1827 | 82.7085 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 1 | 6.2525 | 0.1827 | 82.7345 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 2 | 6.2525 | 0.1827 | 82.7345 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WICHITA7 345.00] TO [BENTON 7 345.00] CKT 1 | 6.2514 | 0.1827 | 82.7326 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WICHITA7 345.00] TO [EXPEDITION7 345.00] CKT 1 | 6.2501 | 0.1827 | 82.7315 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WICHITA7 345.00] TO [EVANS N4 138.00] TO [WICH11 1 13.800] CKT 1 | 6.2528 | 0.1827 | 82.7254 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WICHITA7 345.00] TO [EVANS N4 138.00] TO [WICH12 1 13.800] CKT 1 | 6.2528 | 0.1827 | 82.7266 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VIOLA 7 345.00] TO [RENFROW7 345.00] CKT 1 | 6.2316 | 0.1825 | 82.5038 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VIOLA 4 138.00] TO [SUMNER 4 138.00] CKT 1 | 6.2527 | 0.1827 | 82.719 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VIOLA 4 138.00] TO [CLEARWT4 138.00] CKT 1 | 6.2525 | 0.1827 | 82.711 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VIOLA 4 138.00] TO [GILL 4 138.00] CKT 1 | 6.2525 | 0.1827 | 82.7108 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VIOLA 4 138.00] TO [MILAN_GOAB 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7214 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VIOLA 4 138.00] TO [CONWAY 138.00] CKT 1 | 6.2528 | 0.1827 | 82.7218 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [G17-075-TAP 345.00] TO [SUNNYSD7 345.00] CKT 1 | 6.252 | 0.1827 | 82.7347 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GEN-2015-093345.00] TO [G15-093XFMR134.500] CKT 1 | 6.2532 | 0.1827 | 82.7069 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [G16-030-XFMR34.500] TO [GEN-2016-030138.00] CKT 1 | 6.2528 | 0.1827 | 82.7213 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [G16-030-XFMR34.500] TO [G16-030-GSU134.500] CKT 1 | 6.2528 | 0.1827 | 82.7213 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [G16-037XFMR134.500] TO [GEN-2016-037345.00] CKT 1 | 6.2538 | 0.1827 | 82.6811 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [G16-037XFMR134.500] TO [G16-037-GSU134.500] CKT 1 | 6.2538 | 0.1827 | 82.6811 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [G16-091-TAP 345.00] TO [GEN-2016-091345.00] CKT 1 | 6.2533 | 0.1827 | 82.7022 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [G16-091-TAP 345.00] TO [GEN-2016-095345.00] CKT 1 | 6.2531 | 0.1827 | 82.7125 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GEN-2016-118138.00] TO [DOVERSW4 138.00] CKT 1 | 6.3248 | 0.1826 | 82.6351 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [G16-118XFMR134.500] TO [G16-118-GSU134.500] CKT 1 | 6.307 | 0.1817 | 81.7309 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [G16-118XFMR234.500] TO [G16-118-GSU234.500] CKT 1 | 6.3087 | 0.1817 | 81.7016 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [G16133G16146345.00] TO [G16133_345GS345.00] CKT 1 | 6.2522 | 0.1827 | 82.7295 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GEN-2016-128345.00] TO [G16-128XFMR134.500] CKT 1 | 6.2529 | 0.1827 | 82.7212 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [G16-153-TAP 345.00] TO [FR2EAST7 345.00] CKT 1 | 6.2521 | 0.1828 | 82.7735 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [G16-153-TAP 345.00] TO [GEN-2016-153345.00] CKT 1 | 6.2528 | 0.1827 | 82.7249 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [G16-153-TAP 345.00] TO [GEN-2017-086345.00] CKT 1 | 6.2528 | 0.1827 | 82.7249 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GEN-2017-075345.00] TO [G17-075XFMR134.500] CKT 1 | 6.2529 | 0.1827 | 82.7176 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GEN-2017-092345.00] TO [G17-092-SWYD345.00] CKT 1 | 6.2529 | 0.1827 | 82.7187 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GEN-2017-092345.00] TO [G17-092XFMR134.500] CKT 1 | 6.2529 | 0.1827 | 82.7207 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GEN-2017-092345.00] TO [G17-092XFMR234.500] CKT 1 | 6.2529 | 0.1827 | 82.72 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LIEBERM4 138.00] TO [LIEBR3-1 13.800] CKT 2 | 6.2528 | 0.1827 | 82.7222 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LIEBERM4 138.00] TO [LIEBR4-1 13.800] CKT 2 | 6.2528 | 0.1827 | 82.7222 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILKES 4 138.00] TO [WILKE1-1 20.000] CKT 2 | 6.2529 | 0.1827 | 82.7196 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILKES 4 138.00] TO [WILKE2-1 22.000] CKT 2 | 6.2529 | 0.1827 | 82.7199 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDBUD 7 345.00] TO [ARCADIA7 345.00] CKT 2 | 6.2526 | 0.1826 | 82.6284 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDBUD 7 345.00] TO [ARCADIA7 345.00] CKT 3 | 6.2525 | 0.1826 | 82.6249 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDBUD 7 345.00] TO [ARCADIA7 345.00] CKT 3 | 6.2525 | 0.1826 | 82.6152 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SEMINOL4 138.00] TO [MAUD 4 138.00] CKT 2 | 6.2523 | 0.1827 | 82.732 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MUSKOGE7 345.00] TO [PECANCK7 345.00] CKT 2 | 6.2526 | 0.1827 | 82.7268 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MUSKOGE7 345.00] TO [FIREWHL-TAP 345.00] CKT 2 | 6.2502 | 0.1828 | 82.7605 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MATHWSN7 345.00] TO [TATONGA7 345.00] CKT 2 | 6.2522 | 0.1828 | 82.7623 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRACMNT4 138.00] TO [ANADARK4 138.00] CKT 2 | 6.2525 | 0.1827 | 82.7251 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRACMNT4 138.00] TO [WASHITA4 138.00] CKT 2 | 6.2523 | 0.1827 | 82.7244 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 2 | 6.244 | 0.1831 | 83.0897 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | Base | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [4MEMORALT 138.00] TO [JNSKAMO4 138.00] CKT 1 | 6.2015 | 0.1816 | 81.5931 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [3SAREPTA! 115.00] TO [7SAREPTA% 345.00] CKT 1 | 6.2023 | 0.1816 | 81.5658 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [7SAREPTA% 345.00] TO [7EL DORADO 345.00] CKT 1 | 6.2023 | 0.1816 | 81.5651 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DOLHILL7 345.00] TO [SW SHV 7 345.00] CKT 1 | 6.2023 | 0.1816 | 81.5643 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRANDPR5 161.00] TO [GRNDPRT5 161.00] CKT 1 | 6.2023 | 0.1816 | 81.5665 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [TUPELO 4 138.00] TO [S BROWN4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5663 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [S BROWN4 138.00] TO [DENISON4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5669 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [S BROWN4 138.00] TO [COLBRTP4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.567 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [S BROWN4 138.00] TO [KIERSEY4 138.00] CKT 1 | 6.2021 | 0.1816 | 81.5671 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [S BROWN4 138.00] TO [RUSSETT4 138.00] CKT 1 | 6.2021 | 0.1816 | 81.5698 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [S BROWN4 138.00] TO [SCLMNJC4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5657 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHAMSPR1 13.800] TO [CHAMSPR5 161.00] TO [CHAMSPR7 345.00] CKT 1 | 6.2022 | 0.1816 | 81.5655 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHAMSPR7 345.00] TO [TONTITN7 345.00] CKT 1 | 6.2023 | 0.1816 | 81.5651 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [BOONVIL2 69.000] TO [BRANCH 2 69.000] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NMAGZIN5 161.00] TO [WBOONVL5 161.00] CKT 1 | 6.2023 | 0.1816 | 81.5665 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NMAGZIN5 161.00] TO [MAGZREC5 161.00] CKT 1 | 6.2023 | 0.1816 | 81.5654 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SW SHV 4 138.00] TO [SW SHV 7 345.00] TO [SWSHV1-1 13.800] CKT 1 | 6.2023 | 0.1816 | 81.5669 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SW SHV 4 138.00] TO [SW SHV 7 345.00] TO [SWSHV2-1 13.800] CKT 2 | 6.2023 | 0.1816 | 81.5669 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SW SHV 7 345.00] TO [DIANA 7 345.00] CKT 1 | 6.2023 | 0.1816 | 81.5639 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORAM 4 138.00] TO [LONGWD 4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WELSH 7 345.00] TO [DIANA 7 345.00] CKT 1 | 6.2023 | 0.1816 | 81.5649 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WELSH 7 345.00] TO [DIANA 7 345.00] CKT 2 | 6.2023 | 0.1816 | 81.565 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WELSH 7 345.00] TO [WILKES 7 345.00] CKT 1 | 6.2023 | 0.1816 | 81.5637 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SCOTTSV4 138.00] TO [LONGWD 4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5664 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LIEBERM4 138.00] TO [LONGWD 4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5669 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LONGWD 4 138.00] TO [OAKPH 4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILKES-1 13.200] TO [WILKES 4 138.00] TO [WILKES 7 345.00] CKT 1 | 6.2023 | 0.1816 | 81.5671 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILKES 7 345.00] TO [WILKE3-1 22.000] CKT 1 | 6.2023 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILKES 7 345.00] TO [WILKE3-1 22.000] CKT 2 | 6.2023 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [36&OLY-4 138.00] TO [CARSN-T4 138.00] CKT 1 | 6.2021 | 0.1816 | 81.5632 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OAKS W4 138.00] TO [OAKSWTP4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5663 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DENVTAP4 138.00] TO [T.NO.--4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5666 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILLPIP2 69.000] TO [T.P.S.-2 69.000] CKT 1 | 6.2023 | 0.1816 | 81.5664 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WEKIWA-7 345.00] TO [T.NO.--7 345.00] CKT 1 | 6.2019 | 0.1816 | 81.5677 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WEKIWA-7 345.00] TO [SAPLPRD7 345.00] CKT 1 | 6.2008 | 0.1816 | 81.5649 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WEKIWA-7 345.00] TO [SOONER 7 345.00] CKT 1 | 6.1956 | 0.1816 | 81.6001 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CARSN-S4 138.00] TO [KENSH-W4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5662 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RSS T1 4 138.00] TO [R.S.S.-4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5666 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RSS T1 4 138.00] TO [R.S.S.-7 345.00] TO [RSST1 T1 13.800] CKT 1 | 6.2022 | 0.1816 | 81.5666 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [52DELTP4 138.00] TO [36LEWIS4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5655 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-7 345.00] TO [ONETA--7 345.00] CKT 1 | 6.2018 | 0.1816 | 81.5661 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-7 345.00] TO [COGENT 7 345.00] CKT 1 | 6.2017 | 0.1816 | 81.5696 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-7 345.00] TO [SAPLPRD7 345.00] CKT 1 | 6.2015 | 0.1816 | 81.5629 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-7 345.00] TO [REDBUD 7 345.00] CKT 1 | 6.1967 | 0.1816 | 81.5874 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-7 345.00] TO [G16133G16146345.00] CKT 1 | 6.2008 | 0.1816 | 81.5885 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-7 345.00] TO [RSS T2 4 138.00] TO [RSST2 T1 13.800] CKT 1 | 6.2022 | 0.1816 | 81.5666 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-4 138.00] TO [52DELWT4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5678 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-4 138.00] TO [OAKSETP4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5679 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-4 138.00] TO [RSS T2 4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5666 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ONETA--4 138.00] TO [ONETA--7 345.00] TO [ONETA1-1 13.800] CKT 1 | 6.2023 | 0.1816 | 81.567 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ONETA--4 138.00] TO [ONETA--7 345.00] TO [ONETA2-1 34.500] CKT 2 | 6.2023 | 0.1816 | 81.5671 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ONETA--4 138.00] TO [ONETA--7 345.00] TO [ONETA5-1 34.500] CKT 3 | 6.2023 | 0.1816 | 81.5671 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ONETA--7 345.00] TO [OEC 7 345.00] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ONETA--7 345.00] TO [OEC 7 345.00] CKT 2 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ONETA--7 345.00] TO [N.E.S.-7 345.00] CKT 1 | 6.2022 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [52DELWT4 138.00] TO [S HILLW4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5662 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [T.NO.--4 138.00] TO [CDC-ET 4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5669 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [T.NO.--4 138.00] TO [CDC-WT 4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.567 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [T.NO.--4 138.00] TO [OWASOTP4 138.00] CKT 1 | 6.2021 | 0.1816 | 81.5665 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [T.NO.--4 138.00] TO [P&P WTP4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5655 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [T.NO.--4 138.00] TO [SKIATOK4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5675 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [T.NO.--4 138.00] TO [46ST-TP-4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [T.NO.--4 138.00] TO [N.E.S.-4 138.00] CKT 1 | 6.2021 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OAKS--E4 138.00] TO [OAKSETP4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5664 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OAKSWTP4 138.00] TO [SAPLPRD4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5666 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [T.NO.--7 345.00] TO [N.E.S.-7 345.00] CKT 1 | 6.2008 | 0.1816 | 81.5684 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [T.NO.--7 345.00] TO [CLEVLND7 345.00] CKT 1 | 6.1955 | 0.1816 | 81.5746 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [T.NO.--7 345.00] TO [IGLOOV 7 345.00] CKT 1 | 6.2002 | 0.1816 | 81.5646 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SAPLPRD4 138.00] TO [72ELWOD4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5666 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [PITTSB-7 345.00] TO [VALIANT7 345.00] CKT 1 | 6.2006 | 0.1816 | 81.5729 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [PITTSB-7 345.00] TO [KIOWA 7 345.00] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [PITTSB-7 345.00] TO [SEMINOL7 345.00] CKT 1 | 6.2003 | 0.1816 | 81.5694 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [PITTSB-7 345.00] TO [C-RIVER7 345.00] CKT 1 | 6.2018 | 0.1816 | 81.571 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VALIANT7 345.00] TO [HUGO 7 345.00] CKT 1 | 6.202 | 0.1816 | 81.5714 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [C-RIVER4 138.00] TO [C-RIVER7 345.00] TO [C-RIVER1 13.800] CKT 1 | 6.202 | 0.1816 | 81.5786 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LES#5-1 13.800] TO [L.E.S.-4 138.00] TO [L.E.S.-7 345.00] CKT 2 | 6.2026 | 0.1816 | 81.5659 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LES#4-1 13.800] TO [L.E.S.-4 138.00] TO [L.E.S.-7 345.00] CKT 1 | 6.2021 | 0.1816 | 81.5659 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [O.K.U.-7 345.00] TO [L.E.S.-7 345.00] CKT 1 | 6.2017 | 0.1815 | 81.5404 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [L.E.S.-7 345.00] TO [G16-091-TAP 345.00] CKT 1 | 6.1983 | 0.1816 | 81.5809 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CAN_GAS4 138.00] TO [JENSEN 4 138.00] CKT 1 | 6.1974 | 0.1814 | 81.4481 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHISHOLM7 345.00] TO [BECKHAM7 345.00] CKT 1 | 6.203 | 0.1815 | 81.5442 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHISHOLM7 345.00] TO [CHISHOLM6 230.00] TO [CHISHOLM1 13.200] CKT 1 | 6.2027 | 0.1815 | 81.5478 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RSHSPR1_TER113.800] TO [RSHSPR1_COL134.500] TO [RSHSPR1_MPT1345.00] CKT 1 | 6.2023 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OTTER 4 138.00] TO [WOODRNG4 138.00] CKT 1 | 6.1297 | 0.1816 | 81.6388 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [FRMNTAP4 138.00] TO [WOODRNG4 138.00] CKT 1 | 6.1882 | 0.1818 | 81.7522 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WAUKOMI4 138.00] TO [WAUKOTP4 138.00] CKT 1 | 4.0535 | 0.1868 | 86.7576 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WAUKOMI4 138.00] TO [HENESEY4 138.00] CKT 1 | 4.0514 | 0.1868 | 86.8439 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WAUKOTP4 138.00] TO [WOODRNG4 138.00] CKT 1 | 5.9354 | 0.1821 | 82.0888 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WOODRNG4 138.00] TO [MARSHL 4 138.00] CKT 1 | 6.1928 | 0.1816 | 81.5899 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MARSHL 4 138.00] TO [CTNWOOD4 138.00] CKT 1 | 6.1924 | 0.1816 | 81.6009 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DOVERTP2 69.000] TO [DOVERSW2 69.000] CKT 1 | 5.9389 | 0.1826 | 82.5596 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HENESEY4 138.00] TO [BULFTTP4 138.00] CKT 1 | 6.0144 | 0.1819 | 81.8863 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SOONER 7 345.00] TO [PINTAIL7 345.00] CKT 1 | 6.1501 | 0.1816 | 81.5752 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [JOHNCO 4 138.00] TO [RUSSET-4 138.00] CKT 1 | 6.2021 | 0.1816 | 81.5701 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [JOHNCO 4 138.00] TO [SXMLCKT4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5658 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [JOHNCO 4 138.00] TO [CANEYCK4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5688 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [YUKON 2 69.000] TO [MSTANG 2 69.000] CKT 1 | 6.1766 | 0.1816 | 81.638 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [JENSENT4 138.00] TO [JENSEN 4 138.00] CKT 1 | 6.1315 | 0.1821 | 82.091 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [JENSENT4 138.00] TO [CIMARON4 138.00] CKT 1 | 6.1711 | 0.1818 | 81.8007 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CTNWOOD4 138.00] TO [ARCADIA4 138.00] CKT 1 | 6.0644 | 0.1821 | 82.064 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHTWOOD4 138.00] TO [LGARBER4 138.00] CKT 1 | 6.2019 | 0.1816 | 81.5743 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHTWOOD4 138.00] TO [JONESSB4 138.00] CKT 1 | 6.2019 | 0.1816 | 81.5745 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LAKESID4 138.00] TO [DVISION4 138.00] CKT 1 | 6.2019 | 0.1816 | 81.5834 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SLVRLAK4 138.00] TO [DVISION4 138.00] CKT 1 | 6.2021 | 0.1816 | 81.5715 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DVISION4 138.00] TO [RICHRDS4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5677 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DVISION4 138.00] TO [HAYMAKR4 138.00] CKT 1 | 6.2016 | 0.1816 | 81.5686 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MSTANG 2 69.000] TO [WODLAWN2 69.000] CKT 1 | 6.2019 | 0.1816 | 81.5873 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MSTANG 2 69.000] TO [WILROGR2 69.000] CKT 1 | 6.202 | 0.1816 | 81.5698 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MSTANG 2 69.000] TO [MCARTHR2 69.000] CKT 1 | 6.2019 | 0.1816 | 81.5812 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MSTANG 2 69.000] TO [MSTNG 6G 13.800] CKT 1 | 6.2 | 0.1815 | 81.5426 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MSTANG 2 69.000] TO [MSTNG 7G 13.800] CKT 1 | 6.2 | 0.1815 | 81.5426 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HAYMAKR4 138.00] TO [CIMARON4 138.00] CKT 1 | 6.2014 | 0.1816 | 81.5707 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [COUNCIL4 138.00] TO [WESTOAK4 138.00] CKT 1 | 6.2015 | 0.1816 | 81.5997 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORTWST4 138.00] TO [NORTWST7 345.00] TO [NORTWS21 13.800] CKT 1 | 6.2015 | 0.1816 | 81.5694 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORTWST4 138.00] TO [NORTWST7 345.00] TO [NORTWS31 13.800] CKT 1 | 6.2016 | 0.1816 | 81.5664 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORTWST4 138.00] TO [NORTWST7 345.00] TO [NORTWS41 13.800] CKT 1 | 6.2012 | 0.1816 | 81.5946 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORTWST7 345.00] TO [SPRNGCK7 345.00] CKT 1 | 6.1999 | 0.1816 | 81.601 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORTWST7 345.00] TO [CIMARON7 345.00] CKT 1 | 6.2021 | 0.1816 | 81.5705 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORTWST7 345.00] TO [MATHWSN7 345.00] CKT 1 | 6.2008 | 0.1816 | 81.5941 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DUNJEE 4 138.00] TO [RENO 4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5714 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [36&MER 4 138.00] TO [SW 5TH 4 138.00] CKT 1 | 6.202 | 0.1816 | 81.5664 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [36&MER 4 138.00] TO [HOBBYLO4 138.00] CKT 1 | 6.2024 | 0.1816 | 81.5639 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SMITHCO4 138.00] TO [DAYTON 4 138.00] CKT 1 | 6.1993 | 0.1816 | 81.5651 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DAYTON 4 138.00] TO [HOBBYLO4 138.00] CKT 1 | 6.2018 | 0.1816 | 81.571 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [XEROX 4 138.00] TO [MORGAN 4 138.00] CKT 1 | 6.2004 | 0.1815 | 81.5238 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CIMARON4 138.00] TO [CIMARON7 345.00] TO [CIMARO11 13.800] CKT 1 | 6.1979 | 0.1816 | 81.6408 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CIMARON4 138.00] TO [CIMARON7 345.00] TO [CIMARO21 13.800] CKT 2 | 6.1982 | 0.1817 | 81.6598 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDBUD1S 18.000] TO [REDBUD 7 345.00] TO [REDBUD1G 18.000] CKT 1 | 6.195 | 0.1816 | 81.5759 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDBUD2S 18.000] TO [REDBUD 7 345.00] TO [REDBUD2G 18.000] CKT 1 | 6.195 | 0.1816 | 81.5759 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CIMARON7 345.00] TO [MATHWSN7 345.00] CKT 1 | 6.2014 | 0.1816 | 81.5829 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CIMARON7 345.00] TO [MATHWSN7 345.00] CKT 2 | 6.2014 | 0.1816 | 81.5829 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CIMARON7 345.00] TO [FSHRTAP7 345.00] CKT 1 | 6.1946 | 0.1816 | 81.5955 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CIMARON7 345.00] TO [NORMHLL7 345.00] CKT 1 | 6.1985 | 0.1816 | 81.5815 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDBUD3S 18.000] TO [REDBUD 7 345.00] TO [REDBUD3G 18.000] CKT 1 | 6.195 | 0.1816 | 81.5759 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [JNSKAMO4 138.00] TO [ARCADIA4 138.00] CKT 1 | 6.2015 | 0.1816 | 81.5706 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ARCADIA4 138.00] TO [RNDBARN4 138.00] CKT 1 | 6.201 | 0.1816 | 81.5993 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ARCADIA4 138.00] TO [LGARBER4 138.00] CKT 1 | 6.2019 | 0.1816 | 81.5751 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDBUD 7 345.00] TO [REDBUD4S 18.000] TO [REDBUD4G 18.000] CKT 1 | 6.195 | 0.1816 | 81.5759 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SW 5TH 2 69.000] TO [SW 5TH 4 138.00] TO [SW 5TH 1 13.800] CKT 1 | 6.2024 | 0.1816 | 81.5606 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SW 5TH 4 138.00] TO [CLASSEN4 138.00] CKT 1 | 6.2018 | 0.1816 | 81.5794 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HSLEAST2 69.000] TO [HSLWEST2 69.000] CKT 1 | 6.202 | 0.1816 | 81.5661 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DRAPER 7 345.00] TO [SEMINOL7 345.00] CKT 1 | 6.2002 | 0.1816 | 81.5827 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DRAPER 7 345.00] TO [SEMINOL7 345.00] CKT 2 | 6.2002 | 0.1816 | 81.5827 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DRAPER 7 345.00] TO [SEMINOL7 345.00] CKT 3 | 6.2011 | 0.1816 | 81.5857 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DRAPER 7 345.00] TO [NORMHLL7 345.00] CKT 1 | 6.2014 | 0.1816 | 81.5768 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DRAPER 7 345.00] TO [NORMHLL7 345.00] CKT 2 | 6.2014 | 0.1816 | 81.5766 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NE10TH 4 138.00] TO [MIDWAY 4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.57 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NE10TH 4 138.00] TO [RENO 4 138.00] CKT 1 | 6.2021 | 0.1816 | 81.5727 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GLENDAL4 138.00] TO [SE15TH 4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5665 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DALE 4 138.00] TO [SQUIRCK4 138.00] CKT 1 | 6.2011 | 0.1816 | 81.5598 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SE15TH 4 138.00] TO [BARNES 4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.568 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SEMINL2G 17.100] TO [SEMINOL7 345.00] CKT 1 | 6.1958 | 0.1816 | 81.6131 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SEMINL3G 20.900] TO [SEMINOL7 345.00] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRTPLNS4 138.00] TO [LNWOODT4 138.00] CKT 1 | 6.202 | 0.1816 | 81.5669 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SEMINOL4 138.00] TO [SEMINOL7 345.00] TO [SEMINO11 14.400] CKT 1 | 6.2017 | 0.1816 | 81.5684 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SEMINOL4 138.00] TO [SEMINOL7 345.00] TO [SEMINO21 14.400] CKT 1 | 6.2017 | 0.1816 | 81.5684 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HAMMTAP4 138.00] TO [LINCOLN4 138.00] CKT 1 | 6.2018 | 0.1816 | 81.5635 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HAMMTAP4 138.00] TO [HAMMETT4 138.00] CKT 1 | 6.2024 | 0.1816 | 81.5637 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WARWICK4 138.00] TO [WFROSST4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WARWICK4 138.00] TO [BELLCOW4 138.00] CKT 1 | 6.2017 | 0.1816 | 81.5675 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RUSSET-4 138.00] TO [RUSSETT4 138.00] CKT 1 | 6.2021 | 0.1816 | 81.5699 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SUNNYSD4 138.00] TO [UNIROY 4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5684 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SUNNYSD4 138.00] TO [LONEGRV4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5675 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SUNNYSD4 138.00] TO [ROCKYPT4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5695 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SUNNYSD4 138.00] TO [CARTRCO4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5663 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [BROWNTP4 138.00] TO [STRRDTP4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [COLEMNT4 138.00] TO [STRRDTP4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5663 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MUSKOG4G 18.000] TO [MUSKOGE7 345.00] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MUSKOGE7 345.00] TO [MUSKOG5G 18.000] CKT 1 | 6.2013 | 0.1816 | 81.5697 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MUSKOGE7 345.00] TO [MUSKOG6G 24.000] CKT 1 | 6.2009 | 0.1816 | 81.576 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MUSKOGE7 345.00] TO [FTSMITH7 345.00] CKT 1 | 6.2016 | 0.1816 | 81.5794 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [5TRIBES5 161.00] TO [PECANCK5 161.00] CKT 1 | 6.2022 | 0.1816 | 81.5674 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [AGENCY 5 161.00] TO [PECANCK5 161.00] CKT 1 | 6.2022 | 0.1816 | 81.5672 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [PECANCK4 138.00] TO [PECANCK5 161.00] TO [PECANC31 13.200] CKT 1 | 6.2016 | 0.1816 | 81.5686 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [BRANCH 2 69.000] TO [PENDER 2 69.000] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VBI 5 161.00] TO [GRNDPRT5 161.00] CKT 1 | 6.2023 | 0.1816 | 81.5663 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SHORTMT5 161.00] TO [SUBIACT5 161.00] CKT 1 | 6.2023 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WFROSST4 138.00] TO [LINCOLN4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5666 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LINWOOD4 138.00] TO [LNWOODT4 138.00] CKT 1 | 6.2024 | 0.1816 | 81.5596 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MNCOWND1 34.500] TO [MCNOWND7 345.00] CKT 1 | 6.2024 | 0.1816 | 81.5661 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ACORN 4 138.00] TO [JONESSB4 138.00] CKT 1 | 6.2019 | 0.1816 | 81.5634 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HUNTERS7 345.00] TO [CHSHLMV7 345.00] CKT 1 | 6.2027 | 0.1816 | 81.5699 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MATHWSN7 345.00] TO [REDNGTN7 345.00] CKT 1 | 6.1769 | 0.1815 | 81.5442 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [KNIPE 4 138.00] TO [SPGVLLY4 138.00] CKT 1 | 6.2008 | 0.1816 | 81.5791 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RENFROW4 138.00] TO [GRANTCO4 138.00] CKT 1 | 6.1979 | 0.1816 | 81.6066 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RENFROW4 138.00] TO [MDFRDTP4 138.00] CKT 1 | 6.2018 | 0.1816 | 81.567 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RENFROW4 138.00] TO [WFEC_RNFRO4 138.00] CKT 1 | 6.2006 | 0.1816 | 81.5594 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MNCWND37 345.00] TO [MNCWND31 34.500] CKT 1 | 6.2023 | 0.1816 | 81.5656 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MNCWND37 345.00] TO [MNCWND47 345.00] CKT 1 | 6.2023 | 0.1816 | 81.5759 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRNTWD 7 345.00] TO [GRNTWD12 34.500] TO [GRNTWDT2 12.500] CKT 1 | 6.202 | 0.1816 | 81.5748 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRNTWD 7 345.00] TO [GRNTWD11 34.500] TO [GRNTWDT1 12.500] CKT 1 | 6.202 | 0.1816 | 81.5749 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRACMNT7 345.00] TO [GEN-2015-093345.00] CKT 1 | 6.2025 | 0.1816 | 81.5624 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRACMNT7 345.00] TO [G16-091-TAP 345.00] CKT 1 | 6.1989 | 0.1816 | 81.5688 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRACMNT7 345.00] TO [GRACMNT4 138.00] TO [GRCMNT11 13.800] CKT 1 | 6.2016 | 0.1816 | 81.5872 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDNGTN7 345.00] TO [REDDIRT7 345.00] CKT Z1 | 6.2028 | 0.1816 | 81.5605 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [BULFOOT4 138.00] TO [BULFTTP4 138.00] CKT 1 | 6.1988 | 0.1815 | 81.5061 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SKELTON7 345.00] TO [GEN-2016-128345.00] CKT 1 | 6.2026 | 0.1816 | 81.5604 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SKELTON7 345.00] TO [SKELTL11 34.500] TO [SKELTT11 13.800] CKT 1 | 6.2017 | 0.1816 | 81.5983 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DMNDSL11 34.500] TO [DMNDSPG7 345.00] TO [DMNDST11 12.450] CKT 1 | 6.2022 | 0.1816 | 81.568 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DMNDSL21 34.500] TO [DMNDSPG7 345.00] TO [DMNDST21 12.450] CKT 1 | 6.2022 | 0.1816 | 81.5681 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [PINTAIL7 345.00] TO [KINGWD 7 345.00] CKT Z1 | 6.2011 | 0.1816 | 81.6117 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORMHLL7 345.00] TO [NORMHLL4 138.00] TO [NORMHL11 13.800] CKT 1 | 6.2024 | 0.1816 | 81.5632 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORMHLL7 345.00] TO [NORMHLL4 138.00] TO [NORMHL21 13.800] CKT 2 | 6.2024 | 0.1816 | 81.5632 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [KGFSJCT4 138.00] TO [NKNGFSH4 138.00] CKT 1 | 5.3148 | 0.183 | 82.973 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MUSTANG4 138.00] TO [SARA RD4 138.00] CKT 1 | 6.1833 | 0.1815 | 81.5304 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CANA 4 138.00] TO [SCOTTSW4 138.00] CKT 1 | 5.4321 | 0.183 | 83.0457 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WATNGSW4 138.00] TO [OKEENE 4 138.00] CKT 1 | 6.1814 | 0.1818 | 81.8213 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [TWNLAKE4 138.00] TO [DOVER 4 138.00] CKT 1 | 5.1802 | 0.1837 | 83.6879 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDCNTP4 138.00] TO [SCOTTSW4 138.00] CKT 1 | 6.1019 | 0.1816 | 81.6497 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CDRDLTP4 138.00] TO [OKEENE 4 138.00] CKT 1 | 5.8537 | 0.1822 | 82.1606 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DOVERSW2 69.000] TO [HENESEY2 69.000] CKT 1 | 6.1998 | 0.1815 | 81.5161 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DOVERSW2 69.000] TO [LACEY 2 69.000] CKT 1 | 6.2 | 0.1815 | 81.5397 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OKEENE 2 69.000] TO [OKEENE 4 138.00] TO [OKENTERT 13.800] CKT 1 | 6.0671 | 0.1818 | 81.8003 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HUGO 7 345.00] TO [G17-075-TAP 345.00] CKT 1 | 6.2006 | 0.1816 | 81.5873 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WICHITA7 345.00] TO [VIOLA 7 345.00] CKT 1 | 6.192 | 0.1815 | 81.5328 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VIOLA 7 345.00] TO [G16-153-TAP 345.00] CKT 1 | 6.2025 | 0.1816 | 81.5779 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VIOLA 7 345.00] TO [VIOLA 4 138.00] TO [SCJ1X1 13.800] CKT 2 | 6.2019 | 0.1816 | 81.5651 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VIOLA 7 345.00] TO [VIOLA 4 138.00] TO [VIOLA1X1 13.800] CKT 1 | 6.202 | 0.1816 | 81.5505 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [G17-075-TAP 345.00] TO [GEN-2017-075345.00] CKT 1 | 6.2022 | 0.1816 | 81.5679 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GEN-2016-118138.00] TO [G16-118XFMR134.500] CKT 1 | 6.2606 | 0.1809 | 80.9037 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GEN-2016-118138.00] TO [G16-118XFMR234.500] CKT 1 | 6.2624 | 0.1809 | 80.8882 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [4MEMORALT 138.00] TO [4LUTHER 138.00] CKT 1 | 6.2013 | 0.1816 | 81.6044 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [4MEMORALT 138.00] TO [4MEMORAL 138.00] CKT 1 | 6.2024 | 0.1816 | 81.5634 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [3SAREPTA! 115.00] TO [3MINDEN_LA! 115.00] CKT 1 | 6.2023 | 0.1816 | 81.5662 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [3SAREPTA! 115.00] TO [3CULLEN 115.00] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [3SAREPTA! 115.00] TO [3SPRINGHILL 115.00] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [3SAREPTA! 115.00] TO [3HAYNESVILLE115.00] CKT 1 | 6.2023 | 0.1816 | 81.5666 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [7SAREPTA% 345.00] TO [LONGWD 7 345.00] CKT 1 | 6.2024 | 0.1816 | 81.5615 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [7EL DORADO 345.00] TO [8EL DORADO% 500.00] TO [1EL DORADO2 13.800] CKT 1 | 6.2023 | 0.1816 | 81.5652 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DOLHILL7 345.00] TO [DOLHILL6 230.00] CKT 1 | 6.2025 | 0.1816 | 81.5581 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DOLHILL7 345.00] TO [G1DOLHIL 24.000] CKT 1 | 6.2018 | 0.1816 | 81.5848 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [TUPELO 4 138.00] TO [ALLEN 4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5666 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [TUPELO 4 138.00] TO [CENTRATAP4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5671 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [TUPELO 4 138.00] TO [ALLENGT4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5664 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [TUPELO 4 138.00] TO [TUPELO 4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [TUPELO 4 138.00] TO [STNWLSW4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [TUPELO 4 138.00] TO [BOGGY4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [S BROWN4 138.00] TO [BROWN 4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5669 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DENISON4 138.00] TO [DEN #1 1 13.800] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DENISON4 138.00] TO [DEN #2 1 13.800] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHAMSPR5 161.00] TO [SILOAMSP 5 161.00] CKT 1 | 6.2023 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHAMSPR5 161.00] TO [SILOAM 5 161.00] CKT 1 | 6.2023 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHAMSPR5 161.00] TO [TONTITN5 161.00] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHAMSPR5 161.00] TO [WEDINGTON 161.00] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHAMSPR5 161.00] TO [GEN-2017-076161.00] CKT 1 | 6.2023 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHAMSPR7 345.00] TO [CLARKSV7 345.00] CKT 1 | 6.2022 | 0.1816 | 81.5592 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [TONTITN7 345.00] TO [TONTITN5 161.00] TO [TONTITN1 13.800] CKT 1 | 6.2023 | 0.1816 | 81.5651 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [BOONVIL2 69.000] TO [BOONEVIL 2 69.000] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NMAGZIN5 161.00] TO [BRANCH 5 161.00] CKT 1 | 6.2023 | 0.1816 | 81.5664 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WBOONVL5 161.00] TO [NHUNTNT5 161.00] CKT 1 | 6.2023 | 0.1816 | 81.5665 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WBOONVL5 161.00] TO [WBOONVL2 69.000] TO [WBOONVL1 12.470] CKT 1 | 6.2023 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MAGZREC5 161.00] TO [5DANVLE AR! 161.00] CKT 1 | 6.2023 | 0.1816 | 81.5654 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SW SHV 4 138.00] TO [GENMOTR4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SW SHV 4 138.00] TO [POWELL 4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SW SHV 4 138.00] TO [S SHV 4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SW SHV 4 138.00] TO [SPRIDGE4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SW SHV 4 138.00] TO [LEASIDE 4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SW SHV 7 345.00] TO [LONGWD 7 345.00] CKT 1 | 6.2023 | 0.1816 | 81.5669 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORAM 4 138.00] TO [RAINES 4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WELSH 7 345.00] TOSPPMAINBUS 345.00] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WELSH 7 345.00] TO [NWTXARK7 345.00] CKT 1 | 6.2023 | 0.1816 | 81.5652 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WELSH 7 345.00] TO [LYDIA 7 345.00] CKT 1 | 6.202 | 0.1816 | 81.5605 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WELSH 7 345.00] TO [WELSH1-1 18.000] CKT 1 | 6.2017 | 0.1816 | 81.5857 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WELSH 7 345.00] TO [WELSH3-1 18.000] CKT 1 | 6.2017 | 0.1816 | 81.5858 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SCOTTSV4 138.00] TO [SEMRSHL4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5663 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LIEBERM4 138.00] TO [ARSHILL4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LIEBERM4 138.00] TO [IPCJEFF4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5664 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LIEBERM4 138.00] TO [LIEBR2-1 13.800] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LIEBERM4 138.00] TO [LIEBR3-1 13.800] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LIEBERM4 138.00] TO [LIEBR3-1 13.800] CKT 2 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LIEBERM4 138.00] TO [LIEBR4-1 13.800] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LIEBERM4 138.00] TO [LIEBR4-1 13.800] CKT 2 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LIEBERM4 138.00] TO [G16-167-TAP 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LIEBERM4 138.00] TO [LIEBERM2 69.000] TO [LBMN1-1 13.200] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LIEBERM4 138.00] TO [LIEBERM2 69.000] TO [LBMN2-1 13.200] CKT 2 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LIEBERM4 138.00] TO [LIEBERM2 69.000] TO [LBMN3-1 13.200] CKT 3 | 6.2023 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LONGWD 4 138.00] TO [LONGWD 7 345.00] TO [LONGW1-1 13.200] CKT 1 | 6.2023 | 0.1816 | 81.5672 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OAKPH 4 138.00] TO [FLOURNY4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DIANA 7 345.00] TO [PIRKEY 7 345.00] CKT 1 | 6.2023 | 0.1816 | 81.5656 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DIANA 7 345.00] TO [DIANA 4 138.00] TO [DIANA-S1 13.800] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DIANA 7 345.00] TO [DIANA 4 138.00] TO [DIANA-M1 13.800] CKT 2 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DIANA 7 345.00] TO [DIANA 4 138.00] TO [DIANA-N1 13.800] CKT 3 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILKES 4 138.00] TO [MUNZCTY4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5664 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILKES 4 138.00] TO [WATLANT4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILKES 4 138.00] TO [LSSOUTH4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5669 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILKES 4 138.00] TO [WELSHRE4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.567 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILKES 4 138.00] TO [JEFFRSN4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5663 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILKES 4 138.00] TO [WILKE1-1 20.000] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILKES 4 138.00] TO [WILKE1-1 20.000] CKT 2 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILKES 4 138.00] TO [WILKE2-1 22.000] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILKES 4 138.00] TO [WILKE2-1 22.000] CKT 2 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILKES 7 345.00] TO [LONGWD 7 345.00] CKT 1 | 6.2024 | 0.1816 | 81.5609 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [36&OLY-4 138.00] TO [T.P.S.-4 138.00] CKT 1 | 6.2019 | 0.1816 | 81.568 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CARSN-T4 138.00] TO [UNIONAV4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5662 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CARSN-T4 138.00] TO [S.S.---4 138.00] CKT 1 | 6.2021 | 0.1816 | 81.5626 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DENVTAP4 138.00] TO [DENVR-E4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DENVTAP4 138.00] TO [W.ED.-E4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5665 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILLPIP2 69.000] TO [OGMARTN2 69.000] CKT 1 | 6.2023 | 0.1816 | 81.5665 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WEKIWA-7 345.00] TO [WEKIWA-4 138.00] TO [WEKIW1-1 34.500] CKT 1 | 6.2015 | 0.1816 | 81.5971 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CARSN-S4 138.00] TO [T.P.S.-4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5665 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [52DELTP4 138.00] TO [S52DEL 4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [52DELTP4 138.00] TO [T.S.E.-4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5671 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [52DELTP4 138.00] TO [ZUNIS-S4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5665 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [KENSH-W4 138.00] TO [DENVR-C4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-7 345.00] TO [PECANCK7 345.00] CKT 1 | 6.2019 | 0.1816 | 81.5718 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-4 138.00] TO [116JENK4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5685 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-4 138.00] TO [136YALE4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5664 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-4 138.00] TO [ORU ETP4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5671 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-4 138.00] TO [ORU-WTP4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-4 138.00] TO [OKMULGE4 138.00] CKT 1 | 6.2021 | 0.1816 | 81.5708 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-4 138.00] TO [EXP_OKM4 138.00] CKT 1 | 6.2021 | 0.1816 | 81.5718 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-4 138.00] TO [RSS1-1 24.000] CKT 1 | 6.2013 | 0.1816 | 81.5703 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-4 138.00] TO [RSS2-1 22.000] CKT 1 | 6.201 | 0.1816 | 81.5759 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-4 138.00] TO [EXPGLNT4 138.00] CKT 1 | 6.2013 | 0.1816 | 81.5849 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [R.S.S.-4 138.00] TO [RSS NG3 13.800] TO [RSS NG4 13.800] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [T.P.S.-2 69.000] TO [T.P.S.-4 138.00] TO [TPS5-1 13.800] CKT 1 | 6.2022 | 0.1816 | 81.5662 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [36LEWIS4 138.00] TO [T.P.S.-4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.567 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ONETA--4 138.00] TO [BA101ST4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ONETA--4 138.00] TO [BA101-N4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5673 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ONETA--4 138.00] TO [BA.N-ST4 138.00] CKT 1 | 6.2024 | 0.1816 | 81.5674 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ONETA--4 138.00] TO [121LYNN4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5674 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ONETA--4 138.00] TO [BA_71ST4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5674 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ONETA--7 345.00] TO [CLARKSV7 345.00] CKT 1 | 6.2021 | 0.1816 | 81.5708 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [52DELWT4 138.00] TO [T.P.S.-4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5679 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [T.NO.--4 138.00] TO [T.NO.2-4 138.00] CKT 1 | 6.2017 | 0.1816 | 81.5706 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [COGENT 7 345.00] TO [COGEN G1 18.000] TO [COGEN S1 13.800] CKT 1 | 6.2017 | 0.1816 | 81.5696 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [COGENT 7 345.00] TO [COGEN G2 18.000] TO [COGEN S2 13.800] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [COGENT 7 345.00] TO [COGEN G3 18.000] TO [COGEN S3 13.800] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OEC 7 345.00] TO [OECSTM 1 18.000] CKT 1 | 6.2018 | 0.1816 | 81.5686 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OEC 7 345.00] TO [OECGT1-1 18.000] CKT 1 | 6.2019 | 0.1816 | 81.5688 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OEC 7 345.00] TO [OECGT1-2 18.000] CKT 1 | 6.2022 | 0.1816 | 81.5666 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OEC 7 345.00] TO [OECSTM 2 18.000] CKT 1 | 6.2018 | 0.1816 | 81.5686 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OEC 7 345.00] TO [OECGT2-1 18.000] CKT 1 | 6.2019 | 0.1816 | 81.5688 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OEC 7 345.00] TO [OECGT2-2 18.000] CKT 1 | 6.2022 | 0.1816 | 81.5666 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CDC-ET 4 138.00] TO [CIP 4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5657 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CDC-ET 4 138.00] TO [OWAS88_4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5671 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CDC-WT 4 138.00] TO [A.A.---4 138.00] CKT 1 | 6.2021 | 0.1816 | 81.567 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CDC-WT 4 138.00] TO [WHIRLPO4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5663 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OWASOTP4 138.00] TO [OWASO1_4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5666 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OWASOTP4 138.00] TO [OWAS1094 138.00] CKT 1 | 6.2021 | 0.1816 | 81.5665 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OAKSWTP4 138.00] TO [T.P.S.-4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5666 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OAKSETP4 138.00] TO [T.P.S.-4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5679 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [P&P WTP4 138.00] TO [WEKIWA-4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5653 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [P&P WTP4 138.00] TO [PP----W4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5663 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [T.NO.--7 345.00] TO [T.NO.2-4 138.00] TO [TNO2-1 34.500] CKT 1 | 6.2017 | 0.1816 | 81.5676 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [S HILLW4 138.00] TO [52DEL-W4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5666 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SAPLPRD7 345.00] TO [SAPLPRD4 138.00] TO [SAPLPRD1 13.800] CKT 1 | 6.2022 | 0.1816 | 81.568 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SAPLPRD4 138.00] TO [JENKS--4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5681 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SAPLPRD4 138.00] TO [DENV_WTAP4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5658 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SKIATOK4 138.00] TO [BARNSAL4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5669 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [72ELWOD4 138.00] TO [T.P.S.-4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5666 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [46ST-TP-4 138.00] TO [46ST--E4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5663 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [46ST-TP-4 138.00] TO [PPTAP 4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [N.E.S.-4 138.00] TO [OWASO2_4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5676 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [N.E.S.-4 138.00] TO [OWAS1094 138.00] CKT 1 | 6.2021 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [N.E.S.-4 138.00] TO [CLARTOK4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5677 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [N.E.S.-4 138.00] TO [WATOVA 4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [N.E.S.-4 138.00] TO [RICE CK4 138.00] CKT 1 | 6.2021 | 0.1816 | 81.5678 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [N.E.S.-4 138.00] TO [HAWTHRN4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.566 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [N.E.S.-4 138.00] TO [NES1-1 14.400] CKT 1 | 6.2021 | 0.1816 | 81.5677 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [N.E.S.-4 138.00] TO [NES1-1A 18.000] CKT 1 | 6.2021 | 0.1816 | 81.5679 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [N.E.S.-4 138.00] TO [NES1-1B 18.000] CKT 1 | 6.2021 | 0.1816 | 81.5679 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [N.E.S.-4 138.00] TO [NES2-1 22.000] CKT 1 | 6.2016 | 0.1816 | 81.5711 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [N.E.S.-4 138.00] TO [OOLOGAHKM 4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5705 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [N.E.S.-7 345.00] TO [DELWARE7 345.00] CKT 1 | 6.2027 | 0.1815 | 81.5486 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [N.E.S.-7 345.00] TO [NES3-1 22.000] CKT 1 | 6.201 | 0.1816 | 81.5753 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [PITTSB-7 345.00] TO [JOHNCO 7 345.00] CKT 1 | 6.2021 | 0.1816 | 81.5746 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VALIANT7 345.00] TO [NWTXARK7 345.00] CKT 1 | 6.2019 | 0.1816 | 81.565 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VALIANT7 345.00] TO [LYDIA 7 345.00] CKT 1 | 6.2017 | 0.1816 | 81.5609 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VALIANT7 345.00] TO [VALIANT4 138.00] TO [VALN2-1 13.800] CKT 2 | 6.2022 | 0.1816 | 81.567 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VALIANT7 345.00] TO [VALIANT4 138.00] TO [VALN3-1 13.800] CKT 1 | 6.2022 | 0.1816 | 81.567 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [KIOWA 7 345.00] TO [KIOWA G1 18.000] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [KIOWA 7 345.00] TO [KIOWA G2 18.000] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [KIOWA 7 345.00] TO [KIOWA S1 18.000] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [KIOWA 7 345.00] TO [KIOWA S2 18.000] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [KIOWA 7 345.00] TO [KIOWA G3 18.000] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [KIOWA 7 345.00] TO [KIOWA G4 18.000] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [C-RIVER4 138.00] TO [TALAWANDA 4138.00] CKT 1 | 6.2019 | 0.1816 | 81.5788 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [O.K.U.-7 345.00] TO [OKLAUN HVDC7345.00] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [O.K.U.-7 345.00] TO [GEN-2017-033345.00] CKT 1 | 6.2023 | 0.1816 | 81.5675 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [O.K.U.-7 345.00] TO [G18-015-TAP 345.00] CKT 1 | 6.2017 | 0.1815 | 81.5389 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [L.E.S.-4 138.00] TO [FLE TAP4 138.00] CKT 1 | 6.202 | 0.1816 | 81.5655 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [L.E.S.-4 138.00] TO [COMANC-4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5673 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [L.E.S.-4 138.00] TO [LWSTAP 4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5663 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [L.E.S.-4 138.00] TO [SHERID4 138.00] CKT 1 | 6.2021 | 0.1816 | 81.5661 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [L.E.S.-4 138.00] TO [ELGINJT4 138.00] CKT 1 | 6.202 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [L.E.S.-4 138.00] TO [COMMTAP4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5669 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [L.E.S.-4 138.00] TO [L.E.S.-2 69.000] TO [LES#1-1 13.800] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [L.E.S.-4 138.00] TO [L.E.S.-2 69.000] TO [LES#2-1 13.800] CKT 2 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [L.E.S.-7 345.00] TO [G17-171-TAP 345.00] CKT 1 | 6.2006 | 0.1816 | 81.5728 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CAN_GAS4 138.00] TO [REDROCKRD4 138.00] CKT 1 | 6.1961 | 0.1815 | 81.5114 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CAN_GAS4 138.00] TO [TLBEART4 138.00] CKT 1 | 6.2035 | 0.1815 | 81.5127 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHISHOLM7 345.00] TO [G16-037-TAP 345.00] CKT 1 | 6.2039 | 0.1815 | 81.5114 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHISHOLM6 230.00] TO [ELKCITY6 230.00] CKT 1 | 6.2011 | 0.1816 | 81.5649 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHISHOLM6 230.00] TO [SWEETWT6 230.00] CKT 1 | 6.1997 | 0.1816 | 81.5801 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RUSHSPR1-1 13.800] TO [RUSHSPR7 345.00] TO [RUSHSPRW1-1 34.500] CKT 1 | 6.2023 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [TPS2-1 14.400] TO [T.P.S.-4 138.00] CKT 1 | 6.202 | 0.1816 | 81.5643 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [TPS4-1 14.400] TO [T.P.S.-4 138.00] CKT 1 | 6.202 | 0.1816 | 81.5645 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RUSHSPRW1-1 34.500] TO [RUSHSPRWD0 0.7000] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RUSHSPRW1-1 34.500] TO [RSHSPR1_GSU134.500] CKT 1 | 6.2023 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RSHSPR1_COL134.500] TO [RSHSPR1_GSU134.500] CKT 1 | 6.2023 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RSHSPR1_MPT1345.00] TO [TERRYRD7 345.00] CKT 1 | 6.2023 | 0.1816 | 81.5678 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CLEVLND7 345.00] TO [G15-066T 345.00] CKT 1 | 6.1951 | 0.1816 | 81.6244 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CLEVLND7 345.00] TO [CLEVLND 4 138.00] TO [CLEVLND1 13.800] CKT 1 | 6.201 | 0.1816 | 81.6105 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [IGLOOV 7 345.00] TO [GREC TAP5 345.00] CKT 1 | 6.2003 | 0.1816 | 81.5642 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [IGLOOV 7 345.00] TO [IGLOOV1 5 161.00] TO [IGLOTER1 1 13.200] CKT 1 | 6.2023 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [IGLOOV 7 345.00] TO [IGLOOV2 5 161.00] TO [IGLOTER2 1 13.200] CKT 2 | 6.2023 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OTTER 4 138.00] TO [WRVALLY4 138.00] CKT 1 | 6.1236 | 0.1817 | 81.6613 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OTTER 4 138.00] TO [ARMFTWD4 138.00] CKT 1 | 6.2039 | 0.1816 | 81.6153 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [FRMNTAP4 138.00] TO [FAIRMON4 138.00] CKT 1 | 6.202 | 0.1816 | 81.6165 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [FRMNTAP4 138.00] TO [SO4TH 4 138.00] CKT 1 | 6.1879 | 0.1816 | 81.6101 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WAUKOTP4 138.00] TO [SO4TH 4 138.00] CKT 1 | 6.0868 | 0.1817 | 81.7123 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WOODRNG4 138.00] TO [WOODRNG7 345.00] TO [WOODRNG1 13.800] CKT 1 | 5.7433 | 0.1824 | 82.4292 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MARSHL 4 138.00] TO [MARSHAL4 138.00] CKT Z1 | 6.2022 | 0.1816 | 81.5638 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DOVERTP2 69.000] TO [TURCRKT2 69.000] CKT 1 | 5.9294 | 0.182 | 81.988 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DOVERTP2 69.000] TO [REDWING2 69.000] CKT 1 | 6.2071 | 0.182 | 82.0431 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HENESEY4 138.00] TO [DOVERSW4 138.00] CKT 1 | 6.0007 | 0.1819 | 81.9346 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SOONER 7 345.00] TO [SOONER2G 20.000] CKT 1 | 6.1907 | 0.1816 | 81.5567 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SOONER 7 345.00] TO [RANCHRD7 345.00] CKT 1 | 6.196 | 0.1816 | 81.5708 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SOONER 7 345.00] TO [THUNDER7 345.00] CKT 1 | 6.2025 | 0.1816 | 81.5651 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SOONER 7 345.00] TO [G15-066T 345.00] CKT 1 | 6.1958 | 0.1816 | 81.6062 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SOONER 7 345.00] TO [G16-119-TAP 345.00] CKT 1 | 6.2002 | 0.1816 | 81.5765 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SOONER 7 345.00] TO [SOONER 4 138.00] TO [SOONER 1 13.800] CKT 1 | 6.1995 | 0.1816 | 81.5851 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [JOHNCO 4 138.00] TO [JOHNCO 7 345.00] TO [JOHNCO11 13.800] CKT 1 | 6.202 | 0.1816 | 81.5752 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [YUKON 2 69.000] TO [SVCELRN2 69.000] CKT 1 | 6.1773 | 0.1816 | 81.6135 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [JENSENT4 138.00] TO [EL-RENO4 138.00] CKT 1 | 6.1988 | 0.1816 | 81.5906 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [JENSEN 4 138.00] TO [EL RENO4 138.00] CKT 1 | 6.0809 | 0.1819 | 81.9198 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CTNWOOD4 138.00] TO [PINE ST4 138.00] CKT 1 | 6.1658 | 0.1814 | 81.3738 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CTNWOOD4 138.00] TO [LBRTYLK4 138.00] CKT 1 | 6.1194 | 0.1817 | 81.7099 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CTNWOOD4 138.00] TO [CRESENT4 138.00] CKT 1 | 5.4539 | 0.1829 | 82.9167 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LAKESID4 138.00] TO [HEFNER 4 138.00] CKT 1 | 6.202 | 0.1816 | 81.5801 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SLVRLAK4 138.00] TO [QUAILCK4 138.00] CKT 1 | 6.2019 | 0.1816 | 81.577 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SLVRLAK4 138.00] TO [BRADEN 4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5703 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DVISION4 138.00] TO [MUSTANG4 138.00] CKT 1 | 6.202 | 0.1815 | 81.5339 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MSTANG 2 69.000] TO [MUSTANG4 138.00] TO [MUSTANG1 13.200] CKT 1 | 6.2022 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RICHRDS4 138.00] TO [PIEDMNT4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5676 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [COUNCIL4 138.00] TO [MUSTANG4 138.00] CKT 1 | 6.2011 | 0.1816 | 81.6078 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WESTOAK4 138.00] TO [MERIDAN4 138.00] CKT 1 | 6.2017 | 0.1816 | 81.5931 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORTWST4 138.00] TO [KETCHTP4 138.00] CKT 1 | 6.1944 | 0.1817 | 81.6624 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORTWST4 138.00] TO [BRADEN 4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5711 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORTWST4 138.00] TO [PIEDMNT4 138.00] CKT 1 | 6.2021 | 0.1816 | 81.5681 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORTWST4 138.00] TO [LNEOAK 4 138.00] CKT 1 | 6.2018 | 0.1816 | 81.5886 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORTWST7 345.00] TO [ARCADIA7 345.00] CKT 1 | 6.1991 | 0.1816 | 81.5635 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SPRNGCK7 345.00] TO [SPGCK1&2 13.800] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SPRNGCK7 345.00] TO [SPGCK3&4 13.800] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SPRNGCK7 345.00] TO [G16-119-TAP 345.00] CKT 1 | 6.2001 | 0.1816 | 81.5982 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DUNJEE 4 138.00] TO [HSL 4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5709 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [36&MER 4 138.00] TO [WRAIRPT4 138.00] CKT 1 | 6.2021 | 0.1816 | 81.5669 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SMITHCO4 138.00] TO [SMITH 1G 13.800] TO [SMITH 1S 13.800] CKT 1 | 6.1993 | 0.1816 | 81.5651 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DAYTON 4 138.00] TO [MUSTANG4 138.00] CKT 1 | 6.2016 | 0.1816 | 81.5747 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [XEROX 4 138.00] TO [CZECHAL4 138.00] CKT 1 | 6.2005 | 0.1815 | 81.5196 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MORGAN 4 138.00] TO [MUSTANG4 138.00] CKT 1 | 6.2002 | 0.1815 | 81.5321 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CIMARON4 138.00] TO [TUTCONT4 138.00] CKT 1 | 6.2019 | 0.1815 | 81.535 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CIMARON4 138.00] TO [EL-RENO4 138.00] CKT 1 | 6.1764 | 0.1818 | 81.7751 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CIMARON4 138.00] TO [CZECHAL4 138.00] CKT 1 | 6.2006 | 0.1815 | 81.5114 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CIMARON4 138.00] TO [SARA 4 138.00] CKT 1 | 6.1992 | 0.1815 | 81.5174 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CIMARON7 345.00] TO [MINCO 7 345.00] CKT 1 | 6.1993 | 0.1816 | 81.5956 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [JNSKAMO4 138.00] TO [HSL 4 138.00] CKT 1 | 6.2014 | 0.1816 | 81.5693 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ARCADIA4 138.00] TO [ARCADIA7 345.00] TO [ARCADI21 13.800] CKT 1 | 6.1964 | 0.1816 | 81.5946 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ARCADIA4 138.00] TO [ARCADIA7 345.00] TO [ARCADI31 13.800] CKT 1 | 6.1969 | 0.1816 | 81.5894 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ARCADIA4 138.00] TO [ARCADIA7 345.00] TO [ARCADI41 13.800] CKT 1 | 6.194 | 0.1817 | 81.6659 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDBUD 7 345.00] TO [ARCADIA7 345.00] CKT 1 | 6.202 | 0.1815 | 81.5475 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDBUD 7 345.00] TO [ARCADIA7 345.00] CKT 2 | 6.202 | 0.1815 | 81.5453 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDBUD 7 345.00] TO [ARCADIA7 345.00] CKT 3 | 6.202 | 0.1815 | 81.5444 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WODLAWN2 69.000] TO [BETHANY2 69.000] CKT 1 | 6.202 | 0.1816 | 81.5773 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MCARTHR2 69.000] TO [SW 64TH2 69.000] CKT 1 | 6.2022 | 0.1816 | 81.5735 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SW 5TH 2 69.000] TO [MAY AVE2 69.000] CKT 1 | 6.2022 | 0.1816 | 81.5687 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SW 5TH 2 69.000] TO [SW22ND 2 69.000] CKT 1 | 6.2021 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SW 5TH 4 138.00] TO [MUSTANG4 138.00] CKT 1 | 6.2021 | 0.1816 | 81.5773 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CLASSEN4 138.00] TO [DOUGLTP4 138.00] CKT 1 | 6.202 | 0.1816 | 81.5626 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CLASSEN4 138.00] TO [CROSTWN4 138.00] CKT 1 | 6.2019 | 0.1816 | 81.577 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HSLEAST2 69.000] TO [GRNPAST2 69.000] CKT 1 | 6.2023 | 0.1816 | 81.5674 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HSLEAST2 69.000] TO [TXSTELA2 69.000] CKT 1 | 6.2022 | 0.1816 | 81.5626 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HSLEAST2 69.000] TO [MCLOUDT2 69.000] CKT 1 | 6.2022 | 0.1816 | 81.5662 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DRAPER 7 345.00] TO [DRAPER 4 138.00] TO [DRAPER21 13.800] CKT 2 | 6.2018 | 0.1816 | 81.583 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DRAPER 7 345.00] TO [DRAPER 4 138.00] TO [DRAPER31 13.800] CKT 3 | 6.2019 | 0.1816 | 81.5631 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DRAPER 7 345.00] TO [DRAPER 4 138.00] TO [DRAPER41 13.800] CKT 4 | 6.2019 | 0.1816 | 81.5631 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HSL 7S 20.900] TO [HSL 4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.566 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HSLWEST2 69.000] TO [HSL 4 138.00] TO [HSL 1 13.800] CKT 1 | 6.202 | 0.1816 | 81.5654 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HSL 8G 22.800] TO [HSL 4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5659 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HSL 9G 13.800] TO [HSL 4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HSL 10G 13.800] TO [HSL 4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MIDWAY 4 138.00] TO [HSL 4 138.00] CKT 1 | 6.2021 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RENO 4 138.00] TO [TROSPER4 138.00] CKT 1 | 6.2024 | 0.1816 | 81.5587 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RENO 4 138.00] TO [WASHPRK4 138.00] CKT 1 | 6.202 | 0.1816 | 81.5716 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RENO 4 138.00] TO [RENO 2 69.000] TO [RENO 1 13.800] CKT 1 | 6.2021 | 0.1816 | 81.5662 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GLENDAL4 138.00] TO [TINKER74 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5666 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DALE 4 138.00] TO [HSL 4 138.00] CKT 1 | 6.2011 | 0.1816 | 81.5597 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SE15TH 4 138.00] TO [HSL 4 138.00] CKT 1 | 6.2021 | 0.1816 | 81.5617 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [BARNES 4 138.00] TO [DRAPER 4 138.00] CKT 1 | 6.2016 | 0.1816 | 81.588 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [BARNES 4 138.00] TO [TINKER54 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5683 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRTPLNS4 138.00] TO [GRNWOOD4 138.00] CKT 1 | 6.202 | 0.1816 | 81.5682 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SEMINOL4 138.00] TO [SEMINL1G 20.900] CKT 1 | 6.1959 | 0.1816 | 81.57 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SEMINOL4 138.00] TO [MAUD 4 138.00] CKT 1 | 6.2017 | 0.1816 | 81.577 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SEMINOL4 138.00] TO [MAUD 4 138.00] CKT 2 | 6.2021 | 0.1816 | 81.5691 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SEMINOL4 138.00] TO [PAOLI- 4 138.00] CKT 1 | 6.2015 | 0.1816 | 81.5739 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SEMINOL4 138.00] TO [VANOSTP4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5673 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SEMINOL4 138.00] TO [LKKONWA4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5721 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SEMINOL7 345.00] TO [ARCADIA7 345.00] CKT 1 | 6.1998 | 0.1816 | 81.5921 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SEMINOL7 345.00] TO [FIREWHL-TAP 345.00] CKT 1 | 6.1999 | 0.1816 | 81.575 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HAMMTAP4 138.00] TO [HSL 4 138.00] CKT 1 | 6.2017 | 0.1816 | 81.565 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WARWICK4 138.00] TO [TRYON 4 138.00] CKT 1 | 6.2018 | 0.1816 | 81.5686 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SQUIRCK4 138.00] TO [INGLEWD4 138.00] CKT 1 | 6.202 | 0.1816 | 81.5761 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SQUIRCK4 138.00] TO [STRLGTP4 138.00] CKT 1 | 6.2005 | 0.1816 | 81.5731 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RUSSET-4 138.00] TO [GLASSES4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5672 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RUSSET-4 138.00] TO [STIRLNG4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.567 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SXMLCKT4 138.00] TO [MILLCKT4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5658 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SXMLCKT4 138.00] TO [HOWE 4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5666 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SUNNYSD4 138.00] TO [SUNNYSD7 345.00] TO [SUNYSD 1 13.800] CKT 1 | 6.2023 | 0.1816 | 81.568 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SUNNYSD4 138.00] TO [SUNNYSD7 345.00] TO [SUNNYSD1 13.800] CKT 1 | 6.2023 | 0.1816 | 81.5651 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [UNIROY 4 138.00] TO [ARDWEST4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5679 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LONEGRV4 138.00] TO [CHEEKTP4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5672 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CANEYCK4 138.00] TO [MADINDT4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5666 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CANEYCK4 138.00] TO [LTLCITY4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5677 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CANEYCK4 138.00] TO [TEXOMAJ4 138.00] CKT 1 | 6.2021 | 0.1816 | 81.5673 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [BROWNTP4 138.00] TO [LTLCITY4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5676 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [BROWNTP4 138.00] TO [BODLE 4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.567 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [COLEMNT4 138.00] TO [EXPLRPL4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5663 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [COLBRTP4 138.00] TO [BODLE 4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [COLBRTP4 138.00] TO [BUTRFLD4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ROCKYPT4 138.00] TO [MRIETA 2 138.00] CKT 1 | 6.2021 | 0.1816 | 81.5704 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ROCKYPT4 138.00] TO [SPRNDAL4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5669 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ROCKYPT4 138.00] TO [ROCKYPT2 69.000] TO [ROCKYPT1 13.200] CKT 1 | 6.2023 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MUSKOGE7 345.00] TO [CLARKSV7 345.00] CKT 1 | 6.2023 | 0.1816 | 81.565 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MUSKOGE7 345.00] TO [PECANCK7 345.00] CKT 1 | 6.2022 | 0.1816 | 81.5676 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MUSKOGE7 345.00] TO [PECANCK7 345.00] CKT 2 | 6.2022 | 0.1816 | 81.5682 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MUSKOGE7 345.00] TO [FIREWHL-TAP 345.00] CKT 1 | 6.2018 | 0.1816 | 81.5663 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MUSKOGE7 345.00] TO [FIREWHL-TAP 345.00] CKT 2 | 6.2017 | 0.1816 | 81.5661 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [5TRIBES5 161.00] TO [HANCOK-5 161.00] CKT 1 | 6.2022 | 0.1816 | 81.5671 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [5TRIBES5 161.00] TO [5TRIBES2 69.000] TO [5TRIBES1 13.200] CKT 1 | 6.2023 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [AGENCY 5 161.00] TO [EUCLID 5 161.00] CKT 1 | 6.2022 | 0.1816 | 81.567 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [AGENCY 5 161.00] TO [AGENCY 2 69.000] TO [AGENCY 1 13.800] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [PECANCK4 138.00] TO [BEGGS 4 138.00] CKT 1 | 6.2016 | 0.1816 | 81.5709 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [PECANCK5 161.00] TO [PECANCK7 345.00] TO [PECANC11 13.800] CKT 1 | 6.2022 | 0.1816 | 81.5689 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [PECANCK5 161.00] TO [PECANCK7 345.00] TO [PECANC21 13.800] CKT 2 | 6.2022 | 0.1816 | 81.5705 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [FTSMITH7 345.00] TO [FTSMITH8 500.00] TO [FTSMTH11 13.800] CKT 1 | 6.2022 | 0.1816 | 81.5652 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [FTSMITH7 345.00] TO [FTSMTHW5 161.00] TO [FTSMTH51 13.800] CKT 5 | 6.2023 | 0.1816 | 81.5673 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [BRANCH 2 69.000] TO [BRANCH 5 161.00] TO [BRANCH21 13.200] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [PENDER 2 69.000] TO [HELBERG2 69.000] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HOBBYLO4 138.00] TO [CHEMTRN4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5664 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VBI 5 161.00] TO [VAN BUR5 161.00] CKT Z1 | 6.2024 | 0.1816 | 81.5633 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VBI 5 161.00] TO [OAKGROV5 161.00] CKT 1 | 6.2023 | 0.1816 | 81.5664 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VBI 5 161.00] TO [TWNBRDG5 161.00] CKT 1 | 6.2023 | 0.1816 | 81.5664 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VBI 5 161.00] TO [ADABELL5 161.00] CKT 1 | 6.2023 | 0.1816 | 81.5663 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VBI 5 161.00] TO [HWY59TP5 161.00] CKT 1 | 6.2023 | 0.1816 | 81.5666 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VBI 5 161.00] TO [VBI 2 69.000] TO [VBI 1 13.800] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SHORTMT5 161.00] TO [BRANCH 5 161.00] CKT 1 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WFROSST4 138.00] TO [RSSVILE4 138.00] CKT Z1 | 6.2024 | 0.1816 | 81.5648 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [BELLCOW4 138.00] TO [KEYWEST4 138.00] CKT 1 | 6.2017 | 0.1816 | 81.5689 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [C-RIVER7 345.00] TO [FIREWHL-TAP 345.00] CKT 1 | 6.2016 | 0.1816 | 81.577 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SUBIACT5 161.00] TO [RAZRBAK5 161.00] CKT 1 | 6.2023 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SUBIACT5 161.00] TO [SUBIACO5 161.00] CKT 1 | 6.2023 | 0.1816 | 81.5666 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LINCOLN4 138.00] TO [JACKTWN4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5645 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LINCOLN4 138.00] TO [MEEKER 4 138.00] CKT 1 | 6.202 | 0.1816 | 81.5663 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MNCOWND1 34.500] TO [MNCOWNC1 34.500] CKT 1 | 6.2024 | 0.1816 | 81.5662 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MCNOWND7 345.00] TO [MINCO 7 345.00] CKT 1 | 6.2024 | 0.1816 | 81.5661 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LNWOODT4 138.00] TO [TRYON 4 138.00] CKT 1 | 6.202 | 0.1816 | 81.5683 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [ACORN 4 138.00] TO [BRYANT 4 138.00] CKT 1 | 6.2019 | 0.1816 | 81.5622 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RNDBARN4 138.00] TO [BURGETT4 138.00] CKT 1 | 6.201 | 0.1816 | 81.5993 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HUNTERS7 345.00] TO [WOODRNG7 345.00] CKT 1 | 6.187 | 0.1815 | 81.5251 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HUNTERS7 345.00] TO [RENFROW7 345.00] CKT 1 | 6.1874 | 0.1815 | 81.4714 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHSHLMV7 345.00] TO [CHSHMVE1 34.500] TO [CHSHMVET 13.200] CKT 1 | 6.2025 | 0.1816 | 81.5677 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CHSHLMV7 345.00] TO [CHSHMVW1 34.500] TO [CHSHMVWT 13.200] CKT 1 | 6.2025 | 0.1816 | 81.5677 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [JONESSB4 138.00] TO [HSL 4 138.00] CKT 1 | 6.2015 | 0.1815 | 81.5479 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MATHWSN7 345.00] TO [TATONGA7 345.00] CKT 1 | 6.2008 | 0.1816 | 81.6241 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MATHWSN7 345.00] TO [TATONGA7 345.00] CKT 2 | 6.2008 | 0.1816 | 81.6242 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MATHWSN7 345.00] TO [TRAVERSE3 345.00] CKT 1 | 6.2025 | 0.1816 | 81.5916 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [KNIPE 4 138.00] TO [TRYON 4 138.00] CKT 1 | 6.2008 | 0.1816 | 81.5796 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRNDPRT5 161.00] TO [BRANCH 5 161.00] CKT 1 | 6.2023 | 0.1816 | 81.5663 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RENFROW4 138.00] TO [RENFROW7 345.00] TO [RENFRO11 13.800] CKT 1 | 6.2006 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRANTCO4 138.00] TO [GRANTCO2 69.000] TO [GRANTC11 13.200] CKT 1 | 6.1984 | 0.1815 | 81.5497 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MNCWND37 345.00] TO [MINCO 7 345.00] CKT 1 | 6.2023 | 0.1816 | 81.5795 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MNCWND31 34.500] TO [MINCO-CB3 34.500] CKT 1 | 6.2023 | 0.1816 | 81.5656 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CARTRCO4 138.00] TO [RATLIFF4 138.00] CKT 1 | 6.2021 | 0.1816 | 81.5714 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CARTRCO4 138.00] TO [POOLVIL4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5664 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CARTRCO4 138.00] TO [ORIGINW4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5693 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CARTRCO4 138.00] TO [GEN-2017-027138.00] CKT 1 | 6.2022 | 0.1816 | 81.5713 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MDFRDTP4 138.00] TO [RDRUNNR4 138.00] CKT 1 | 6.2018 | 0.1816 | 81.5675 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MDFRDTP4 138.00] TO [MEDFORD4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5672 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SPGVLLY4 138.00] TO [STILWTR4 138.00] CKT 1 | 6.1959 | 0.1816 | 81.61 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SPGVLLY4 138.00] TO [PAYNESB4 138.00] CKT 1 | 6.2004 | 0.1816 | 81.5787 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [FSHRTAP7 345.00] TO [KNGFSHR7 345.00] CKT 1 | 6.1947 | 0.1816 | 81.578 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [FSHRTAP7 345.00] TO [CANADN7 345.00] CKT 1 | 6.2022 | 0.1816 | 81.5765 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRNTWD 7 345.00] TO [RENFROW7 345.00] CKT 1 | 6.2017 | 0.1816 | 81.5883 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRNTWD11 34.500] TO [GRNTWDC1 34.500] CKT 1 | 6.202 | 0.1816 | 81.575 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRNTWD12 34.500] TO [GRNTWDC2 34.500] CKT 1 | 6.202 | 0.1816 | 81.5748 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MSTNG 8G 13.800] TO [MUSTANG4 138.00] TO [MSTNG 9G 13.800] CKT 1 | 6.198 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MSTNG10G 13.800] TO [MUSTANG4 138.00] TO [MSTNG11G 13.800] CKT 1 | 6.1977 | 0.1816 | 81.5669 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MSTNG12G 13.800] TO [MUSTANG4 138.00] CKT 1 | 6.2001 | 0.1816 | 81.5664 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRACMNT7 345.00] TO [MINCO 7 345.00] CKT 1 | 6.2 | 0.1816 | 81.5721 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRACMNT7 345.00] TO [G16-037-TAP 345.00] CKT 1 | 6.2007 | 0.1816 | 81.6219 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRACMNT4 138.00] TO [ANADARK4 138.00] CKT 1 | 6.2021 | 0.1816 | 81.5688 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRACMNT4 138.00] TO [ANADARK4 138.00] CKT 2 | 6.2021 | 0.1816 | 81.5688 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRACMNT4 138.00] TO [WASHITA4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5672 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRACMNT4 138.00] TO [WASHITA4 138.00] CKT 2 | 6.2022 | 0.1816 | 81.5671 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDNGTN7 345.00] TO [WOODRNG7 345.00] CKT 1 | 6.1773 | 0.1816 | 81.566 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDDIRT7 345.00] TO [RDDIRT11 34.500] TO [RDDRTT11 12.500] CKT 1 | 6.2025 | 0.1816 | 81.5649 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDDIRT7 345.00] TO [RDDIRT21 34.500] TO [RDDRTT21 12.500] CKT 1 | 6.2025 | 0.1816 | 81.562 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MNCWND47 345.00] TO [MNCWND57 345.00] CKT 1 | 6.2023 | 0.1816 | 81.5727 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MNCWND47 345.00] TO [MNCO4L11 34.500] TO [MNCO4T11 13.800] CKT 1 | 6.2023 | 0.1816 | 81.5653 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [STRRDTP4 138.00] TO [BROWN 4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SKELTON7 345.00] TO [WOODRNG7 345.00] CKT 1 | 6.2015 | 0.1816 | 81.6182 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SKELTL11 34.500] TO [SKELTC11 34.500] CKT 1 | 6.2017 | 0.1816 | 81.5987 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DMNDSL11 34.500] TO [DMNDSC11 34.500] CKT 1 | 6.2022 | 0.1816 | 81.568 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DMNDSL21 34.500] TO [DMNDSC21 34.500] CKT 1 | 6.2022 | 0.1816 | 81.5681 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DMNDSPG7 345.00] TO [JOHNCO 7 345.00] CKT 1 | 6.2022 | 0.1816 | 81.5701 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [PINTAIL7 345.00] TO [WOODRNG7 345.00] CKT 1 | 6.1496 | 0.1816 | 81.6256 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [KINGWD 7 345.00] TO [KNGWDL11 34.500] TO [KNGWDT11 13.200] CKT 1 | 6.2022 | 0.1816 | 81.5691 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [KINGWD 7 345.00] TO [KNGWDL21 34.500] TO [KNGWDT21 13.200] CKT 1 | 6.2022 | 0.1816 | 81.5692 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [BECKHAM7 345.00] TO [WWRDEHV7 345.00] CKT 1 | 6.2011 | 0.1816 | 81.5783 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [BECKHAM7 345.00] TO [BORDER 7345.00] CKT 1 | 6.1992 | 0.1816 | 81.582 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORMHLL7 345.00] TO [MINCO 7 345.00] CKT 1 | 6.2009 | 0.1816 | 81.6113 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORMHLL4 138.00] TO [MCCLAIN4 138.00] CKT 1 | 6.2021 | 0.1816 | 81.5626 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORMHLL4 138.00] TO [CHERYCK4 138.00] CKT 1 | 6.2012 | 0.1816 | 81.6059 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NORMHLL4 138.00] TO [TURNER 4 138.00] CKT 1 | 6.2024 | 0.1816 | 81.5645 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [KGFSJCT4 138.00] TO [EKFSHTP4 138.00] CKT 1 | 5.3143 | 0.1829 | 82.9484 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WFEC_RNFRO4 138.00] TO [WAKTASW4 138.00] CKT 1 | 6.2005 | 0.1816 | 81.5642 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MUSTANG4 138.00] TO [EL RENO4 138.00] CKT 1 | 6.1831 | 0.1815 | 81.5471 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CANA 4 138.00] TO [CALUMET4 138.00] CKT 1 | 5.431 | 0.183 | 83.0058 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [BULFTTP4 138.00] TO [DOVERSW4 138.00] CKT 1 | 6.013 | 0.1819 | 81.8899 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WATNGSW4 138.00] TO [CALUMET4 138.00] CKT 1 | 6.0995 | 0.1818 | 81.8016 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WATNGSW4 138.00] TO [OMEGA 4 138.00] CKT 1 | 6.1583 | 0.1817 | 81.6938 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WATNGSW4 138.00] TO [WATONGA4 138.00] CKT 1 | 6.201 | 0.1815 | 81.4856 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [TWNLAKE4 138.00] TO [TWNLKSW4 138.00] CKT Z1 | 5.1816 | 0.1836 | 83.6092 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDCNTP4 138.00] TO [REDCORN4 138.00] CKT 1 | 6.2026 | 0.1815 | 81.548 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDCNTP4 138.00] TO [COGAR 4 138.00] CKT 1 | 6.1018 | 0.1817 | 81.6719 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [NKNGFSH4 138.00] TO [DOVERSW4 138.00] CKT 1 | 5.3127 | 0.183 | 83.0143 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CDRDLTP4 138.00] TO [PIC4 138.00] CKT 1 | 5.8533 | 0.182 | 82.0175 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [CDRDLTP4 138.00] TO [CEDRDAL4 138.00] CKT 1 | 6.2021 | 0.1816 | 81.5705 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DOVER 4 138.00] TO [DOVERSW4 138.00] CKT 1 | 5.1696 | 0.1836 | 83.5869 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [DOVERSW2 69.000] TO [DOVERSW4 138.00] TO [DVRTERT 13.800] CKT 1 | 5.9335 | 0.1825 | 82.5034 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SCOTTSW4 138.00] TO [EL RENO4 138.00] CKT 1 | 5.9631 | 0.1821 | 82.1082 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [KIERSEY4 138.00] TO [COLBERT4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5668 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SARA RD4 138.00] TO [SUNSHIN4 138.00] CKT 1 | 6.1831 | 0.1816 | 81.5501 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OKEENE 2 69.000] TO [CANTON-2 69.000] CKT 1 | 6.1375 | 0.1817 | 81.6778 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OKEENE 2 69.000] TO [FAIRVEW2 69.000] CKT 1 | 6.1649 | 0.1816 | 81.6258 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [OKEENE 4 138.00] TO [DOVERSW4 138.00] CKT 1 | 5.4981 | 0.183 | 83.0346 | 74.1 | 87.1 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [RUSSETT4 138.00] TO [REAGAN 4 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5665 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SCLMNJC4 138.00] TO [SCOLEMN4 138.00] CKT 1 | 6.2024 | 0.1816 | 81.5659 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SCLMNJC4 138.00] TO [DURANTP4 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5661 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [HUGO 7 345.00] TO [HUGOITC4 138.00] TO [HUGO TERTA 13.800] CKT 1 | 6.2021 | 0.1816 | 81.5655 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WICHITA7 345.00] TO [RENO 7 345.00] CKT 1 | 6.2002 | 0.1816 | 81.5708 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 1 | 6.2018 | 0.1816 | 81.5783 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 2 | 6.2018 | 0.1816 | 81.5783 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WICHITA7 345.00] TO [BENTON 7 345.00] CKT 1 | 6.2004 | 0.1816 | 81.5762 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WICHITA7 345.00] TO [EXPEDITION7 345.00] CKT 1 | 6.1985 | 0.1816 | 81.5872 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WICHITA7 345.00] TO [EVANS N4 138.00] TO [WICH11 1 13.800] CKT 1 | 6.2023 | 0.1816 | 81.5679 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WICHITA7 345.00] TO [EVANS N4 138.00] TO [WICH12 1 13.800] CKT 1 | 6.2023 | 0.1816 | 81.5681 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VIOLA 7 345.00] TO [RENFROW7 345.00] CKT 1 | 6.1763 | 0.1815 | 81.4894 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VIOLA 4 138.00] TO [SUMNER 4 138.00] CKT 1 | 6.2021 | 0.1816 | 81.5655 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VIOLA 4 138.00] TO [CLEARWT4 138.00] CKT 1 | 6.2018 | 0.1816 | 81.5631 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VIOLA 4 138.00] TO [GILL 4 138.00] CKT 1 | 6.2018 | 0.1816 | 81.5628 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VIOLA 4 138.00] TO [MILAN_GOAB 138.00] CKT 1 | 6.2023 | 0.1816 | 81.5669 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [VIOLA 4 138.00] TO [CONWAY 138.00] CKT 1 | 6.2022 | 0.1816 | 81.5674 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [G17-075-TAP 345.00] TO [SUNNYSD7 345.00] CKT 1 | 6.2007 | 0.1816 | 81.5881 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GEN-2015-093345.00] TO [G15-093XFMR134.500] CKT 1 | 6.2025 | 0.1816 | 81.5604 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [G16-030-XFMR34.500] TO [GEN-2016-030138.00] CKT 1 | 6.2021 | 0.1816 | 81.5677 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [G16-030-XFMR34.500] TO [G16-030-GSU134.500] CKT 1 | 6.2021 | 0.1816 | 81.5677 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [G16-037XFMR134.500] TO [GEN-2016-037345.00] CKT 1 | 6.2032 | 0.1815 | 81.537 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [G16-037XFMR134.500] TO [G16-037-GSU134.500] CKT 1 | 6.2032 | 0.1815 | 81.537 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [G16-091-TAP 345.00] TO [GEN-2016-091345.00] CKT 1 | 6.2026 | 0.1816 | 81.5578 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [G16-091-TAP 345.00] TO [GEN-2016-095345.00] CKT 1 | 6.2024 | 0.1816 | 81.564 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GEN-2016-118138.00] TO [DOVERSW4 138.00] CKT 1 | 6.2884 | 0.1814 | 81.4183 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [G16-118XFMR134.500] TO [G16-118-GSU134.500] CKT 1 | 6.2606 | 0.1809 | 80.9037 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [G16-118XFMR234.500] TO [G16-118-GSU234.500] CKT 1 | 6.2624 | 0.1809 | 80.8882 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [G16133G16146345.00] TO [G16133_345GS345.00] CKT 1 | 6.2008 | 0.1816 | 81.5885 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GEN-2016-128345.00] TO [G16-128XFMR134.500] CKT 1 | 6.2026 | 0.1816 | 81.5574 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [G16-153-TAP 345.00] TO [FR2EAST7 345.00] CKT 1 | 6.2026 | 0.1816 | 81.5681 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [G16-153-TAP 345.00] TO [GEN-2016-153345.00] CKT 1 | 6.2022 | 0.1816 | 81.5695 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [G16-153-TAP 345.00] TO [GEN-2017-086345.00] CKT 1 | 6.2022 | 0.1816 | 81.5695 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GEN-2017-075345.00] TO [G17-075XFMR134.500] CKT 1 | 6.2023 | 0.1816 | 81.5679 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GEN-2017-092345.00] TO [G17-092-SWYD345.00] CKT 1 | 6.2021 | 0.1816 | 81.5719 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GEN-2017-092345.00] TO [G17-092XFMR134.500] CKT 1 | 6.2022 | 0.1816 | 81.5687 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GEN-2017-092345.00] TO [G17-092XFMR234.500] CKT 1 | 6.2022 | 0.1816 | 81.5697 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LIEBERM4 138.00] TO [LIEBR3-1 13.800] CKT 2 | 6.2023 | 0.1816 | 81.5666 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [LIEBERM4 138.00] TO [LIEBR4-1 13.800] CKT 2 | 6.2023 | 0.1816 | 81.5667 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILKES 4 138.00] TO [WILKE1-1 20.000] CKT 2 | 6.2022 | 0.1816 | 81.5676 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WILKES 4 138.00] TO [WILKE2-1 22.000] CKT 2 | 6.2021 | 0.1816 | 81.5715 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDBUD 7 345.00] TO [ARCADIA7 345.00] CKT 2 | 6.2011 | 0.1815 | 81.4986 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDBUD 7 345.00] TO [ARCADIA7 345.00] CKT 3 | 6.2008 | 0.1815 | 81.4961 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [REDBUD 7 345.00] TO [ARCADIA7 345.00] CKT 3 | 6.2007 | 0.1815 | 81.489 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [SEMINOL4 138.00] TO [MAUD 4 138.00] CKT 2 | 6.2003 | 0.1816 | 81.5987 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MUSKOGE7 345.00] TO [PECANCK7 345.00] CKT 2 | 6.202 | 0.1816 | 81.5725 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MUSKOGE7 345.00] TO [FIREWHL-TAP 345.00] CKT 2 | 6.1986 | 0.1816 | 81.5697 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [MATHWSN7 345.00] TO [TATONGA7 345.00] CKT 2 | 6.1961 | 0.1818 | 81.7759 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRACMNT4 138.00] TO [ANADARK4 138.00] CKT 2 | 6.2019 | 0.1816 | 81.5773 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [GRACMNT4 138.00] TO [WASHITA4 138.00] CKT 2 | 6.2022 | 0.1816 | 81.568 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-011 | Dover 138 kV Switching Station | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 2 | 6.1917 | 0.1819 | 81.8967 | 74.1 | 87.1 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | Base | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [7FAIRPT 345.00] TO [ST JOE 7 345.00] CKT 1 | 5.4761 | 0.1365 | 36.4821 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [7FAIRPT 345.00] TO [COOPER 3 345.00] CKT 1 | 5.4766 | 0.1365 | 36.475 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5CLINTN 161.00] TO [5HOLDENB2 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4732 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5CLINTN 161.00] TO [2CLINTN 69.000] CKT 1 | 5.4768 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5CLINTN 161.00] TO [2CLINTN 69.000] CKT 3 | 5.4768 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5CLINTN 161.00] TO [5OSCEOKCTP 161.00] CKT 1 | 5.4767 | 0.1365 | 36.4743 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5CLINTN 161.00] TO [TRUMAN 5 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4726 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5CLINTN 161.00] TO [WINDSR 5 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5CLINTN 161.00] TO [CLINTON5 161.00] CKT Z1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5NEWMAD 161.00] TO [N MADRD5 161.00] CKT 1 | 5.4769 | 0.1365 | 36.4715 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5NEWMAD 161.00] TO [SIKETAP5 161.00] CKT 1 | 5.4769 | 0.1365 | 36.4718 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [7BLACKBERRY 345.00] TO [7SPORTSMAN 345.00] CKT 1 | 5.4765 | 0.1365 | 36.4744 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [7BLACKBERRY 345.00] TO [7JASPER 345.00] CKT 1 | 5.4772 | 0.1365 | 36.4595 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [7BLACKBERRY 345.00] TO [WOLFCRK7 345.00] CKT 1 | 5.4759 | 0.1365 | 36.485 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5MINER 1 161.00] TO [SIKESTN5 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4718 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [N MADRD5 161.00] TO [KENNETT5 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4722 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [N MADRD5 161.00] TO [N MADRD2 69.000] TO [NMA X1 1 13.800] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [N MADRD5 161.00] TO [N MADRD2 69.000] TO [NMA X2 1 13.800] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SIKETAP5 161.00] TO [SIKESTN5 161.00] CKT 1 | 5.4769 | 0.1365 | 36.4718 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SIKESTN5 161.00] TO [SIKGEN 1 13.800] CKT 1 | 5.477 | 0.1365 | 36.4697 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SIKESTN5 161.00] TO [IDALIA 5 161.00] CKT 1 | 5.4769 | 0.1365 | 36.4715 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SIKESTN5 161.00] TO [SIKESTN2 69.000] TO [SIK X1 1 13.800] CKT 1 | 5.4768 | 0.1365 | 36.4723 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [DELAWAR1 13.800] TO [DELWARE4 138.00] TO [DELWARE7 345.00] CKT 1 | 5.4768 | 0.1365 | 36.472 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [DELWARE7 345.00] TO [N.E.S.-7 345.00] CKT 1 | 5.4763 | 0.1365 | 36.4765 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WWRDEHV7 345.00] TO [DGRASSE7 345.00] CKT 1 | 5.4755 | 0.1365 | 36.4711 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WWRDEHV7 345.00] TO [DGRASSE7 345.00] CKT 2 | 5.4755 | 0.1365 | 36.4711 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [DGRASSE7 345.00] TO [DGRASSE4 138.00] TO [DGRASSE1 13.800] CKT 1 | 5.4765 | 0.1365 | 36.4666 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WALKMYR1 13.800] TO [WALKMYR2 69.000] TO [WALKMYR3 115.00] CKT 1 | 5.4768 | 0.1365 | 36.4714 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WALKMYR3 115.00] TO [HUGOTON3 115.00] CKT 1 | 5.4768 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WALKMYR3 115.00] TO [HARBNGR3 115.00] CKT 1 | 5.4768 | 0.1365 | 36.4722 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SEWARD-3 115.00] TO [N-CIMRN3 115.00] CKT 1 | 5.4768 | 0.1365 | 36.472 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SPERVIL7 345.00] TO [CLARKCOUNTY7345.00] CKT 1 | 5.4765 | 0.1365 | 36.4793 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NSES 2X1 13.200] TO [NEOSHO 4 138.00] TO [NEOSHOS2 69.000] CKT 1 | 5.4768 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EEC GT1 13.800] TO [EVANS S4 138.00] CKT 1 | 5.4769 | 0.1365 | 36.4715 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EEC GT2 13.800] TO [EVANS S4 138.00] CKT 1 | 5.4769 | 0.1365 | 36.4715 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EEC GT3 18.000] TO [EVANS S4 138.00] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EMPEC 7 345.00] TO [SWISVAL7 345.00] CKT 1 | 5.4708 | 0.1365 | 36.5184 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EMPEC 7 345.00] TO [EXPEDITION7 345.00] CKT 1 | 5.474 | 0.1365 | 36.5389 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [RENO 7 345.00] TO [WICHITA7 345.00] CKT 1 | 5.3186 | 0.1366 | 36.5752 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUMMIT 7 345.00] TO [G17-004-TAP 345.00] CKT 1 | 5.4437 | 0.1368 | 36.8078 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SWISVAL7 345.00] TO [SWISVAL6 230.00] TO [SWISV1X1 14.400] CKT 1 | 5.4755 | 0.1365 | 36.479 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SWISVAL7 345.00] TO [SWISVAL6 230.00] TO [SWISV2X2 14.400] CKT 2 | 5.4755 | 0.1365 | 36.4789 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [87TH 7 345.00] TO [CRAIG 7 345.00] CKT 1 | 5.4759 | 0.1365 | 36.4812 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [G17-009-TAP 345.00] TO [GEN-2017-009345.00] CKT 1 | 5.4768 | 0.1365 | 36.4734 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [G17-009-TAP 345.00] TO [CANEYRV7 345.00] CKT 1 | 5.4753 | 0.1365 | 36.4683 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [KINGMAN7 345.00] TO [NINN1WF7 345.00] CKT 1 | 5.4759 | 0.1365 | 36.4937 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [KINGMAN7 345.00] TO [K1 LV 1 34.500] TO [K1 WFTX1 13.800] CKT 1 | 5.4767 | 0.1365 | 36.474 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [KINGMAN7 345.00] TO [K2 LV 1 34.500] TO [K2 WFTX1 13.800] CKT 1 | 5.4766 | 0.1365 | 36.4758 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BENTON 7 345.00] TO [WICHITA7 345.00] CKT 1 | 5.4599 | 0.1365 | 36.4832 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BENTON 7 345.00] TO [WOLFCRK7 345.00] CKT 1 | 5.4723 | 0.1365 | 36.5092 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WICHITA7 345.00] TO [VIOLA 7 345.00] CKT 1 | 5.4687 | 0.1365 | 36.5113 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WICHITA7 345.00] TO [EXPEDITION7 345.00] CKT 1 | 5.4704 | 0.1366 | 36.6012 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WOLFCRK7 345.00] TO [WAVERLY7 345.00] CKT 1 | 5.4771 | 0.1365 | 36.4655 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [VIOLA 7 345.00] TO [VIOLA 4 138.00] TO [VIOLA1X1 13.800] CKT 1 | 5.4768 | 0.1365 | 36.4734 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [VIOLA 7 345.00] TO [VIOLA 4 138.00] TO [SCJ1X1 13.800] CKT 2 | 5.4767 | 0.1365 | 36.4731 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WAVERLY7 345.00] TO [LACYGNE7 345.00] CKT 1 | 5.4773 | 0.1365 | 36.4625 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NMANHT6 230.00] TO [ELMCREK6 230.00] CKT 1 | 5.4689 | 0.1365 | 36.5334 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LITCH 5 161.00] TO [FRANKLIN5 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4729 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LITCH 5 161.00] TO [LITCH S2 69.000] TO [LITCH1 1 13.200] CKT 1 | 5.4769 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LITCH 5 161.00] TO [LITCH N2 69.000] TO [LITCH2 1 13.200] CKT 1 | 5.4769 | 0.1365 | 36.4715 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [MARMTNW5 161.00] TO [NEOSHO 5 161.00] CKT 1 | 5.4769 | 0.1365 | 36.4708 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEOSHO 5 161.00] TO [RIV4525 161.00] CKT 1 | 5.4768 | 0.1365 | 36.47 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEOSHO 5 161.00] TO [NEOSHO 4 138.00] TO [NEOSH4 1 13.200] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEOSHO 5 161.00] TO [NEOSHOS4 138.00] TO [NEOSH5 1 13.200] CKT 1 | 5.4769 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRESWLN4 138.00] TO [OXFORD 4 138.00] CKT 1 | 5.4763 | 0.1365 | 36.4725 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [TCROCK 4 138.00] TO [TIMBJCT4 138.00] CKT 1 | 5.477 | 0.1365 | 36.4691 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [TIMBJCT4 138.00] TO [TIMBJCT2 69.000] TO [TIMBJCT1 13.200] CKT 1 | 5.4766 | 0.1365 | 36.4723 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [TIOGA 4 138.00] TO [ALTOONA4 138.00] CKT 1 | 5.4768 | 0.1365 | 36.4713 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [OTTRCRK4 138.00] TO [ALTOONA4 138.00] CKT 1 | 5.4756 | 0.1365 | 36.4749 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ALTOONA4 138.00] TO [TAYLOR 4 138.00] CKT 1 | 5.4768 | 0.1365 | 36.472 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ALTOONA4 138.00] TO [ALTOO W2 69.000] TO [ALTOO1 1 13.200] CKT 1 | 5.4768 | 0.1365 | 36.4719 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ALTOONA4 138.00] TO [ALTOO E2 69.000] TO [ALTOO3 1 13.200] CKT 1 | 5.4769 | 0.1365 | 36.4715 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEPARSN4 138.00] TO [NEOSHON4 138.00] CKT 1 | 5.4768 | 0.1365 | 36.4712 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BENTLEY4 138.00] TO [SG12COL4 138.00] CKT 1 | 5.4708 | 0.1365 | 36.5191 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEOSHOS4 138.00] TO [NEOSHO 4 138.00] CKT Z1 | 5.4768 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEOSHO 4 138.00] TO [NEOSHON4 138.00] CKT Z1 | 5.4769 | 0.1365 | 36.4711 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CHISHLM4 138.00] TO [MAIZE 4 138.00] CKT 1 | 5.4758 | 0.1365 | 36.4738 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CLEARWT4 138.00] TO [GILL 4 138.00] CKT 1 | 5.4767 | 0.1365 | 36.4758 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CLEARWT4 138.00] TO [VIOLA 4 138.00] CKT 1 | 5.4765 | 0.1365 | 36.4763 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EVANS S4 138.00] TO [LAKERDG4 138.00] CKT 1 | 5.4757 | 0.1365 | 36.481 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EVANS S4 138.00] TO [45TH ST4 138.00] CKT 1 | 5.4758 | 0.1365 | 36.478 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [FARBER 4 138.00] TO [SC10BEL4 138.00] CKT 1 | 5.4766 | 0.1365 | 36.4744 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GILL 4 138.00] TO [VIOLA 4 138.00] CKT 1 | 5.4767 | 0.1365 | 36.4767 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [VIOLA 4 138.00] TO [MILAN_GOAB 138.00] CKT 1 | 5.4769 | 0.1365 | 36.4718 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [VIOLA 4 138.00] TO [CONWAY 138.00] CKT 1 | 5.4768 | 0.1365 | 36.472 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [AEC 3 115.00] TO [EABILEN3 115.00] CKT 1 | 2.8991 | 0.1436 | 43.578 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [AEC 3 115.00] TO [AEC E1 34.500] CKT 2 | 5.4704 | 0.1365 | 36.5049 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [AEC 3 115.00] TO [AEC W1 34.500] CKT 1 | 5.4514 | 0.1364 | 36.4044 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NORTHST3 115.00] TO [NORTHVW3 115.00] CKT 1 | 5.3073 | 0.1366 | 36.61 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NORTHVW3 115.00] TO [SUMMIT 3 115.00] CKT 1 | 4.5437 | 0.1384 | 38.3963 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LITCH N2 69.000] TO [LITCH S2 69.000] CKT Z1 | 5.4769 | 0.1365 | 36.4715 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [MRWYP16 230.00] TO [ELMCREK6 230.00] CKT 1 | 5.4771 | 0.1365 | 36.4945 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [FLATRDG4 138.00] TO [THISTLE4 138.00] CKT 1 | 5.4763 | 0.1365 | 36.4789 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ELMCREK6 230.00] TO [CONCRD6 230.00] CKT 1 | 5.4562 | 0.1365 | 36.5349 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAYNE3 115.00] TO [NLIB 3 115.00] CKT 1 | 5.4768 | 0.1365 | 36.472 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [KISMET 3 115.00] TO [CMRIVTP3 115.00] CKT 1 | 5.4763 | 0.1365 | 36.4721 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CMRIVTP3 115.00] TO [E-LIBER3 115.00] CKT 1 | 5.4768 | 0.1365 | 36.4721 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CIM-PLT1 13.800] TO [CIM-PLT 13.800] CKT Z1 | 5.4768 | 0.1365 | 36.4722 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [N-CIMRN3 115.00] TO [N-CMRN 1 34.500] TO [N-CMRN-T 13.800] CKT 1 | 5.4769 | 0.1365 | 36.4714 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [TRANSFORMER 345.00] CKT 1 | 5.4771 | 0.1365 | 36.4664 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [GEN-2011-008345.00] CKT 1 | 5.4768 | 0.1365 | 36.4796 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [G16-046-TAP 345.00] CKT 1 | 5.4767 | 0.1365 | 36.4747 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [MULLNCR7 345.00] TO [MC REAC1 345.00] CKT Z1 | 5.4769 | 0.1365 | 36.4712 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [MULLNCR7 345.00] TO [MC REAC2 345.00] CKT Z1 | 5.4769 | 0.1365 | 36.4712 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [MULLNCR7 345.00] TO [MC REAC3 345.00] CKT Z1 | 5.4769 | 0.1365 | 36.4707 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [MULLNCR7 345.00] TO [KETCHEM7 345.00] CKT 1 | 5.4769 | 0.1365 | 36.4705 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [PECULR 7 345.00] TO [STILWEL7 345.00] CKT 1 | 5.476 | 0.1365 | 36.4759 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ST JOE 7 345.00] TO [EASTOWN7 345.00] CKT 1 | 5.4753 | 0.1365 | 36.4931 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ST JOE 7 345.00] TO [COOPER 3 345.00] CKT 1 | 5.4762 | 0.1365 | 36.4806 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ST JOE 7 345.00] TO [ST JOE 5 161.00] TO [STJOE 1T 13.800] CKT 22 | 5.4768 | 0.1365 | 36.4718 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ST JOE 7 345.00] TO [ST JOE 5 161.00] TO [STJOE 2T 13.800] CKT 33 | 5.4768 | 0.1365 | 36.4718 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ARCHIE 5 161.00] TO [HSNVL 5 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4718 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ARCHIE 5 161.00] TO [ADRIAN 5 161.00] CKT 1 | 5.4766 | 0.1365 | 36.4758 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ARCHIE 5 161.00] TO [S.HARP 5 161.00] CKT 1 | 5.4767 | 0.1365 | 36.4727 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S.HARP 5 161.00] TO [STILWEL5 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4719 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EASTOWN7 345.00] TO [IATAN 7 345.00] CKT 1 | 5.4736 | 0.1365 | 36.5196 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ROCKCK_TR1_113.200] TO [ROCKCK7 345.00] TO [ROCKCK_T1_1 34.500] CKT 1 | 5.477 | 0.1365 | 36.4703 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ROCKCK_TR2_113.200] TO [ROCKCK7 345.00] TO [ROCKCK_T2_1 34.500] CKT 1 | 5.477 | 0.1365 | 36.4699 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ROCKCK7 345.00] TO [OUTLAW 345.00] CKT 1 | 5.477 | 0.1365 | 36.4681 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LAC G1 1 22.000] TO [LACYGNE7 345.00] CKT 1 | 5.4774 | 0.1364 | 36.4455 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LAC G2 1 24.000] TO [LACYGNE7 345.00] CKT 1 | 5.4782 | 0.1364 | 36.434 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WGARDNR5 161.00] TO [CEDRCRK5 161.00] CKT 1 | 5.4766 | 0.1365 | 36.4756 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WGARDNR5 161.00] TO [CEDARNL5 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4723 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WGARDNR5 161.00] TO [PLSTVAL5 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4726 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WGARDNR5 161.00] TO [BULLCRK5 161.00] CKT 1 | 5.4769 | 0.1365 | 36.4586 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WGARDNR5 161.00] TO [BNSF 5 161.00] CKT 1 | 5.4764 | 0.1365 | 36.4793 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WGARDNR5 161.00] TO [WGARDNR1 34.500] CKT 7 | 5.4767 | 0.1365 | 36.4731 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [STILWEL7 345.00] TO [LACYGNE7 345.00] CKT 1 | 5.4777 | 0.1365 | 36.4563 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [STILWEL7 345.00] TO [STILWEL5 161.00] TO [STIL T11 13.800] CKT 11 | 5.4768 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [STILWEL7 345.00] TO [STILWEL5 161.00] TO [STIL T22 13.800] CKT 22 | 5.4768 | 0.1365 | 36.4718 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [STILWEL5 161.00] TO [HICKMAN5 161.00] CKT 1 | 5.4769 | 0.1365 | 36.4713 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [STILWEL5 161.00] TO [ANTIOCH5 161.00] CKT 1 | 5.4769 | 0.1365 | 36.4719 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [STILWEL5 161.00] TO [REDEL 5 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4712 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [STILWEL5 161.00] TO [BUCYRUS5 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4725 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [STILWEL5 161.00] TO [LACKMAN5 161.00] CKT 1 | 5.4767 | 0.1365 | 36.4726 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTH 7 345.00] TO [NASHUA 7 345.00] CKT 1 | 5.4761 | 0.1365 | 36.4814 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTHS5 161.00] TO [SUB M-161 161.00] CKT 1 | 5.4768 | 0.1365 | 36.472 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRAIG 7 345.00] TO [CRAIG 5 161.00] TO [CRAI T11 13.800] CKT 11 | 5.4765 | 0.1365 | 36.4746 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRAIG 7 345.00] TO [CRAIG 5 161.00] TO [CRAI T22 13.800] CKT 22 | 5.4765 | 0.1365 | 36.4745 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRAIG 7 345.00] TO [CRAIG 5 161.00] TO [CRAI T33 13.800] CKT 33 | 5.4768 | 0.1365 | 36.4701 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRAIG 5 161.00] TO [CEDRCRK5 161.00] CKT 1 | 5.4768 | 0.1365 | 36.472 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NASHUA 7 345.00] TO [IATAN 7 345.00] CKT 1 | 5.4745 | 0.1365 | 36.5055 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NASHUA 7 345.00] TO [NASHUA-5 161.00] TO [NASH T11 13.800] CKT 11 | 5.4768 | 0.1365 | 36.4739 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NASHUA 7 345.00] TO [NASHUA-5 161.00] TO [NASH T12 13.800] CKT 12 | 5.4768 | 0.1365 | 36.4728 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LACYGNE7 345.00] TO [LACYGNE11_7 345.00] CKT 1 | 5.4768 | 0.1365 | 36.4731 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LACYGNE7 345.00] TO [LACYGNE22_7 345.00] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LACYGNE7 345.00] TO [LAC3_STAR7 345.00] CKT H | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LACYGNE7 345.00] TO [LAC8_STAR7 345.00] CKT H | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LACYGNE7 345.00] TO [LACYGNE2 69.000] TO [LACYGN7_TER16.9000] CKT 7 | 5.4768 | 0.1365 | 36.4722 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BLUMILS5 161.00] TO [ECKLES-161 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BLUMILS5 161.00] TO [BLUEMLS2 69.000] TO [BLUMILS_TER112.500] CKT 3 | 5.4768 | 0.1365 | 36.472 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LAKCTYJ2 69.000] TO [BLUVLY 69.000] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CJ 366 5 161.00] TO [FIR417 5 161.00] CKT 1 | 5.4769 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CAR395 5 161.00] TO [PUR421 5 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4719 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB K 69.000] TO [BLUVLY 69.000] CKT 1 | 5.4768 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB H 69.000] TO [BLUVLY 69.000] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB H 69.000] TO [SUB M 69.000] CKT 1 | 5.4769 | 0.1365 | 36.4715 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BLUVLY 13.8 13.800] TO [BLUVLY 69.000] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BLUVLY 69.000] TO [SUB B 69.000] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BLUVLY 69.000] TO [SUB J 69.000] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BLUVLY 69.000] TO [SUB P 69.000] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB B 69.000] TO [SUB J 69.000] CKT 1 | 5.4768 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB J 69.000] TO [SUB M 69.000] CKT 1 | 5.4769 | 0.1365 | 36.4715 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB M-161 161.00] TO [SUB M 69.000] CKT 1 | 5.4768 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GEN-2017-004345.00] TO [G17-004-TAP 345.00] CKT 1 | 5.4761 | 0.1365 | 36.5186 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GEN-2017-018345.00] TO [G17-018XFMR134.500] CKT 1 | 5.4766 | 0.1365 | 36.4761 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GEN-2017-018345.00] TO [G17-018XFMR234.500] CKT 1 | 5.4766 | 0.1365 | 36.4761 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GEN-2017-068138.00] TO [G17-068XFMR134.500] CKT 1 | 5.4763 | 0.1365 | 36.4818 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GEN-2017-082161.00] TO [G17-082XFMR134.500] CKT 1 | 5.4769 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [COOPER 3 345.00] TO [S3458 3 345.00] CKT 1 | 5.4767 | 0.1365 | 36.4735 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEBCTY1G 18.000] TO [S3458 3 345.00] CKT 1 | 5.4782 | 0.1364 | 36.4454 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEBCTY2G 23.000] TO [S3458 3 345.00] CKT 1 | 5.4782 | 0.1364 | 36.4449 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S3456 3 345.00] TO [S3458 3 345.00] CKT 1 | 5.4766 | 0.1365 | 36.4754 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S3458 3 345.00] TO [S3740 3 345.00] CKT 1 | 5.4767 | 0.1365 | 36.4751 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S3458 3 345.00] TO [103&ROKEBY3 345.00] CKT 1 | 5.4764 | 0.1365 | 36.4809 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [7FAIRPT 345.00] TO [5FAIRPTXF3 161.00] CKT 3 | 5.4766 | 0.1365 | 36.4749 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5CLINTN 161.00] TO [G17-108-TAP 161.00] CKT 1 | 5.4765 | 0.1365 | 36.478 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5NEWMAD 161.00] TO [5GIBSON 161.00] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M0 161.00] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M1 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4722 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M2 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4722 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M3 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4722 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5NEWMAD 161.00] TO [5NEWMADCP 161.00] CKT Z1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5NEWMAD 161.00] TO [5NEWMADXF12 161.00] CKT Z1 | 5.4769 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5NEWMAD 161.00] TO [5NEWMADGSU1 161.00] CKT 1 | 5.4771 | 0.1365 | 36.4678 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5NEWMAD 161.00] TO [5NMDSU100HS 161.00] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5NEWMAD 161.00] TO [5NMDSU200HS 161.00] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5NEWMAD 161.00] TO [5PORTAGEVLE 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4719 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5NEWMAD 161.00] TO [5TIPTONVL TN161.00] CKT 1 | 5.4768 | 0.1365 | 36.4731 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5HOLDENB2 161.00] TO [1HOLDNG11 13.800] CKT 11 | 5.4771 | 0.1365 | 36.4665 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5HOLDENB2 161.00] TO [1HOLDNG12 13.800] CKT 12 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5HOLDENB2 161.00] TO [2HOLDEN 69.000] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5HOLDENB2 161.00] TO [5HOLDENB1 161.00] CKT Z1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [2CLINTN 69.000] TO [2LINCLN 69.000] CKT 1 | 5.4768 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [2CLINTN 69.000] TO [2GAINES 69.000] CKT 1 | 5.4768 | 0.1365 | 36.472 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [2CLINTN 69.000] TO [2LEETON 69.000] CKT 1 | 5.4768 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [2CLINTN 69.000] TO [2PIPER 69.000] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [2CLINTN 69.000] TO [2CLINTNLD 69.000] CKT 1 | 5.4768 | 0.1365 | 36.472 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [7BLACKBERRY 345.00] TO [NEOSHO 7 345.00] CKT 1 | 5.4768 | 0.1365 | 36.4695 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [7SPORTSMAN 345.00] TO [5SPORTSMAN 161.00] CKT 1 | 5.4769 | 0.1365 | 36.4714 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [7SPORTSMAN 345.00] TO [5SPORTSMAN 161.00] CKT 2 | 5.4769 | 0.1365 | 36.4714 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [7SPORTSMAN 345.00] TO [GRDA1 7 345.00] CKT 1 | 5.4766 | 0.1365 | 36.4764 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [7JASPER 345.00] TO [7MORGAN 345.00] CKT 1 | 5.477 | 0.1365 | 36.4657 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [7JASPER 345.00] TO [5JASPER 161.00] CKT 1 | 5.477 | 0.1365 | 36.4691 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5OSCEOKCTP 161.00] TO [5OSCEOLTP 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4736 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5OSCEOKCTP 161.00] TO [5OSCEOKC 161.00] CKT 1 | 5.4769 | 0.1365 | 36.4718 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5MINER 1 161.00] TO [5CHARLSTN 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4718 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5MINER 1 161.00] TO [5BULLION 161.00] CKT 1 | 5.4768 | 0.1365 | 36.472 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5MINER 1 161.00] TO [5MINER 2 161.00] CKT Z | 5.4769 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [N MADRD5 161.00] TO [G17-202-TAP 161.00] CKT 1 | 5.4768 | 0.1365 | 36.472 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [N MADRD2 69.000] TO [2STJUDEW 69.000] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [N MADRD2 69.000] TO [2LILBRN 69.000] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [N MADRD2 69.000] TO [MALDEN 2 69.000] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [KENNETT5 161.00] TO [PARAGLD5 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4721 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [KENNETT5 161.00] TO [KENNETT2 69.000] TO [KEN X1 1 13.800] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [KENNETT5 161.00] TO [KENNETT2 69.000] TO [KEN X2 1 13.800] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SIKETAP5 161.00] TO [SIKE SW5 161.00] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SIKESTN5 161.00] TO [G17-202-TAP 161.00] CKT 1 | 5.4769 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [IDALIA 5 161.00] TO [5ESSEX 161.00] CKT 1 | 5.4769 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [IDALIA 5 161.00] TO [2IDALIA 69.000] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [IDALIA 5 161.00] TO [2IDALIA 69.000] CKT 2 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [IDALIA 5 161.00] TO [ASHRVL5 161.00] CKT 1 | 5.4769 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [TRUMAN 5 161.00] TO [5LOSTVALY 161.00] CKT 1 | 5.4766 | 0.1365 | 36.4764 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [TRUMAN 5 161.00] TO [TRU123 1 13.800] CKT 1 | 5.477 | 0.1365 | 36.4685 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [TRUMAN 5 161.00] TO [TRU456 1 13.800] CKT 1 | 5.477 | 0.1365 | 36.4685 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [DELWARE4 138.00] TO [FARML 4 138.00] CKT 1 | 5.4768 | 0.1365 | 36.472 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [DELWARE7 345.00] TO [NEOSHO 7 345.00] CKT 1 | 5.4761 | 0.1365 | 36.4812 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [N.E.S.-7 345.00] TO [ONETA--7 345.00] CKT 1 | 5.4767 | 0.1365 | 36.4739 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [N.E.S.-7 345.00] TO [T.NO.--7 345.00] CKT 1 | 5.4766 | 0.1365 | 36.4763 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [N.E.S.-7 345.00] TO [NES3-1 22.000] CKT 1 | 5.4761 | 0.1365 | 36.4857 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WWRDEHV7 345.00] TO [TATONGA7 345.00] CKT 1 | 5.4765 | 0.1365 | 36.4739 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WWRDEHV7 345.00] TO [TATONGA7 345.00] CKT 2 | 5.4765 | 0.1365 | 36.4738 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WWRDEHV7 345.00] TO [G07621119-20345.00] CKT 1 | 5.4768 | 0.1365 | 36.473 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WWRDEHV7 345.00] TO [GUTHRIE7 345.00] CKT 1 | 5.4768 | 0.1365 | 36.472 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WWRDEHV7 345.00] TO [BECKHAM7 345.00] CKT 1 | 5.4762 | 0.1365 | 36.4689 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WWRDEHV7 345.00] TO [G16-003-TAP 345.00] CKT 1 | 5.4769 | 0.1365 | 36.4699 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WWRDEHV7 345.00] TO [G16-003-TAP 345.00] CKT 2 | 5.4769 | 0.1365 | 36.4699 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WWRDEHV7 345.00] TO [WWRDEHV4 138.00] TO [WWDEHV31 13.800] CKT 1 | 5.4769 | 0.1365 | 36.4708 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WWRDEHV7 345.00] TO [WWRDEHV4 138.00] TO [WWDEHV21 13.800] CKT 2 | 5.4769 | 0.1365 | 36.4702 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [DGRASSE7 345.00] TO [THISTLE7 345.00] CKT 1 | 5.4748 | 0.1365 | 36.4689 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [DGRASSE7 345.00] TO [THISTLE7 345.00] CKT 2 | 5.4748 | 0.1365 | 36.4689 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [DGRASSE4 138.00] TO [KNOBHIL4 138.00] CKT 1 | 5.4768 | 0.1365 | 36.4719 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [DGRASSE4 138.00] TO [ROSEVLY4 138.00] CKT 1 | 5.4768 | 0.1365 | 36.4719 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [DGRASSE4 138.00] TO [MOORLND4 138.00] CKT 1 | 5.4765 | 0.1365 | 36.473 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WALKMYR2 69.000] TO [NORTH6T2 69.000] CKT 1 | 5.4769 | 0.1365 | 36.4714 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WALKMYR2 69.000] TO [WOODS 2 69.000] CKT 1 | 5.4769 | 0.1365 | 36.4714 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WALKMYR3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 5.4768 | 0.1365 | 36.4722 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SEWARD-3 115.00] TO [HASKELL3 115.00] CKT 1 | 5.4768 | 0.1365 | 36.4721 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SEWARD-3 115.00] TO [CMSSWRD2 69.000] TO [SEWARD 1 13.800] CKT 1 | 5.4768 | 0.1365 | 36.4715 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SPERVIL7 345.00] TO [POSTROCK7 345.00] CKT 1 | 5.4719 | 0.1365 | 36.4661 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SPERVIL7 345.00] TO [BUCKNER7 345.00] CKT 1 | 5.4712 | 0.1365 | 36.4705 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SPERVIL7 345.00] TO [IRONWOOD7 345.00] CKT 1 | 5.4766 | 0.1365 | 36.4726 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SPERVIL7 345.00] TO [SPRVL 3 115.00] TO [SPRVL-T 13.800] CKT 1 | 5.4769 | 0.1365 | 36.4709 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SPERVIL7 345.00] TO [SPEARVL6 230.00] TO [SPERTER1 13.800] CKT 1 | 5.4736 | 0.1365 | 36.4742 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HUGOTON3 115.00] TO [GRANTTP3 115.00] CKT 1 | 5.4768 | 0.1365 | 36.4725 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HUGOTON3 115.00] TO [ABBK 2 115.00] CKT 1 | 5.4768 | 0.1365 | 36.4714 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HUGOTON3 115.00] TO [HUGOTON2 69.000] TO [HUGOTON1 13.800] CKT 1 | 5.4768 | 0.1365 | 36.471 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HARBNGR3 115.00] TO [HARBNGR7 345.00] TO [HARBNGR-T 13.800] CKT 1 | 5.4768 | 0.1365 | 36.4722 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EEC GT1 13.800] TO [DG TIE 1 4.1600] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EEC GT2 13.800] TO [EEC DG 1 4.1600] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC121 13.800] CKT 1 | 5.4747 | 0.1365 | 36.4639 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC341 13.800] CKT 1 | 5.4747 | 0.1365 | 36.4639 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC5 1 18.000] CKT 1 | 5.4719 | 0.1365 | 36.4592 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC6 1 18.000] CKT 1 | 5.4722 | 0.1365 | 36.4531 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC7 1 18.000] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EMPEC 7 345.00] TO [LANG 7 345.00] CKT 1 | 5.4733 | 0.1365 | 36.5263 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EMPEC 7 345.00] TO [MORRIS 7 345.00] CKT 1 | 5.4439 | 0.1366 | 36.5572 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EMPEC 7 345.00] TO [READWF 7 345.00] CKT 1 | 5.4774 | 0.1365 | 36.4628 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [RENO 7 345.00] TO [G16-111-TAP 345.00] CKT 1 | 5.3532 | 0.1366 | 36.6194 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [RENO 7 345.00] TO [RENO 3 115.00] TO [RENO 1X1 14.400] CKT 1 | 5.4755 | 0.1365 | 36.46 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [RENO 7 345.00] TO [RENO 3 115.00] TO [RENO 2X1 14.400] CKT 1 | 5.4754 | 0.1365 | 36.4616 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUMMIT 7 345.00] TO [GEARY 7 345.00] CKT 1 | 5.4643 | 0.1368 | 36.778 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUMMIT 7 345.00] TO [G16-111-TAP 345.00] CKT 1 | 5.3559 | 0.1367 | 36.713 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUMMIT 7 345.00] TO [SUMMIT 6 230.00] TO [SUMMIT 1 14.400] CKT 1 | 5.2549 | 0.1368 | 36.7539 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SWISVAL7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 5.4561 | 0.1365 | 36.5143 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [87TH 7 345.00] TO [STRANGR7 345.00] CKT 1 | 5.4749 | 0.1365 | 36.5021 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [87TH 7 345.00] TO [87TH 3 115.00] TO [87TH 1X1 13.800] CKT 1 | 5.4768 | 0.1365 | 36.472 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [G17-009-TAP 345.00] TO [NEOSHO 7 345.00] CKT 1 | 5.476 | 0.1365 | 36.4511 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GEN-2017-009345.00] TO [G17-009XFMR134.500] CKT 1 | 5.4768 | 0.1365 | 36.4722 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GEN-2017-009345.00] TO [G17-009XFMR234.500] CKT 1 | 5.4768 | 0.1365 | 36.4723 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CANEYRV7 345.00] TO [CANEYWF7 345.00] CKT 1 | 5.4767 | 0.1365 | 36.4749 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CANEYRV7 345.00] TO [LATHAMS7 345.00] CKT 1 | 5.475 | 0.1365 | 36.4748 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [KINGMAN7 345.00] TO [BUFFALO7 345.00] CKT 1 | 5.4746 | 0.1365 | 36.5219 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NINN1WF7 345.00] TO [PRATTWF7 345.00] CKT 1 | 5.4767 | 0.1365 | 36.4758 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NINN1WF7 345.00] TO [N1 LV 1 34.500] TO [N1 WFTX1 13.800] CKT 1 | 5.4763 | 0.1365 | 36.4818 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BENTON 7 345.00] TO [ROSEHIL7 345.00] CKT 1 | 5.4696 | 0.1365 | 36.491 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BENTON 7 345.00] TO [BENTON 4 138.00] TO [BENTN1 1 13.800] CKT 1 | 5.4762 | 0.1365 | 36.4777 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BENTON 7 345.00] TO [BENTON 4 138.00] TO [BENTN2 1 13.800] CKT 1 | 5.4762 | 0.1365 | 36.4774 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 1 | 5.4766 | 0.1365 | 36.4712 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 2 | 5.4766 | 0.1365 | 36.4712 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WICHITA7 345.00] TO [EVANS N4 138.00] TO [WICH11 1 13.800] CKT 1 | 5.477 | 0.1365 | 36.4614 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WICHITA7 345.00] TO [EVANS N4 138.00] TO [WICH12 1 13.800] CKT 1 | 5.4772 | 0.1365 | 36.4591 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WOLFCRK7 345.00] TO [WCGS U1 25.000] CKT 1 | 5.4762 | 0.1364 | 36.438 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WOLFCRK7 345.00] TO [ROSEHIL7 345.00] CKT 1 | 5.474 | 0.1365 | 36.5065 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WOLFCRK7 345.00] TO [WOLFCRK2 69.000] TO [WOLFCRK1 17.000] CKT 1 | 5.4768 | 0.1365 | 36.4731 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [VIOLA 7 345.00] TO [RENFROW7 345.00] CKT 1 | 5.4695 | 0.1365 | 36.483 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [VIOLA 7 345.00] TO [G16-153-TAP 345.00] CKT 1 | 5.4747 | 0.1365 | 36.5177 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WAVERLY7 345.00] TO [WAVERTX7 345.00] CKT 1 | 5.4769 | 0.1365 | 36.4708 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EXPEDITION7 345.00] TO [GEN-2014-001345.00] CKT 1 | 5.4769 | 0.1365 | 36.4762 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [N345 1 1 13.800] TO [NEOSHO 7 345.00] TO [NEOSHO 4 138.00] CKT 1 | 5.4768 | 0.1365 | 36.4718 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [N345 2 1 13.800] TO [NEOSHO 7 345.00] TO [NEOSHO 5 161.00] CKT 1 | 5.4769 | 0.1365 | 36.4707 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SWISVAL6 230.00] TO [AUBURN 6 230.00] CKT 1 | 5.4725 | 0.1365 | 36.5047 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SWISVAL6 230.00] TO [LAWHILL6 230.00] CKT 1 | 5.4717 | 0.1365 | 36.4794 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SWISVAL6 230.00] TO [TECHILL6 230.00] CKT 1 | 5.4756 | 0.1365 | 36.496 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SWISVAL6 230.00] TO [MORRIS 6 230.00] CKT 1 | 5.455 | 0.1365 | 36.489 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NMANHT6 230.00] TO [EMANHAT6 230.00] CKT 1 | 5.4574 | 0.1365 | 36.4855 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NMANHT6 230.00] TO [NMANHT3 115.00] TO [NMANHX1 14.400] CKT 1 | 5.4656 | 0.1365 | 36.4859 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LITCH 5 161.00] TO [ASB349 5 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4725 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [MARMTNW5 161.00] TO [MARMTNE5 161.00] CKT Z1 | 5.4768 | 0.1365 | 36.4728 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [MARMTNW5 161.00] TO [MARMATN2 69.000] TO [MARMATN1 13.200] CKT 1 | 5.4767 | 0.1365 | 36.473 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [FRANKLIN5 161.00] TO [G17-005-TAP 161.00] CKT 1 | 5.4766 | 0.1365 | 36.4751 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [FRANKLIN5 161.00] TO [FRANKLIN2 69.000] TO [FRANKLIN1 12.470] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRESWLN4 138.00] TO [MIDLTNT4 138.00] CKT 1 | 5.4767 | 0.1365 | 36.4706 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRESWLN4 138.00] TO [SLATECRK4 138.00] CKT 1 | 5.4764 | 0.1365 | 36.4766 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRESWLN4 138.00] TO [CRESWLN2 69.000] TO [CRESW1 1 13.200] CKT 1 | 5.4769 | 0.1365 | 36.472 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRESWLN4 138.00] TO [CRESWLS2 69.000] TO [CRESW2 1 13.200] CKT 1 | 5.4769 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [OXFORD 4 138.00] TO [SUMNER 4 138.00] CKT 1 | 5.4763 | 0.1365 | 36.4723 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [TIMBJCT4 138.00] TO [SUMNER 4 138.00] CKT 1 | 5.4768 | 0.1365 | 36.4724 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [TIOGA 4 138.00] TO [TIOGA 2 69.000] TO [TIOGA 1 13.200] CKT 1 | 5.4768 | 0.1365 | 36.4712 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [OTTRCRK4 138.00] TO [BUTLER 4 138.00] CKT 1 | 5.4768 | 0.1365 | 36.4745 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [OTTRCRK4 138.00] TO [OTTRCRK3 115.00] TO [OTTRX1 1 13.800] CKT 1 | 5.4755 | 0.1365 | 36.4786 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ALTOONA4 138.00] TO [G17-022-TAP 138.00] CKT 1 | 5.4767 | 0.1365 | 36.4736 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEPARSN4 138.00] TO [G17-022-TAP 138.00] CKT 1 | 5.4768 | 0.1365 | 36.4719 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [TAYLOR 4 138.00] TO [MONTGOM4 138.00] CKT 1 | 5.4768 | 0.1365 | 36.4719 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BENTLEY4 138.00] TO [HALSTD 4 138.00] CKT 1 | 5.471 | 0.1365 | 36.5149 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BENTLEY4 138.00] TO [WWUPLNT4 138.00] CKT 1 | 5.4769 | 0.1365 | 36.4701 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEOSHOS4 138.00] TO [TV1MNDV4 138.00] CKT 1 | 5.4768 | 0.1365 | 36.4734 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEOSHON4 138.00] TO [NEOSHON2 69.000] TO [NEC U3 12.000] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CHISHLM4 138.00] TO [PARKCTY4 138.00] CKT 1 | 5.4767 | 0.1365 | 36.4741 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CHISHLM4 138.00] TO [17TH 4 138.00] CKT 1 | 5.4763 | 0.1365 | 36.4733 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CHISHLM4 138.00] TO [CHISHLM2 69.000] TO [CHISOLM1 13.200] CKT 1 | 5.4763 | 0.1365 | 36.4768 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EVANS S4 138.00] TO [EVANS N4 138.00] CKT Z1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EVANS S4 138.00] TO [EVANS N4 138.00] CKT Z2 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [FARBER 4 138.00] TO [ELPASOE4 138.00] CKT 1 | 5.4766 | 0.1365 | 36.4725 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GILL 4 138.00] TO [GILL W 4 138.00] CKT Z1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GILL 4 138.00] TO [GILL S 4 138.00] CKT Z1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LAKERDG4 138.00] TO [HOOVERN4 138.00] CKT 1 | 5.4759 | 0.1365 | 36.4777 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [MAIZE 4 138.00] TO [EVANS N4 138.00] CKT 1 | 5.4757 | 0.1365 | 36.4748 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SC10BEL4 138.00] TO [SUMNER 4 138.00] CKT 1 | 5.4766 | 0.1365 | 36.4749 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SG12COL4 138.00] TO [EVANS N4 138.00] CKT 1 | 5.4707 | 0.1365 | 36.521 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [45TH ST4 138.00] TO [COWSKIN4 138.00] CKT 1 | 5.4759 | 0.1365 | 36.4775 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [VIOLA 4 138.00] TO [SUMNER 4 138.00] CKT 1 | 5.4766 | 0.1365 | 36.4718 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [AEC 3 115.00] TO [G17-120-TAP 115.00] CKT 1 | 2.8607 | 0.1443 | 44.283 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EABILEN3 115.00] TO [CHAPMAN3 115.00] CKT 1 | 2.9113 | 0.1434 | 43.4221 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NORTHST3 115.00] TO [SALINA 3 115.00] CKT 1 | 5.3052 | 0.1368 | 36.79 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NORTHVW3 115.00] TO [G17-120-TAP 115.00] CKT 1 | 2.7078 | 0.1454 | 45.363 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUMMIT 3 115.00] TO [MENTOR 3 115.00] CKT 1 | 5.4682 | 0.1363 | 36.3299 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUMMIT 3 115.00] TO [SO GATE3 115.00] CKT 1 | 5.474 | 0.1365 | 36.5244 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUMMIT 3 115.00] TO [SUMMIT 6 230.00] TO [SUMIT2 1 13.800] CKT 1 | 5.2798 | 0.137 | 36.9594 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUMMIT 3 115.00] TO [SUMMIT 6 230.00] TO [SUMIT3 1 13.800] CKT 1 | 5.2763 | 0.137 | 36.9705 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [TIMBJCT2 69.000] TO [AKRON 2 69.000] CKT 1 | 5.477 | 0.1365 | 36.47 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [TIMBJCT2 69.000] TO [UDALL 2 69.000] CKT 1 | 5.4769 | 0.1365 | 36.4715 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [TIMBJCT2 69.000] TO [WINFLD 2 69.000] CKT 1 | 5.4767 | 0.1365 | 36.4728 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ALTOO E2 69.000] TO [NEODJCT2 69.000] CKT 1 | 5.4769 | 0.1365 | 36.4711 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ALTOO E2 69.000] TO [RA5HIPR2 69.000] CKT Z1 | 5.4769 | 0.1365 | 36.4714 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ALTOO W2 69.000] TO [STUDBKR2 69.000] CKT 1 | 5.4769 | 0.1365 | 36.471 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LITCH N2 69.000] TO [AQUARS 2 69.000] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LITCH N2 69.000] TO [PITNAC 2 69.000] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LITCH S2 69.000] TO [ROUSE 2 69.000] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LITCH S2 69.000] TO [SOPITT 2 69.000] CKT 1 | 5.4768 | 0.1365 | 36.4719 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEOSHOS2 69.000] TO [BAKER 2 69.000] CKT 1 | 5.4769 | 0.1365 | 36.4713 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEOSHOS2 69.000] TO [ORDNJCT2 69.000] CKT 1 | 5.4768 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEOSHOS2 69.000] TO [CRAWFOR2 69.000] CKT 1 | 5.4769 | 0.1365 | 36.4714 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEOSHOS2 69.000] TO [NEOSHON2 69.000] CKT Z1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [K1 LV 1 34.500] TO [K1 CLCT1 34.500] CKT 1 | 5.4767 | 0.1365 | 36.474 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [K2 LV 1 34.500] TO [K2 CLCT1 34.500] CKT 1 | 5.4768 | 0.1365 | 36.4759 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [MILAN_GOAB 138.00] TO [CLDWELL4 138.00] CKT 1 | 5.4768 | 0.1365 | 36.472 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [MILAN_GOAB 138.00] TO [MILAN 4 138.00] CKT 1 | 5.4769 | 0.1365 | 36.4709 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CONWAY 138.00] TO [MILANTP4 138.00] CKT 1 | 5.4769 | 0.1365 | 36.4718 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [MRWYP16 230.00] TO [MRWYP26 230.00] CKT 1 | 5.4772 | 0.1365 | 36.4805 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [MRWYP16 230.00] TO [MRWYG11 34.500] TO [MRWYP1T1 13.800] CKT 1 | 5.4773 | 0.1365 | 36.4743 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [FLATRDG4 138.00] TO [FLATRWD4 138.00] CKT 1 | 5.4763 | 0.1365 | 36.4749 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [FLATRDG4 138.00] TO [HARPER 4 138.00] CKT 1 | 5.4767 | 0.1365 | 36.4737 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [FLATRDG4 138.00] TO [BARBER 4 138.00] CKT 1 | 5.475 | 0.1365 | 36.4891 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ELMCREK6 230.00] TO [ELMCREEK7 345.00] TO [ELMCREEK1 13.800] CKT 1 | 5.4526 | 0.1365 | 36.4945 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAYNE3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 5.4768 | 0.1365 | 36.4722 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [KISMET 3 115.00] TO [CUDAHY 3 115.00] CKT 1 | 5.4763 | 0.1365 | 36.4723 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CMRIVTP3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 5.4768 | 0.1365 | 36.4714 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CONCRD6 230.00] TO [CONCORD3 115.00] TO [CONCOD-T 13.800] CKT 1 | 5.4563 | 0.1365 | 36.528 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [E-LIBER3 115.00] TO [TXPHSF 3115.00] CKT 1 | 5.4768 | 0.1365 | 36.4719 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [E-LIBER3 115.00] TO [E-PINE 3 115.00] CKT 1 | 5.4768 | 0.1365 | 36.4713 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [E-LIBER3 115.00] TO [NATBEEF3 115.00] CKT 1 | 5.4768 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [E-LIBER3 115.00] TO [E-LIBER1 34.500] TO [ELIB-T 2.4000] CKT 1 | 5.4768 | 0.1365 | 36.4713 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NLIB 3 115.00] TO [W-LIBER3 115.00] CKT 1 | 5.4768 | 0.1365 | 36.4715 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NLIB 3 115.00] TO [NATBEEF3 115.00] CKT 1 | 5.4768 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NLIB 3 115.00] TO [NLIB 1 34.500] TO [N-LIB-T 13.800] CKT 1 | 5.4768 | 0.1365 | 36.4711 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [N-CIMRN3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 5.4768 | 0.1365 | 36.4718 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CIM-PLT 13.800] TO [CIM-PLT3 115.00] CKT 1 | 5.4766 | 0.1365 | 36.4712 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [THISTLE7 345.00] CKT 1 | 5.476 | 0.1365 | 36.4892 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [THISTLE7 345.00] CKT 2 | 5.476 | 0.1365 | 36.4892 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [THISTLE T1 13.800] TO [THISTLE7 345.00] TO [THISTLE4 138.00] CKT 1 | 5.4763 | 0.1365 | 36.4788 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [TRANSFORMER 345.00] TO [SUB34.5KVB 34.500] TO [TERTIARYBUS 19.900] CKT 1 | 5.4771 | 0.1365 | 36.4664 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GEN-2011-008345.00] TO [G-2011-008-1345.00] CKT 1 | 5.4769 | 0.1365 | 36.4715 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GEN-2011-008345.00] TO [G-2011-008-2345.00] CKT 1 | 5.4767 | 0.1365 | 36.476 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GEN-2011-008345.00] TO [G-2011-008-3345.00] CKT 1 | 5.4771 | 0.1365 | 36.4724 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [MULLNCR7 345.00] TO [HOLT 7 345.00] CKT 1 | 5.4768 | 0.1365 | 36.4729 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [PECULR 7 345.00] TO [PHILL 7 345.00] CKT 1 | 5.4762 | 0.1365 | 36.4755 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [PECULR 7 345.00] TO [PECULR 5 161.00] TO [PECULRT 13.800] CKT 11 | 5.4768 | 0.1365 | 36.4721 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ST JOE 7 345.00] TO [G17-183-TAP 345.00] CKT 1 | 5.4768 | 0.1365 | 36.4723 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ARCHIE 5 161.00] TO [G17-108-TAP 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4721 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WINDSR 5 161.00] TO [5SEDALA 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HSNVL 5 161.00] TO [5SHARSNV 161.00] CKT 1 | 5.4768 | 0.1365 | 36.472 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HSNVL 5 161.00] TO [PHILL 5 161.00] CKT 1 | 5.4767 | 0.1365 | 36.4742 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HSNVL 5 161.00] TO [HSNVL 2 69.000] CKT 1 | 5.4768 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HSNVL 5 161.00] TO [HSNVL 2 69.000] CKT 2 | 5.4768 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ADRIAN 5 161.00] TO [5BUTLER 161.00] CKT 1 | 5.4767 | 0.1365 | 36.4753 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CLINTON5 161.00] TO [CLNTN N2 69.000] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CLINTON5 161.00] TO [CLNTN S2 69.000] CKT 2 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ST JOE 5 161.00] TO [ST JOE_CAP5 161.00] CKT R | 5.4767 | 0.1365 | 36.4751 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ST JOE 5 161.00] TO [COOK 5 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ST JOE 5 161.00] TO [WOODBIN5 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4719 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ST JOE 5 161.00] TO [AVENUECTY 5 161.00] CKT 1 | 5.4767 | 0.1365 | 36.4731 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP#1 13.800] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP#2 13.800] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP#3 13.800] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP 2 69.000] CKT 1 | 5.4768 | 0.1365 | 36.4718 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S.HARP 5 161.00] TO [PECULRS5 161.00] CKT 1 | 5.4768 | 0.1365 | 36.472 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EASTOWN7 345.00] TO [EASTOWN5 161.00] TO [EASTOWN1 13.800] CKT 11 | 5.4766 | 0.1365 | 36.4741 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [KETCHEM7 345.00] TO [SIBLEY 7 345.00] CKT 1 | 5.4768 | 0.1365 | 36.4728 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [KETCHEM7 345.00] TO [OSBORN7 345.00] CKT 1 | 5.4771 | 0.1365 | 36.4676 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ROCKCK7 345.00] TO [HOLT 7 345.00] CKT 1 | 5.4772 | 0.1365 | 36.4649 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ROCKCK_T1_1 34.500] TO [ROCKCK_P1_1 34.500] CKT 1 | 5.477 | 0.1365 | 36.4698 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ROCKCK_T2_1 34.500] TO [ROCKCK_P2_1 34.500] CKT 1 | 5.477 | 0.1365 | 36.4694 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HOLT_REACT7 345.00] TO [HOLT 7 345.00] CKT Z1 | 5.4769 | 0.1365 | 36.4712 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [OUTLAW 345.00] TO [OUTLAW_T2_1 34.500] TO [OUTLAW_TR2_113.800] CKT 1 | 5.477 | 0.1365 | 36.4693 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [OUTLAW 345.00] TO [OUTLAW_T1_1 34.500] TO [OUTLAW_TR1_113.800] CKT 1 | 5.4769 | 0.1365 | 36.4702 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WGARDNR5 161.00] TO [W.GRDNR7 345.00] TO [WGAR T11 13.800] CKT 11 | 5.4763 | 0.1365 | 36.4667 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [STILWEL7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 5.4745 | 0.1365 | 36.4811 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [STILWEL5 161.00] TO [G17-108-TAP 161.00] CKT 1 | 5.4767 | 0.1365 | 36.4729 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTH 7 345.00] TO [SIBLEY 7 345.00] CKT 1 | 5.4767 | 0.1365 | 36.4736 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTH 7 345.00] TO [HAWTHN5 161.00] TO [HAWT T20 13.800] CKT 20 | 5.4768 | 0.1365 | 36.4719 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTH 7 345.00] TO [HAWTHN5 161.00] TO [HAWT T22 13.800] CKT 22 | 5.4766 | 0.1365 | 36.4718 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTHS5 161.00] TO [HAW G9 1 13.800] CKT 1 | 5.4771 | 0.1365 | 36.4655 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTHS5 161.00] TO [LEEDS 5 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4722 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTHS5 161.00] TO [LEEDS 5 161.00] CKT 2 | 5.4768 | 0.1365 | 36.4722 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTH_B2_1 13.200] CKT 1 | 5.4768 | 0.1365 | 36.4728 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTHS5 161.00] TO [BRMGHAM5 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4728 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHS_G65 161.00] CKT Z1 | 5.4771 | 0.1365 | 36.4664 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHS_XF5 161.00] CKT Z2 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHN5 161.00] CKT @1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHN5 161.00] CKT @2 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRAIG 7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 5.477 | 0.1365 | 36.4654 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRAIG 5 161.00] TO [CRAIG_CAP 5 161.00] CKT R | 5.4767 | 0.1365 | 36.4754 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRAIG 5 161.00] TO [PFLUMM 5 161.00] CKT 1 | 5.4767 | 0.1365 | 36.4722 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRAIG 5 161.00] TO [LENEXA 5 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRAIG 5 161.00] TO [LENEXA 5 161.00] CKT 2 | 5.4768 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRAIG 5 161.00] TO [COLLEGE5 161.00] CKT 1 | 5.4769 | 0.1365 | 36.4707 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NASHUA 7 345.00] TO [G17-183-TAP 345.00] CKT 1 | 5.4766 | 0.1365 | 36.4761 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LACYGNE7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 5.4766 | 0.1365 | 36.4605 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LACYGNE7 345.00] TO [G17-209-TAP 345.00] CKT 1 | 5.4757 | 0.1365 | 36.4928 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [IATAN 7 345.00] TO [STRANGR7 345.00] CKT 1 | 5.4745 | 0.1365 | 36.4812 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [IATAN 7 345.00] TO [STRANGR7 345.00] CKT 2 | 5.4748 | 0.1365 | 36.4807 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [IATAN 7 345.00] TO [IAT G1 1 24.000] CKT 1 | 5.4795 | 0.1364 | 36.3981 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [IATAN 7 345.00] TO [IAT G2 1 24.500] CKT 1 | 5.4779 | 0.1364 | 36.4227 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [IATAN 7 345.00] TO [IATAN5 161.00] TO [IATAN 11 14.400] CKT 11 | 5.4765 | 0.1365 | 36.4762 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HICKMAN5 161.00] TO [STHTOWN5 161.00] CKT 1 | 5.4769 | 0.1365 | 36.4712 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BLUMILS5 161.00] TO [BLUVLY-161 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NASHUA-5 161.00] TO [NASHUA 5 161.00] CKT Z1 | 5.4768 | 0.1365 | 36.4723 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NASHUA-5 161.00] TO [RNRIDGE5 161.00] CKT 1 | 5.4768 | 0.1365 | 36.473 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NASHUA-5 161.00] TO [SHOLCRK5 161.00] CKT 1 | 5.4767 | 0.1365 | 36.4734 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CEDRCRK5 161.00] TO [SHWNMSN5 161.00] CKT 1 | 5.4768 | 0.1365 | 36.472 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ANTIOCH5 161.00] TO [OXFORD 5 161.00] CKT 1 | 5.4769 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [REDEL 5 161.00] TO [MARTCIT5 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4712 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BUCYRUS5 161.00] TO [NLOUISB5 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4724 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BUCYRUS5 161.00] TO [WAGSTAF5 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4723 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [PLSTVAL5 161.00] TO [SEOTTWA5 161.00] CKT 1 | 5.4767 | 0.1365 | 36.4733 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [PLSTVAL5 161.00] TO [ASG-2018-010161.00] CKT 1 | 5.477 | 0.1365 | 36.469 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [PLSTVAL5 161.00] TO [PLSTVAL1 34.500] TO [PLSTVL2_TER17.6210] CKT 2 | 5.4768 | 0.1365 | 36.4723 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LAKCTYJ2 69.000] TO [LAKCTY 2 69.000] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 1 13.800] CKT 1 | 5.477 | 0.1365 | 36.4662 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 2 13.800] CKT 1 | 5.477 | 0.1365 | 36.4662 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 3 13.800] CKT 1 | 5.477 | 0.1365 | 36.4663 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 4 13.800] CKT 1 | 5.477 | 0.1365 | 36.4662 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LACKMAN5 161.00] TO [SPRGHL 5 161.00] CKT 1 | 5.4767 | 0.1365 | 36.4724 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BNSF 5 161.00] TO [MOONLT 5 161.00] CKT 1 | 5.4765 | 0.1365 | 36.4786 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WGARDNR1 34.500] TO [BALDWINCTY1 34.500] CKT 1 | 5.4769 | 0.1365 | 36.4711 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LACYGNE11_7 345.00] TO [LAC11_AQC1 13.800] TO [LAC11_TER1 13.800] CKT 11 | 5.4768 | 0.1365 | 36.4731 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LACYGNE22_7 345.00] TO [LAC22_AQC1 13.800] TO [LAC22_TER1 13.800] CKT 22 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LACYGNE2 69.000] TO [LAC_LAKE_2 69.000] CKT 1 | 5.4768 | 0.1365 | 36.4722 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LAC3_STAR7 345.00] TO [LAC3_X1 6.9000] CKT X | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LAC3_STAR7 345.00] TO [LAC3_Y1 6.9000] CKT Y | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LAC3_STAR7 345.00] TO [LAC3_Z1 3.9800] CKT Z | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LAC8_STAR7 345.00] TO [LAC8_X1 6.9000] CKT X | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LAC8_STAR7 345.00] TO [LAC8_Y1 6.9000] CKT Y | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LAC8_STAR7 345.00] TO [LAC8_Z1 4.0000] CKT Z | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [RIV4525 161.00] TO [ORO110 5 161.00] CKT 1 | 5.4769 | 0.1365 | 36.4711 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [RIV4525 161.00] TO [STL439 5 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4714 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [RIV4525 161.00] TO [RIV452T 5 161.00] CKT 1 | 5.4767 | 0.1365 | 36.4736 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [RIV4525 161.00] TO [BAX488 5 161.00] CKT 1 | 5.4768 | 0.1365 | 36.473 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [RIV4525 161.00] TO [RIV167 2 69.000] TO [RIV452 1 12.500] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CJ 366 5 161.00] TO [ASB349 5 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4718 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CAR395 5 161.00] TO [CARTHAG5 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4718 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [FIR417 5 161.00] TO [ORO110 5 161.00] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [PUR421 5 161.00] TO [ASB349 5 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4719 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [A1G349 1 13.800] TO [ASB349 5 161.00] CKT 1 | 5.4769 | 0.1365 | 36.4715 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [A2G349 1 13.800] TO [ASB349 5 161.00] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB K 69.000] TO [SUB R 69.000] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB H 69.000] TO [COURTNY2 69.000] CKT 1 | 5.4768 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB H 69.000] TO [SUGRCK_TP_E269.000] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB H 69.000] TO [SUB H-13B1 13.800] CKT H1 | 5.4768 | 0.1365 | 36.4719 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB H 69.000] TO [SUB H-13B2 13.800] CKT H2 | 5.4768 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BLUVLY 69.000] TO [BLUVLY-161 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BLUVLY 69.000] TO [BLUVLY-161 161.00] CKT 2 | 5.4768 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ECKLES-161 161.00] TO [5LEVASY 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4723 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ECKLES-161 161.00] TO [5MOCITYB1 161.00] CKT 1 | 5.4769 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ECKLES-161 161.00] TO [SIBLEYPL 161.00] CKT 1 | 5.4768 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB J 69.000] TO [SUB J-13B1 13.800] CKT J1 | 5.4769 | 0.1365 | 36.4713 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB J 69.000] TO [SUB J-13B2 13.800] CKT J2 | 5.4768 | 0.1365 | 36.4721 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB M-161 161.00] TO [BLUVLY-161 161.00] CKT 1 | 5.4769 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB M 69.000] TO [SHRNKRD 69.000] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB P 69.000] TO [SUB I 69.000] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [G16-046-TAP 345.00] TO [IRONWOOD7 345.00] CKT 1 | 5.4765 | 0.1365 | 36.4764 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [G16-046-TAP 345.00] TO [GEN-2016-046345.00] CKT 1 | 5.475 | 0.1365 | 36.4779 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GEN-2017-004345.00] TO [G17-004XFMR134.500] CKT 1 | 5.4764 | 0.1365 | 36.5086 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [G17-004-TAP 345.00] TO [ELMCREEK7 345.00] CKT 1 | 5.4487 | 0.1367 | 36.6851 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GEN-2017-018345.00] TO [THISTLE7 345.00] CKT 1 | 5.4763 | 0.1365 | 36.4813 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [G17-018XFMR134.500] TO [G17-018-GSU134.500] CKT 1 | 5.4766 | 0.1365 | 36.4761 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [G17-018XFMR234.500] TO [G17-018-GSU234.500] CKT 1 | 5.4766 | 0.1365 | 36.4761 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GEN-2017-068138.00] TO [EVANS N4 138.00] CKT 1 | 5.4763 | 0.1365 | 36.4822 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [G17-068XFMR134.500] TO [G17-068-GSU134.500] CKT 1 | 5.4763 | 0.1365 | 36.4818 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GEN-2017-082161.00] TO [ASB349 5 161.00] CKT 1 | 5.4769 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [G17-082XFMR134.500] TO [G17-082-GSU134.500] CKT 1 | 5.4769 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [COOPER 3 345.00] TO [ATCHSN 3 345.00] CKT 1 | 5.4765 | 0.1365 | 36.4777 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [COOPER 3 345.00] TO [COOPER1G 22.000] CKT 1 | 5.4787 | 0.1364 | 36.4351 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [COOPER 3 345.00] TO [MONOLITH 3 345.00] CKT 1 | 5.4762 | 0.1365 | 36.4845 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [COOPER 3 345.00] TO [COOPER 5 161.00] TO [COOPER T2 913.800] CKT 1 | 5.4768 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [COOPER 3 345.00] TO [COOPER 5 161.00] TO [COOPER T5 913.800] CKT 1 | 5.4768 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEBCTY1G 18.000] TO [NC1GA1X9 4.2000] TO [NC1GA1Y9 4.2000] CKT 1 | 5.4768 | 0.1365 | 36.4726 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEBCTY1G 18.000] TO [NC1GA2X9 4.2000] TO [NC1GA2Y9 4.2000] CKT 1 | 5.4768 | 0.1365 | 36.4726 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEBCTY2G 23.000] TO [NC2GA1X9 4.2000] TO [NC2GA1Y9 4.2000] CKT 1 | 5.4768 | 0.1365 | 36.472 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEBCTY2G 23.000] TO [NC2GA2X9 13.800] TO [NC2GA2Y9 13.800] CKT 1 | 5.4767 | 0.1365 | 36.4742 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S3456 3 345.00] TO [CBLUFFS3 345.00] CKT 1 | 5.4768 | 0.1365 | 36.4728 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S3456 3 345.00] TO [S3455 3 345.00] CKT 1 | 5.4768 | 0.1365 | 36.4725 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S3456 3 345.00] TO [S3459 3 345.00] CKT 1 | 5.4768 | 0.1365 | 36.4723 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S3456 3 345.00] TO [S1206 5 161.00] TO [S3456T49 13.800] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S3458 3 345.00] TO [HOLT 7 345.00] CKT 1 | 5.4766 | 0.1365 | 36.4754 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S3740 3 345.00] TO [CASS 1G 15.000] CKT 1 | 5.4772 | 0.1365 | 36.4647 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S3740 3 345.00] TO [CASS 2G 15.000] CKT 1 | 5.4772 | 0.1365 | 36.4648 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S3740 3 345.00] TO [S3454 3 345.00] CKT 1 | 5.4768 | 0.1365 | 36.4726 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S3740 3 345.00] TO [S3455 3 345.00] CKT 1 | 5.4768 | 0.1365 | 36.4722 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S3740 3 345.00] TO [GEN-2018-033345.00] CKT 1 | 5.4769 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [103&ROKEBY3 345.00] TO [MOORE 3 345.00] CKT 1 | 5.4767 | 0.1365 | 36.473 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [103&ROKEBY3 345.00] TO [WAGENER 3 345.00] CKT 1 | 5.4768 | 0.1365 | 36.4716 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [7SPORTSMAN 345.00] TO [5SPORTSMAN 161.00] CKT 2 | 5.4769 | 0.1365 | 36.4706 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [IDALIA 5 161.00] TO [2IDALIA 69.000] CKT 2 | 5.4769 | 0.1365 | 36.4715 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WWRDEHV7 345.00] TO [TATONGA7 345.00] CKT 2 | 5.4754 | 0.1365 | 36.4764 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WWRDEHV7 345.00] TO [G16-003-TAP 345.00] CKT 2 | 5.4769 | 0.1365 | 36.4655 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [DGRASSE7 345.00] TO [THISTLE7 345.00] CKT 2 | 5.4668 | 0.1365 | 36.4618 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 2 | 5.4688 | 0.1365 | 36.538 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EVANS S4 138.00] TO [EVANS N4 138.00] CKT Z2 | 5.4736 | 0.1365 | 36.499 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [THISTLE7 345.00] CKT 2 | 5.4729 | 0.1365 | 36.5464 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HSNVL 5 161.00] TO [HSNVL 2 69.000] CKT 2 | 5.4768 | 0.1365 | 36.4717 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTHS5 161.00] TO [LEEDS 5 161.00] CKT 2 | 5.4767 | 0.1365 | 36.4743 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHN5 161.00] CKT @2 | 5.4767 | 0.1365 | 36.4748 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRAIG 5 161.00] TO [LENEXA 5 161.00] CKT 2 | 5.4766 | 0.1365 | 36.4723 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [IATAN 7 345.00] TO [STRANGR7 345.00] CKT 2 | 5.4632 | 0.1365 | 36.5191 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BLUVLY 69.000] TO [BLUVLY-161 161.00] CKT 2 | 5.4769 | 0.1365 | 36.4714 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | Base | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [7FAIRPT 345.00] TO [ST JOE 7 345.00] CKT 1 | 5.2372 | 0.1365 | 36.5193 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [7FAIRPT 345.00] TO [COOPER 3 345.00] CKT 1 | 5.2374 | 0.1365 | 36.5216 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5CLINTN 161.00] TO [5HOLDENB2 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5096 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5CLINTN 161.00] TO [2CLINTN 69.000] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5CLINTN 161.00] TO [2CLINTN 69.000] CKT 3 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5CLINTN 161.00] TO [5OSCEOKCTP 161.00] CKT 1 | 5.2385 | 0.1365 | 36.5074 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5CLINTN 161.00] TO [TRUMAN 5 161.00] CKT 1 | 5.2384 | 0.1365 | 36.509 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5CLINTN 161.00] TO [WINDSR 5 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5CLINTN 161.00] TO [CLINTON5 161.00] CKT Z1 | 5.2383 | 0.1365 | 36.5101 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5NEWMAD 161.00] TO [N MADRD5 161.00] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5NEWMAD 161.00] TO [SIKETAP5 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [7BLACKBERRY 345.00] TO [7SPORTSMAN 345.00] CKT 1 | 5.2379 | 0.1365 | 36.512 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [7BLACKBERRY 345.00] TO [7JASPER 345.00] CKT 1 | 5.2365 | 0.1365 | 36.5371 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [7BLACKBERRY 345.00] TO [WOLFCRK7 345.00] CKT 1 | 5.2366 | 0.1365 | 36.5371 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5MINER 1 161.00] TO [SIKESTN5 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [N MADRD5 161.00] TO [KENNETT5 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5098 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [N MADRD5 161.00] TO [N MADRD2 69.000] TO [NMA X1 1 13.800] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [N MADRD5 161.00] TO [N MADRD2 69.000] TO [NMA X2 1 13.800] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SIKETAP5 161.00] TO [SIKESTN5 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SIKESTN5 161.00] TO [SIKGEN 1 13.800] CKT 1 | 5.2384 | 0.1365 | 36.5107 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SIKESTN5 161.00] TO [IDALIA 5 161.00] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SIKESTN5 161.00] TO [SIKESTN2 69.000] TO [SIK X1 1 13.800] CKT 1 | 5.2385 | 0.1365 | 36.5097 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [DELAWAR1 13.800] TO [DELWARE4 138.00] TO [DELWARE7 345.00] CKT 1 | 5.2384 | 0.1365 | 36.5109 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [DELWARE7 345.00] TO [N.E.S.-7 345.00] CKT 1 | 5.2377 | 0.1365 | 36.5119 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WWRDEHV7 345.00] TO [DGRASSE7 345.00] CKT 1 | 5.2356 | 0.1365 | 36.5182 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WWRDEHV7 345.00] TO [DGRASSE7 345.00] CKT 2 | 5.2356 | 0.1365 | 36.5182 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [DGRASSE7 345.00] TO [DGRASSE4 138.00] TO [DGRASSE1 13.800] CKT 1 | 5.2374 | 0.1365 | 36.5096 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WALKMYR1 13.800] TO [WALKMYR2 69.000] TO [WALKMYR3 115.00] CKT 1 | 5.2383 | 0.1365 | 36.5112 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WALKMYR3 115.00] TO [HUGOTON3 115.00] CKT 1 | 5.2384 | 0.1365 | 36.5105 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WALKMYR3 115.00] TO [HARBNGR3 115.00] CKT 1 | 5.2382 | 0.1365 | 36.5126 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SEWARD-3 115.00] TO [N-CIMRN3 115.00] CKT 1 | 5.2384 | 0.1365 | 36.5102 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SPERVIL7 345.00] TO [CLARKCOUNTY7345.00] CKT 1 | 5.238 | 0.1365 | 36.5194 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NSES 2X1 13.200] TO [NEOSHO 4 138.00] TO [NEOSHOS2 69.000] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EEC GT1 13.800] TO [EVANS S4 138.00] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EEC GT2 13.800] TO [EVANS S4 138.00] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EEC GT3 18.000] TO [EVANS S4 138.00] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EMPEC 7 345.00] TO [SWISVAL7 345.00] CKT 1 | 5.2289 | 0.1366 | 36.605 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EMPEC 7 345.00] TO [EXPEDITION7 345.00] CKT 1 | 5.2383 | 0.1365 | 36.5136 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [RENO 7 345.00] TO [WICHITA7 345.00] CKT 1 | 5.0205 | 0.1367 | 36.6899 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUMMIT 7 345.00] TO [G17-004-TAP 345.00] CKT 1 | 5.2207 | 0.1367 | 36.7206 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SWISVAL7 345.00] TO [SWISVAL6 230.00] TO [SWISV1X1 14.400] CKT 1 | 5.2356 | 0.1365 | 36.4936 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SWISVAL7 345.00] TO [SWISVAL6 230.00] TO [SWISV2X2 14.400] CKT 2 | 5.235 | 0.1365 | 36.517 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [87TH 7 345.00] TO [CRAIG 7 345.00] CKT 1 | 5.2382 | 0.1365 | 36.4706 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [G17-009-TAP 345.00] TO [GEN-2017-009345.00] CKT 1 | 5.2384 | 0.1365 | 36.512 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [G17-009-TAP 345.00] TO [CANEYRV7 345.00] CKT 1 | 5.2349 | 0.1365 | 36.5181 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [KINGMAN7 345.00] TO [NINN1WF7 345.00] CKT 1 | 5.239 | 0.1365 | 36.5057 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [KINGMAN7 345.00] TO [K1 LV 1 34.500] TO [K1 WFTX1 13.800] CKT 1 | 5.2385 | 0.1365 | 36.5064 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [KINGMAN7 345.00] TO [K2 LV 1 34.500] TO [K2 WFTX1 13.800] CKT 1 | 5.2386 | 0.1365 | 36.5067 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BENTON 7 345.00] TO [WICHITA7 345.00] CKT 1 | 5.2117 | 0.1365 | 36.5321 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BENTON 7 345.00] TO [WOLFCRK7 345.00] CKT 1 | 5.2333 | 0.1365 | 36.5231 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WICHITA7 345.00] TO [VIOLA 7 345.00] CKT 1 | 5.2267 | 0.1366 | 36.5555 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WICHITA7 345.00] TO [EXPEDITION7 345.00] CKT 1 | 5.2361 | 0.1365 | 36.5392 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WOLFCRK7 345.00] TO [WAVERLY7 345.00] CKT 1 | 5.2383 | 0.1365 | 36.5112 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [VIOLA 7 345.00] TO [VIOLA 4 138.00] TO [VIOLA1X1 13.800] CKT 1 | 5.2384 | 0.1365 | 36.5105 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [VIOLA 7 345.00] TO [VIOLA 4 138.00] TO [SCJ1X1 13.800] CKT 2 | 5.2384 | 0.1365 | 36.5105 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WAVERLY7 345.00] TO [LACYGNE7 345.00] CKT 1 | 5.2376 | 0.1365 | 36.5262 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NMANHT6 230.00] TO [ELMCREK6 230.00] CKT 1 | 5.2352 | 0.1366 | 36.5872 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LITCH 5 161.00] TO [FRANKLIN5 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5097 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LITCH 5 161.00] TO [LITCH S2 69.000] TO [LITCH1 1 13.200] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LITCH 5 161.00] TO [LITCH N2 69.000] TO [LITCH2 1 13.200] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [MARMTNW5 161.00] TO [NEOSHO 5 161.00] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEOSHO 5 161.00] TO [RIV4525 161.00] CKT 1 | 5.2381 | 0.1365 | 36.5081 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEOSHO 5 161.00] TO [NEOSHO 4 138.00] TO [NEOSH4 1 13.200] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEOSHO 5 161.00] TO [NEOSHOS4 138.00] TO [NEOSH5 1 13.200] CKT 1 | 5.2384 | 0.1365 | 36.5098 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRESWLN4 138.00] TO [OXFORD 4 138.00] CKT 1 | 5.2374 | 0.1365 | 36.5116 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [TCROCK 4 138.00] TO [TIMBJCT4 138.00] CKT 1 | 5.2384 | 0.1365 | 36.5087 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [TIMBJCT4 138.00] TO [TIMBJCT2 69.000] TO [TIMBJCT1 13.200] CKT 1 | 5.2381 | 0.1365 | 36.5115 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [TIOGA 4 138.00] TO [ALTOONA4 138.00] CKT 1 | 5.2383 | 0.1365 | 36.5091 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [OTTRCRK4 138.00] TO [ALTOONA4 138.00] CKT 1 | 5.2361 | 0.1365 | 36.515 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ALTOONA4 138.00] TO [TAYLOR 4 138.00] CKT 1 | 5.2383 | 0.1365 | 36.5092 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ALTOONA4 138.00] TO [ALTOO W2 69.000] TO [ALTOO1 1 13.200] CKT 1 | 5.2384 | 0.1365 | 36.5097 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ALTOONA4 138.00] TO [ALTOO E2 69.000] TO [ALTOO3 1 13.200] CKT 1 | 5.2383 | 0.1365 | 36.5103 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEPARSN4 138.00] TO [NEOSHON4 138.00] CKT 1 | 5.2383 | 0.1365 | 36.5094 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BENTLEY4 138.00] TO [SG12COL4 138.00] CKT 1 | 5.232 | 0.1365 | 36.5345 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEOSHOS4 138.00] TO [NEOSHO 4 138.00] CKT Z1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEOSHO 4 138.00] TO [NEOSHON4 138.00] CKT Z1 | 5.2384 | 0.1365 | 36.5095 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CHISHLM4 138.00] TO [MAIZE 4 138.00] CKT 1 | 5.2367 | 0.1365 | 36.518 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CLEARWT4 138.00] TO [GILL 4 138.00] CKT 1 | 5.2384 | 0.1365 | 36.5127 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CLEARWT4 138.00] TO [VIOLA 4 138.00] CKT 1 | 5.2382 | 0.1365 | 36.5131 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EVANS S4 138.00] TO [LAKERDG4 138.00] CKT 1 | 5.2371 | 0.1365 | 36.5188 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EVANS S4 138.00] TO [45TH ST4 138.00] CKT 1 | 5.2371 | 0.1365 | 36.5172 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [FARBER 4 138.00] TO [SC10BEL4 138.00] CKT 1 | 5.2381 | 0.1365 | 36.5126 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GILL 4 138.00] TO [VIOLA 4 138.00] CKT 1 | 5.2382 | 0.1365 | 36.5135 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [VIOLA 4 138.00] TO [MILAN_GOAB 138.00] CKT 1 | 5.2384 | 0.1365 | 36.5102 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [VIOLA 4 138.00] TO [CONWAY 138.00] CKT 1 | 5.2384 | 0.1365 | 36.5107 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [AEC 3 115.00] TO [EABILEN3 115.00] CKT 1 | 2.8452 | 0.1444 | 44.4409 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [AEC 3 115.00] TO [AEC E1 34.500] CKT 2 | 5.2349 | 0.1365 | 36.5378 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [AEC 3 115.00] TO [AEC W1 34.500] CKT 1 | 5.2157 | 0.1365 | 36.4572 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NORTHST3 115.00] TO [NORTHVW3 115.00] CKT 1 | 5.0786 | 0.1369 | 36.8774 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NORTHVW3 115.00] TO [SUMMIT 3 115.00] CKT 1 | 4.3577 | 0.1385 | 38.4851 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LITCH N2 69.000] TO [LITCH S2 69.000] CKT Z1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [MRWYP16 230.00] TO [ELMCREK6 230.00] CKT 1 | 5.2388 | 0.1366 | 36.5746 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [FLATRDG4 138.00] TO [THISTLE4 138.00] CKT 1 | 5.2385 | 0.1365 | 36.5086 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ELMCREK6 230.00] TO [CONCRD6 230.00] CKT 1 | 5.2168 | 0.1365 | 36.5471 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAYNE3 115.00] TO [NLIB 3 115.00] CKT 1 | 5.2383 | 0.1365 | 36.5102 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [KISMET 3 115.00] TO [CMRIVTP3 115.00] CKT 1 | 5.2376 | 0.1365 | 36.5114 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CMRIVTP3 115.00] TO [E-LIBER3 115.00] CKT 1 | 5.2384 | 0.1365 | 36.5104 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CIM-PLT1 13.800] TO [CIM-PLT 13.800] CKT Z1 | 5.2382 | 0.1365 | 36.5136 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [N-CIMRN3 115.00] TO [N-CMRN 1 34.500] TO [N-CMRN-T 13.800] CKT 1 | 5.2384 | 0.1365 | 36.5103 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [TRANSFORMER 345.00] CKT 1 | 5.2391 | 0.1365 | 36.4969 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [GEN-2011-008345.00] CKT 1 | 5.2398 | 0.1365 | 36.4951 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [G16-046-TAP 345.00] CKT 1 | 5.238 | 0.1365 | 36.521 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [MULLNCR7 345.00] TO [MC REAC1 345.00] CKT Z1 | 5.2386 | 0.1365 | 36.5091 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [MULLNCR7 345.00] TO [MC REAC2 345.00] CKT Z1 | 5.2386 | 0.1365 | 36.5091 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [MULLNCR7 345.00] TO [MC REAC3 345.00] CKT Z1 | 5.2385 | 0.1365 | 36.5082 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [MULLNCR7 345.00] TO [KETCHEM7 345.00] CKT 1 | 5.2374 | 0.1365 | 36.5243 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [PECULR 7 345.00] TO [STILWEL7 345.00] CKT 1 | 5.2363 | 0.1365 | 36.5208 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ST JOE 7 345.00] TO [EASTOWN7 345.00] CKT 1 | 5.2364 | 0.1365 | 36.5215 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ST JOE 7 345.00] TO [COOPER 3 345.00] CKT 1 | 5.2364 | 0.1365 | 36.5286 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ST JOE 7 345.00] TO [ST JOE 5 161.00] TO [STJOE 1T 13.800] CKT 22 | 5.2384 | 0.1365 | 36.5105 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ST JOE 7 345.00] TO [ST JOE 5 161.00] TO [STJOE 2T 13.800] CKT 33 | 5.2384 | 0.1365 | 36.5104 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ARCHIE 5 161.00] TO [HSNVL 5 161.00] CKT 1 | 5.2385 | 0.1365 | 36.5089 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ARCHIE 5 161.00] TO [ADRIAN 5 161.00] CKT 1 | 5.2385 | 0.1365 | 36.5065 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ARCHIE 5 161.00] TO [S.HARP 5 161.00] CKT 1 | 5.2383 | 0.1365 | 36.5086 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S.HARP 5 161.00] TO [STILWEL5 161.00] CKT 1 | 5.2383 | 0.1365 | 36.5102 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EASTOWN7 345.00] TO [IATAN 7 345.00] CKT 1 | 5.2352 | 0.1365 | 36.5258 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ROCKCK_TR1_113.200] TO [ROCKCK7 345.00] TO [ROCKCK_T1_1 34.500] CKT 1 | 5.2384 | 0.1365 | 36.5096 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ROCKCK_TR2_113.200] TO [ROCKCK7 345.00] TO [ROCKCK_T2_1 34.500] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ROCKCK7 345.00] TO [OUTLAW 345.00] CKT 1 | 5.2385 | 0.1365 | 36.508 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LAC G1 1 22.000] TO [LACYGNE7 345.00] CKT 1 | 5.2344 | 0.1365 | 36.5371 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LAC G2 1 24.000] TO [LACYGNE7 345.00] CKT 1 | 5.2364 | 0.1365 | 36.5064 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WGARDNR5 161.00] TO [CEDRCRK5 161.00] CKT 1 | 5.2382 | 0.1365 | 36.512 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WGARDNR5 161.00] TO [CEDARNL5 161.00] CKT 1 | 5.2385 | 0.1365 | 36.5092 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WGARDNR5 161.00] TO [PLSTVAL5 161.00] CKT 1 | 5.2381 | 0.1365 | 36.5125 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WGARDNR5 161.00] TO [BULLCRK5 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WGARDNR5 161.00] TO [BNSF 5 161.00] CKT 1 | 5.238 | 0.1365 | 36.5142 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WGARDNR5 161.00] TO [WGARDNR1 34.500] CKT 7 | 5.2387 | 0.1365 | 36.5075 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [STILWEL7 345.00] TO [LACYGNE7 345.00] CKT 1 | 5.2343 | 0.1366 | 36.5824 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [STILWEL7 345.00] TO [STILWEL5 161.00] TO [STIL T11 13.800] CKT 11 | 5.2382 | 0.1365 | 36.5144 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [STILWEL7 345.00] TO [STILWEL5 161.00] TO [STIL T22 13.800] CKT 22 | 5.2381 | 0.1365 | 36.5147 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [STILWEL5 161.00] TO [HICKMAN5 161.00] CKT 1 | 5.2382 | 0.1365 | 36.5127 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [STILWEL5 161.00] TO [ANTIOCH5 161.00] CKT 1 | 5.2379 | 0.1365 | 36.5205 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [STILWEL5 161.00] TO [REDEL 5 161.00] CKT 1 | 5.2382 | 0.1365 | 36.5106 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [STILWEL5 161.00] TO [BUCYRUS5 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5103 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [STILWEL5 161.00] TO [LACKMAN5 161.00] CKT 1 | 5.2381 | 0.1365 | 36.5108 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTH 7 345.00] TO [NASHUA 7 345.00] CKT 1 | 5.2377 | 0.1365 | 36.5088 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTHS5 161.00] TO [SUB M-161 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5093 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRAIG 7 345.00] TO [CRAIG 5 161.00] TO [CRAI T11 13.800] CKT 11 | 5.2379 | 0.1365 | 36.5125 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRAIG 7 345.00] TO [CRAIG 5 161.00] TO [CRAI T22 13.800] CKT 22 | 5.2379 | 0.1365 | 36.5123 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRAIG 7 345.00] TO [CRAIG 5 161.00] TO [CRAI T33 13.800] CKT 33 | 5.2383 | 0.1365 | 36.5061 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRAIG 5 161.00] TO [CEDRCRK5 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5101 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NASHUA 7 345.00] TO [IATAN 7 345.00] CKT 1 | 5.2363 | 0.1365 | 36.5195 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NASHUA 7 345.00] TO [NASHUA-5 161.00] TO [NASH T11 13.800] CKT 11 | 5.2384 | 0.1365 | 36.5123 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NASHUA 7 345.00] TO [NASHUA-5 161.00] TO [NASH T12 13.800] CKT 12 | 5.2383 | 0.1365 | 36.5124 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LACYGNE7 345.00] TO [LACYGNE11_7 345.00] CKT 1 | 5.2385 | 0.1365 | 36.5086 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LACYGNE7 345.00] TO [LACYGNE22_7 345.00] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LACYGNE7 345.00] TO [LAC3_STAR7 345.00] CKT H | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LACYGNE7 345.00] TO [LAC8_STAR7 345.00] CKT H | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LACYGNE7 345.00] TO [LACYGNE2 69.000] TO [LACYGN7_TER16.9000] CKT 7 | 5.2384 | 0.1365 | 36.5096 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BLUMILS5 161.00] TO [ECKLES-161 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5102 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BLUMILS5 161.00] TO [BLUEMLS2 69.000] TO [BLUMILS_TER112.500] CKT 3 | 5.2385 | 0.1365 | 36.509 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LAKCTYJ2 69.000] TO [BLUVLY 69.000] CKT 1 | 5.2385 | 0.1365 | 36.5096 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CJ 366 5 161.00] TO [FIR417 5 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CAR395 5 161.00] TO [PUR421 5 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB K 69.000] TO [BLUVLY 69.000] CKT 1 | 5.2384 | 0.1365 | 36.5101 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB H 69.000] TO [BLUVLY 69.000] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB H 69.000] TO [SUB M 69.000] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BLUVLY 13.8 13.800] TO [BLUVLY 69.000] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BLUVLY 69.000] TO [SUB B 69.000] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BLUVLY 69.000] TO [SUB J 69.000] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BLUVLY 69.000] TO [SUB P 69.000] CKT 1 | 5.2384 | 0.1365 | 36.5101 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB B 69.000] TO [SUB J 69.000] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB J 69.000] TO [SUB M 69.000] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB M-161 161.00] TO [SUB M 69.000] CKT 1 | 5.2383 | 0.1365 | 36.5103 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GEN-2017-004345.00] TO [G17-004-TAP 345.00] CKT 1 | 5.2385 | 0.1366 | 36.5599 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GEN-2017-018345.00] TO [G17-018XFMR134.500] CKT 1 | 5.2389 | 0.1365 | 36.5008 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GEN-2017-018345.00] TO [G17-018XFMR234.500] CKT 1 | 5.2389 | 0.1365 | 36.5008 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GEN-2017-068138.00] TO [G17-068XFMR134.500] CKT 1 | 5.2386 | 0.1365 | 36.5057 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GEN-2017-082161.00] TO [G17-082XFMR134.500] CKT 1 | 5.2384 | 0.1365 | 36.5101 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [COOPER 3 345.00] TO [S3458 3 345.00] CKT 1 | 5.2379 | 0.1365 | 36.5116 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEBCTY1G 18.000] TO [S3458 3 345.00] CKT 1 | 5.2382 | 0.1365 | 36.5103 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEBCTY2G 23.000] TO [S3458 3 345.00] CKT 1 | 5.2381 | 0.1365 | 36.5109 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S3456 3 345.00] TO [S3458 3 345.00] CKT 1 | 5.2384 | 0.1365 | 36.5086 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S3458 3 345.00] TO [S3740 3 345.00] CKT 1 | 5.2385 | 0.1365 | 36.5082 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S3458 3 345.00] TO [103&ROKEBY3 345.00] CKT 1 | 5.2387 | 0.1365 | 36.5051 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [7FAIRPT 345.00] TO [5FAIRPTXF3 161.00] CKT 3 | 5.2383 | 0.1365 | 36.5086 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5CLINTN 161.00] TO [G17-108-TAP 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5056 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5NEWMAD 161.00] TO [5GIBSON 161.00] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M0 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M1 161.00] CKT 1 | 5.2385 | 0.1365 | 36.5096 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M2 161.00] CKT 1 | 5.2385 | 0.1365 | 36.5096 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M3 161.00] CKT 1 | 5.2385 | 0.1365 | 36.5096 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5NEWMAD 161.00] TO [5NEWMADCP 161.00] CKT Z1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5NEWMAD 161.00] TO [5NEWMADXF12 161.00] CKT Z1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5NEWMAD 161.00] TO [5NEWMADGSU1 161.00] CKT 1 | 5.2383 | 0.1365 | 36.5116 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5NEWMAD 161.00] TO [5NMDSU100HS 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5NEWMAD 161.00] TO [5NMDSU200HS 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5NEWMAD 161.00] TO [5PORTAGEVLE 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5NEWMAD 161.00] TO [5TIPTONVL TN161.00] CKT 1 | 5.2385 | 0.1365 | 36.5093 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5HOLDENB2 161.00] TO [1HOLDNG11 13.800] CKT 11 | 5.2379 | 0.1365 | 36.5192 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5HOLDENB2 161.00] TO [1HOLDNG12 13.800] CKT 12 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5HOLDENB2 161.00] TO [2HOLDEN 69.000] CKT 1 | 5.2384 | 0.1365 | 36.5103 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5HOLDENB2 161.00] TO [5HOLDENB1 161.00] CKT Z1 | 5.2383 | 0.1365 | 36.5115 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [2CLINTN 69.000] TO [2LINCLN 69.000] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [2CLINTN 69.000] TO [2GAINES 69.000] CKT 1 | 5.2384 | 0.1365 | 36.5098 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [2CLINTN 69.000] TO [2LEETON 69.000] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [2CLINTN 69.000] TO [2PIPER 69.000] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [2CLINTN 69.000] TO [2CLINTNLD 69.000] CKT 1 | 5.2385 | 0.1365 | 36.5097 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [7BLACKBERRY 345.00] TO [NEOSHO 7 345.00] CKT 1 | 5.238 | 0.1365 | 36.5092 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [7SPORTSMAN 345.00] TO [5SPORTSMAN 161.00] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [7SPORTSMAN 345.00] TO [5SPORTSMAN 161.00] CKT 2 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [7SPORTSMAN 345.00] TO [GRDA1 7 345.00] CKT 1 | 5.2384 | 0.1365 | 36.5102 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [7JASPER 345.00] TO [7MORGAN 345.00] CKT 1 | 5.2372 | 0.1365 | 36.5234 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [7JASPER 345.00] TO [5JASPER 161.00] CKT 1 | 5.2382 | 0.1365 | 36.5134 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5OSCEOKCTP 161.00] TO [5OSCEOLTP 161.00] CKT 1 | 5.2385 | 0.1365 | 36.508 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5OSCEOKCTP 161.00] TO [5OSCEOKC 161.00] CKT 1 | 5.2385 | 0.1365 | 36.5095 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5MINER 1 161.00] TO [5CHARLSTN 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5MINER 1 161.00] TO [5BULLION 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [5MINER 1 161.00] TO [5MINER 2 161.00] CKT Z | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [N MADRD5 161.00] TO [G17-202-TAP 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [N MADRD2 69.000] TO [2STJUDEW 69.000] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [N MADRD2 69.000] TO [2LILBRN 69.000] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [N MADRD2 69.000] TO [MALDEN 2 69.000] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [KENNETT5 161.00] TO [PARAGLD5 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5098 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [KENNETT5 161.00] TO [KENNETT2 69.000] TO [KEN X1 1 13.800] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [KENNETT5 161.00] TO [KENNETT2 69.000] TO [KEN X2 1 13.800] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SIKETAP5 161.00] TO [SIKE SW5 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SIKESTN5 161.00] TO [G17-202-TAP 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [IDALIA 5 161.00] TO [5ESSEX 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [IDALIA 5 161.00] TO [2IDALIA 69.000] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [IDALIA 5 161.00] TO [2IDALIA 69.000] CKT 2 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [IDALIA 5 161.00] TO [ASHRVL5 161.00] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [TRUMAN 5 161.00] TO [5LOSTVALY 161.00] CKT 1 | 5.2386 | 0.1365 | 36.5062 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [TRUMAN 5 161.00] TO [TRU123 1 13.800] CKT 1 | 5.2382 | 0.1365 | 36.5133 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [TRUMAN 5 161.00] TO [TRU456 1 13.800] CKT 1 | 5.2382 | 0.1365 | 36.5133 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [DELWARE4 138.00] TO [FARML 4 138.00] CKT 1 | 5.2384 | 0.1365 | 36.511 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [DELWARE7 345.00] TO [NEOSHO 7 345.00] CKT 1 | 5.2377 | 0.1365 | 36.5122 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [N.E.S.-7 345.00] TO [ONETA--7 345.00] CKT 1 | 5.2383 | 0.1365 | 36.5096 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [N.E.S.-7 345.00] TO [T.NO.--7 345.00] CKT 1 | 5.2385 | 0.1365 | 36.5097 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [N.E.S.-7 345.00] TO [NES3-1 22.000] CKT 1 | 5.2384 | 0.1365 | 36.5083 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WWRDEHV7 345.00] TO [TATONGA7 345.00] CKT 1 | 5.2377 | 0.1365 | 36.5172 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WWRDEHV7 345.00] TO [TATONGA7 345.00] CKT 2 | 5.2377 | 0.1365 | 36.5173 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WWRDEHV7 345.00] TO [G07621119-20345.00] CKT 1 | 5.2384 | 0.1365 | 36.5114 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WWRDEHV7 345.00] TO [GUTHRIE7 345.00] CKT 1 | 5.2384 | 0.1365 | 36.5104 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WWRDEHV7 345.00] TO [BECKHAM7 345.00] CKT 1 | 5.2368 | 0.1365 | 36.5163 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WWRDEHV7 345.00] TO [G16-003-TAP 345.00] CKT 1 | 5.2384 | 0.1365 | 36.5094 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WWRDEHV7 345.00] TO [G16-003-TAP 345.00] CKT 2 | 5.2384 | 0.1365 | 36.5094 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WWRDEHV7 345.00] TO [WWRDEHV4 138.00] TO [WWDEHV31 13.800] CKT 1 | 5.2384 | 0.1365 | 36.5092 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WWRDEHV7 345.00] TO [WWRDEHV4 138.00] TO [WWDEHV21 13.800] CKT 2 | 5.2384 | 0.1365 | 36.5086 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [DGRASSE7 345.00] TO [THISTLE7 345.00] CKT 1 | 5.2342 | 0.1365 | 36.5209 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [DGRASSE7 345.00] TO [THISTLE7 345.00] CKT 2 | 5.2342 | 0.1365 | 36.5208 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [DGRASSE4 138.00] TO [KNOBHIL4 138.00] CKT 1 | 5.2383 | 0.1365 | 36.5106 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [DGRASSE4 138.00] TO [ROSEVLY4 138.00] CKT 1 | 5.2383 | 0.1365 | 36.5106 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [DGRASSE4 138.00] TO [MOORLND4 138.00] CKT 1 | 5.2377 | 0.1365 | 36.5118 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WALKMYR2 69.000] TO [NORTH6T2 69.000] CKT 1 | 5.2384 | 0.1365 | 36.5105 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WALKMYR2 69.000] TO [WOODS 2 69.000] CKT 1 | 5.2384 | 0.1365 | 36.5104 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WALKMYR3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 5.2384 | 0.1365 | 36.5114 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SEWARD-3 115.00] TO [HASKELL3 115.00] CKT 1 | 5.2384 | 0.1365 | 36.5103 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SEWARD-3 115.00] TO [CMSSWRD2 69.000] TO [SEWARD 1 13.800] CKT 1 | 5.2384 | 0.1365 | 36.5104 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SPERVIL7 345.00] TO [POSTROCK7 345.00] CKT 1 | 5.2332 | 0.1365 | 36.4826 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SPERVIL7 345.00] TO [BUCKNER7 345.00] CKT 1 | 5.2306 | 0.1365 | 36.4959 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SPERVIL7 345.00] TO [IRONWOOD7 345.00] CKT 1 | 5.2385 | 0.1365 | 36.5045 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SPERVIL7 345.00] TO [SPRVL 3 115.00] TO [SPRVL-T 13.800] CKT 1 | 5.2385 | 0.1365 | 36.5082 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SPERVIL7 345.00] TO [SPEARVL6 230.00] TO [SPERTER1 13.800] CKT 1 | 5.2339 | 0.1365 | 36.5001 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HUGOTON3 115.00] TO [GRANTTP3 115.00] CKT 1 | 5.2383 | 0.1365 | 36.5113 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HUGOTON3 115.00] TO [ABBK 2 115.00] CKT 1 | 5.2384 | 0.1365 | 36.5106 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HUGOTON3 115.00] TO [HUGOTON2 69.000] TO [HUGOTON1 13.800] CKT 1 | 5.2383 | 0.1365 | 36.5112 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HARBNGR3 115.00] TO [HARBNGR7 345.00] TO [HARBNGR-T 13.800] CKT 1 | 5.2382 | 0.1365 | 36.5126 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EEC GT1 13.800] TO [DG TIE 1 4.1600] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EEC GT2 13.800] TO [EEC DG 1 4.1600] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC121 13.800] CKT 1 | 5.2323 | 0.1365 | 36.5112 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC341 13.800] CKT 1 | 5.2322 | 0.1365 | 36.5112 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC5 1 18.000] CKT 1 | 5.2246 | 0.1365 | 36.5146 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC6 1 18.000] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC7 1 18.000] CKT 1 | 5.2247 | 0.1365 | 36.5149 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EMPEC 7 345.00] TO [LANG 7 345.00] CKT 1 | 5.2351 | 0.1365 | 36.54 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EMPEC 7 345.00] TO [MORRIS 7 345.00] CKT 1 | 5.1561 | 0.1366 | 36.5773 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EMPEC 7 345.00] TO [READWF 7 345.00] CKT 1 | 5.2386 | 0.1365 | 36.5094 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [RENO 7 345.00] TO [G16-111-TAP 345.00] CKT 1 | 5.0634 | 0.1366 | 36.6262 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [RENO 7 345.00] TO [RENO 3 115.00] TO [RENO 1X1 14.400] CKT 1 | 5.238 | 0.1365 | 36.4752 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [RENO 7 345.00] TO [RENO 3 115.00] TO [RENO 2X1 14.400] CKT 1 | 5.2379 | 0.1365 | 36.4766 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUMMIT 7 345.00] TO [GEARY 7 345.00] CKT 1 | 5.2281 | 0.1368 | 36.8094 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUMMIT 7 345.00] TO [G16-111-TAP 345.00] CKT 1 | 5.0691 | 0.1368 | 36.7529 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUMMIT 7 345.00] TO [SUMMIT 6 230.00] TO [SUMMIT 1 14.400] CKT 1 | 5.0532 | 0.1367 | 36.6522 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SWISVAL7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 5.1951 | 0.1366 | 36.55 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [87TH 7 345.00] TO [STRANGR7 345.00] CKT 1 | 5.2379 | 0.1365 | 36.4878 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [87TH 7 345.00] TO [87TH 3 115.00] TO [87TH 1X1 13.800] CKT 1 | 5.2384 | 0.1365 | 36.5089 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [G17-009-TAP 345.00] TO [NEOSHO 7 345.00] CKT 1 | 5.2352 | 0.1365 | 36.5062 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GEN-2017-009345.00] TO [G17-009XFMR134.500] CKT 1 | 5.2384 | 0.1365 | 36.5107 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GEN-2017-009345.00] TO [G17-009XFMR234.500] CKT 1 | 5.2384 | 0.1365 | 36.5108 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CANEYRV7 345.00] TO [CANEYWF7 345.00] CKT 1 | 5.2384 | 0.1365 | 36.5108 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CANEYRV7 345.00] TO [LATHAMS7 345.00] CKT 1 | 5.2349 | 0.1365 | 36.5189 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [KINGMAN7 345.00] TO [BUFFALO7 345.00] CKT 1 | 5.2383 | 0.1365 | 36.5268 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NINN1WF7 345.00] TO [PRATTWF7 345.00] CKT 1 | 5.2391 | 0.1365 | 36.5002 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NINN1WF7 345.00] TO [N1 LV 1 34.500] TO [N1 WFTX1 13.800] CKT 1 | 5.2385 | 0.1365 | 36.5072 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BENTON 7 345.00] TO [ROSEHIL7 345.00] CKT 1 | 5.2269 | 0.1365 | 36.5367 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BENTON 7 345.00] TO [BENTON 4 138.00] TO [BENTN1 1 13.800] CKT 1 | 5.2384 | 0.1365 | 36.5123 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BENTON 7 345.00] TO [BENTON 4 138.00] TO [BENTN2 1 13.800] CKT 1 | 5.2384 | 0.1365 | 36.5123 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 1 | 5.2378 | 0.1365 | 36.5119 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 2 | 5.2378 | 0.1365 | 36.5119 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WICHITA7 345.00] TO [EVANS N4 138.00] TO [WICH11 1 13.800] CKT 1 | 5.2385 | 0.1365 | 36.4989 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WICHITA7 345.00] TO [EVANS N4 138.00] TO [WICH12 1 13.800] CKT 1 | 5.2385 | 0.1365 | 36.4964 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WOLFCRK7 345.00] TO [WCGS U1 25.000] CKT 1 | 5.2354 | 0.1365 | 36.4665 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WOLFCRK7 345.00] TO [ROSEHIL7 345.00] CKT 1 | 5.2361 | 0.1365 | 36.5191 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WOLFCRK7 345.00] TO [WOLFCRK2 69.000] TO [WOLFCRK1 17.000] CKT 1 | 5.2383 | 0.1365 | 36.512 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [VIOLA 7 345.00] TO [RENFROW7 345.00] CKT 1 | 5.224 | 0.1366 | 36.5559 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [VIOLA 7 345.00] TO [G16-153-TAP 345.00] CKT 1 | 5.2388 | 0.1365 | 36.5155 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WAVERLY7 345.00] TO [WAVERTX7 345.00] CKT 1 | 5.2386 | 0.1365 | 36.5074 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EXPEDITION7 345.00] TO [GEN-2014-001345.00] CKT 1 | 5.2387 | 0.1365 | 36.5133 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [N345 1 1 13.800] TO [NEOSHO 7 345.00] TO [NEOSHO 4 138.00] CKT 1 | 5.2384 | 0.1365 | 36.509 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [N345 2 1 13.800] TO [NEOSHO 7 345.00] TO [NEOSHO 5 161.00] CKT 1 | 5.2383 | 0.1365 | 36.5103 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SWISVAL6 230.00] TO [AUBURN 6 230.00] CKT 1 | 5.2209 | 0.1365 | 36.523 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SWISVAL6 230.00] TO [LAWHILL6 230.00] CKT 1 | 5.2273 | 0.1365 | 36.5303 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SWISVAL6 230.00] TO [TECHILL6 230.00] CKT 1 | 5.2372 | 0.1365 | 36.5394 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SWISVAL6 230.00] TO [MORRIS 6 230.00] CKT 1 | 5.2106 | 0.1365 | 36.5475 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NMANHT6 230.00] TO [EMANHAT6 230.00] CKT 1 | 5.2292 | 0.1365 | 36.5091 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NMANHT6 230.00] TO [NMANHT3 115.00] TO [NMANHX1 14.400] CKT 1 | 5.2306 | 0.1365 | 36.5302 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LITCH 5 161.00] TO [ASB349 5 161.00] CKT 1 | 5.2383 | 0.1365 | 36.5097 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [MARMTNW5 161.00] TO [MARMTNE5 161.00] CKT Z1 | 5.2385 | 0.1365 | 36.5093 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [MARMTNW5 161.00] TO [MARMATN2 69.000] TO [MARMATN1 13.200] CKT 1 | 5.2384 | 0.1365 | 36.5095 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [FRANKLIN5 161.00] TO [G17-005-TAP 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5094 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [FRANKLIN5 161.00] TO [FRANKLIN2 69.000] TO [FRANKLIN1 12.470] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRESWLN4 138.00] TO [MIDLTNT4 138.00] CKT 1 | 5.2377 | 0.1365 | 36.5114 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRESWLN4 138.00] TO [SLATECRK4 138.00] CKT 1 | 5.2381 | 0.1365 | 36.5133 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRESWLN4 138.00] TO [CRESWLN2 69.000] TO [CRESW1 1 13.200] CKT 1 | 5.2385 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRESWLN4 138.00] TO [CRESWLS2 69.000] TO [CRESW2 1 13.200] CKT 1 | 5.2384 | 0.1365 | 36.5108 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [OXFORD 4 138.00] TO [SUMNER 4 138.00] CKT 1 | 5.2374 | 0.1365 | 36.5114 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [TIMBJCT4 138.00] TO [SUMNER 4 138.00] CKT 1 | 5.2383 | 0.1365 | 36.5126 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [TIOGA 4 138.00] TO [TIOGA 2 69.000] TO [TIOGA 1 13.200] CKT 1 | 5.2383 | 0.1365 | 36.509 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [OTTRCRK4 138.00] TO [BUTLER 4 138.00] CKT 1 | 5.2382 | 0.1365 | 36.5116 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [OTTRCRK4 138.00] TO [OTTRCRK3 115.00] TO [OTTRX1 1 13.800] CKT 1 | 5.2353 | 0.1365 | 36.516 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ALTOONA4 138.00] TO [G17-022-TAP 138.00] CKT 1 | 5.2382 | 0.1365 | 36.513 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEPARSN4 138.00] TO [G17-022-TAP 138.00] CKT 1 | 5.2383 | 0.1365 | 36.5111 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [TAYLOR 4 138.00] TO [MONTGOM4 138.00] CKT 1 | 5.2383 | 0.1365 | 36.5091 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BENTLEY4 138.00] TO [HALSTD 4 138.00] CKT 1 | 5.2321 | 0.1365 | 36.5326 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BENTLEY4 138.00] TO [WWUPLNT4 138.00] CKT 1 | 5.2384 | 0.1365 | 36.5097 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEOSHOS4 138.00] TO [TV1MNDV4 138.00] CKT 1 | 5.2384 | 0.1365 | 36.5101 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEOSHON4 138.00] TO [NEOSHON2 69.000] TO [NEC U3 12.000] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CHISHLM4 138.00] TO [PARKCTY4 138.00] CKT 1 | 5.2382 | 0.1365 | 36.5111 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CHISHLM4 138.00] TO [17TH 4 138.00] CKT 1 | 5.2379 | 0.1365 | 36.5117 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CHISHLM4 138.00] TO [CHISHLM2 69.000] TO [CHISOLM1 13.200] CKT 1 | 5.2382 | 0.1365 | 36.5131 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EVANS S4 138.00] TO [EVANS N4 138.00] CKT Z1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EVANS S4 138.00] TO [EVANS N4 138.00] CKT Z2 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [FARBER 4 138.00] TO [ELPASOE4 138.00] CKT 1 | 5.2382 | 0.1365 | 36.5116 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GILL 4 138.00] TO [GILL W 4 138.00] CKT Z1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GILL 4 138.00] TO [GILL S 4 138.00] CKT Z1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LAKERDG4 138.00] TO [HOOVERN4 138.00] CKT 1 | 5.2373 | 0.1365 | 36.5167 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [MAIZE 4 138.00] TO [EVANS N4 138.00] CKT 1 | 5.2365 | 0.1365 | 36.519 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SC10BEL4 138.00] TO [SUMNER 4 138.00] CKT 1 | 5.2381 | 0.1365 | 36.5131 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SG12COL4 138.00] TO [EVANS N4 138.00] CKT 1 | 5.232 | 0.1365 | 36.5351 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [45TH ST4 138.00] TO [COWSKIN4 138.00] CKT 1 | 5.2372 | 0.1365 | 36.5169 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [VIOLA 4 138.00] TO [SUMNER 4 138.00] CKT 1 | 5.238 | 0.1365 | 36.5113 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [AEC 3 115.00] TO [G17-120-TAP 115.00] CKT 1 | 2.8067 | 0.1445 | 44.4506 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EABILEN3 115.00] TO [CHAPMAN3 115.00] CKT 1 | 2.8522 | 0.1443 | 44.333 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NORTHST3 115.00] TO [SALINA 3 115.00] CKT 1 | 5.08 | 0.1369 | 36.8709 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NORTHVW3 115.00] TO [G17-120-TAP 115.00] CKT 1 | 2.6085 | 0.146 | 46.0028 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUMMIT 3 115.00] TO [MENTOR 3 115.00] CKT 1 | 5.2288 | 0.1366 | 36.5526 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUMMIT 3 115.00] TO [SO GATE3 115.00] CKT 1 | 5.2362 | 0.1365 | 36.5365 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUMMIT 3 115.00] TO [SUMMIT 6 230.00] TO [SUMIT2 1 13.800] CKT 1 | 5.0532 | 0.1369 | 36.9082 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUMMIT 3 115.00] TO [SUMMIT 6 230.00] TO [SUMIT3 1 13.800] CKT 1 | 5.0499 | 0.1369 | 36.9176 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [TIMBJCT2 69.000] TO [AKRON 2 69.000] CKT 1 | 5.2384 | 0.1365 | 36.5094 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [TIMBJCT2 69.000] TO [UDALL 2 69.000] CKT 1 | 5.2384 | 0.1365 | 36.5101 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [TIMBJCT2 69.000] TO [WINFLD 2 69.000] CKT 1 | 5.2382 | 0.1365 | 36.5151 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ALTOO E2 69.000] TO [NEODJCT2 69.000] CKT 1 | 5.2384 | 0.1365 | 36.5097 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ALTOO E2 69.000] TO [RA5HIPR2 69.000] CKT Z1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ALTOO W2 69.000] TO [STUDBKR2 69.000] CKT 1 | 5.2384 | 0.1365 | 36.5098 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LITCH N2 69.000] TO [AQUARS 2 69.000] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LITCH N2 69.000] TO [PITNAC 2 69.000] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LITCH S2 69.000] TO [ROUSE 2 69.000] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LITCH S2 69.000] TO [SOPITT 2 69.000] CKT 1 | 5.2384 | 0.1365 | 36.5101 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEOSHOS2 69.000] TO [BAKER 2 69.000] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEOSHOS2 69.000] TO [ORDNJCT2 69.000] CKT 1 | 5.2384 | 0.1365 | 36.5096 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEOSHOS2 69.000] TO [CRAWFOR2 69.000] CKT 1 | 5.2384 | 0.1365 | 36.5102 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEOSHOS2 69.000] TO [NEOSHON2 69.000] CKT Z1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [K1 LV 1 34.500] TO [K1 CLCT1 34.500] CKT 1 | 5.2385 | 0.1365 | 36.5064 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [K2 LV 1 34.500] TO [K2 CLCT1 34.500] CKT 1 | 5.2385 | 0.1365 | 36.5067 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [MILAN_GOAB 138.00] TO [CLDWELL4 138.00] CKT 1 | 5.2384 | 0.1365 | 36.5106 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [MILAN_GOAB 138.00] TO [MILAN 4 138.00] CKT 1 | 5.2384 | 0.1365 | 36.5098 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CONWAY 138.00] TO [MILANTP4 138.00] CKT 1 | 5.2384 | 0.1365 | 36.5107 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [MRWYP16 230.00] TO [MRWYP26 230.00] CKT 1 | 5.239 | 0.1365 | 36.5337 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [MRWYP16 230.00] TO [MRWYG11 34.500] TO [MRWYP1T1 13.800] CKT 1 | 5.2392 | 0.1365 | 36.5277 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [FLATRDG4 138.00] TO [FLATRWD4 138.00] CKT 1 | 5.2378 | 0.1365 | 36.5077 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [FLATRDG4 138.00] TO [HARPER 4 138.00] CKT 1 | 5.2382 | 0.1365 | 36.5142 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [FLATRDG4 138.00] TO [BARBER 4 138.00] CKT 1 | 5.2372 | 0.1365 | 36.5128 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ELMCREK6 230.00] TO [ELMCREEK7 345.00] TO [ELMCREEK1 13.800] CKT 1 | 5.224 | 0.1366 | 36.5622 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAYNE3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 5.2383 | 0.1365 | 36.5102 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [KISMET 3 115.00] TO [CUDAHY 3 115.00] CKT 1 | 5.2375 | 0.1365 | 36.5116 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CMRIVTP3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 5.2383 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CONCRD6 230.00] TO [CONCORD3 115.00] TO [CONCOD-T 13.800] CKT 1 | 5.2168 | 0.1365 | 36.5391 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [E-LIBER3 115.00] TO [TXPHSF 3115.00] CKT 1 | 5.2383 | 0.1365 | 36.5098 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [E-LIBER3 115.00] TO [E-PINE 3 115.00] CKT 1 | 5.2383 | 0.1365 | 36.5112 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [E-LIBER3 115.00] TO [NATBEEF3 115.00] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [E-LIBER3 115.00] TO [E-LIBER1 34.500] TO [ELIB-T 2.4000] CKT 1 | 5.2383 | 0.1365 | 36.5112 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NLIB 3 115.00] TO [W-LIBER3 115.00] CKT 1 | 5.2382 | 0.1365 | 36.5116 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NLIB 3 115.00] TO [NATBEEF3 115.00] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NLIB 3 115.00] TO [NLIB 1 34.500] TO [N-LIB-T 13.800] CKT 1 | 5.2383 | 0.1365 | 36.5112 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [N-CIMRN3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 5.2384 | 0.1365 | 36.5101 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CIM-PLT 13.800] TO [CIM-PLT3 115.00] CKT 1 | 5.238 | 0.1365 | 36.5177 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [THISTLE7 345.00] CKT 1 | 5.2368 | 0.1365 | 36.5436 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [THISTLE7 345.00] CKT 2 | 5.2368 | 0.1365 | 36.5436 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [THISTLE T1 13.800] TO [THISTLE7 345.00] TO [THISTLE4 138.00] CKT 1 | 5.2385 | 0.1365 | 36.5085 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [TRANSFORMER 345.00] TO [SUB34.5KVB 34.500] TO [TERTIARYBUS 19.900] CKT 1 | 5.2391 | 0.1365 | 36.4969 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GEN-2011-008345.00] TO [G-2011-008-1345.00] CKT 1 | 5.2389 | 0.1365 | 36.5026 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GEN-2011-008345.00] TO [G-2011-008-2345.00] CKT 1 | 5.2387 | 0.1365 | 36.5065 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GEN-2011-008345.00] TO [G-2011-008-3345.00] CKT 1 | 5.2391 | 0.1365 | 36.5033 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [MULLNCR7 345.00] TO [HOLT 7 345.00] CKT 1 | 5.2372 | 0.1365 | 36.5303 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [PECULR 7 345.00] TO [PHILL 7 345.00] CKT 1 | 5.2367 | 0.1365 | 36.5193 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [PECULR 7 345.00] TO [PECULR 5 161.00] TO [PECULRT 13.800] CKT 11 | 5.2383 | 0.1365 | 36.5119 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ST JOE 7 345.00] TO [G17-183-TAP 345.00] CKT 1 | 5.2382 | 0.1365 | 36.5151 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ARCHIE 5 161.00] TO [G17-108-TAP 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5096 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WINDSR 5 161.00] TO [5SEDALA 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HSNVL 5 161.00] TO [5SHARSNV 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5098 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HSNVL 5 161.00] TO [PHILL 5 161.00] CKT 1 | 5.2383 | 0.1365 | 36.5121 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HSNVL 5 161.00] TO [HSNVL 2 69.000] CKT 1 | 5.2384 | 0.1365 | 36.5101 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HSNVL 5 161.00] TO [HSNVL 2 69.000] CKT 2 | 5.2384 | 0.1365 | 36.5101 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ADRIAN 5 161.00] TO [5BUTLER 161.00] CKT 1 | 5.2385 | 0.1365 | 36.5068 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CLINTON5 161.00] TO [CLNTN N2 69.000] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CLINTON5 161.00] TO [CLNTN S2 69.000] CKT 2 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ST JOE 5 161.00] TO [ST JOE_CAP5 161.00] CKT R | 5.2381 | 0.1365 | 36.5177 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ST JOE 5 161.00] TO [COOK 5 161.00] CKT 1 | 5.2383 | 0.1365 | 36.5123 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ST JOE 5 161.00] TO [WOODBIN5 161.00] CKT 1 | 5.2383 | 0.1365 | 36.5115 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ST JOE 5 161.00] TO [AVENUECTY 5 161.00] CKT 1 | 5.2383 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP#1 13.800] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP#2 13.800] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP#3 13.800] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP 2 69.000] CKT 1 | 5.2384 | 0.1365 | 36.5103 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S.HARP 5 161.00] TO [PECULRS5 161.00] CKT 1 | 5.2383 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EASTOWN7 345.00] TO [EASTOWN5 161.00] TO [EASTOWN1 13.800] CKT 11 | 5.2383 | 0.1365 | 36.5109 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [KETCHEM7 345.00] TO [SIBLEY 7 345.00] CKT 1 | 5.2366 | 0.1365 | 36.5425 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [KETCHEM7 345.00] TO [OSBORN7 345.00] CKT 1 | 5.2382 | 0.1365 | 36.5143 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ROCKCK7 345.00] TO [HOLT 7 345.00] CKT 1 | 5.2384 | 0.1365 | 36.5093 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ROCKCK_T1_1 34.500] TO [ROCKCK_P1_1 34.500] CKT 1 | 5.2384 | 0.1365 | 36.5096 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ROCKCK_T2_1 34.500] TO [ROCKCK_P2_1 34.500] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HOLT_REACT7 345.00] TO [HOLT 7 345.00] CKT Z1 | 5.2385 | 0.1365 | 36.5094 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [OUTLAW 345.00] TO [OUTLAW_T2_1 34.500] TO [OUTLAW_TR2_113.800] CKT 1 | 5.2385 | 0.1365 | 36.509 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [OUTLAW 345.00] TO [OUTLAW_T1_1 34.500] TO [OUTLAW_TR1_113.800] CKT 1 | 5.2385 | 0.1365 | 36.5086 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WGARDNR5 161.00] TO [W.GRDNR7 345.00] TO [WGAR T11 13.800] CKT 11 | 5.2375 | 0.1365 | 36.5148 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [STILWEL7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 5.2331 | 0.1365 | 36.5085 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [STILWEL5 161.00] TO [G17-108-TAP 161.00] CKT 1 | 5.2382 | 0.1365 | 36.5103 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTH 7 345.00] TO [SIBLEY 7 345.00] CKT 1 | 5.2381 | 0.1365 | 36.5134 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTH 7 345.00] TO [HAWTHN5 161.00] TO [HAWT T20 13.800] CKT 20 | 5.2382 | 0.1365 | 36.5138 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTH 7 345.00] TO [HAWTHN5 161.00] TO [HAWT T22 13.800] CKT 22 | 5.2383 | 0.1365 | 36.5127 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTHS5 161.00] TO [HAW G9 1 13.800] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTHS5 161.00] TO [LEEDS 5 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5108 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTHS5 161.00] TO [LEEDS 5 161.00] CKT 2 | 5.2384 | 0.1365 | 36.5108 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTH_B2_1 13.200] CKT 1 | 5.2386 | 0.1365 | 36.5067 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTHS5 161.00] TO [BRMGHAM5 161.00] CKT 1 | 5.2385 | 0.1365 | 36.508 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHS_G65 161.00] CKT Z1 | 5.2385 | 0.1365 | 36.5094 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHS_XF5 161.00] CKT Z2 | 5.2384 | 0.1365 | 36.5098 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHN5 161.00] CKT @1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHN5 161.00] CKT @2 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRAIG 7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 5.2375 | 0.1365 | 36.5277 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRAIG 5 161.00] TO [CRAIG_CAP 5 161.00] CKT R | 5.238 | 0.1365 | 36.5209 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRAIG 5 161.00] TO [PFLUMM 5 161.00] CKT 1 | 5.2382 | 0.1365 | 36.5095 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRAIG 5 161.00] TO [LENEXA 5 161.00] CKT 1 | 5.2383 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRAIG 5 161.00] TO [LENEXA 5 161.00] CKT 2 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRAIG 5 161.00] TO [COLLEGE5 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5083 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NASHUA 7 345.00] TO [G17-183-TAP 345.00] CKT 1 | 5.2373 | 0.1365 | 36.5335 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LACYGNE7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 5.2327 | 0.1366 | 36.5567 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LACYGNE7 345.00] TO [G17-209-TAP 345.00] CKT 1 | 5.2383 | 0.1365 | 36.5116 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [IATAN 7 345.00] TO [STRANGR7 345.00] CKT 1 | 5.2303 | 0.1365 | 36.5331 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [IATAN 7 345.00] TO [STRANGR7 345.00] CKT 2 | 5.2313 | 0.1365 | 36.5324 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [IATAN 7 345.00] TO [IAT G1 1 24.000] CKT 1 | 5.2315 | 0.1365 | 36.5334 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [IATAN 7 345.00] TO [IAT G2 1 24.500] CKT 1 | 5.2271 | 0.1366 | 36.598 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [IATAN 7 345.00] TO [IATAN5 161.00] TO [IATAN 11 14.400] CKT 11 | 5.2382 | 0.1365 | 36.5097 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HICKMAN5 161.00] TO [STHTOWN5 161.00] CKT 1 | 5.2383 | 0.1365 | 36.5113 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BLUMILS5 161.00] TO [BLUVLY-161 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5097 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NASHUA-5 161.00] TO [NASHUA 5 161.00] CKT Z1 | 5.2384 | 0.1365 | 36.5108 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NASHUA-5 161.00] TO [RNRIDGE5 161.00] CKT 1 | 5.2382 | 0.1365 | 36.5138 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NASHUA-5 161.00] TO [SHOLCRK5 161.00] CKT 1 | 5.2382 | 0.1365 | 36.5138 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CEDRCRK5 161.00] TO [SHWNMSN5 161.00] CKT 1 | 5.2382 | 0.1365 | 36.5102 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ANTIOCH5 161.00] TO [OXFORD 5 161.00] CKT 1 | 5.238 | 0.1365 | 36.5184 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [REDEL 5 161.00] TO [MARTCIT5 161.00] CKT 1 | 5.2383 | 0.1365 | 36.5105 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BUCYRUS5 161.00] TO [NLOUISB5 161.00] CKT 1 | 5.2385 | 0.1365 | 36.5088 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BUCYRUS5 161.00] TO [WAGSTAF5 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5109 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [PLSTVAL5 161.00] TO [SEOTTWA5 161.00] CKT 1 | 5.2382 | 0.1365 | 36.5105 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [PLSTVAL5 161.00] TO [ASG-2018-010161.00] CKT 1 | 5.2381 | 0.1365 | 36.5136 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [PLSTVAL5 161.00] TO [PLSTVAL1 34.500] TO [PLSTVL2_TER17.6210] CKT 2 | 5.2385 | 0.1365 | 36.5091 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LAKCTYJ2 69.000] TO [LAKCTY 2 69.000] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 1 13.800] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 2 13.800] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 3 13.800] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 4 13.800] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LACKMAN5 161.00] TO [SPRGHL 5 161.00] CKT 1 | 5.2381 | 0.1365 | 36.5103 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BNSF 5 161.00] TO [MOONLT 5 161.00] CKT 1 | 5.2381 | 0.1365 | 36.5134 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WGARDNR1 34.500] TO [BALDWINCTY1 34.500] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LACYGNE11_7 345.00] TO [LAC11_AQC1 13.800] TO [LAC11_TER1 13.800] CKT 11 | 5.2385 | 0.1365 | 36.5086 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LACYGNE22_7 345.00] TO [LAC22_AQC1 13.800] TO [LAC22_TER1 13.800] CKT 22 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LACYGNE2 69.000] TO [LAC_LAKE_2 69.000] CKT 1 | 5.2384 | 0.1365 | 36.5096 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LAC3_STAR7 345.00] TO [LAC3_X1 6.9000] CKT X | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LAC3_STAR7 345.00] TO [LAC3_Y1 6.9000] CKT Y | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LAC3_STAR7 345.00] TO [LAC3_Z1 3.9800] CKT Z | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LAC8_STAR7 345.00] TO [LAC8_X1 6.9000] CKT X | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LAC8_STAR7 345.00] TO [LAC8_Y1 6.9000] CKT Y | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [LAC8_STAR7 345.00] TO [LAC8_Z1 4.0000] CKT Z | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [RIV4525 161.00] TO [ORO110 5 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5103 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [RIV4525 161.00] TO [STL439 5 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [RIV4525 161.00] TO [RIV452T 5 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5107 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [RIV4525 161.00] TO [BAX488 5 161.00] CKT 1 | 5.2385 | 0.1365 | 36.5094 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [RIV4525 161.00] TO [RIV167 2 69.000] TO [RIV452 1 12.500] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CJ 366 5 161.00] TO [ASB349 5 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CAR395 5 161.00] TO [CARTHAG5 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [FIR417 5 161.00] TO [ORO110 5 161.00] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [PUR421 5 161.00] TO [ASB349 5 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [A1G349 1 13.800] TO [ASB349 5 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5098 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [A2G349 1 13.800] TO [ASB349 5 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB K 69.000] TO [SUB R 69.000] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB H 69.000] TO [COURTNY2 69.000] CKT 1 | 5.2384 | 0.1365 | 36.5102 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB H 69.000] TO [SUGRCK_TP_E269.000] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB H 69.000] TO [SUB H-13B1 13.800] CKT H1 | 5.2385 | 0.1365 | 36.5092 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB H 69.000] TO [SUB H-13B2 13.800] CKT H2 | 5.2383 | 0.1365 | 36.5104 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BLUVLY 69.000] TO [BLUVLY-161 161.00] CKT 1 | 5.2383 | 0.1365 | 36.5103 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BLUVLY 69.000] TO [BLUVLY-161 161.00] CKT 2 | 5.2383 | 0.1365 | 36.5103 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ECKLES-161 161.00] TO [5LEVASY 161.00] CKT 1 | 5.2382 | 0.1365 | 36.512 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ECKLES-161 161.00] TO [5MOCITYB1 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5104 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [ECKLES-161 161.00] TO [SIBLEYPL 161.00] CKT 1 | 5.2383 | 0.1365 | 36.5104 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB J 69.000] TO [SUB J-13B1 13.800] CKT J1 | 5.2385 | 0.1365 | 36.5094 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB J 69.000] TO [SUB J-13B2 13.800] CKT J2 | 5.2385 | 0.1365 | 36.5092 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB M-161 161.00] TO [BLUVLY-161 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5096 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB M 69.000] TO [SHRNKRD 69.000] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [SUB P 69.000] TO [SUB I 69.000] CKT 1 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [G16-046-TAP 345.00] TO [IRONWOOD7 345.00] CKT 1 | 5.2379 | 0.1365 | 36.5155 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [G16-046-TAP 345.00] TO [GEN-2016-046345.00] CKT 1 | 5.2369 | 0.1365 | 36.4879 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GEN-2017-004345.00] TO [G17-004XFMR134.500] CKT 1 | 5.2387 | 0.1365 | 36.5487 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [G17-004-TAP 345.00] TO [ELMCREEK7 345.00] CKT 1 | 5.2247 | 0.1366 | 36.6309 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GEN-2017-018345.00] TO [THISTLE7 345.00] CKT 1 | 5.2393 | 0.1365 | 36.4922 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [G17-018XFMR134.500] TO [G17-018-GSU134.500] CKT 1 | 5.2389 | 0.1365 | 36.5008 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [G17-018XFMR234.500] TO [G17-018-GSU234.500] CKT 1 | 5.2389 | 0.1365 | 36.5008 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GEN-2017-068138.00] TO [EVANS N4 138.00] CKT 1 | 5.2386 | 0.1365 | 36.5061 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [G17-068XFMR134.500] TO [G17-068-GSU134.500] CKT 1 | 5.2386 | 0.1365 | 36.5057 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [GEN-2017-082161.00] TO [ASB349 5 161.00] CKT 1 | 5.2384 | 0.1365 | 36.5101 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [G17-082XFMR134.500] TO [G17-082-GSU134.500] CKT 1 | 5.2384 | 0.1365 | 36.5101 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [COOPER 3 345.00] TO [ATCHSN 3 345.00] CKT 1 | 5.2383 | 0.1365 | 36.5085 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [COOPER 3 345.00] TO [COOPER1G 22.000] CKT 1 | 5.2371 | 0.1365 | 36.524 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [COOPER 3 345.00] TO [MONOLITH 3 345.00] CKT 1 | 5.2388 | 0.1365 | 36.5029 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [COOPER 3 345.00] TO [COOPER 5 161.00] TO [COOPER T2 913.800] CKT 1 | 5.2383 | 0.1365 | 36.5104 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [COOPER 3 345.00] TO [COOPER 5 161.00] TO [COOPER T5 913.800] CKT 1 | 5.2383 | 0.1365 | 36.5104 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEBCTY1G 18.000] TO [NC1GA1X9 4.2000] TO [NC1GA1Y9 4.2000] CKT 1 | 5.2384 | 0.1365 | 36.5102 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEBCTY1G 18.000] TO [NC1GA2X9 4.2000] TO [NC1GA2Y9 4.2000] CKT 1 | 5.2384 | 0.1365 | 36.5102 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEBCTY2G 23.000] TO [NC2GA1X9 4.2000] TO [NC2GA1Y9 4.2000] CKT 1 | 5.2384 | 0.1365 | 36.5101 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [NEBCTY2G 23.000] TO [NC2GA2X9 13.800] TO [NC2GA2Y9 13.800] CKT 1 | 5.2384 | 0.1365 | 36.5106 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S3456 3 345.00] TO [CBLUFFS3 345.00] CKT 1 | 5.2383 | 0.1365 | 36.511 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S3456 3 345.00] TO [S3455 3 345.00] CKT 1 | 5.2384 | 0.1365 | 36.5105 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S3456 3 345.00] TO [S3459 3 345.00] CKT 1 | 5.2385 | 0.1365 | 36.5094 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S3456 3 345.00] TO [S1206 5 161.00] TO [S3456T49 13.800] CKT 1 | 5.2384 | 0.1365 | 36.5102 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S3458 3 345.00] TO [HOLT 7 345.00] CKT 1 | 5.2382 | 0.1365 | 36.5081 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S3740 3 345.00] TO [CASS 1G 15.000] CKT 1 | 5.2384 | 0.1365 | 36.5084 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S3740 3 345.00] TO [CASS 2G 15.000] CKT 1 | 5.2384 | 0.1365 | 36.5084 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S3740 3 345.00] TO [S3454 3 345.00] CKT 1 | 5.2385 | 0.1365 | 36.5095 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S3740 3 345.00] TO [S3455 3 345.00] CKT 1 | 5.2384 | 0.1365 | 36.5097 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [S3740 3 345.00] TO [GEN-2018-033345.00] CKT 1 | 5.2384 | 0.1365 | 36.5099 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [103&ROKEBY3 345.00] TO [MOORE 3 345.00] CKT 1 | 5.2382 | 0.1365 | 36.5114 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [103&ROKEBY3 345.00] TO [WAGENER 3 345.00] CKT 1 | 5.2383 | 0.1365 | 36.5107 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [7SPORTSMAN 345.00] TO [5SPORTSMAN 161.00] CKT 2 | 5.2384 | 0.1365 | 36.5102 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [IDALIA 5 161.00] TO [2IDALIA 69.000] CKT 2 | 5.2384 | 0.1365 | 36.51 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WWRDEHV7 345.00] TO [TATONGA7 345.00] CKT 2 | 5.2348 | 0.1365 | 36.5425 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WWRDEHV7 345.00] TO [G16-003-TAP 345.00] CKT 2 | 5.2377 | 0.1365 | 36.5175 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [DGRASSE7 345.00] TO [THISTLE7 345.00] CKT 2 | 5.2169 | 0.1366 | 36.5768 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 2 | 5.2245 | 0.1366 | 36.6214 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [EVANS S4 138.00] TO [EVANS N4 138.00] CKT Z2 | 5.2346 | 0.1365 | 36.5342 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [THISTLE7 345.00] CKT 2 | 5.2298 | 0.1367 | 36.6786 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HSNVL 5 161.00] TO [HSNVL 2 69.000] CKT 2 | 5.2384 | 0.1365 | 36.5107 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTHS5 161.00] TO [LEEDS 5 161.00] CKT 2 | 5.2382 | 0.1365 | 36.5136 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHN5 161.00] CKT @2 | 5.2383 | 0.1365 | 36.5138 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [CRAIG 5 161.00] TO [LENEXA 5 161.00] CKT 2 | 5.2379 | 0.1365 | 36.5091 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [IATAN 7 345.00] TO [STRANGR7 345.00] CKT 2 | 5.1872 | 0.1366 | 36.6245 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-013 | Abilene Energy Center-Northview 115kV Line | OPEN LINE FROM [BLUVLY 69.000] TO [BLUVLY-161 161.00] CKT 2 | 5.2381 | 0.1365 | 36.5112 | 77.4 | 91.8 | FAIL | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [O.K.U.-7 345.00] TO [L.E.S.-7 345.00] CKT 1 | 5.1458 | 4.9576 | 4857.5594 | 126 | 143.8 | FAIL | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [O.K.U.-7 345.00] TO [L.E.S.-7 345.00] CKT 1 | 5.1458 | 4.9576 | 4857.5594 | 126 | 143.8 | FAIL | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [BORDER 7345.00] TO [TUCO_INT 7345.00] CKT 1 | 9.8537 | 4.1941 | 4094.0999 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [BORDER 7345.00] TO [TUCO_INT 7345.00] CKT 1 | 9.8537 | 4.1941 | 4094.0999 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_TR1 113.200] TO [TUCO_INT 7345.00] TO [TUCO_INT 6230.00] CKT 1 | 9.9275 | 4.3422 | 4242.1635 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_TR1 113.200] TO [TUCO_INT 7345.00] TO [TUCO_INT 6230.00] CKT 1 | 9.9275 | 4.3422 | 4242.1635 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_TR2 113.200] TO [TUCO_INT 7345.00] TO [TUCO_INT 6230.00] CKT 2 | 9.9756 | 4.3499 | 4249.8921 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_TR2 113.200] TO [TUCO_INT 7345.00] TO [TUCO_INT 6230.00] CKT 2 | 9.9756 | 4.3499 | 4249.8921 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 7345.00] TO [YOAKUM_345 345.00] CKT 1 | 9.8675 | 4.4277 | 4327.6662 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 7345.00] TO [YOAKUM_345 345.00] CKT 1 | 9.8675 | 4.4277 | 4327.6662 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [O.K.U.-7 345.00] TO [G18-015-TAP 345.00] CKT 1 | 5.5096 | 5.0721 | 4972.0694 | 126 | 143.8 | FAIL | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [O.K.U.-7 345.00] TO [G18-015-TAP 345.00] CKT 1 | 5.5096 | 5.0721 | 4972.0694 | 126 | 143.8 | FAIL | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [L.E.S.-7 345.00] TO [G16-091-TAP 345.00] CKT 1 | 9.4978 | 4.3997 | 4299.7183 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [L.E.S.-7 345.00] TO [G16-091-TAP 345.00] CKT 1 | 9.4978 | 4.3997 | 4299.7183 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [L.E.S.-7 345.00] TO [G17-171-TAP 345.00] CKT 1 | 9.8899 | 4.4849 | 4384.8574 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [L.E.S.-7 345.00] TO [G17-171-TAP 345.00] CKT 1 | 9.8899 | 4.4849 | 4384.8574 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [BORDER 7345.00] TO [BECKHAM7 345.00] CKT 1 | 9.8531 | 4.215 | 4114.9752 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [BORDER 7345.00] TO [BECKHAM7 345.00] CKT 1 | 9.8531 | 4.215 | 4114.9752 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 7345.00] TO [G17-151TAP 345.00] CKT 1 | 4.3902 | 4.9232 | 4823.171 | 126 | 143.8 | FAIL | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 7345.00] TO [G17-151TAP 345.00] CKT 1 | 4.3902 | 4.9232 | 4823.171 | 126 | 143.8 | FAIL | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | Base | 9.7073 | 4.38 | 4280.0204 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | Base | 9.7073 | 4.38 | 4280.0204 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [O.K.U.-7 345.00] TO [L.E.S.-7 345.00] CKT 1 | 4.7385 | 5.264 | 5164.005 | 126 | 143.8 | FAIL | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [O.K.U.-7 345.00] TO [L.E.S.-7 345.00] CKT 1 | 4.7385 | 5.264 | 5164.005 | 126 | 143.8 | FAIL | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [O.K.U.-7 345.00] TO [OKLAUN HVDC7345.00] CKT 1 | 9.7346 | 4.2097 | 4109.6961 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [O.K.U.-7 345.00] TO [OKLAUN HVDC7345.00] CKT 1 | 9.7346 | 4.2097 | 4109.6961 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [O.K.U.-7 345.00] TO [GEN-2017-033345.00] CKT 1 | 9.7195 | 4.4021 | 4302.1396 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [O.K.U.-7 345.00] TO [GEN-2017-033345.00] CKT 1 | 9.7195 | 4.4021 | 4302.1396 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [BORDER 7345.00] TO [TUCO_INT 7345.00] CKT 1 | 9.3598 | 4.1807 | 4080.7287 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [BORDER 7345.00] TO [TUCO_INT 7345.00] CKT 1 | 9.3598 | 4.1807 | 4080.7287 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [POTTER_CO 7345.00] TO [TOLK 7345.00] CKT 1 | 9.6954 | 4.3572 | 4257.1757 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [POTTER_CO 7345.00] TO [TOLK 7345.00] CKT 1 | 9.6954 | 4.3572 | 4257.1757 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [BUSHLAND 6230.00] TO [DEAFSMITH 6230.00] CKT 1 | 9.7088 | 4.3855 | 4285.5343 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [BUSHLAND 6230.00] TO [DEAFSMITH 6230.00] CKT 1 | 9.7088 | 4.3855 | 4285.5343 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [DFSMTH_EST 3115.00] TO [DEAFSMITH 6230.00] TO [DEFSMTH_TR2113.800] CKT 2 | 9.7075 | 4.3806 | 4280.5765 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [DFSMTH_EST 3115.00] TO [DEAFSMITH 6230.00] TO [DEFSMTH_TR2113.800] CKT 2 | 9.7075 | 4.3806 | 4280.5765 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [DEFSMTH_TR1113.200] TO [DEAFSMITH 6230.00] TO [DFSMTH_WST 3115.00] CKT 1 | 9.7076 | 4.3806 | 4280.587 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [DEFSMTH_TR1113.200] TO [DEAFSMITH 6230.00] TO [DFSMTH_WST 3115.00] CKT 1 | 9.7076 | 4.3806 | 4280.587 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLSNT_HILL 6230.00] TO [OASIS 6230.00] CKT 1 | 9.7073 | 4.3799 | 4279.9165 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLSNT_HILL 6230.00] TO [OASIS 6230.00] CKT 1 | 9.7073 | 4.3799 | 4279.9165 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLSNT_HILL 6230.00] TO [ROOSEVELT 6230.00] CKT 1 | 9.7074 | 4.3801 | 4280.1076 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLSNT_HILL 6230.00] TO [ROOSEVELT 6230.00] CKT 1 | 9.7074 | 4.3801 | 4280.1076 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [OASIS 6230.00] TO [ROOSEVELT 6230.00] CKT 1 | 9.7079 | 4.3808 | 4280.8406 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [OASIS 6230.00] TO [ROOSEVELT 6230.00] CKT 1 | 9.7079 | 4.3808 | 4280.8406 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [ROSEVLT_TR1113.200] TO [ROOSEVELT 6230.00] TO [ROOSEVELT 3115.00] CKT 1 | 9.7073 | 4.3798 | 4279.8327 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [ROSEVLT_TR1113.200] TO [ROOSEVELT 6230.00] TO [ROOSEVELT 3115.00] CKT 1 | 9.7073 | 4.3798 | 4279.8327 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SWISHER 6230.00] TO [NEWHART 6230.00] CKT 1 | 9.6876 | 4.397 | 4296.951 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SWISHER 6230.00] TO [NEWHART 6230.00] CKT 1 | 9.6876 | 4.397 | 4296.951 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SWISHER 6230.00] TO [TUCO_INT 6230.00] CKT 1 | 9.5914 | 4.3908 | 4290.834 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SWISHER 6230.00] TO [TUCO_INT 6230.00] CKT 1 | 9.5914 | 4.3908 | 4290.834 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [NEWHART 6230.00] TO [PLANT_X 6230.00] CKT 1 | 9.7002 | 4.3811 | 4281.1121 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [NEWHART 6230.00] TO [PLANT_X 6230.00] CKT 1 | 9.7002 | 4.3811 | 4281.1121 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLANTX_TR1 113.200] TO [PLANT_X 6230.00] TO [PLANT_X 3115.00] CKT 1 | 9.7063 | 4.3834 | 4283.3666 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLANTX_TR1 113.200] TO [PLANT_X 6230.00] TO [PLANT_X 3115.00] CKT 1 | 9.7063 | 4.3834 | 4283.3666 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLANT_X 3115.00] TO [LAMB_CNTY 3115.00] CKT 1 | 9.7068 | 4.3791 | 4279.1397 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLANT_X 3115.00] TO [LAMB_CNTY 3115.00] CKT 1 | 9.7068 | 4.3791 | 4279.1397 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLANT_X 6230.00] TO [PLANT_X4 120.000] CKT 1 | 9.7489 | 4.5113 | 4411.3045 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLANT_X 6230.00] TO [PLANT_X4 120.000] CKT 1 | 9.7489 | 4.5113 | 4411.3045 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLANT_X 6230.00] TO [SUNDOWN 6230.00] CKT 1 | 9.7043 | 4.3888 | 4288.7646 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLANT_X 6230.00] TO [SUNDOWN 6230.00] CKT 1 | 9.7043 | 4.3888 | 4288.7646 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TOLK 7345.00] TO [CROSSROADS 7345.00] CKT 1 | 9.7148 | 4.3948 | 4294.8444 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TOLK 7345.00] TO [CROSSROADS 7345.00] CKT 1 | 9.7148 | 4.3948 | 4294.8444 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [BLUECLDPOI 6230.00] TO [NEEDMORE 6230.00] CKT Z1 | 9.7291 | 4.4312 | 4331.1892 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [BLUECLDPOI 6230.00] TO [NEEDMORE 6230.00] CKT Z1 | 9.7291 | 4.4312 | 4331.1892 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [NEEDMORE 6230.00] TO [YOAKUM 6230.00] CKT 1 | 9.7073 | 4.3816 | 4281.5674 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [NEEDMORE 6230.00] TO [YOAKUM 6230.00] CKT 1 | 9.7073 | 4.3816 | 4281.5674 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [LAMB_TR3 113.200] TO [LAMB_CNTY 6230.00] TO [LAMB_CNTY 3115.00] CKT 1 | 9.7066 | 4.379 | 4279.0172 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [LAMB_TR3 113.200] TO [LAMB_CNTY 6230.00] TO [LAMB_CNTY 3115.00] CKT 1 | 9.7066 | 4.379 | 4279.0172 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_TR3 113.200] TO [TUCO_INT 6230.00] TO [TUCO_INT 3115.00] CKT 2 | 9.6945 | 4.3813 | 4281.2984 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_TR3 113.200] TO [TUCO_INT 6230.00] TO [TUCO_INT 3115.00] CKT 2 | 9.6945 | 4.3813 | 4281.2984 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_SVC 113.000] TO [TUCO_INT 6230.00] CKT 1 | 9.6734 | 4.3064 | 4206.3999 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_SVC 113.000] TO [TUCO_INT 6230.00] CKT 1 | 9.6734 | 4.3064 | 4206.3999 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_TR4 113.200] TO [TUCO_INT 6230.00] TO [TUCO_INT 3115.00] CKT 1 | 9.6936 | 4.3814 | 4281.39 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_TR4 113.200] TO [TUCO_INT 6230.00] TO [TUCO_INT 3115.00] CKT 1 | 9.6936 | 4.3814 | 4281.39 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_TR1 113.200] TO [TUCO_INT 7345.00] TO [TUCO_INT 6230.00] CKT 1 | 9.4471 | 4.3644 | 4264.3543 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_TR1 113.200] TO [TUCO_INT 7345.00] TO [TUCO_INT 6230.00] CKT 1 | 9.4471 | 4.3644 | 4264.3543 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_TR2 113.200] TO [TUCO_INT 7345.00] TO [TUCO_INT 6230.00] CKT 2 | 9.5013 | 4.3675 | 4267.4714 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_TR2 113.200] TO [TUCO_INT 7345.00] TO [TUCO_INT 6230.00] CKT 2 | 9.5013 | 4.3675 | 4267.4714 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 6230.00] TO [ANTELOPE_1 6230.00] CKT 1 | 9.7073 | 4.38 | 4279.9979 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 6230.00] TO [ANTELOPE_1 6230.00] CKT 1 | 9.7073 | 4.38 | 4279.9979 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 6230.00] TO [HALE_WNDCL16230.00] CKT 1 | 9.7477 | 4.4449 | 4344.8693 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 6230.00] TO [HALE_WNDCL16230.00] CKT 1 | 9.7477 | 4.4449 | 4344.8693 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 6230.00] TO [CARLISLE 6230.00] CKT 1 | 9.6335 | 4.4012 | 4301.2305 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 6230.00] TO [CARLISLE 6230.00] CKT 1 | 9.6335 | 4.4012 | 4301.2305 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 6230.00] TO [JONES 6230.00] CKT 1 | 9.5709 | 4.4345 | 4334.4633 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 6230.00] TO [JONES 6230.00] CKT 1 | 9.5709 | 4.4345 | 4334.4633 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 7345.00] TO [ELK_CT1 345.00] CKT 1 | 9.7065 | 4.3783 | 4278.2558 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 7345.00] TO [ELK_CT1 345.00] CKT 1 | 9.7065 | 4.3783 | 4278.2558 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 7345.00] TO [YOAKUM_345 345.00] CKT 1 | 9.321 | 4.4812 | 4381.1871 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 7345.00] TO [YOAKUM_345 345.00] CKT 1 | 9.321 | 4.4812 | 4381.1871 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [LG-CLAUENE 3115.00] TO [TERRY_CNTY 3115.00] CKT 1 | 9.7073 | 4.38 | 4279.9774 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [LG-CLAUENE 3115.00] TO [TERRY_CNTY 3115.00] CKT 1 | 9.7073 | 4.38 | 4279.9774 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [WOLFFORTH 3115.00] TO [TERRY_CNTY 3115.00] CKT 1 | 9.6977 | 4.3802 | 4280.2078 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [WOLFFORTH 3115.00] TO [TERRY_CNTY 3115.00] CKT 1 | 9.6977 | 4.3802 | 4280.2078 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TERRY_TR1 113.200] TO [TERRY_CNTY 3115.00] TO [TERRY_CNTY 269.000] CKT 1 | 9.7071 | 4.3799 | 4279.9174 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TERRY_TR1 113.200] TO [TERRY_CNTY 3115.00] TO [TERRY_CNTY 269.000] CKT 1 | 9.7071 | 4.3799 | 4279.9174 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TERRY_TR2 113.200] TO [TERRY_CNTY 3115.00] TO [TERRY_CNTY 269.000] CKT 2 | 9.7071 | 4.3799 | 4279.9182 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TERRY_TR2 113.200] TO [TERRY_CNTY 3115.00] TO [TERRY_CNTY 269.000] CKT 2 | 9.7071 | 4.3799 | 4279.9182 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TERRY_CNTY 3115.00] TO [PRENTICE 3115.00] CKT 1 | 9.7069 | 4.38 | 4279.9607 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TERRY_CNTY 3115.00] TO [PRENTICE 3115.00] CKT 1 | 9.7069 | 4.38 | 4279.9607 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TERRY_CNTY 3115.00] TO [DENVER_N 3115.00] CKT 1 | 9.7048 | 4.3811 | 4281.0861 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TERRY_CNTY 3115.00] TO [DENVER_N 3115.00] CKT 1 | 9.7048 | 4.3811 | 4281.0861 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [AMOCOWASSON6230.00] TO [MUSTANG 6230.00] CKT 1 | 9.7032 | 4.3801 | 4280.1245 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [AMOCOWASSON6230.00] TO [MUSTANG 6230.00] CKT 1 | 9.7032 | 4.3801 | 4280.1245 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [YOAKUM 6230.00] TO [BRU_SUB 6230.00] CKT 1 | 9.702 | 4.381 | 4281.0041 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [YOAKUM 6230.00] TO [BRU_SUB 6230.00] CKT 1 | 9.702 | 4.381 | 4281.0041 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [YOAKUM 6230.00] TO [MUSTANG 6230.00] CKT 1 | 9.7021 | 4.3803 | 4280.323 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [YOAKUM 6230.00] TO [MUSTANG 6230.00] CKT 1 | 9.7021 | 4.3803 | 4280.323 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [YOAKUM_345 345.00] TO [HOBBS_INT 7345.00] CKT 1 | 9.6259 | 4.3645 | 4264.5277 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [YOAKUM_345 345.00] TO [HOBBS_INT 7345.00] CKT 1 | 9.6259 | 4.3645 | 4264.5277 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [BRU_SUB 6230.00] TO [OXYBRU 6230.00] CKT 1 | 9.7003 | 4.3668 | 4266.7608 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [BRU_SUB 6230.00] TO [OXYBRU 6230.00] CKT 1 | 9.7003 | 4.3668 | 4266.7608 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [DENVER_N 3115.00] TO [MUSTANG 3115.00] CKT 1 | 9.7069 | 4.3801 | 4280.0811 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [DENVER_N 3115.00] TO [MUSTANG 3115.00] CKT 1 | 9.7069 | 4.3801 | 4280.0811 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MUSTANG 3115.00] TO [SEAGRAVES 3115.00] CKT 1 | 9.7064 | 4.3813 | 4281.3468 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MUSTANG 3115.00] TO [SEAGRAVES 3115.00] CKT 1 | 9.7064 | 4.3813 | 4281.3468 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [LG-PLSHILL 3115.00] TO [SEAGRAVES 3115.00] CKT 1 | 9.707 | 4.3801 | 4280.051 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [LG-PLSHILL 3115.00] TO [SEAGRAVES 3115.00] CKT 1 | 9.707 | 4.3801 | 4280.051 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SEAGRAV_TR1113.200] TO [SEAGRAVES 3115.00] TO [SEAGRAVES 269.000] CKT 1 | 9.696 | 4.3583 | 4258.3075 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SEAGRAV_TR1113.200] TO [SEAGRAVES 3115.00] TO [SEAGRAVES 269.000] CKT 1 | 9.696 | 4.3583 | 4258.3075 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [DIMNDBK_TR1113.200] TO [DIAMONDBACK3115.00] TO [DIAMONDBACK269.000] CKT 1 | 9.6985 | 4.3628 | 4262.8283 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [DIMNDBK_TR1113.200] TO [DIAMONDBACK3115.00] TO [DIAMONDBACK269.000] CKT 1 | 9.6985 | 4.3628 | 4262.8283 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SLPHUR_TR1 113.200] TO [SULPHUR 3115.00] TO [SULPHUR 269.000] CKT 1 | 9.7072 | 4.38 | 4279.9897 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SLPHUR_TR1 113.200] TO [SULPHUR 3115.00] TO [SULPHUR 269.000] CKT 1 | 9.7072 | 4.38 | 4279.9897 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SLPHUR_TR2 113.200] TO [SULPHUR 3115.00] TO [SULPHUR 269.000] CKT 2 | 9.7072 | 4.38 | 4279.9987 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SLPHUR_TR2 113.200] TO [SULPHUR 3115.00] TO [SULPHUR 269.000] CKT 2 | 9.7072 | 4.38 | 4279.9987 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CROSSROADS 7345.00] TO [HOBBS_INT 7345.00] CKT BA | 9.7082 | 4.3813 | 4281.2928 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CROSSROADS 7345.00] TO [HOBBS_INT 7345.00] CKT BA | 9.7082 | 4.3813 | 4281.2928 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CROSSROADS 7345.00] TO [HOBBS_INT 7345.00] CKT LX | 9.7082 | 4.3813 | 4281.2928 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CROSSROADS 7345.00] TO [HOBBS_INT 7345.00] CKT LX | 9.7082 | 4.3813 | 4281.2928 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CUNNINHAM 3115.00] TO [HOBBS_INT 3115.00] CKT 1 | 9.7072 | 4.38 | 4280.0015 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CUNNINHAM 3115.00] TO [HOBBS_INT 3115.00] CKT 1 | 9.7072 | 4.38 | 4280.0015 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CUNNINHAM 3115.00] TO [HOBBS_INT 3115.00] CKT 2 | 9.7072 | 4.3801 | 4280.0684 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CUNNINHAM 3115.00] TO [HOBBS_INT 3115.00] CKT 2 | 9.7072 | 4.3801 | 4280.0684 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CUNNINHAM 3115.00] TO [MADDOX 3115.00] CKT 1 | 9.7074 | 4.3801 | 4280.0585 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CUNNINHAM 3115.00] TO [MADDOX 3115.00] CKT 1 | 9.7074 | 4.3801 | 4280.0585 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [HOBBS_INT 3115.00] TO [MADDOX 3115.00] CKT 1 | 9.7073 | 4.3805 | 4280.4785 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [HOBBS_INT 3115.00] TO [MADDOX 3115.00] CKT 1 | 9.7073 | 4.3805 | 4280.4785 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [HOBBS_INT 7345.00] TO [KIOWA 7345.00] CKT 1 | 9.7074 | 4.3821 | 4282.0705 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [HOBBS_INT 7345.00] TO [KIOWA 7345.00] CKT 1 | 9.7074 | 4.3821 | 4282.0705 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [HOBBS_INT 7345.00] TO [RDRUNNER 7345.00] CKT UC | 9.7068 | 4.3788 | 4278.75 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [HOBBS_INT 7345.00] TO [RDRUNNER 7345.00] CKT UC | 9.7068 | 4.3788 | 4278.75 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [HOBBS_INT 7345.00] TO [RDRUNNER 7345.00] CKT XA | 9.7068 | 4.3788 | 4278.75 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [HOBBS_INT 7345.00] TO [RDRUNNER 7345.00] CKT XA | 9.7068 | 4.3788 | 4278.75 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [KIOWA 7345.00] TO [RDRUNNER 7345.00] CKT 1 | 9.7074 | 4.3807 | 4280.6795 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [KIOWA 7345.00] TO [RDRUNNER 7345.00] CKT 1 | 9.7074 | 4.3807 | 4280.6795 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PHANTOM 7345.00] TO [RDRUNNER 7345.00] CKT 1 | 9.708 | 4.3819 | 4281.926 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PHANTOM 7345.00] TO [RDRUNNER 7345.00] CKT 1 | 9.708 | 4.3819 | 4281.926 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SAND_DUNES 3115.00] TO [RED_BLUFF 3115.00] CKT 1 | 9.707 | 4.3801 | 4280.1266 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SAND_DUNES 3115.00] TO [RED_BLUFF 3115.00] CKT 1 | 9.707 | 4.3801 | 4280.1266 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [RED_BLUFF 3115.00] TO [WOLFCAMP_TP3115.00] CKT 1 | 9.707 | 4.3793 | 4279.3349 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [RED_BLUFF 3115.00] TO [WOLFCAMP_TP3115.00] CKT 1 | 9.707 | 4.3793 | 4279.3349 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [RDRUNNR_SVC115.000] TO [RR_SVC_HV 3115.00] CKT 1 | 9.7072 | 4.38 | 4279.9877 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [RDRUNNR_SVC115.000] TO [RR_SVC_HV 3115.00] CKT 1 | 9.7072 | 4.38 | 4279.9877 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [AGAVE_RHILL3115.00] TO [OCHOA 3115.00] CKT 1 | 9.7026 | 4.3699 | 4269.8993 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [AGAVE_RHILL3115.00] TO [OCHOA 3115.00] CKT 1 | 9.7026 | 4.3699 | 4269.8993 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CUSTERMTN 3115.00] TO [PONDEROSA 3115.00] CKT 1 | 9.6977 | 4.3595 | 4259.4863 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CUSTERMTN 3115.00] TO [PONDEROSA 3115.00] CKT 1 | 9.6977 | 4.3595 | 4259.4863 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CUSTERMTN 3115.00] TO [WHITTEN 3115.00] CKT 1 | 9.7065 | 4.3799 | 4279.8887 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CUSTERMTN 3115.00] TO [WHITTEN 3115.00] CKT 1 | 9.7065 | 4.3799 | 4279.8887 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MADDOX 3115.00] TO [MADDOX_1 113.800] CKT 1 | 9.7447 | 4.4669 | 4366.9009 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MADDOX 3115.00] TO [MADDOX_1 113.800] CKT 1 | 9.7447 | 4.4669 | 4366.9009 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MADDOX 3115.00] TO [PEARLE 3115.00] CKT 1 | 9.7073 | 4.3805 | 4280.4829 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MADDOX 3115.00] TO [PEARLE 3115.00] CKT 1 | 9.7073 | 4.3805 | 4280.4829 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MADDOX 3115.00] TO [MONUMENT 3115.00] CKT 1 | 9.7078 | 4.3813 | 4281.2886 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MADDOX 3115.00] TO [MONUMENT 3115.00] CKT 1 | 9.7078 | 4.3813 | 4281.2886 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SANGER_SW 3115.00] TO [OXYPERMIAN 3115.00] CKT 1 | 9.71 | 4.3856 | 4285.6097 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SANGER_SW 3115.00] TO [OXYPERMIAN 3115.00] CKT 1 | 9.71 | 4.3856 | 4285.6097 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [GEN-2016-121115.00] TO [G16-121XFMR134.500] CKT 1 | 9.7478 | 4.4678 | 4367.7898 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [GEN-2016-121115.00] TO [G16-121XFMR134.500] CKT 1 | 9.7478 | 4.4678 | 4367.7898 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [O.K.U.-7 345.00] TO [G18-015-TAP 345.00] CKT 1 | 5.2011 | 5.2054 | 5105.3975 | 126 | 143.8 | FAIL | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [O.K.U.-7 345.00] TO [G18-015-TAP 345.00] CKT 1 | 5.2011 | 5.2054 | 5105.3975 | 126 | 143.8 | FAIL | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [L.E.S.-7 345.00] TO [G16-091-TAP 345.00] CKT 1 | 9.0447 | 4.3588 | 4258.7776 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [L.E.S.-7 345.00] TO [G16-091-TAP 345.00] CKT 1 | 9.0447 | 4.3588 | 4258.7776 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [L.E.S.-7 345.00] TO [G17-171-TAP 345.00] CKT 1 | 9.4372 | 4.5543 | 4454.3428 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [L.E.S.-7 345.00] TO [G17-171-TAP 345.00] CKT 1 | 9.4372 | 4.5543 | 4454.3428 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [L.E.S.-7 345.00] TO [L.E.S.-4 138.00] TO [LES#4-1 13.800] CKT 1 | 9.6635 | 4.3835 | 4283.5358 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [L.E.S.-7 345.00] TO [L.E.S.-4 138.00] TO [LES#4-1 13.800] CKT 1 | 9.6635 | 4.3835 | 4283.5358 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [L.E.S.-7 345.00] TO [L.E.S.-4 138.00] TO [LES#5-1 13.800] CKT 2 | 9.6236 | 4.3866 | 4286.5861 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [L.E.S.-7 345.00] TO [L.E.S.-4 138.00] TO [LES#5-1 13.800] CKT 2 | 9.6236 | 4.3866 | 4286.5861 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [BORDER 7345.00] TO [BECKHAM7 345.00] CKT 1 | 9.3574 | 4.2066 | 4106.5918 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [BORDER 7345.00] TO [BECKHAM7 345.00] CKT 1 | 9.3574 | 4.2066 | 4106.5918 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [POTTER_CO 7345.00] TO [HITCHLAND 7345.00] CKT 1 | 9.6497 | 4.2576 | 4157.6364 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [POTTER_CO 7345.00] TO [HITCHLAND 7345.00] CKT 1 | 9.6497 | 4.2576 | 4157.6364 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [POTTER_CO 7345.00] TO [SPNSPUR_WND7345.00] CKT 1 | 9.7225 | 4.4124 | 4312.3531 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [POTTER_CO 7345.00] TO [SPNSPUR_WND7345.00] CKT 1 | 9.7225 | 4.4124 | 4312.3531 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [POTTER_CO 7345.00] TO [POTTER_CO 6230.00] TO [POTTER_TR 113.200] CKT 1 | 9.7039 | 4.3731 | 4273.1237 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [POTTER_CO 7345.00] TO [POTTER_CO 6230.00] TO [POTTER_TR 113.200] CKT 1 | 9.7039 | 4.3731 | 4273.1237 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [BUSHLAND 6230.00] TO [POTTER_CO 6230.00] CKT 1 | 9.7064 | 4.3797 | 4279.7125 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [BUSHLAND 6230.00] TO [POTTER_CO 6230.00] CKT 1 | 9.7064 | 4.3797 | 4279.7125 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [BUSHLAND 6230.00] TO [WILDOR2_JUS6230.00] CKT 1 | 9.7273 | 4.4236 | 4323.6498 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [BUSHLAND 6230.00] TO [WILDOR2_JUS6230.00] CKT 1 | 9.7273 | 4.4236 | 4323.6498 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [BUSHLAND 6230.00] TO [BUSHLAND 3115.00] TO [BSHLND_TR1 113.200] CKT 1 | 9.7067 | 4.3787 | 4278.7227 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [BUSHLAND 6230.00] TO [BUSHLAND 3115.00] TO [BSHLND_TR1 113.200] CKT 1 | 9.7067 | 4.3787 | 4278.7227 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [DFSMTH_EST 3115.00] TO [TIERABLANCA3115.00] CKT 1 | 9.7075 | 4.3806 | 4280.6143 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [DFSMTH_EST 3115.00] TO [TIERABLANCA3115.00] CKT 1 | 9.7075 | 4.3806 | 4280.6143 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [DFSMTH_WST 3115.00] TO [TIERABLANCA3115.00] CKT 2 | 9.7075 | 4.3806 | 4280.552 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [DFSMTH_WST 3115.00] TO [TIERABLANCA3115.00] CKT 2 | 9.7075 | 4.3806 | 4280.552 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [DEAFSMITH 6230.00] TO [G17-146-TAP 230.00] CKT 1 | 9.6997 | 4.3636 | 4263.5886 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [DEAFSMITH 6230.00] TO [G17-146-TAP 230.00] CKT 1 | 9.6997 | 4.3636 | 4263.5886 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLSNT_HILL 6230.00] TO [PLSNT_HILL 3115.00] TO [PLSNHIL_TR1113.200] CKT 1 | 9.7074 | 4.38 | 4280.0403 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLSNT_HILL 6230.00] TO [PLSNT_HILL 3115.00] TO [PLSNHIL_TR1113.200] CKT 1 | 9.7074 | 4.38 | 4280.0403 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [OASIS 6230.00] TO [SN_JUAN_TAP6230.00] CKT 1 | 9.7082 | 4.3811 | 4281.0579 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [OASIS 6230.00] TO [SN_JUAN_TAP6230.00] CKT 1 | 9.7082 | 4.3811 | 4281.0579 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [OASIS 6230.00] TO [OASIS 3115.00] TO [OASIS_TR1 113.200] CKT 1 | 9.7073 | 4.3798 | 4279.8182 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [OASIS 6230.00] TO [OASIS 3115.00] TO [OASIS_TR1 113.200] CKT 1 | 9.7073 | 4.3798 | 4279.8182 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [ROOSEVELT 3115.00] TO [CURRY 3115.00] CKT 2 | 9.7073 | 4.3798 | 4279.7894 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [ROOSEVELT 3115.00] TO [CURRY 3115.00] CKT 2 | 9.7073 | 4.3798 | 4279.7894 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [ROOSEVELT 3115.00] TO [PORTALES 3115.00] CKT 1 | 9.7071 | 4.3803 | 4280.3362 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [ROOSEVELT 3115.00] TO [PORTALES 3115.00] CKT 1 | 9.7071 | 4.3803 | 4280.3362 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [ROOSEVELT 6230.00] TO [TOLK 6230.00] CKT 1 | 9.7083 | 4.3812 | 4281.1936 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [ROOSEVELT 6230.00] TO [TOLK 6230.00] CKT 1 | 9.7083 | 4.3812 | 4281.1936 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [ROOSEVELT 6230.00] TO [TOLK 6230.00] CKT 2 | 9.7083 | 4.3812 | 4281.166 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [ROOSEVELT 6230.00] TO [TOLK 6230.00] CKT 2 | 9.7083 | 4.3812 | 4281.166 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SWISHER 6230.00] TO [AMA_SOUTH 6230.00] CKT 1 | 9.6825 | 4.3935 | 4293.4741 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SWISHER 6230.00] TO [AMA_SOUTH 6230.00] CKT 1 | 9.6825 | 4.3935 | 4293.4741 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SWISHER 6230.00] TO [SWISHER 3115.00] TO [SWISHER_TR1113.200] CKT 1 | 9.7062 | 4.3797 | 4279.6547 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SWISHER 6230.00] TO [SWISHER 3115.00] TO [SWISHER_TR1113.200] CKT 1 | 9.7062 | 4.3797 | 4279.6547 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [NEWHART 6230.00] TO [POTTER_CO 6230.00] CKT 1 | 9.6973 | 4.383 | 4282.9839 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [NEWHART 6230.00] TO [POTTER_CO 6230.00] CKT 1 | 9.6973 | 4.383 | 4282.9839 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [NEWHART 6230.00] TO [NEWHART 3115.00] TO [NEWHART_TR2113.200] CKT 2 | 9.7073 | 4.3802 | 4280.2202 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [NEWHART 6230.00] TO [NEWHART 3115.00] TO [NEWHART_TR2113.200] CKT 2 | 9.7073 | 4.3802 | 4280.2202 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [NEWHART 6230.00] TO [NEWHART 3115.00] TO [NEWHART_TR1113.200] CKT 1 | 9.7073 | 4.3802 | 4280.2009 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [NEWHART 6230.00] TO [NEWHART 3115.00] TO [NEWHART_TR1113.200] CKT 1 | 9.7073 | 4.3802 | 4280.2009 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLANT_X 3115.00] TO [MULSHVLY_TP3115.00] CKT 1 | 9.7075 | 4.3813 | 4281.2746 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLANT_X 3115.00] TO [MULSHVLY_TP3115.00] CKT 1 | 9.7075 | 4.3813 | 4281.2746 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLANT_X 3115.00] TO [BC-EARTH 3115.00] CKT 1 | 9.7075 | 4.3805 | 4280.5008 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLANT_X 3115.00] TO [BC-EARTH 3115.00] CKT 1 | 9.7075 | 4.3805 | 4280.5008 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLANT_X 3115.00] TO [RKYFORD_TP 3115.00] CKT 1 | 9.7056 | 4.3813 | 4281.3436 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLANT_X 3115.00] TO [RKYFORD_TP 3115.00] CKT 1 | 9.7056 | 4.3813 | 4281.3436 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLANT_X 3115.00] TO [HALE_CNTY 3115.00] CKT 1 | 9.7041 | 4.3817 | 4281.6882 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLANT_X 3115.00] TO [HALE_CNTY 3115.00] CKT 1 | 9.7041 | 4.3817 | 4281.6882 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLANT_X 3115.00] TO [PLANT_X1 113.800] CKT 1 | 9.7073 | 4.38 | 4280.0204 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLANT_X 3115.00] TO [PLANT_X1 113.800] CKT 1 | 9.7073 | 4.38 | 4280.0204 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLANT_X 3115.00] TO [PLANT_X2 113.800] CKT 1 | 9.7073 | 4.38 | 4280.0204 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLANT_X 3115.00] TO [PLANT_X2 113.800] CKT 1 | 9.7073 | 4.38 | 4280.0204 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLANT_X 3115.00] TO [PLANT_X3 113.800] CKT 1 | 9.7073 | 4.38 | 4280.0204 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLANT_X 3115.00] TO [PLANT_X3 113.800] CKT 1 | 9.7073 | 4.38 | 4280.0204 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLANT_X 6230.00] TO [TOLK 6230.00] CKT 1 | 9.7074 | 4.3802 | 4280.2183 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLANT_X 6230.00] TO [TOLK 6230.00] CKT 1 | 9.7074 | 4.3802 | 4280.2183 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLANT_X 6230.00] TO [TOLK 6230.00] CKT 2 | 9.7072 | 4.3802 | 4280.2497 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLANT_X 6230.00] TO [TOLK 6230.00] CKT 2 | 9.7072 | 4.3802 | 4280.2497 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLANT_X 6230.00] TO [G17-146-TAP 230.00] CKT 1 | 9.7045 | 4.3755 | 4275.5115 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLANT_X 6230.00] TO [G17-146-TAP 230.00] CKT 1 | 9.7045 | 4.3755 | 4275.5115 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TOLK_TR 113.200] TO [TOLK 7345.00] TO [TOLK 6230.00] CKT 1 | 9.7065 | 4.3785 | 4278.4552 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TOLK_TR 113.200] TO [TOLK 7345.00] TO [TOLK 6230.00] CKT 1 | 9.7065 | 4.3785 | 4278.4552 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TOLK_TR 2 13.200] TO [TOLK 7345.00] TO [TOLK 6230.00] CKT 2 | 9.7065 | 4.3785 | 4278.4552 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TOLK_TR 2 13.200] TO [TOLK 7345.00] TO [TOLK 6230.00] CKT 2 | 9.7065 | 4.3785 | 4278.4552 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TOLK_1 124.000] TO [TOLK 6230.00] CKT 1 | 9.7739 | 4.5927 | 4492.6885 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TOLK_1 124.000] TO [TOLK 6230.00] CKT 1 | 9.7739 | 4.5927 | 4492.6885 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TOLK_2 124.000] TO [TOLK 6230.00] CKT 1 | 9.6817 | 4.3916 | 4291.5693 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TOLK_2 124.000] TO [TOLK 6230.00] CKT 1 | 9.6817 | 4.3916 | 4291.5693 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [BLUECLDPOI 6230.00] TO [BLUECLDCOL 6230.00] CKT 1 | 9.7291 | 4.4312 | 4331.1892 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [BLUECLDPOI 6230.00] TO [BLUECLDCOL 6230.00] CKT 1 | 9.7291 | 4.4312 | 4331.1892 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [NEEDMORE 6230.00] TO [TOLK 6230.00] CKT 1 | 9.7071 | 4.379 | 4279.028 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [NEEDMORE 6230.00] TO [TOLK 6230.00] CKT 1 | 9.7071 | 4.379 | 4279.028 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [LAMB_CNTY 3115.00] TO [HOCKLEY 3115.00] CKT 1 | 9.7073 | 4.382 | 4282.0296 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [LAMB_CNTY 3115.00] TO [HOCKLEY 3115.00] CKT 1 | 9.7073 | 4.382 | 4282.0296 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [LAMB_CNTY 3115.00] TO [LAMB_CNTY 269.000] TO [LAMB_TR1 113.200] CKT 1 | 9.7072 | 4.38 | 4279.9879 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [LAMB_CNTY 3115.00] TO [LAMB_CNTY 269.000] TO [LAMB_TR1 113.200] CKT 1 | 9.7072 | 4.38 | 4279.9879 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [LAMB_CNTY 3115.00] TO [LAMB_CNTY 269.000] TO [LAMB_TR2 113.200] CKT 2 | 9.7072 | 4.38 | 4279.9873 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [LAMB_CNTY 3115.00] TO [LAMB_CNTY 269.000] TO [LAMB_TR2 113.200] CKT 2 | 9.7072 | 4.38 | 4279.9873 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [LAMB_CNTY 6230.00] TO [TOLK 6230.00] CKT 1 | 9.7066 | 4.379 | 4279.004 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [LAMB_CNTY 6230.00] TO [TOLK 6230.00] CKT 1 | 9.7066 | 4.379 | 4279.004 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 3115.00] TO [HALE_CNTY 3115.00] CKT 1 | 9.6921 | 4.3804 | 4280.439 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 3115.00] TO [HALE_CNTY 3115.00] CKT 1 | 9.6921 | 4.3804 | 4280.439 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 3115.00] TO [FLOYD_CNTY 3115.00] CKT 1 | 9.7015 | 4.3812 | 4281.2041 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 3115.00] TO [FLOYD_CNTY 3115.00] CKT 1 | 9.7015 | 4.3812 | 4281.2041 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 3115.00] TO [STANTON_W 3115.00] CKT 1 | 9.7011 | 4.3807 | 4280.685 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 3115.00] TO [STANTON_W 3115.00] CKT 1 | 9.7011 | 4.3807 | 4280.685 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 3115.00] TO [LUBBCK_EST 3115.00] CKT 1 | 9.6951 | 4.3838 | 4283.8456 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 3115.00] TO [LUBBCK_EST 3115.00] CKT 1 | 9.6951 | 4.3838 | 4283.8456 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 3115.00] TO [TUCO_INT2 269.000] TO [TUCO_TR7 113.200] CKT 1 | 9.7029 | 4.3721 | 4272.0609 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 3115.00] TO [TUCO_INT2 269.000] TO [TUCO_TR7 113.200] CKT 1 | 9.7029 | 4.3721 | 4272.0609 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 3115.00] TO [TUCO_INT 269.000] TO [TUCO_TR5 113.200] CKT 2 | 9.7072 | 4.3797 | 4279.7417 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 3115.00] TO [TUCO_INT 269.000] TO [TUCO_TR5 113.200] CKT 2 | 9.7072 | 4.3797 | 4279.7417 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 3115.00] TO [TUCO_INT 269.000] TO [TUCO_TR6 113.200] CKT 1 | 9.7072 | 4.3797 | 4279.7396 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 3115.00] TO [TUCO_INT 269.000] TO [TUCO_TR6 113.200] CKT 1 | 9.7072 | 4.3797 | 4279.7396 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 6230.00] TO [TOLK 6230.00] CKT 1 | 9.5671 | 4.4258 | 4325.803 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 6230.00] TO [TOLK 6230.00] CKT 1 | 9.5671 | 4.4258 | 4325.803 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 7345.00] TO [G17-151TAP 345.00] CKT 1 | 4.3029 | 5.0358 | 4935.8306 | 126 | 143.8 | FAIL | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TUCO_INT 7345.00] TO [G17-151TAP 345.00] CKT 1 | 4.3029 | 5.0358 | 4935.8306 | 126 | 143.8 | FAIL | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [ANTELOPE_1 6230.00] TO [ANTELOPE_A 113.800] CKT 1 | 9.7073 | 4.38 | 4280.0204 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [ANTELOPE_1 6230.00] TO [ANTELOPE_A 113.800] CKT 1 | 9.7073 | 4.38 | 4280.0204 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [ANTELOPE_1 6230.00] TO [ANTELOPE_B 113.800] CKT 1 | 9.7073 | 4.38 | 4280.0204 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [ANTELOPE_1 6230.00] TO [ANTELOPE_B 113.800] CKT 1 | 9.7073 | 4.38 | 4280.0204 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [ANTELOPE_1 6230.00] TO [ANTELOPE_C 113.800] CKT 1 | 9.7073 | 4.38 | 4280.0204 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [ANTELOPE_1 6230.00] TO [ANTELOPE_C 113.800] CKT 1 | 9.7073 | 4.38 | 4280.0204 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [ELK_CT1 345.00] TO [ELK_1 118.000] CKT 1 | 9.7073 | 4.38 | 4280.0205 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [ELK_CT1 345.00] TO [ELK_1 118.000] CKT 1 | 9.7073 | 4.38 | 4280.0205 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [ELK_CT1 345.00] TO [ELK_2 1 18.000] CKT 1 | 9.7073 | 4.38 | 4280.0204 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [ELK_CT1 345.00] TO [ELK_2 1 18.000] CKT 1 | 9.7073 | 4.38 | 4280.0204 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [HALE_WNDCL16230.00] TO [HALEWD_COL1134.500] TO [HALE_WD_TR1113.200] CKT 1 | 9.7209 | 4.4057 | 4305.7396 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [HALE_WNDCL16230.00] TO [HALEWD_COL1134.500] TO [HALE_WD_TR1113.200] CKT 1 | 9.7209 | 4.4057 | 4305.7396 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [HALE_WNDCL16230.00] TO [HALEWD_COL2134.500] TO [HALE_WD_TR2113.200] CKT 1 | 9.7215 | 4.4058 | 4305.7823 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [HALE_WNDCL16230.00] TO [HALEWD_COL2134.500] TO [HALE_WD_TR2113.200] CKT 1 | 9.7215 | 4.4058 | 4305.7823 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [HALE_WNDCL16230.00] TO [HALEWD_COL3134.500] TO [HALE_WD_TR3113.200] CKT 1 | 9.7217 | 4.4082 | 4308.1683 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [HALE_WNDCL16230.00] TO [HALEWD_COL3134.500] TO [HALE_WD_TR3113.200] CKT 1 | 9.7217 | 4.4082 | 4308.1683 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CARLISLE 6230.00] TO [WOLFFORTH 6230.00] CKT 1 | 9.6651 | 4.3961 | 4296.0584 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CARLISLE 6230.00] TO [WOLFFORTH 6230.00] CKT 1 | 9.6651 | 4.3961 | 4296.0584 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CARLISLE 6230.00] TO [CARLISLE 3115.00] TO [CRLSLE_TR1 113.200] CKT 1 | 9.7066 | 4.3844 | 4284.3805 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CARLISLE 6230.00] TO [CARLISLE 3115.00] TO [CRLSLE_TR1 113.200] CKT 1 | 9.7066 | 4.3844 | 4284.3805 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [JONES 6230.00] TO [LUBBCK_STH 6230.00] CKT 1 | 9.706 | 4.3793 | 4279.3398 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [JONES 6230.00] TO [LUBBCK_STH 6230.00] CKT 1 | 9.706 | 4.3793 | 4279.3398 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [JONES 6230.00] TO [LUBBCK_STH 6230.00] CKT 2 | 9.706 | 4.3793 | 4279.3398 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [JONES 6230.00] TO [LUBBCK_STH 6230.00] CKT 2 | 9.706 | 4.3793 | 4279.3398 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [JONES 6230.00] TO [LUBBCK_EST 6230.00] CKT 1 | 9.7026 | 4.376 | 4275.9995 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [JONES 6230.00] TO [LUBBCK_EST 6230.00] CKT 1 | 9.7026 | 4.376 | 4275.9995 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [JONES 6230.00] TO [JONES_1 122.000] CKT 1 | 9.7367 | 4.5418 | 4441.8335 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [JONES 6230.00] TO [JONES_1 122.000] CKT 1 | 9.7367 | 4.5418 | 4441.8335 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [JONES 6230.00] TO [JONES_2 122.000] CKT 1 | 9.7451 | 4.5564 | 4456.4475 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [JONES 6230.00] TO [JONES_2 122.000] CKT 1 | 9.7451 | 4.5564 | 4456.4475 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [JONES 6230.00] TO [JONES_3 116.500] CKT 1 | 9.7231 | 4.5246 | 4424.6118 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [JONES 6230.00] TO [JONES_3 116.500] CKT 1 | 9.7231 | 4.5246 | 4424.6118 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [JONES 6230.00] TO [JONES_4 116.500] CKT 1 | 9.7349 | 4.5258 | 4425.7983 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [JONES 6230.00] TO [JONES_4 116.500] CKT 1 | 9.7349 | 4.5258 | 4425.7983 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [JONES 6230.00] TO [GRASSLAND 6230.00] CKT 1 | 9.708 | 4.3805 | 4280.5065 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [JONES 6230.00] TO [GRASSLAND 6230.00] CKT 1 | 9.708 | 4.3805 | 4280.5065 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SUNDOWN 6230.00] TO [AMOCO_SS 6230.00] CKT 1 | 9.7029 | 4.3777 | 4277.7114 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SUNDOWN 6230.00] TO [AMOCO_SS 6230.00] CKT 1 | 9.7029 | 4.3777 | 4277.7114 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SUNDOWN 6230.00] TO [WOLFFORTH 6230.00] CKT 1 | 9.6782 | 4.3678 | 4267.779 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SUNDOWN 6230.00] TO [WOLFFORTH 6230.00] CKT 1 | 9.6782 | 4.3678 | 4267.779 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SUNDOWN 6230.00] TO [SUNDOWN 3115.00] TO [SUNDOWN_TR1113.800] CKT 1 | 9.7061 | 4.3788 | 4278.786 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SUNDOWN 6230.00] TO [SUNDOWN 3115.00] TO [SUNDOWN_TR1113.800] CKT 1 | 9.7061 | 4.3788 | 4278.786 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [LG-CLAUENE 3115.00] TO [LG-LEVELAND3115.00] CKT 1 | 9.7073 | 4.3801 | 4280.1058 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [LG-CLAUENE 3115.00] TO [LG-LEVELAND3115.00] CKT 1 | 9.7073 | 4.3801 | 4280.1058 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [WOLFFORTH 3115.00] TO [YUMA_INT 3115.00] CKT 1 | 9.7027 | 4.3822 | 4282.2152 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [WOLFFORTH 3115.00] TO [YUMA_INT 3115.00] CKT 1 | 9.7027 | 4.3822 | 4282.2152 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [WOLFFORTH 3115.00] TO [WOLFFORTH 6230.00] TO [WOLFRTH_TR1113.200] CKT 1 | 9.7068 | 4.3784 | 4278.4421 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [WOLFFORTH 3115.00] TO [WOLFFORTH 6230.00] TO [WOLFRTH_TR1113.200] CKT 1 | 9.7068 | 4.3784 | 4278.4421 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TERRY_CNTY 269.000] TO [LG-DOCWEBR 269.000] CKT 1 | 9.7009 | 4.3669 | 4266.9404 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TERRY_CNTY 269.000] TO [LG-DOCWEBR 269.000] CKT 1 | 9.7009 | 4.3669 | 4266.9404 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TERRY_CNTY 269.000] TO [LG-BROWNFLD269.000] CKT 1 | 9.6979 | 4.3609 | 4260.9356 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TERRY_CNTY 269.000] TO [LG-BROWNFLD269.000] CKT 1 | 9.6979 | 4.3609 | 4260.9356 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TERRY_CNTY 3115.00] TO [FLATLAND 3115.00] CKT 1 | 9.7062 | 4.3806 | 4280.5538 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [TERRY_CNTY 3115.00] TO [FLATLAND 3115.00] CKT 1 | 9.7062 | 4.3806 | 4280.5538 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [AMOCOWASSON6230.00] TO [XTO_MAHONEY6230.00] CKT 1 | 9.7024 | 4.3806 | 4280.6288 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [AMOCOWASSON6230.00] TO [XTO_MAHONEY6230.00] CKT 1 | 9.7024 | 4.3806 | 4280.6288 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PRENTICE 3115.00] TO [YOAKUM 3115.00] CKT 1 | 9.7068 | 4.3805 | 4280.5 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PRENTICE 3115.00] TO [YOAKUM 3115.00] CKT 1 | 9.7068 | 4.3805 | 4280.5 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [YOAKUM 6230.00] TO [AMOCO_SS 6230.00] CKT 1 | 9.7053 | 4.3801 | 4280.1294 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [YOAKUM 6230.00] TO [AMOCO_SS 6230.00] CKT 1 | 9.7053 | 4.3801 | 4280.1294 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [YOAKUM 6230.00] TO [INK_BASIN 6230.00] CKT 1 | 9.6991 | 4.382 | 4282.0161 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [YOAKUM 6230.00] TO [INK_BASIN 6230.00] CKT 1 | 9.6991 | 4.382 | 4282.0161 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [YOAKUM 6230.00] TO [YOAKUM 3115.00] TO [YOAKUM_TR1 113.200] CKT 1 | 9.7066 | 4.3798 | 4279.7557 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [YOAKUM 6230.00] TO [YOAKUM 3115.00] TO [YOAKUM_TR1 113.200] CKT 1 | 9.7066 | 4.3798 | 4279.7557 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [YOAKUM 6230.00] TO [YOAKUM 3115.00] TO [YOAKUM_TR2 113.200] CKT 2 | 9.7066 | 4.3797 | 4279.7478 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [YOAKUM 6230.00] TO [YOAKUM 3115.00] TO [YOAKUM_TR2 113.200] CKT 2 | 9.7066 | 4.3797 | 4279.7478 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [YOAKUM 6230.00] TO [YOAKUM_345 345.00] TO [YOAKUM_TR1 13.200] CKT 1 | 9.6413 | 4.3999 | 4299.8753 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [YOAKUM 6230.00] TO [YOAKUM_345 345.00] TO [YOAKUM_TR1 13.200] CKT 1 | 9.6413 | 4.3999 | 4299.8753 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [BRU_SUB 6230.00] TO [XTO_MAHONEY6230.00] CKT 1 | 9.702 | 4.3812 | 4281.1505 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [BRU_SUB 6230.00] TO [XTO_MAHONEY6230.00] CKT 1 | 9.702 | 4.3812 | 4281.1505 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [DENVER_N 3115.00] TO [EL_PASO 3115.00] CKT 1 | 9.7071 | 4.3801 | 4280.0618 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [DENVER_N 3115.00] TO [EL_PASO 3115.00] CKT 1 | 9.7071 | 4.3801 | 4280.0618 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [DENVER_N 3115.00] TO [HIGGEAST 3115.00] CKT 1 | 9.7068 | 4.3805 | 4280.5003 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [DENVER_N 3115.00] TO [HIGGEAST 3115.00] CKT 1 | 9.7068 | 4.3805 | 4280.5003 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [DENVER_N 3115.00] TO [DENVER_CTY 269.000] TO [DNVER_N_TR1113.200] CKT 1 | 9.707 | 4.3799 | 4279.935 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [DENVER_N 3115.00] TO [DENVER_CTY 269.000] TO [DNVER_N_TR1113.200] CKT 1 | 9.707 | 4.3799 | 4279.935 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MUSTANG 3115.00] TO [SHELL_CO2 3115.00] CKT 1 | 9.7066 | 4.3802 | 4280.1639 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MUSTANG 3115.00] TO [SHELL_CO2 3115.00] CKT 1 | 9.7066 | 4.3802 | 4280.1639 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MUSTANG 3115.00] TO [DENVER_S 3115.00] CKT 2 | 9.7069 | 4.3801 | 4280.0736 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MUSTANG 3115.00] TO [DENVER_S 3115.00] CKT 2 | 9.7069 | 4.3801 | 4280.0736 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MUSTANG 3115.00] TO [MUSTANG_1 118.000] CKT 1 | 9.7552 | 4.4985 | 4398.5134 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MUSTANG 3115.00] TO [MUSTANG_1 118.000] CKT 1 | 9.7552 | 4.4985 | 4398.5134 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MUSTANG 3115.00] TO [MUSTANG_2 118.000] CKT 1 | 9.7553 | 4.4978 | 4397.788 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MUSTANG 3115.00] TO [MUSTANG_2 118.000] CKT 1 | 9.7553 | 4.4978 | 4397.788 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MUSTANG 3115.00] TO [SEMINOLE 3115.00] CKT 1 | 9.7072 | 4.3799 | 4279.8819 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MUSTANG 3115.00] TO [SEMINOLE 3115.00] CKT 1 | 9.7072 | 4.3799 | 4279.8819 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MUSTANG 3115.00] TO [MUSTANG 6230.00] TO [MUSTANG_TR1113.200] CKT 1 | 9.7056 | 4.3794 | 4279.4346 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MUSTANG 3115.00] TO [MUSTANG 6230.00] TO [MUSTANG_TR1113.200] CKT 1 | 9.7056 | 4.3794 | 4279.4346 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MUSTANG 6230.00] TO [MUSTANG_3 119.000] CKT 1 | 9.7552 | 4.5017 | 4401.7252 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MUSTANG 6230.00] TO [MUSTANG_3 119.000] CKT 1 | 9.7552 | 4.5017 | 4401.7252 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MUSTANG 6230.00] TO [SEMINOLE 6230.00] CKT 1 | 9.7068 | 4.3805 | 4280.5387 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MUSTANG 6230.00] TO [SEMINOLE 6230.00] CKT 1 | 9.7068 | 4.3805 | 4280.5387 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [LG-PLSHILL 3115.00] TO [YOAKUM 3115.00] CKT 1 | 9.7069 | 4.38 | 4279.9894 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [LG-PLSHILL 3115.00] TO [YOAKUM 3115.00] CKT 1 | 9.7069 | 4.38 | 4279.9894 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SEAGRAVES 269.000] TO [LG-WELLMAN 269.000] CKT 1 | 9.7062 | 4.3779 | 4277.9197 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SEAGRAVES 269.000] TO [LG-WELLMAN 269.000] CKT 1 | 9.7062 | 4.3779 | 4277.9197 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SEAGRAVES 269.000] TO [MOSS 269.000] CKT 1 | 9.7015 | 4.3685 | 4268.5015 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SEAGRAVES 269.000] TO [MOSS 269.000] CKT 1 | 9.7015 | 4.3685 | 4268.5015 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SEAGRAVES 269.000] TO [LG-MC&SMNL+269.000] CKT 1 | 9.7038 | 4.373 | 4273.0177 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SEAGRAVES 269.000] TO [LG-MC&SMNL+269.000] CKT 1 | 9.7038 | 4.373 | 4273.0177 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SEAGRAVES 3115.00] TO [FLATLAND 3115.00] CKT 1 | 9.7061 | 4.3807 | 4280.6873 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SEAGRAVES 3115.00] TO [FLATLAND 3115.00] CKT 1 | 9.7061 | 4.3807 | 4280.6873 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [DIAMONDBACK269.000] TO [OZRK_MAH02 269.000] CKT 1 | 9.7046 | 4.3745 | 4274.5076 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [DIAMONDBACK269.000] TO [OZRK_MAH02 269.000] CKT 1 | 9.7046 | 4.3745 | 4274.5076 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [DIAMONDBACK269.000] TO [LG-ASHMORE 269.000] CKT 1 | 9.7069 | 4.3793 | 4279.3006 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [DIAMONDBACK269.000] TO [LG-ASHMORE 269.000] CKT 1 | 9.7069 | 4.3793 | 4279.3006 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [DIAMONDBACK269.000] TO [OXY_CEDRLKE269.000] CKT 1 | 9.7018 | 4.3691 | 4269.1289 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [DIAMONDBACK269.000] TO [OXY_CEDRLKE269.000] CKT 1 | 9.7018 | 4.3691 | 4269.1289 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [DIAMONDBACK3115.00] TO [FLATLAND 3115.00] CKT 1 | 9.6967 | 4.3574 | 4257.3681 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [DIAMONDBACK3115.00] TO [FLATLAND 3115.00] CKT 1 | 9.6967 | 4.3574 | 4257.3681 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SULPHUR 269.000] TO [ADAIR 269.000] CKT 1 | 9.7032 | 4.3719 | 4271.9079 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SULPHUR 269.000] TO [ADAIR 269.000] CKT 1 | 9.7032 | 4.3719 | 4271.9079 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SULPHUR 269.000] TO [LG-FOSTER +269.000] CKT 1 | 9.7017 | 4.3689 | 4268.9204 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SULPHUR 269.000] TO [LG-FOSTER +269.000] CKT 1 | 9.7017 | 4.3689 | 4268.9204 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SULPHUR 3115.00] TO [FLATLAND 3115.00] CKT 1 | 9.7073 | 4.38 | 4280.0198 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SULPHUR 3115.00] TO [FLATLAND 3115.00] CKT 1 | 9.7073 | 4.38 | 4280.0198 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SULPHUR 3115.00] TO [FLATLAND 3115.00] CKT 2 | 9.7073 | 4.38 | 4280.0198 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SULPHUR 3115.00] TO [FLATLAND 3115.00] CKT 2 | 9.7073 | 4.38 | 4280.0198 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CROSSROADS 7345.00] TO [SAGA_SCOL 7345.00] CKT 1 | 9.7842 | 4.5475 | 4447.4771 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CROSSROADS 7345.00] TO [SAGA_SCOL 7345.00] CKT 1 | 9.7842 | 4.5475 | 4447.4771 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CROSSROADS 7345.00] TO [RSVLT_CC_E 7345.00] CKT 1 | 9.734 | 4.4559 | 4355.8529 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CROSSROADS 7345.00] TO [RSVLT_CC_E 7345.00] CKT 1 | 9.734 | 4.4559 | 4355.8529 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CROSSROADS 7345.00] TO [EDDY_CNTY 7345.00] CKT 1 | 9.7109 | 4.3879 | 4287.9253 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CROSSROADS 7345.00] TO [EDDY_CNTY 7345.00] CKT 1 | 9.7109 | 4.3879 | 4287.9253 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CUNNINHAM 3115.00] TO [CUNINGHAM1 113.800] CKT 1 | 9.7073 | 4.38 | 4280.0204 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CUNNINHAM 3115.00] TO [CUNINGHAM1 113.800] CKT 1 | 9.7073 | 4.38 | 4280.0204 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CUNNINHAM 3115.00] TO [CUNINGHAM4 113.800] CKT 1 | 9.7439 | 4.4639 | 4363.9024 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CUNNINHAM 3115.00] TO [CUNINGHAM4 113.800] CKT 1 | 9.7439 | 4.4639 | 4363.9024 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CUNNINHAM 3115.00] TO [BUCKEYE_TP 3115.00] CKT 1 | 9.7125 | 4.3908 | 4290.8351 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CUNNINHAM 3115.00] TO [BUCKEYE_TP 3115.00] CKT 1 | 9.7125 | 4.3908 | 4290.8351 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CUNNINHAM 3115.00] TO [QUAHADA 3115.00] CKT 1 | 9.7073 | 4.3804 | 4280.3685 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CUNNINHAM 3115.00] TO [QUAHADA 3115.00] CKT 1 | 9.7073 | 4.3804 | 4280.3685 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CUNNINHAM 3115.00] TO [MONUMNT_TP 3115.00] CKT 1 | 9.7077 | 4.3814 | 4281.358 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CUNNINHAM 3115.00] TO [MONUMNT_TP 3115.00] CKT 1 | 9.7077 | 4.3814 | 4281.358 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CUNNINHAM 3115.00] TO [CUNNIGHM_S 6230.00] TO [CUNNHM_TR1 113.200] CKT 1 | 9.707 | 4.38 | 4279.9599 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CUNNINHAM 3115.00] TO [CUNNIGHM_S 6230.00] TO [CUNNHM_TR1 113.200] CKT 1 | 9.707 | 4.38 | 4279.9599 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [HOBBS_INT 3115.00] TO [HOBBS_PLT1 118.000] CKT 1 | 9.7627 | 4.5062 | 4406.237 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [HOBBS_INT 3115.00] TO [HOBBS_PLT1 118.000] CKT 1 | 9.7627 | 4.5062 | 4406.237 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [HOBBS_INT 3115.00] TO [HOBBS_PLT2 118.000] CKT 1 | 9.762 | 4.5046 | 4404.5886 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [HOBBS_INT 3115.00] TO [HOBBS_PLT2 118.000] CKT 1 | 9.762 | 4.5046 | 4404.5886 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [HOBBS_INT 3115.00] TO [LE-WEST_SUB3115.00] CKT 1 | 9.7074 | 4.3807 | 4280.6637 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [HOBBS_INT 3115.00] TO [LE-WEST_SUB3115.00] CKT 1 | 9.7074 | 4.3807 | 4280.6637 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [HOBBS_INT 3115.00] TO [BENSING 3115.00] CKT 1 | 9.7071 | 4.3805 | 4280.4506 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [HOBBS_INT 3115.00] TO [BENSING 3115.00] CKT 1 | 9.7071 | 4.3805 | 4280.4506 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [HOBBS_INT 3115.00] TO [MILLEN_TPW 3115.00] CKT 1 | 9.7076 | 4.3808 | 4280.7842 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [HOBBS_INT 3115.00] TO [MILLEN_TPW 3115.00] CKT 1 | 9.7076 | 4.3808 | 4280.7842 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [HOBBS_INT 3115.00] TO [HOBBS_INT 6230.00] TO [HOBBS_TR1 113.200] CKT 1 | 9.7067 | 4.38 | 4280.0392 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [HOBBS_INT 3115.00] TO [HOBBS_INT 6230.00] TO [HOBBS_TR1 113.200] CKT 1 | 9.7067 | 4.38 | 4280.0392 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [HOBBS_INT 3115.00] TO [HOBBS_INT 6230.00] TO [HOBBS_TR2 113.200] CKT 2 | 9.7065 | 4.3802 | 4280.1571 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [HOBBS_INT 3115.00] TO [HOBBS_INT 6230.00] TO [HOBBS_TR2 113.200] CKT 2 | 9.7065 | 4.3802 | 4280.1571 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [HOBBS_INT 7345.00] TO [HOBBS_INT 6230.00] TO [HOBBS_TR3 113.200] CKT 1 | 9.6982 | 4.3877 | 4287.6523 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [HOBBS_INT 7345.00] TO [HOBBS_INT 6230.00] TO [HOBBS_TR3 113.200] CKT 1 | 9.6982 | 4.3877 | 4287.6523 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [KIOWA 7345.00] TO [EDDY_CNTY 7345.00] CKT 1 | 9.7074 | 4.3808 | 4280.8192 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [KIOWA 7345.00] TO [EDDY_CNTY 7345.00] CKT 1 | 9.7074 | 4.3808 | 4280.8192 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [KIOWA 7345.00] TO [N_LOVING 7345.00] CKT 1 | 9.7129 | 4.3938 | 4293.7729 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [KIOWA 7345.00] TO [N_LOVING 7345.00] CKT 1 | 9.7129 | 4.3938 | 4293.7729 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [KIOWA 7345.00] TO [KIOWA 3115.00] TO [KIOWA_TR1 113.200] CKT 1 | 9.7064 | 4.3799 | 4279.9102 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [KIOWA 7345.00] TO [KIOWA 3115.00] TO [KIOWA_TR1 113.200] CKT 1 | 9.7064 | 4.3799 | 4279.9102 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PHANTOM 7345.00] TO [CHINA_DRAW 7345.00] CKT 1 | 9.7075 | 4.3803 | 4280.3304 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PHANTOM 7345.00] TO [CHINA_DRAW 7345.00] CKT 1 | 9.7075 | 4.3803 | 4280.3304 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PHANTOM 7345.00] TO [PHANTOM 3115.00] TO [PHANTOM TR1113.200] CKT 1 | 9.7077 | 4.381 | 4281.0045 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PHANTOM 7345.00] TO [PHANTOM 3115.00] TO [PHANTOM TR1113.200] CKT 1 | 9.7077 | 4.381 | 4281.0045 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PHANTOM 7345.00] TO [PHANTOM 3115.00] TO [PHANTOM TR2113.200] CKT 2 | 9.7077 | 4.381 | 4281.0045 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PHANTOM 7345.00] TO [PHANTOM 3115.00] TO [PHANTOM TR2113.200] CKT 2 | 9.7077 | 4.381 | 4281.0045 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SAND_DUNES 3115.00] TO [WIPP 3115.00] CKT 1 | 9.7072 | 4.3801 | 4280.0952 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SAND_DUNES 3115.00] TO [WIPP 3115.00] CKT 1 | 9.7072 | 4.3801 | 4280.0952 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [RED_BLUFF 3115.00] TO [RDRUNNER 3115.00] CKT 1 | 9.7073 | 4.3799 | 4279.9499 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [RED_BLUFF 3115.00] TO [RDRUNNER 3115.00] CKT 1 | 9.7073 | 4.3799 | 4279.9499 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [RDRNNER_TR1113.200] TO [RDRUNNER 7345.00] TO [RDRUNNER 3115.00] CKT 1 | 9.7069 | 4.3803 | 4280.2657 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [RDRNNER_TR1113.200] TO [RDRUNNER 7345.00] TO [RDRUNNER 3115.00] CKT 1 | 9.7069 | 4.3803 | 4280.2657 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [RR_SVC_HV 3115.00] TO [RDRUNNER 3115.00] CKT Z1 | 9.707 | 4.3788 | 4278.814 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [RR_SVC_HV 3115.00] TO [RDRUNNER 3115.00] CKT Z1 | 9.707 | 4.3788 | 4278.814 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [BATTLE_AXE 3115.00] TO [RDRUNNER 3115.00] CKT 1 | 9.6893 | 4.3415 | 4241.5458 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [BATTLE_AXE 3115.00] TO [RDRUNNER 3115.00] CKT 1 | 9.6893 | 4.3415 | 4241.5458 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [AGAVE_RHILL3115.00] TO [RDRUNNER 3115.00] CKT 1 | 9.6987 | 4.3629 | 4262.8821 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [AGAVE_RHILL3115.00] TO [RDRUNNER 3115.00] CKT 1 | 9.6987 | 4.3629 | 4262.8821 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [AGAVE_RHIL23115.00] TO [RDRUNNER 3115.00] CKT 1 | 9.6726 | 4.3059 | 4205.8776 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [AGAVE_RHIL23115.00] TO [RDRUNNER 3115.00] CKT 1 | 9.6726 | 4.3059 | 4205.8776 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [WOLFCAMP_TP3115.00] TO [BOPCO_PKRLK3115.00] CKT 1 | 9.707 | 4.3794 | 4279.3959 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [WOLFCAMP_TP3115.00] TO [BOPCO_PKRLK3115.00] CKT 1 | 9.707 | 4.3794 | 4279.3959 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [WOLFCAMP_TP3115.00] TO [WOLFCAMP 3115.00] CKT 1 | 9.6989 | 4.3619 | 4261.9061 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [WOLFCAMP_TP3115.00] TO [WOLFCAMP 3115.00] CKT 1 | 9.6989 | 4.3619 | 4261.9061 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CUSTERMTN 3115.00] TO [RDRUNNER 3115.00] CKT 1 | 9.7067 | 4.3807 | 4280.6527 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [CUSTERMTN 3115.00] TO [RDRUNNER 3115.00] CKT 1 | 9.7067 | 4.3807 | 4280.6527 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MADDOXG23 3115.00] TO [MADDOX_2 113.800] CKT 1 | 9.7073 | 4.38 | 4280.0204 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MADDOXG23 3115.00] TO [MADDOX_2 113.800] CKT 1 | 9.7073 | 4.38 | 4280.0204 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MADDOXG23 3115.00] TO [MADDOX_3 112.500] CKT 1 | 9.7073 | 4.38 | 4280.0204 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MADDOXG23 3115.00] TO [MADDOX_3 112.500] CKT 1 | 9.7073 | 4.38 | 4280.0204 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MADDOX 3115.00] TO [G18-004-TAP 115.00] CKT 1 | 9.708 | 4.3835 | 4283.5144 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MADDOX 3115.00] TO [G18-004-TAP 115.00] CKT 1 | 9.708 | 4.3835 | 4283.5144 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PEARLE 3115.00] TO [ENRON_TP 3115.00] CKT 1 | 9.7066 | 4.3799 | 4279.8737 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PEARLE 3115.00] TO [ENRON_TP 3115.00] CKT 1 | 9.7066 | 4.3799 | 4279.8737 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SANGER_SW 3115.00] TO [G18-004-TAP 115.00] CKT 1 | 9.71 | 4.3856 | 4285.6085 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SANGER_SW 3115.00] TO [G18-004-TAP 115.00] CKT 1 | 9.71 | 4.3856 | 4285.6085 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SW_4J44 3115.00] TO [OXY_S_HOBBS3115.00] CKT 1 | 9.7076 | 4.3806 | 4280.6 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SW_4J44 3115.00] TO [OXY_S_HOBBS3115.00] CKT 1 | 9.7076 | 4.3806 | 4280.6 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SW_4J44 3115.00] TO [W_HOBBS 3115.00] CKT 1 | 9.7076 | 4.3806 | 4280.6005 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SW_4J44 3115.00] TO [W_HOBBS 3115.00] CKT 1 | 9.7076 | 4.3806 | 4280.6005 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MONUMENT 3115.00] TO [MONUMENT 112.470] CKT 1 | 9.7026 | 4.37 | 4270.0179 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MONUMENT 3115.00] TO [MONUMENT 112.470] CKT 1 | 9.7026 | 4.37 | 4270.0179 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MONUMENT 3115.00] TO [W_HOBBS 3115.00] CKT 1 | 9.7076 | 4.3809 | 4280.8877 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [MONUMENT 3115.00] TO [W_HOBBS 3115.00] CKT 1 | 9.7076 | 4.3809 | 4280.8877 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [WHITTEN 3115.00] TO [WARD 3115.00] CKT 1 | 9.7068 | 4.3796 | 4279.6221 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [WHITTEN 3115.00] TO [WARD 3115.00] CKT 1 | 9.7068 | 4.3796 | 4279.6221 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [WHITTEN 3115.00] TO [S_JAL 3115.00] CKT 1 | 9.7071 | 4.3803 | 4280.2526 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [WHITTEN 3115.00] TO [S_JAL 3115.00] CKT 1 | 9.7071 | 4.3803 | 4280.2526 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [OXYPERMIAN 3115.00] TO [OXY_NHU_RCF3115.00] CKT 1 | 9.709 | 4.3837 | 4283.684 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [OXYPERMIAN 3115.00] TO [OXY_NHU_RCF3115.00] CKT 1 | 9.709 | 4.3837 | 4283.684 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [GEN-2016-121115.00] TO [RDRUNNER 3115.00] CKT 1 | 9.7478 | 4.4678 | 4367.7897 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [GEN-2016-121115.00] TO [RDRUNNER 3115.00] CKT 1 | 9.7478 | 4.4678 | 4367.7897 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [G16-121XFMR134.500] TO [G16-121-GSU134.500] CKT 1 | 9.7478 | 4.4678 | 4367.7905 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [G16-121XFMR134.500] TO [G16-121-GSU134.500] CKT 1 | 9.7478 | 4.4678 | 4367.7905 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [GEN-2017-033345.00] TO [G17-033XFMR134.500] CKT 1 | 9.7143 | 4.4152 | 4315.2031 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [GEN-2017-033345.00] TO [G17-033XFMR134.500] CKT 1 | 9.7143 | 4.4152 | 4315.2031 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [GEN-2017-033345.00] TO [G17-033XFMR234.500] CKT 1 | 9.7161 | 4.4161 | 4316.0905 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [GEN-2017-033345.00] TO [G17-033XFMR234.500] CKT 1 | 9.7161 | 4.4161 | 4316.0905 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [ROOSEVELT 6230.00] TO [TOLK 6230.00] CKT 2 | 9.7143 | 4.3906 | 4290.6328 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [ROOSEVELT 6230.00] TO [TOLK 6230.00] CKT 2 | 9.7143 | 4.3906 | 4290.6328 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLANT_X 6230.00] TO [TOLK 6230.00] CKT 2 | 9.7071 | 4.3813 | 4281.2517 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [PLANT_X 6230.00] TO [TOLK 6230.00] CKT 2 | 9.7071 | 4.3813 | 4281.2517 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [JONES 6230.00] TO [LUBBCK_STH 6230.00] CKT 2 | 9.6869 | 4.3626 | 4262.5717 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [JONES 6230.00] TO [LUBBCK_STH 6230.00] CKT 2 | 9.6869 | 4.3626 | 4262.5717 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SULPHUR 3115.00] TO [FLATLAND 3115.00] CKT 2 | 9.6972 | 4.3603 | 4260.3315 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-015 | Tuco-Oklaunion 345kV Line | OPEN LINE FROM [SULPHUR 3115.00] TO [FLATLAND 3115.00] CKT 2 | 9.6972 | 4.3603 | 4260.3315 | 126 | 143.8 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-021 | Chisholm-Gracemont 345kV Line | OPEN LINE FROM [CHISHOLM7 345.00] TO [BECKHAM7 345.00] CKT 1 | 9.9688 | 3.4987 | 3398.6643 | 74.1 | 86.4 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-021 | Chisholm-Gracemont 345kV Line | OPEN LINE FROM [CHISHOLM7 345.00] TO [G16-037-TAP 345.00] CKT 1 | 7.578 | 3.5036 | 3403.6183 | 74.1 | 86.4 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-021 | Chisholm-Gracemont 345kV Line | OPEN LINE FROM [GRACMNT7 345.00] TO [G16-037-TAP 345.00] CKT 1 | 5.8758 | 3.3788 | 3278.8202 | 74.1 | 86.4 | FAIL | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-021 | Chisholm-Gracemont 345kV Line | OPEN LINE FROM [CHISHOLM7 345.00] TO [BECKHAM7 345.00] CKT 1 | 9.6955 | 3.5385 | 3438.475 | 74.1 | 86.4 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-021 | Chisholm-Gracemont 345kV Line | OPEN LINE FROM [CHISHOLM7 345.00] TO [G16-037-TAP 345.00] CKT 1 | 7.3781 | 3.4575 | 3357.5344 | 74.1 | 86.4 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-021 | Chisholm-Gracemont 345kV Line | OPEN LINE FROM [GRACMNT7 345.00] TO [G16-037-TAP 345.00] CKT 1 | 5.8172 | 3.3189 | 3218.8858 | 74.1 | 86.4 | FAIL | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | Base | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | Base | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7FAIRPT 345.00] TO [ST JOE 7 345.00] CKT 1 | 31.743 | 0.2757 | 175.6765 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7FAIRPT 345.00] TO [ST JOE 7 345.00] CKT 1 | 31.743 | 0.2757 | 175.6765 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7FAIRPT 345.00] TO [COOPER 3 345.00] CKT 1 | 31.7467 | 0.2755 | 175.4674 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7FAIRPT 345.00] TO [COOPER 3 345.00] CKT 1 | 31.7467 | 0.2755 | 175.4674 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [5HOLDENB2 161.00] CKT 1 | 31.74 | 0.2757 | 175.6638 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [5HOLDENB2 161.00] CKT 1 | 31.74 | 0.2757 | 175.6638 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [2CLINTN 69.000] CKT 1 | 31.748 | 0.2754 | 175.4403 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [2CLINTN 69.000] CKT 1 | 31.748 | 0.2754 | 175.4403 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [2CLINTN 69.000] CKT 3 | 31.748 | 0.2754 | 175.4405 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [2CLINTN 69.000] CKT 3 | 31.748 | 0.2754 | 175.4405 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [5OSCEOKCTP 161.00] CKT 1 | 31.7183 | 0.2761 | 176.1446 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [5OSCEOKCTP 161.00] CKT 1 | 31.7183 | 0.2761 | 176.1446 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [TRUMAN 5 161.00] CKT 1 | 31.7431 | 0.2756 | 175.6116 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [TRUMAN 5 161.00] CKT 1 | 31.7431 | 0.2756 | 175.6116 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [WINDSR 5 161.00] CKT 1 | 31.7443 | 0.2754 | 175.3637 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [WINDSR 5 161.00] CKT 1 | 31.7443 | 0.2754 | 175.3637 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [CLINTON5 161.00] CKT Z1 | 31.748 | 0.2755 | 175.4782 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [CLINTON5 161.00] CKT Z1 | 31.748 | 0.2755 | 175.4782 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [N MADRD5 161.00] CKT 1 | 31.7483 | 0.2754 | 175.4309 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [N MADRD5 161.00] CKT 1 | 31.7483 | 0.2754 | 175.4309 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [SIKETAP5 161.00] CKT 1 | 31.7481 | 0.2754 | 175.4477 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [SIKETAP5 161.00] CKT 1 | 31.7481 | 0.2754 | 175.4477 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7BLACKBERRY 345.00] TO [7SPORTSMAN 345.00] CKT 1 | 29.9749 | 0.2796 | 179.5691 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7BLACKBERRY 345.00] TO [7SPORTSMAN 345.00] CKT 1 | 29.9749 | 0.2796 | 179.5691 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7BLACKBERRY 345.00] TO [7JASPER 345.00] CKT 1 | 29.2335 | 0.2735 | 173.5319 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7BLACKBERRY 345.00] TO [7JASPER 345.00] CKT 1 | 29.2335 | 0.2735 | 173.5319 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7BLACKBERRY 345.00] TO [WOLFCRK7 345.00] CKT 1 | 30.6158 | 0.2775 | 177.4822 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7BLACKBERRY 345.00] TO [WOLFCRK7 345.00] CKT 1 | 30.6158 | 0.2775 | 177.4822 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5MINER 1 161.00] TO [SIKESTN5 161.00] CKT 1 | 31.7479 | 0.2755 | 175.4506 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5MINER 1 161.00] TO [SIKESTN5 161.00] CKT 1 | 31.7479 | 0.2755 | 175.4506 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N MADRD5 161.00] TO [KENNETT5 161.00] CKT 1 | 31.7476 | 0.2755 | 175.4737 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N MADRD5 161.00] TO [KENNETT5 161.00] CKT 1 | 31.7476 | 0.2755 | 175.4737 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N MADRD5 161.00] TO [N MADRD2 69.000] TO [NMA X1 1 13.800] CKT 1 | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N MADRD5 161.00] TO [N MADRD2 69.000] TO [NMA X1 1 13.800] CKT 1 | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N MADRD5 161.00] TO [N MADRD2 69.000] TO [NMA X2 1 13.800] CKT 1 | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N MADRD5 161.00] TO [N MADRD2 69.000] TO [NMA X2 1 13.800] CKT 1 | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SIKETAP5 161.00] TO [SIKESTN5 161.00] CKT 1 | 31.748 | 0.2754 | 175.4468 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SIKETAP5 161.00] TO [SIKESTN5 161.00] CKT 1 | 31.748 | 0.2754 | 175.4468 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SIKESTN5 161.00] TO [SIKGEN 1 13.800] CKT 1 | 31.7485 | 0.2754 | 175.4125 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SIKESTN5 161.00] TO [SIKGEN 1 13.800] CKT 1 | 31.7485 | 0.2754 | 175.4125 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SIKESTN5 161.00] TO [IDALIA 5 161.00] CKT 1 | 31.7483 | 0.2754 | 175.4302 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SIKESTN5 161.00] TO [IDALIA 5 161.00] CKT 1 | 31.7483 | 0.2754 | 175.4302 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SIKESTN5 161.00] TO [SIKESTN2 69.000] TO [SIK X1 1 13.800] CKT 1 | 31.7482 | 0.2754 | 175.4401 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SIKESTN5 161.00] TO [SIKESTN2 69.000] TO [SIK X1 1 13.800] CKT 1 | 31.7482 | 0.2754 | 175.4401 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DELAWAR1 13.800] TO [DELWARE4 138.00] TO [DELWARE7 345.00] CKT 1 | 31.6565 | 0.2749 | 174.8759 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DELAWAR1 13.800] TO [DELWARE4 138.00] TO [DELWARE7 345.00] CKT 1 | 31.6565 | 0.2749 | 174.8759 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DELWARE7 345.00] TO [N.E.S.-7 345.00] CKT 1 | 26.3799 | 0.2779 | 177.8607 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DELWARE7 345.00] TO [N.E.S.-7 345.00] CKT 1 | 26.3799 | 0.2779 | 177.8607 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [DGRASSE7 345.00] CKT 1 | 31.7363 | 0.2758 | 175.7721 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [DGRASSE7 345.00] CKT 1 | 31.7363 | 0.2758 | 175.7721 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [DGRASSE7 345.00] CKT 2 | 31.7363 | 0.2758 | 175.7724 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [DGRASSE7 345.00] CKT 2 | 31.7363 | 0.2758 | 175.7724 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DGRASSE7 345.00] TO [DGRASSE4 138.00] TO [DGRASSE1 13.800] CKT 1 | 31.7453 | 0.2755 | 175.5246 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DGRASSE7 345.00] TO [DGRASSE4 138.00] TO [DGRASSE1 13.800] CKT 1 | 31.7453 | 0.2755 | 175.5246 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WALKMYR1 13.800] TO [WALKMYR2 69.000] TO [WALKMYR3 115.00] CKT 1 | 31.7472 | 0.2755 | 175.4813 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WALKMYR1 13.800] TO [WALKMYR2 69.000] TO [WALKMYR3 115.00] CKT 1 | 31.7472 | 0.2755 | 175.4813 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WALKMYR3 115.00] TO [HUGOTON3 115.00] CKT 1 | 31.748 | 0.2754 | 175.4369 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WALKMYR3 115.00] TO [HUGOTON3 115.00] CKT 1 | 31.748 | 0.2754 | 175.4369 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WALKMYR3 115.00] TO [HARBNGR3 115.00] CKT 1 | 31.7478 | 0.2755 | 175.4516 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WALKMYR3 115.00] TO [HARBNGR3 115.00] CKT 1 | 31.7478 | 0.2755 | 175.4516 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SEWARD-3 115.00] TO [N-CIMRN3 115.00] CKT 1 | 31.748 | 0.2754 | 175.4421 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SEWARD-3 115.00] TO [N-CIMRN3 115.00] CKT 1 | 31.748 | 0.2754 | 175.4421 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [CLARKCOUNTY7345.00] CKT 1 | 31.7458 | 0.2755 | 175.4659 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [CLARKCOUNTY7345.00] CKT 1 | 31.7458 | 0.2755 | 175.4659 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NSES 2X1 13.200] TO [NEOSHO 4 138.00] TO [NEOSHOS2 69.000] CKT 1 | 31.7203 | 0.2756 | 175.5879 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NSES 2X1 13.200] TO [NEOSHO 4 138.00] TO [NEOSHOS2 69.000] CKT 1 | 31.7203 | 0.2756 | 175.5879 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EEC GT1 13.800] TO [EVANS S4 138.00] CKT 1 | 31.7483 | 0.2754 | 175.4318 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EEC GT1 13.800] TO [EVANS S4 138.00] CKT 1 | 31.7483 | 0.2754 | 175.4318 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EEC GT2 13.800] TO [EVANS S4 138.00] CKT 1 | 31.7483 | 0.2754 | 175.4319 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EEC GT2 13.800] TO [EVANS S4 138.00] CKT 1 | 31.7483 | 0.2754 | 175.4319 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EEC GT3 18.000] TO [EVANS S4 138.00] CKT 1 | 31.7483 | 0.2754 | 175.4325 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EEC GT3 18.000] TO [EVANS S4 138.00] CKT 1 | 31.7483 | 0.2754 | 175.4325 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [SWISVAL7 345.00] CKT 1 | 31.7499 | 0.2753 | 175.3212 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [SWISVAL7 345.00] CKT 1 | 31.7499 | 0.2753 | 175.3212 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EXPEDITION7 345.00] CKT 1 | 31.6953 | 0.2759 | 175.8821 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EXPEDITION7 345.00] CKT 1 | 31.6953 | 0.2759 | 175.8821 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RENO 7 345.00] TO [WICHITA7 345.00] CKT 1 | 31.6905 | 0.2757 | 175.6603 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RENO 7 345.00] TO [WICHITA7 345.00] CKT 1 | 31.6905 | 0.2757 | 175.6603 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 7 345.00] TO [G17-004-TAP 345.00] CKT 1 | 31.7434 | 0.2756 | 175.5659 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 7 345.00] TO [G17-004-TAP 345.00] CKT 1 | 31.7434 | 0.2756 | 175.5659 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SWISVAL7 345.00] TO [SWISVAL6 230.00] TO [SWISV1X1 14.400] CKT 1 | 31.7456 | 0.2754 | 175.4145 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SWISVAL7 345.00] TO [SWISVAL6 230.00] TO [SWISV1X1 14.400] CKT 1 | 31.7456 | 0.2754 | 175.4145 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SWISVAL7 345.00] TO [SWISVAL6 230.00] TO [SWISV2X2 14.400] CKT 2 | 31.7456 | 0.2754 | 175.4156 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SWISVAL7 345.00] TO [SWISVAL6 230.00] TO [SWISV2X2 14.400] CKT 2 | 31.7456 | 0.2754 | 175.4156 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [87TH 7 345.00] TO [CRAIG 7 345.00] CKT 1 | 31.7094 | 0.2753 | 175.2626 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [87TH 7 345.00] TO [CRAIG 7 345.00] CKT 1 | 31.7094 | 0.2753 | 175.2626 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-009-TAP 345.00] TO [GEN-2017-009345.00] CKT 1 | 31.769 | 0.2785 | 178.4543 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-009-TAP 345.00] TO [GEN-2017-009345.00] CKT 1 | 31.769 | 0.2785 | 178.4543 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-009-TAP 345.00] TO [CANEYRV7 345.00] CKT 1 | 27.796 | 0.2807 | 180.6712 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-009-TAP 345.00] TO [CANEYRV7 345.00] CKT 1 | 27.796 | 0.2807 | 180.6712 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KINGMAN7 345.00] TO [NINN1WF7 345.00] CKT 1 | 31.7639 | 0.2745 | 174.5478 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KINGMAN7 345.00] TO [NINN1WF7 345.00] CKT 1 | 31.7639 | 0.2745 | 174.5478 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KINGMAN7 345.00] TO [K1 LV 1 34.500] TO [K1 WFTX1 13.800] CKT 1 | 31.753 | 0.2752 | 175.1946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KINGMAN7 345.00] TO [K1 LV 1 34.500] TO [K1 WFTX1 13.800] CKT 1 | 31.753 | 0.2752 | 175.1946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KINGMAN7 345.00] TO [K2 LV 1 34.500] TO [K2 WFTX1 13.800] CKT 1 | 31.7527 | 0.2752 | 175.2184 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KINGMAN7 345.00] TO [K2 LV 1 34.500] TO [K2 WFTX1 13.800] CKT 1 | 31.7527 | 0.2752 | 175.2184 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTON 7 345.00] TO [WICHITA7 345.00] CKT 1 | 31.4259 | 0.2746 | 174.5939 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTON 7 345.00] TO [WICHITA7 345.00] CKT 1 | 31.4259 | 0.2746 | 174.5939 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTON 7 345.00] TO [WOLFCRK7 345.00] CKT 1 | 31.7201 | 0.2781 | 178.1081 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTON 7 345.00] TO [WOLFCRK7 345.00] CKT 1 | 31.7201 | 0.2781 | 178.1081 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [VIOLA 7 345.00] CKT 1 | 31.7225 | 0.2767 | 176.666 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [VIOLA 7 345.00] CKT 1 | 31.7225 | 0.2767 | 176.666 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [EXPEDITION7 345.00] CKT 1 | 31.6898 | 0.2764 | 176.4151 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [EXPEDITION7 345.00] CKT 1 | 31.6898 | 0.2764 | 176.4151 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WOLFCRK7 345.00] TO [WAVERLY7 345.00] CKT 1 | 31.7723 | 0.2739 | 173.9315 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WOLFCRK7 345.00] TO [WAVERLY7 345.00] CKT 1 | 31.7723 | 0.2739 | 173.9315 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [VIOLA 7 345.00] TO [VIOLA 4 138.00] TO [VIOLA1X1 13.800] CKT 1 | 31.7473 | 0.2755 | 175.4857 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [VIOLA 7 345.00] TO [VIOLA 4 138.00] TO [VIOLA1X1 13.800] CKT 1 | 31.7473 | 0.2755 | 175.4857 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [VIOLA 7 345.00] TO [VIOLA 4 138.00] TO [SCJ1X1 13.800] CKT 2 | 31.747 | 0.2755 | 175.4535 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [VIOLA 7 345.00] TO [VIOLA 4 138.00] TO [SCJ1X1 13.800] CKT 2 | 31.747 | 0.2755 | 175.4535 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WAVERLY7 345.00] TO [LACYGNE7 345.00] CKT 1 | 31.7538 | 0.2753 | 175.273 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WAVERLY7 345.00] TO [LACYGNE7 345.00] CKT 1 | 31.7538 | 0.2753 | 175.273 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NMANHT6 230.00] TO [ELMCREK6 230.00] CKT 1 | 31.746 | 0.2755 | 175.4825 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NMANHT6 230.00] TO [ELMCREK6 230.00] CKT 1 | 31.746 | 0.2755 | 175.4825 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH 5 161.00] TO [FRANKLIN5 161.00] CKT 1 | 31.6632 | 0.2761 | 176.1041 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH 5 161.00] TO [FRANKLIN5 161.00] CKT 1 | 31.6632 | 0.2761 | 176.1041 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH 5 161.00] TO [LITCH S2 69.000] TO [LITCH1 1 13.200] CKT 1 | 31.7386 | 0.2759 | 175.9466 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH 5 161.00] TO [LITCH S2 69.000] TO [LITCH1 1 13.200] CKT 1 | 31.7386 | 0.2759 | 175.9466 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH 5 161.00] TO [LITCH N2 69.000] TO [LITCH2 1 13.200] CKT 1 | 31.7365 | 0.2751 | 175.0924 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH 5 161.00] TO [LITCH N2 69.000] TO [LITCH2 1 13.200] CKT 1 | 31.7365 | 0.2751 | 175.0924 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MARMTNW5 161.00] TO [NEOSHO 5 161.00] CKT 1 | 31.1851 | 0.2737 | 173.6692 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MARMTNW5 161.00] TO [NEOSHO 5 161.00] CKT 1 | 31.1851 | 0.2737 | 173.6692 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHO 5 161.00] TO [RIV4525 161.00] CKT 1 | 29.4783 | 0.2668 | 166.8399 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHO 5 161.00] TO [RIV4525 161.00] CKT 1 | 29.4783 | 0.2668 | 166.8399 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHO 5 161.00] TO [NEOSHO 4 138.00] TO [NEOSH4 1 13.200] CKT 1 | 31.7489 | 0.2755 | 175.4627 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHO 5 161.00] TO [NEOSHO 4 138.00] TO [NEOSH4 1 13.200] CKT 1 | 31.7489 | 0.2755 | 175.4627 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHO 5 161.00] TO [NEOSHOS4 138.00] TO [NEOSH5 1 13.200] CKT 1 | 31.7493 | 0.2755 | 175.4782 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHO 5 161.00] TO [NEOSHOS4 138.00] TO [NEOSH5 1 13.200] CKT 1 | 31.7493 | 0.2755 | 175.4782 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRESWLN4 138.00] TO [OXFORD 4 138.00] CKT 1 | 31.7316 | 0.2756 | 175.6298 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRESWLN4 138.00] TO [OXFORD 4 138.00] CKT 1 | 31.7316 | 0.2756 | 175.6298 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TCROCK 4 138.00] TO [TIMBJCT4 138.00] CKT 1 | 31.7471 | 0.2755 | 175.4507 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TCROCK 4 138.00] TO [TIMBJCT4 138.00] CKT 1 | 31.7471 | 0.2755 | 175.4507 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TIMBJCT4 138.00] TO [TIMBJCT2 69.000] TO [TIMBJCT1 13.200] CKT 1 | 31.747 | 0.2755 | 175.4751 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TIMBJCT4 138.00] TO [TIMBJCT2 69.000] TO [TIMBJCT1 13.200] CKT 1 | 31.747 | 0.2755 | 175.4751 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TIOGA 4 138.00] TO [ALTOONA4 138.00] CKT 1 | 31.5222 | 0.2755 | 175.4919 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TIOGA 4 138.00] TO [ALTOONA4 138.00] CKT 1 | 31.5222 | 0.2755 | 175.4919 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [OTTRCRK4 138.00] TO [ALTOONA4 138.00] CKT 1 | 31.5967 | 0.2751 | 175.117 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [OTTRCRK4 138.00] TO [ALTOONA4 138.00] CKT 1 | 31.5967 | 0.2751 | 175.117 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ALTOONA4 138.00] TO [TAYLOR 4 138.00] CKT 1 | 31.7216 | 0.2765 | 176.549 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ALTOONA4 138.00] TO [TAYLOR 4 138.00] CKT 1 | 31.7216 | 0.2765 | 176.549 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ALTOONA4 138.00] TO [ALTOO W2 69.000] TO [ALTOO1 1 13.200] CKT 1 | 31.747 | 0.2759 | 175.895 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ALTOONA4 138.00] TO [ALTOO W2 69.000] TO [ALTOO1 1 13.200] CKT 1 | 31.747 | 0.2759 | 175.895 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ALTOONA4 138.00] TO [ALTOO E2 69.000] TO [ALTOO3 1 13.200] CKT 1 | 31.746 | 0.2756 | 175.6478 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ALTOONA4 138.00] TO [ALTOO E2 69.000] TO [ALTOO3 1 13.200] CKT 1 | 31.746 | 0.2756 | 175.6478 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEPARSN4 138.00] TO [NEOSHON4 138.00] CKT 1 | 31.1644 | 0.2785 | 178.5224 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEPARSN4 138.00] TO [NEOSHON4 138.00] CKT 1 | 31.1644 | 0.2785 | 178.5224 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTLEY4 138.00] TO [SG12COL4 138.00] CKT 1 | 31.7434 | 0.2754 | 175.4435 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTLEY4 138.00] TO [SG12COL4 138.00] CKT 1 | 31.7434 | 0.2754 | 175.4435 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHOS4 138.00] TO [NEOSHO 4 138.00] CKT Z1 | 31.704 | 0.2754 | 175.4405 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHOS4 138.00] TO [NEOSHO 4 138.00] CKT Z1 | 31.704 | 0.2754 | 175.4405 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHO 4 138.00] TO [NEOSHON4 138.00] CKT Z1 | 31.477 | 0.2775 | 177.4567 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHO 4 138.00] TO [NEOSHON4 138.00] CKT Z1 | 31.477 | 0.2775 | 177.4567 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CHISHLM4 138.00] TO [MAIZE 4 138.00] CKT 1 | 31.7349 | 0.2757 | 175.6936 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CHISHLM4 138.00] TO [MAIZE 4 138.00] CKT 1 | 31.7349 | 0.2757 | 175.6936 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLEARWT4 138.00] TO [GILL 4 138.00] CKT 1 | 31.7448 | 0.2756 | 175.5565 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLEARWT4 138.00] TO [GILL 4 138.00] CKT 1 | 31.7448 | 0.2756 | 175.5565 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLEARWT4 138.00] TO [VIOLA 4 138.00] CKT 1 | 31.7438 | 0.2755 | 175.5378 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLEARWT4 138.00] TO [VIOLA 4 138.00] CKT 1 | 31.7438 | 0.2755 | 175.5378 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EVANS S4 138.00] TO [LAKERDG4 138.00] CKT 1 | 31.742 | 0.276 | 176.0372 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EVANS S4 138.00] TO [LAKERDG4 138.00] CKT 1 | 31.742 | 0.276 | 176.0372 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EVANS S4 138.00] TO [45TH ST4 138.00] CKT 1 | 31.7424 | 0.276 | 175.9987 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EVANS S4 138.00] TO [45TH ST4 138.00] CKT 1 | 31.7424 | 0.276 | 175.9987 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FARBER 4 138.00] TO [SC10BEL4 138.00] CKT 1 | 31.7279 | 0.2756 | 175.5775 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FARBER 4 138.00] TO [SC10BEL4 138.00] CKT 1 | 31.7279 | 0.2756 | 175.5775 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GILL 4 138.00] TO [VIOLA 4 138.00] CKT 1 | 31.745 | 0.2755 | 175.55 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GILL 4 138.00] TO [VIOLA 4 138.00] CKT 1 | 31.745 | 0.2755 | 175.55 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [VIOLA 4 138.00] TO [MILAN_GOAB 138.00] CKT 1 | 31.7475 | 0.2754 | 175.4342 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [VIOLA 4 138.00] TO [MILAN_GOAB 138.00] CKT 1 | 31.7475 | 0.2754 | 175.4342 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [VIOLA 4 138.00] TO [CONWAY 138.00] CKT 1 | 31.7465 | 0.2754 | 175.426 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [VIOLA 4 138.00] TO [CONWAY 138.00] CKT 1 | 31.7465 | 0.2754 | 175.426 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [AEC 3 115.00] TO [EABILEN3 115.00] CKT 1 | 31.7498 | 0.2753 | 175.2761 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [AEC 3 115.00] TO [EABILEN3 115.00] CKT 1 | 31.7498 | 0.2753 | 175.2761 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [AEC 3 115.00] TO [AEC E1 34.500] CKT 2 | 31.7467 | 0.2755 | 175.4955 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [AEC 3 115.00] TO [AEC E1 34.500] CKT 2 | 31.7467 | 0.2755 | 175.4955 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [AEC 3 115.00] TO [AEC W1 34.500] CKT 1 | 31.7445 | 0.2756 | 175.5875 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [AEC 3 115.00] TO [AEC W1 34.500] CKT 1 | 31.7445 | 0.2756 | 175.5875 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NORTHST3 115.00] TO [NORTHVW3 115.00] CKT 1 | 31.7485 | 0.2754 | 175.4224 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NORTHST3 115.00] TO [NORTHVW3 115.00] CKT 1 | 31.7485 | 0.2754 | 175.4224 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NORTHVW3 115.00] TO [SUMMIT 3 115.00] CKT 1 | 31.7481 | 0.2754 | 175.4368 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NORTHVW3 115.00] TO [SUMMIT 3 115.00] CKT 1 | 31.7481 | 0.2754 | 175.4368 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH N2 69.000] TO [LITCH S2 69.000] CKT Z1 | 31.7461 | 0.2752 | 175.2376 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH N2 69.000] TO [LITCH S2 69.000] CKT Z1 | 31.7461 | 0.2752 | 175.2376 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MRWYP16 230.00] TO [ELMCREK6 230.00] CKT 1 | 31.7539 | 0.2751 | 175.0773 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MRWYP16 230.00] TO [ELMCREK6 230.00] CKT 1 | 31.7539 | 0.2751 | 175.0773 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FLATRDG4 138.00] TO [THISTLE4 138.00] CKT 1 | 31.7485 | 0.2754 | 175.4166 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FLATRDG4 138.00] TO [THISTLE4 138.00] CKT 1 | 31.7485 | 0.2754 | 175.4166 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ELMCREK6 230.00] TO [CONCRD6 230.00] CKT 1 | 31.7441 | 0.2756 | 175.5717 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ELMCREK6 230.00] TO [CONCRD6 230.00] CKT 1 | 31.7441 | 0.2756 | 175.5717 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAYNE3 115.00] TO [NLIB 3 115.00] CKT 1 | 31.7483 | 0.2754 | 175.434 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAYNE3 115.00] TO [NLIB 3 115.00] CKT 1 | 31.7483 | 0.2754 | 175.434 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KISMET 3 115.00] TO [CMRIVTP3 115.00] CKT 1 | 31.7474 | 0.2754 | 175.4463 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KISMET 3 115.00] TO [CMRIVTP3 115.00] CKT 1 | 31.7474 | 0.2754 | 175.4463 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CMRIVTP3 115.00] TO [E-LIBER3 115.00] CKT 1 | 31.7482 | 0.2754 | 175.4382 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CMRIVTP3 115.00] TO [E-LIBER3 115.00] CKT 1 | 31.7482 | 0.2754 | 175.4382 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CIM-PLT1 13.800] TO [CIM-PLT 13.800] CKT Z1 | 31.7468 | 0.2755 | 175.5184 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CIM-PLT1 13.800] TO [CIM-PLT 13.800] CKT Z1 | 31.7468 | 0.2755 | 175.5184 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N-CIMRN3 115.00] TO [N-CMRN 1 34.500] TO [N-CMRN-T 13.800] CKT 1 | 31.7479 | 0.2754 | 175.449 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N-CIMRN3 115.00] TO [N-CMRN 1 34.500] TO [N-CMRN-T 13.800] CKT 1 | 31.7479 | 0.2754 | 175.449 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [TRANSFORMER 345.00] CKT 1 | 31.7555 | 0.275 | 174.9783 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [TRANSFORMER 345.00] CKT 1 | 31.7555 | 0.275 | 174.9783 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [GEN-2011-008345.00] CKT 1 | 31.7576 | 0.2749 | 174.9022 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [GEN-2011-008345.00] CKT 1 | 31.7576 | 0.2749 | 174.9022 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [G16-046-TAP 345.00] CKT 1 | 31.7445 | 0.2755 | 175.4606 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [G16-046-TAP 345.00] CKT 1 | 31.7445 | 0.2755 | 175.4606 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MULLNCR7 345.00] TO [MC REAC1 345.00] CKT Z1 | 31.7489 | 0.2754 | 175.4157 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MULLNCR7 345.00] TO [MC REAC1 345.00] CKT Z1 | 31.7489 | 0.2754 | 175.4157 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MULLNCR7 345.00] TO [MC REAC2 345.00] CKT Z1 | 31.7489 | 0.2754 | 175.4157 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MULLNCR7 345.00] TO [MC REAC2 345.00] CKT Z1 | 31.7489 | 0.2754 | 175.4157 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MULLNCR7 345.00] TO [MC REAC3 345.00] CKT Z1 | 31.7488 | 0.2754 | 175.4003 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MULLNCR7 345.00] TO [MC REAC3 345.00] CKT Z1 | 31.7488 | 0.2754 | 175.4003 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MULLNCR7 345.00] TO [KETCHEM7 345.00] CKT 1 | 31.744 | 0.2754 | 175.3596 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MULLNCR7 345.00] TO [KETCHEM7 345.00] CKT 1 | 31.744 | 0.2754 | 175.3596 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [PECULR 7 345.00] TO [STILWEL7 345.00] CKT 1 | 31.6492 | 0.2769 | 176.8963 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [PECULR 7 345.00] TO [STILWEL7 345.00] CKT 1 | 31.6492 | 0.2769 | 176.8963 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 7 345.00] TO [EASTOWN7 345.00] CKT 1 | 31.7417 | 0.2758 | 175.7999 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 7 345.00] TO [EASTOWN7 345.00] CKT 1 | 31.7417 | 0.2758 | 175.7999 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 7 345.00] TO [COOPER 3 345.00] CKT 1 | 31.7437 | 0.2756 | 175.579 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 7 345.00] TO [COOPER 3 345.00] CKT 1 | 31.7437 | 0.2756 | 175.579 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 7 345.00] TO [ST JOE 5 161.00] TO [STJOE 1T 13.800] CKT 22 | 31.7481 | 0.2754 | 175.4391 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 7 345.00] TO [ST JOE 5 161.00] TO [STJOE 1T 13.800] CKT 22 | 31.7481 | 0.2754 | 175.4391 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 7 345.00] TO [ST JOE 5 161.00] TO [STJOE 2T 13.800] CKT 33 | 31.7481 | 0.2754 | 175.4389 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 7 345.00] TO [ST JOE 5 161.00] TO [STJOE 2T 13.800] CKT 33 | 31.7481 | 0.2754 | 175.4389 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ARCHIE 5 161.00] TO [HSNVL 5 161.00] CKT 1 | 31.7382 | 0.2754 | 175.4362 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ARCHIE 5 161.00] TO [HSNVL 5 161.00] CKT 1 | 31.7382 | 0.2754 | 175.4362 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ARCHIE 5 161.00] TO [ADRIAN 5 161.00] CKT 1 | 31.7034 | 0.2764 | 176.4448 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ARCHIE 5 161.00] TO [ADRIAN 5 161.00] CKT 1 | 31.7034 | 0.2764 | 176.4448 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ARCHIE 5 161.00] TO [S.HARP 5 161.00] CKT 1 | 31.7453 | 0.2756 | 175.6139 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ARCHIE 5 161.00] TO [S.HARP 5 161.00] CKT 1 | 31.7453 | 0.2756 | 175.6139 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [STILWEL5 161.00] CKT 1 | 31.7473 | 0.2755 | 175.4788 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [STILWEL5 161.00] CKT 1 | 31.7473 | 0.2755 | 175.4788 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EASTOWN7 345.00] TO [IATAN 7 345.00] CKT 1 | 31.7329 | 0.2763 | 176.304 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EASTOWN7 345.00] TO [IATAN 7 345.00] CKT 1 | 31.7329 | 0.2763 | 176.304 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ROCKCK_TR1_113.200] TO [ROCKCK7 345.00] TO [ROCKCK_T1_1 34.500] CKT 1 | 31.7508 | 0.2753 | 175.3087 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ROCKCK_TR1_113.200] TO [ROCKCK7 345.00] TO [ROCKCK_T1_1 34.500] CKT 1 | 31.7508 | 0.2753 | 175.3087 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ROCKCK_TR2_113.200] TO [ROCKCK7 345.00] TO [ROCKCK_T2_1 34.500] CKT 1 | 31.7516 | 0.2753 | 175.27 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ROCKCK_TR2_113.200] TO [ROCKCK7 345.00] TO [ROCKCK_T2_1 34.500] CKT 1 | 31.7516 | 0.2753 | 175.27 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ROCKCK7 345.00] TO [OUTLAW 345.00] CKT 1 | 31.7531 | 0.2751 | 175.1285 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ROCKCK7 345.00] TO [OUTLAW 345.00] CKT 1 | 31.7531 | 0.2751 | 175.1285 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC G1 1 22.000] TO [LACYGNE7 345.00] CKT 1 | 31.4224 | 0.2721 | 172.1293 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC G1 1 22.000] TO [LACYGNE7 345.00] CKT 1 | 31.4224 | 0.2721 | 172.1293 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC G2 1 24.000] TO [LACYGNE7 345.00] CKT 1 | 31.5723 | 0.2671 | 167.0891 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC G2 1 24.000] TO [LACYGNE7 345.00] CKT 1 | 31.5723 | 0.2671 | 167.0891 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [CEDRCRK5 161.00] CKT 1 | 31.7425 | 0.2757 | 175.6908 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [CEDRCRK5 161.00] CKT 1 | 31.7425 | 0.2757 | 175.6908 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [CEDARNL5 161.00] CKT 1 | 31.7469 | 0.2755 | 175.5073 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [CEDARNL5 161.00] CKT 1 | 31.7469 | 0.2755 | 175.5073 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [PLSTVAL5 161.00] CKT 1 | 31.7388 | 0.2755 | 175.4524 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [PLSTVAL5 161.00] CKT 1 | 31.7388 | 0.2755 | 175.4524 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [BULLCRK5 161.00] CKT 1 | 31.7469 | 0.2737 | 173.7495 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [BULLCRK5 161.00] CKT 1 | 31.7469 | 0.2737 | 173.7495 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [BNSF 5 161.00] CKT 1 | 31.7409 | 0.2759 | 175.8757 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [BNSF 5 161.00] CKT 1 | 31.7409 | 0.2759 | 175.8757 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [WGARDNR1 34.500] CKT 7 | 31.7448 | 0.2756 | 175.5714 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [WGARDNR1 34.500] CKT 7 | 31.7448 | 0.2756 | 175.5714 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL7 345.00] TO [LACYGNE7 345.00] CKT 1 | 31.3926 | 0.2791 | 179.1484 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL7 345.00] TO [LACYGNE7 345.00] CKT 1 | 31.3926 | 0.2791 | 179.1484 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL7 345.00] TO [STILWEL5 161.00] TO [STIL T11 13.800] CKT 11 | 31.7401 | 0.2756 | 175.5545 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL7 345.00] TO [STILWEL5 161.00] TO [STIL T11 13.800] CKT 11 | 31.7401 | 0.2756 | 175.5545 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL7 345.00] TO [STILWEL5 161.00] TO [STIL T22 13.800] CKT 22 | 31.7394 | 0.2756 | 175.5801 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL7 345.00] TO [STILWEL5 161.00] TO [STIL T22 13.800] CKT 22 | 31.7394 | 0.2756 | 175.5801 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [HICKMAN5 161.00] CKT 1 | 31.7393 | 0.2755 | 175.4551 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [HICKMAN5 161.00] CKT 1 | 31.7393 | 0.2755 | 175.4551 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [ANTIOCH5 161.00] CKT 1 | 31.7445 | 0.2752 | 175.2444 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [ANTIOCH5 161.00] CKT 1 | 31.7445 | 0.2752 | 175.2444 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [REDEL 5 161.00] CKT 1 | 31.7388 | 0.2755 | 175.4757 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [REDEL 5 161.00] CKT 1 | 31.7388 | 0.2755 | 175.4757 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [BUCYRUS5 161.00] CKT 1 | 31.7253 | 0.2754 | 175.4462 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [BUCYRUS5 161.00] CKT 1 | 31.7253 | 0.2754 | 175.4462 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [LACKMAN5 161.00] CKT 1 | 31.7463 | 0.2754 | 175.4182 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [LACKMAN5 161.00] CKT 1 | 31.7463 | 0.2754 | 175.4182 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTH 7 345.00] TO [NASHUA 7 345.00] CKT 1 | 31.7434 | 0.2757 | 175.6503 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTH 7 345.00] TO [NASHUA 7 345.00] CKT 1 | 31.7434 | 0.2757 | 175.6503 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [SUB M-161 161.00] CKT 1 | 31.7475 | 0.2755 | 175.4806 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [SUB M-161 161.00] CKT 1 | 31.7475 | 0.2755 | 175.4806 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 7 345.00] TO [CRAIG 5 161.00] TO [CRAI T11 13.800] CKT 11 | 31.7455 | 0.2755 | 175.549 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 7 345.00] TO [CRAIG 5 161.00] TO [CRAI T11 13.800] CKT 11 | 31.7455 | 0.2755 | 175.549 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 7 345.00] TO [CRAIG 5 161.00] TO [CRAI T22 13.800] CKT 22 | 31.7456 | 0.2755 | 175.546 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 7 345.00] TO [CRAIG 5 161.00] TO [CRAI T22 13.800] CKT 22 | 31.7456 | 0.2755 | 175.546 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 7 345.00] TO [CRAIG 5 161.00] TO [CRAI T33 13.800] CKT 33 | 31.7472 | 0.2754 | 175.4463 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 7 345.00] TO [CRAIG 5 161.00] TO [CRAI T33 13.800] CKT 33 | 31.7472 | 0.2754 | 175.4463 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [CEDRCRK5 161.00] CKT 1 | 31.7481 | 0.2754 | 175.4468 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [CEDRCRK5 161.00] CKT 1 | 31.7481 | 0.2754 | 175.4468 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NASHUA 7 345.00] TO [IATAN 7 345.00] CKT 1 | 31.7411 | 0.2759 | 175.8905 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NASHUA 7 345.00] TO [IATAN 7 345.00] CKT 1 | 31.7411 | 0.2759 | 175.8905 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NASHUA 7 345.00] TO [NASHUA-5 161.00] TO [NASH T11 13.800] CKT 11 | 31.7488 | 0.2754 | 175.4081 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NASHUA 7 345.00] TO [NASHUA-5 161.00] TO [NASH T11 13.800] CKT 11 | 31.7488 | 0.2754 | 175.4081 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NASHUA 7 345.00] TO [NASHUA-5 161.00] TO [NASH T12 13.800] CKT 12 | 31.7478 | 0.2755 | 175.4586 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NASHUA 7 345.00] TO [NASHUA-5 161.00] TO [NASH T12 13.800] CKT 12 | 31.7478 | 0.2755 | 175.4586 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [LACYGNE11_7 345.00] CKT 1 | 31.7423 | 0.2756 | 175.5872 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [LACYGNE11_7 345.00] CKT 1 | 31.7423 | 0.2756 | 175.5872 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [LACYGNE22_7 345.00] CKT 1 | 31.7482 | 0.2754 | 175.4362 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [LACYGNE22_7 345.00] CKT 1 | 31.7482 | 0.2754 | 175.4362 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [LAC3_STAR7 345.00] CKT H | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [LAC3_STAR7 345.00] CKT H | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [LAC8_STAR7 345.00] CKT H | 31.7483 | 0.2754 | 175.432 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [LAC8_STAR7 345.00] CKT H | 31.7483 | 0.2754 | 175.432 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [LACYGNE2 69.000] TO [LACYGN7_TER16.9000] CKT 7 | 31.7457 | 0.2755 | 175.5218 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [LACYGNE2 69.000] TO [LACYGN7_TER16.9000] CKT 7 | 31.7457 | 0.2755 | 175.5218 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUMILS5 161.00] TO [ECKLES-161 161.00] CKT 1 | 31.7481 | 0.2754 | 175.4309 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUMILS5 161.00] TO [ECKLES-161 161.00] CKT 1 | 31.7481 | 0.2754 | 175.4309 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUMILS5 161.00] TO [BLUEMLS2 69.000] TO [BLUMILS_TER112.500] CKT 3 | 31.7475 | 0.2755 | 175.4808 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUMILS5 161.00] TO [BLUEMLS2 69.000] TO [BLUMILS_TER112.500] CKT 3 | 31.7475 | 0.2755 | 175.4808 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAKCTYJ2 69.000] TO [BLUVLY 69.000] CKT 1 | 31.7482 | 0.2754 | 175.4354 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAKCTYJ2 69.000] TO [BLUVLY 69.000] CKT 1 | 31.7482 | 0.2754 | 175.4354 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CJ 366 5 161.00] TO [FIR417 5 161.00] CKT 1 | 31.709 | 0.2755 | 175.4797 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CJ 366 5 161.00] TO [FIR417 5 161.00] CKT 1 | 31.709 | 0.2755 | 175.4797 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CAR395 5 161.00] TO [PUR421 5 161.00] CKT 1 | 31.6934 | 0.2755 | 175.47 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CAR395 5 161.00] TO [PUR421 5 161.00] CKT 1 | 31.6934 | 0.2755 | 175.47 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB K 69.000] TO [BLUVLY 69.000] CKT 1 | 31.7482 | 0.2754 | 175.4306 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB K 69.000] TO [BLUVLY 69.000] CKT 1 | 31.7482 | 0.2754 | 175.4306 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB H 69.000] TO [BLUVLY 69.000] CKT 1 | 31.7483 | 0.2754 | 175.4327 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB H 69.000] TO [BLUVLY 69.000] CKT 1 | 31.7483 | 0.2754 | 175.4327 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB H 69.000] TO [SUB M 69.000] CKT 1 | 31.7483 | 0.2754 | 175.431 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB H 69.000] TO [SUB M 69.000] CKT 1 | 31.7483 | 0.2754 | 175.431 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUVLY 13.8 13.800] TO [BLUVLY 69.000] CKT 1 | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUVLY 13.8 13.800] TO [BLUVLY 69.000] CKT 1 | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [SUB B 69.000] CKT 1 | 31.7483 | 0.2754 | 175.4316 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [SUB B 69.000] CKT 1 | 31.7483 | 0.2754 | 175.4316 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [SUB J 69.000] CKT 1 | 31.7483 | 0.2754 | 175.432 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [SUB J 69.000] CKT 1 | 31.7483 | 0.2754 | 175.432 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [SUB P 69.000] CKT 1 | 31.7483 | 0.2754 | 175.4305 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [SUB P 69.000] CKT 1 | 31.7483 | 0.2754 | 175.4305 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB B 69.000] TO [SUB J 69.000] CKT 1 | 31.7481 | 0.2754 | 175.4342 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB B 69.000] TO [SUB J 69.000] CKT 1 | 31.7481 | 0.2754 | 175.4342 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB J 69.000] TO [SUB M 69.000] CKT 1 | 31.7484 | 0.2754 | 175.4277 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB J 69.000] TO [SUB M 69.000] CKT 1 | 31.7484 | 0.2754 | 175.4277 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB M-161 161.00] TO [SUB M 69.000] CKT 1 | 31.7478 | 0.2754 | 175.4348 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB M-161 161.00] TO [SUB M 69.000] CKT 1 | 31.7478 | 0.2754 | 175.4348 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-004345.00] TO [G17-004-TAP 345.00] CKT 1 | 31.7565 | 0.2749 | 174.9367 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-004345.00] TO [G17-004-TAP 345.00] CKT 1 | 31.7565 | 0.2749 | 174.9367 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-018345.00] TO [G17-018XFMR134.500] CKT 1 | 31.7551 | 0.275 | 175.0095 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-018345.00] TO [G17-018XFMR134.500] CKT 1 | 31.7551 | 0.275 | 175.0095 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-018345.00] TO [G17-018XFMR234.500] CKT 1 | 31.7551 | 0.275 | 175.0095 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-018345.00] TO [G17-018XFMR234.500] CKT 1 | 31.7551 | 0.275 | 175.0095 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-068138.00] TO [G17-068XFMR134.500] CKT 1 | 31.7571 | 0.2749 | 174.89 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-068138.00] TO [G17-068XFMR134.500] CKT 1 | 31.7571 | 0.2749 | 174.89 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-082161.00] TO [G17-082XFMR134.500] CKT 1 | 31.7423 | 0.2758 | 175.8364 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-082161.00] TO [G17-082XFMR134.500] CKT 1 | 31.7423 | 0.2758 | 175.8364 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [S3458 3 345.00] CKT 1 | 31.7473 | 0.2755 | 175.4693 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [S3458 3 345.00] CKT 1 | 31.7473 | 0.2755 | 175.4693 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEBCTY1G 18.000] TO [S3458 3 345.00] CKT 1 | 31.7953 | 0.2725 | 172.4941 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEBCTY1G 18.000] TO [S3458 3 345.00] CKT 1 | 31.7953 | 0.2725 | 172.4941 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEBCTY2G 23.000] TO [S3458 3 345.00] CKT 1 | 31.7975 | 0.2724 | 172.3556 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEBCTY2G 23.000] TO [S3458 3 345.00] CKT 1 | 31.7975 | 0.2724 | 172.3556 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3456 3 345.00] TO [S3458 3 345.00] CKT 1 | 31.7454 | 0.2756 | 175.6018 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3456 3 345.00] TO [S3458 3 345.00] CKT 1 | 31.7454 | 0.2756 | 175.6018 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3458 3 345.00] TO [S3740 3 345.00] CKT 1 | 31.7462 | 0.2756 | 175.553 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3458 3 345.00] TO [S3740 3 345.00] CKT 1 | 31.7462 | 0.2756 | 175.553 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3458 3 345.00] TO [103&ROKEBY3 345.00] CKT 1 | 31.7471 | 0.2755 | 175.5074 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3458 3 345.00] TO [103&ROKEBY3 345.00] CKT 1 | 31.7471 | 0.2755 | 175.5074 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7FAIRPT 345.00] TO [5FAIRPTXF3 161.00] CKT 3 | 31.7447 | 0.2756 | 175.6283 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7FAIRPT 345.00] TO [5FAIRPTXF3 161.00] CKT 3 | 31.7447 | 0.2756 | 175.6283 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [G17-108-TAP 161.00] CKT 1 | 31.7297 | 0.2766 | 176.5599 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [G17-108-TAP 161.00] CKT 1 | 31.7297 | 0.2766 | 176.5599 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5GIBSON 161.00] CKT 1 | 31.7481 | 0.2754 | 175.4414 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5GIBSON 161.00] CKT 1 | 31.7481 | 0.2754 | 175.4414 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M0 161.00] CKT 1 | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M0 161.00] CKT 1 | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M1 161.00] CKT 1 | 31.7484 | 0.2754 | 175.4256 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M1 161.00] CKT 1 | 31.7484 | 0.2754 | 175.4256 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M2 161.00] CKT 1 | 31.7484 | 0.2754 | 175.4256 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M2 161.00] CKT 1 | 31.7484 | 0.2754 | 175.4256 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M3 161.00] CKT 1 | 31.7484 | 0.2754 | 175.4256 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M3 161.00] CKT 1 | 31.7484 | 0.2754 | 175.4256 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5NEWMADCP 161.00] CKT Z1 | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5NEWMADCP 161.00] CKT Z1 | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5NEWMADXF12 161.00] CKT Z1 | 31.7483 | 0.2754 | 175.43 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5NEWMADXF12 161.00] CKT Z1 | 31.7483 | 0.2754 | 175.43 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5NEWMADGSU1 161.00] CKT 1 | 31.7474 | 0.2755 | 175.4811 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5NEWMADGSU1 161.00] CKT 1 | 31.7474 | 0.2755 | 175.4811 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5NMDSU100HS 161.00] CKT 1 | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5NMDSU100HS 161.00] CKT 1 | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5NMDSU200HS 161.00] CKT 1 | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5NMDSU200HS 161.00] CKT 1 | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5PORTAGEVLE 161.00] CKT 1 | 31.748 | 0.2755 | 175.454 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5PORTAGEVLE 161.00] CKT 1 | 31.748 | 0.2755 | 175.454 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5TIPTONVL TN161.00] CKT 1 | 31.7487 | 0.2754 | 175.4078 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5TIPTONVL TN161.00] CKT 1 | 31.7487 | 0.2754 | 175.4078 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5HOLDENB2 161.00] TO [1HOLDNG11 13.800] CKT 11 | 31.7512 | 0.275 | 175.0459 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5HOLDENB2 161.00] TO [1HOLDNG11 13.800] CKT 11 | 31.7512 | 0.275 | 175.0459 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5HOLDENB2 161.00] TO [1HOLDNG12 13.800] CKT 12 | 31.7483 | 0.2754 | 175.4326 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5HOLDENB2 161.00] TO [1HOLDNG12 13.800] CKT 12 | 31.7483 | 0.2754 | 175.4326 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5HOLDENB2 161.00] TO [2HOLDEN 69.000] CKT 1 | 31.7483 | 0.2754 | 175.4323 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5HOLDENB2 161.00] TO [2HOLDEN 69.000] CKT 1 | 31.7483 | 0.2754 | 175.4323 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5HOLDENB2 161.00] TO [5HOLDENB1 161.00] CKT Z1 | 31.7488 | 0.2754 | 175.3728 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5HOLDENB2 161.00] TO [5HOLDENB1 161.00] CKT Z1 | 31.7488 | 0.2754 | 175.3728 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [2CLINTN 69.000] TO [2LINCLN 69.000] CKT 1 | 31.7467 | 0.2755 | 175.4564 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [2CLINTN 69.000] TO [2LINCLN 69.000] CKT 1 | 31.7467 | 0.2755 | 175.4564 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [2CLINTN 69.000] TO [2GAINES 69.000] CKT 1 | 31.7466 | 0.2755 | 175.5101 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [2CLINTN 69.000] TO [2GAINES 69.000] CKT 1 | 31.7466 | 0.2755 | 175.5101 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [2CLINTN 69.000] TO [2LEETON 69.000] CKT 1 | 31.7482 | 0.2754 | 175.4321 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [2CLINTN 69.000] TO [2LEETON 69.000] CKT 1 | 31.7482 | 0.2754 | 175.4321 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [2CLINTN 69.000] TO [2PIPER 69.000] CKT 1 | 31.7472 | 0.2754 | 175.4445 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [2CLINTN 69.000] TO [2PIPER 69.000] CKT 1 | 31.7472 | 0.2754 | 175.4445 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [2CLINTN 69.000] TO [2CLINTNLD 69.000] CKT 1 | 31.7442 | 0.2755 | 175.5464 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [2CLINTN 69.000] TO [2CLINTNLD 69.000] CKT 1 | 31.7442 | 0.2755 | 175.5464 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7BLACKBERRY 345.00] TO [NEOSHO 7 345.00] CKT 1 | 23.2437 | 0.2729 | 172.8591 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7BLACKBERRY 345.00] TO [NEOSHO 7 345.00] CKT 1 | 23.2437 | 0.2729 | 172.8591 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7SPORTSMAN 345.00] TO [5SPORTSMAN 161.00] CKT 1 | 31.7232 | 0.2755 | 175.4994 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7SPORTSMAN 345.00] TO [5SPORTSMAN 161.00] CKT 1 | 31.7232 | 0.2755 | 175.4994 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7SPORTSMAN 345.00] TO [5SPORTSMAN 161.00] CKT 2 | 31.7232 | 0.2755 | 175.4995 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7SPORTSMAN 345.00] TO [5SPORTSMAN 161.00] CKT 2 | 31.7232 | 0.2755 | 175.4995 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7SPORTSMAN 345.00] TO [GRDA1 7 345.00] CKT 1 | 31.4958 | 0.2748 | 174.787 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7SPORTSMAN 345.00] TO [GRDA1 7 345.00] CKT 1 | 31.4958 | 0.2748 | 174.787 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7JASPER 345.00] TO [7MORGAN 345.00] CKT 1 | 29.9159 | 0.2735 | 173.4642 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7JASPER 345.00] TO [7MORGAN 345.00] CKT 1 | 29.9159 | 0.2735 | 173.4642 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7JASPER 345.00] TO [5JASPER 161.00] CKT 1 | 31.4931 | 0.2753 | 175.3071 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7JASPER 345.00] TO [5JASPER 161.00] CKT 1 | 31.4931 | 0.2753 | 175.3071 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5OSCEOKCTP 161.00] TO [5OSCEOLTP 161.00] CKT 1 | 31.7205 | 0.2759 | 175.9131 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5OSCEOKCTP 161.00] TO [5OSCEOLTP 161.00] CKT 1 | 31.7205 | 0.2759 | 175.9131 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5OSCEOKCTP 161.00] TO [5OSCEOKC 161.00] CKT 1 | 31.7487 | 0.2754 | 175.3959 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5OSCEOKCTP 161.00] TO [5OSCEOKC 161.00] CKT 1 | 31.7487 | 0.2754 | 175.3959 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5MINER 1 161.00] TO [5CHARLSTN 161.00] CKT 1 | 31.7482 | 0.2754 | 175.436 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5MINER 1 161.00] TO [5CHARLSTN 161.00] CKT 1 | 31.7482 | 0.2754 | 175.436 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5MINER 1 161.00] TO [5BULLION 161.00] CKT 1 | 31.7477 | 0.2755 | 175.4669 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5MINER 1 161.00] TO [5BULLION 161.00] CKT 1 | 31.7477 | 0.2755 | 175.4669 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5MINER 1 161.00] TO [5MINER 2 161.00] CKT Z | 31.7483 | 0.2754 | 175.4352 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5MINER 1 161.00] TO [5MINER 2 161.00] CKT Z | 31.7483 | 0.2754 | 175.4352 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N MADRD5 161.00] TO [G17-202-TAP 161.00] CKT 1 | 31.7478 | 0.2755 | 175.4631 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N MADRD5 161.00] TO [G17-202-TAP 161.00] CKT 1 | 31.7478 | 0.2755 | 175.4631 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N MADRD2 69.000] TO [2STJUDEW 69.000] CKT 1 | 31.7483 | 0.2754 | 175.4339 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N MADRD2 69.000] TO [2STJUDEW 69.000] CKT 1 | 31.7483 | 0.2754 | 175.4339 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N MADRD2 69.000] TO [2LILBRN 69.000] CKT 1 | 31.7483 | 0.2754 | 175.4313 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N MADRD2 69.000] TO [2LILBRN 69.000] CKT 1 | 31.7483 | 0.2754 | 175.4313 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N MADRD2 69.000] TO [MALDEN 2 69.000] CKT 1 | 31.7482 | 0.2754 | 175.4362 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N MADRD2 69.000] TO [MALDEN 2 69.000] CKT 1 | 31.7482 | 0.2754 | 175.4362 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KENNETT5 161.00] TO [PARAGLD5 161.00] CKT 1 | 31.7478 | 0.2755 | 175.4663 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KENNETT5 161.00] TO [PARAGLD5 161.00] CKT 1 | 31.7478 | 0.2755 | 175.4663 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KENNETT5 161.00] TO [KENNETT2 69.000] TO [KEN X1 1 13.800] CKT 1 | 31.7483 | 0.2754 | 175.432 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KENNETT5 161.00] TO [KENNETT2 69.000] TO [KEN X1 1 13.800] CKT 1 | 31.7483 | 0.2754 | 175.432 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KENNETT5 161.00] TO [KENNETT2 69.000] TO [KEN X2 1 13.800] CKT 1 | 31.7483 | 0.2754 | 175.432 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KENNETT5 161.00] TO [KENNETT2 69.000] TO [KEN X2 1 13.800] CKT 1 | 31.7483 | 0.2754 | 175.432 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SIKETAP5 161.00] TO [SIKE SW5 161.00] CKT 1 | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SIKETAP5 161.00] TO [SIKE SW5 161.00] CKT 1 | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SIKESTN5 161.00] TO [G17-202-TAP 161.00] CKT 1 | 31.7481 | 0.2754 | 175.443 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SIKESTN5 161.00] TO [G17-202-TAP 161.00] CKT 1 | 31.7481 | 0.2754 | 175.443 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IDALIA 5 161.00] TO [5ESSEX 161.00] CKT 1 | 31.7479 | 0.2755 | 175.4585 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IDALIA 5 161.00] TO [5ESSEX 161.00] CKT 1 | 31.7479 | 0.2755 | 175.4585 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IDALIA 5 161.00] TO [2IDALIA 69.000] CKT 1 | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IDALIA 5 161.00] TO [2IDALIA 69.000] CKT 1 | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IDALIA 5 161.00] TO [2IDALIA 69.000] CKT 2 | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IDALIA 5 161.00] TO [2IDALIA 69.000] CKT 2 | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IDALIA 5 161.00] TO [ASHRVL5 161.00] CKT 1 | 31.7472 | 0.2755 | 175.4937 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IDALIA 5 161.00] TO [ASHRVL5 161.00] CKT 1 | 31.7472 | 0.2755 | 175.4937 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TRUMAN 5 161.00] TO [5LOSTVALY 161.00] CKT 1 | 31.7329 | 0.2764 | 176.4169 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TRUMAN 5 161.00] TO [5LOSTVALY 161.00] CKT 1 | 31.7329 | 0.2764 | 176.4169 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TRUMAN 5 161.00] TO [TRU123 1 13.800] CKT 1 | 31.7486 | 0.2753 | 175.2746 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TRUMAN 5 161.00] TO [TRU123 1 13.800] CKT 1 | 31.7486 | 0.2753 | 175.2746 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TRUMAN 5 161.00] TO [TRU456 1 13.800] CKT 1 | 31.7487 | 0.2753 | 175.2735 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TRUMAN 5 161.00] TO [TRU456 1 13.800] CKT 1 | 31.7487 | 0.2753 | 175.2735 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DELWARE4 138.00] TO [FARML 4 138.00] CKT 1 | 31.6558 | 0.275 | 174.9973 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DELWARE4 138.00] TO [FARML 4 138.00] CKT 1 | 31.6558 | 0.275 | 174.9973 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DELWARE7 345.00] TO [NEOSHO 7 345.00] CKT 1 | 25.7474 | 0.2805 | 180.5063 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DELWARE7 345.00] TO [NEOSHO 7 345.00] CKT 1 | 25.7474 | 0.2805 | 180.5063 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N.E.S.-7 345.00] TO [ONETA--7 345.00] CKT 1 | 31.079 | 0.2754 | 175.3603 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N.E.S.-7 345.00] TO [ONETA--7 345.00] CKT 1 | 31.079 | 0.2754 | 175.3603 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N.E.S.-7 345.00] TO [T.NO.--7 345.00] CKT 1 | 31.1617 | 0.2754 | 175.3742 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N.E.S.-7 345.00] TO [T.NO.--7 345.00] CKT 1 | 31.1617 | 0.2754 | 175.3742 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N.E.S.-7 345.00] TO [NES3-1 22.000] CKT 1 | 31.3629 | 0.2779 | 177.8754 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N.E.S.-7 345.00] TO [NES3-1 22.000] CKT 1 | 31.3629 | 0.2779 | 177.8754 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [TATONGA7 345.00] CKT 1 | 31.7463 | 0.2756 | 175.5688 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [TATONGA7 345.00] CKT 1 | 31.7463 | 0.2756 | 175.5688 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [TATONGA7 345.00] CKT 2 | 31.7463 | 0.2756 | 175.5708 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [TATONGA7 345.00] CKT 2 | 31.7463 | 0.2756 | 175.5708 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [G07621119-20345.00] CKT 1 | 31.7482 | 0.2755 | 175.4501 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [G07621119-20345.00] CKT 1 | 31.7482 | 0.2755 | 175.4501 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [GUTHRIE7 345.00] CKT 1 | 31.7482 | 0.2754 | 175.4397 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [GUTHRIE7 345.00] CKT 1 | 31.7482 | 0.2754 | 175.4397 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [BECKHAM7 345.00] CKT 1 | 31.7376 | 0.2758 | 175.7931 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [BECKHAM7 345.00] CKT 1 | 31.7376 | 0.2758 | 175.7931 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [G16-003-TAP 345.00] CKT 1 | 31.7479 | 0.2754 | 175.4091 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [G16-003-TAP 345.00] CKT 1 | 31.7479 | 0.2754 | 175.4091 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [G16-003-TAP 345.00] CKT 2 | 31.7479 | 0.2754 | 175.4091 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [G16-003-TAP 345.00] CKT 2 | 31.7479 | 0.2754 | 175.4091 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [WWRDEHV4 138.00] TO [WWDEHV31 13.800] CKT 1 | 31.7482 | 0.2754 | 175.4183 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [WWRDEHV4 138.00] TO [WWDEHV31 13.800] CKT 1 | 31.7482 | 0.2754 | 175.4183 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [WWRDEHV4 138.00] TO [WWDEHV21 13.800] CKT 2 | 31.7482 | 0.2754 | 175.4094 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [WWRDEHV4 138.00] TO [WWDEHV21 13.800] CKT 2 | 31.7482 | 0.2754 | 175.4094 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DGRASSE7 345.00] TO [THISTLE7 345.00] CKT 1 | 31.7316 | 0.2759 | 175.9086 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DGRASSE7 345.00] TO [THISTLE7 345.00] CKT 1 | 31.7316 | 0.2759 | 175.9086 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DGRASSE7 345.00] TO [THISTLE7 345.00] CKT 2 | 31.7316 | 0.2759 | 175.9085 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DGRASSE7 345.00] TO [THISTLE7 345.00] CKT 2 | 31.7316 | 0.2759 | 175.9085 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DGRASSE4 138.00] TO [KNOBHIL4 138.00] CKT 1 | 31.7479 | 0.2754 | 175.4458 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DGRASSE4 138.00] TO [KNOBHIL4 138.00] CKT 1 | 31.7479 | 0.2754 | 175.4458 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DGRASSE4 138.00] TO [ROSEVLY4 138.00] CKT 1 | 31.7479 | 0.2754 | 175.4472 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DGRASSE4 138.00] TO [ROSEVLY4 138.00] CKT 1 | 31.7479 | 0.2754 | 175.4472 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DGRASSE4 138.00] TO [MOORLND4 138.00] CKT 1 | 31.7456 | 0.2755 | 175.4526 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DGRASSE4 138.00] TO [MOORLND4 138.00] CKT 1 | 31.7456 | 0.2755 | 175.4526 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WALKMYR2 69.000] TO [NORTH6T2 69.000] CKT 1 | 31.7477 | 0.2755 | 175.4589 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WALKMYR2 69.000] TO [NORTH6T2 69.000] CKT 1 | 31.7477 | 0.2755 | 175.4589 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WALKMYR2 69.000] TO [WOODS 2 69.000] CKT 1 | 31.7478 | 0.2755 | 175.4533 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WALKMYR2 69.000] TO [WOODS 2 69.000] CKT 1 | 31.7478 | 0.2755 | 175.4533 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WALKMYR3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 31.7481 | 0.2754 | 175.446 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WALKMYR3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 31.7481 | 0.2754 | 175.446 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SEWARD-3 115.00] TO [HASKELL3 115.00] CKT 1 | 31.748 | 0.2754 | 175.4443 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SEWARD-3 115.00] TO [HASKELL3 115.00] CKT 1 | 31.748 | 0.2754 | 175.4443 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SEWARD-3 115.00] TO [CMSSWRD2 69.000] TO [SEWARD 1 13.800] CKT 1 | 31.7478 | 0.2755 | 175.4523 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SEWARD-3 115.00] TO [CMSSWRD2 69.000] TO [SEWARD 1 13.800] CKT 1 | 31.7478 | 0.2755 | 175.4523 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [POSTROCK7 345.00] CKT 1 | 31.7476 | 0.2753 | 175.3436 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [POSTROCK7 345.00] CKT 1 | 31.7476 | 0.2753 | 175.3436 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [BUCKNER7 345.00] CKT 1 | 31.7406 | 0.2753 | 175.3384 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [BUCKNER7 345.00] CKT 1 | 31.7406 | 0.2753 | 175.3384 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [IRONWOOD7 345.00] CKT 1 | 31.7462 | 0.2754 | 175.4447 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [IRONWOOD7 345.00] CKT 1 | 31.7462 | 0.2754 | 175.4447 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [SPRVL 3 115.00] TO [SPRVL-T 13.800] CKT 1 | 31.7483 | 0.2754 | 175.4336 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [SPRVL 3 115.00] TO [SPRVL-T 13.800] CKT 1 | 31.7483 | 0.2754 | 175.4336 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [SPEARVL6 230.00] TO [SPERTER1 13.800] CKT 1 | 31.749 | 0.2754 | 175.4112 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [SPEARVL6 230.00] TO [SPERTER1 13.800] CKT 1 | 31.749 | 0.2754 | 175.4112 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HUGOTON3 115.00] TO [GRANTTP3 115.00] CKT 1 | 31.7478 | 0.2755 | 175.453 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HUGOTON3 115.00] TO [GRANTTP3 115.00] CKT 1 | 31.7478 | 0.2755 | 175.453 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HUGOTON3 115.00] TO [ABBK 2 115.00] CKT 1 | 31.7476 | 0.2755 | 175.4613 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HUGOTON3 115.00] TO [ABBK 2 115.00] CKT 1 | 31.7476 | 0.2755 | 175.4613 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HUGOTON3 115.00] TO [HUGOTON2 69.000] TO [HUGOTON1 13.800] CKT 1 | 31.7468 | 0.2755 | 175.4966 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HUGOTON3 115.00] TO [HUGOTON2 69.000] TO [HUGOTON1 13.800] CKT 1 | 31.7468 | 0.2755 | 175.4966 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HARBNGR3 115.00] TO [HARBNGR7 345.00] TO [HARBNGR-T 13.800] CKT 1 | 31.7478 | 0.2755 | 175.4518 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HARBNGR3 115.00] TO [HARBNGR7 345.00] TO [HARBNGR-T 13.800] CKT 1 | 31.7478 | 0.2755 | 175.4518 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EEC GT1 13.800] TO [DG TIE 1 4.1600] CKT 1 | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EEC GT1 13.800] TO [DG TIE 1 4.1600] CKT 1 | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EEC GT2 13.800] TO [EEC DG 1 4.1600] CKT 1 | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EEC GT2 13.800] TO [EEC DG 1 4.1600] CKT 1 | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC121 13.800] CKT 1 | 31.7507 | 0.275 | 174.9976 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC121 13.800] CKT 1 | 31.7507 | 0.275 | 174.9976 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC341 13.800] CKT 1 | 31.7507 | 0.275 | 174.9976 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC341 13.800] CKT 1 | 31.7507 | 0.275 | 174.9976 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC5 1 18.000] CKT 1 | 31.7505 | 0.2746 | 174.6366 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC5 1 18.000] CKT 1 | 31.7505 | 0.2746 | 174.6366 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC6 1 18.000] CKT 1 | 31.7553 | 0.2743 | 174.3332 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC6 1 18.000] CKT 1 | 31.7553 | 0.2743 | 174.3332 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC7 1 18.000] CKT 1 | 31.7483 | 0.2754 | 175.4332 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC7 1 18.000] CKT 1 | 31.7483 | 0.2754 | 175.4332 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [LANG 7 345.00] CKT 1 | 31.7437 | 0.2755 | 175.528 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [LANG 7 345.00] CKT 1 | 31.7437 | 0.2755 | 175.528 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [MORRIS 7 345.00] CKT 1 | 31.7441 | 0.2754 | 175.3676 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [MORRIS 7 345.00] CKT 1 | 31.7441 | 0.2754 | 175.3676 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [READWF 7 345.00] CKT 1 | 31.7556 | 0.275 | 174.99 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [READWF 7 345.00] CKT 1 | 31.7556 | 0.275 | 174.99 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RENO 7 345.00] TO [G16-111-TAP 345.00] CKT 1 | 31.7113 | 0.2761 | 176.0718 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RENO 7 345.00] TO [G16-111-TAP 345.00] CKT 1 | 31.7113 | 0.2761 | 176.0718 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RENO 7 345.00] TO [RENO 3 115.00] TO [RENO 1X1 14.400] CKT 1 | 31.7476 | 0.2754 | 175.3852 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RENO 7 345.00] TO [RENO 3 115.00] TO [RENO 1X1 14.400] CKT 1 | 31.7476 | 0.2754 | 175.3852 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RENO 7 345.00] TO [RENO 3 115.00] TO [RENO 2X1 14.400] CKT 1 | 31.7475 | 0.2754 | 175.3889 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RENO 7 345.00] TO [RENO 3 115.00] TO [RENO 2X1 14.400] CKT 1 | 31.7475 | 0.2754 | 175.3889 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 7 345.00] TO [GEARY 7 345.00] CKT 1 | 31.7347 | 0.2757 | 175.6671 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 7 345.00] TO [GEARY 7 345.00] CKT 1 | 31.7347 | 0.2757 | 175.6671 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 7 345.00] TO [G16-111-TAP 345.00] CKT 1 | 31.715 | 0.2757 | 175.674 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 7 345.00] TO [G16-111-TAP 345.00] CKT 1 | 31.715 | 0.2757 | 175.674 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 7 345.00] TO [SUMMIT 6 230.00] TO [SUMMIT 1 14.400] CKT 1 | 31.7478 | 0.2754 | 175.4257 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 7 345.00] TO [SUMMIT 6 230.00] TO [SUMMIT 1 14.400] CKT 1 | 31.7478 | 0.2754 | 175.4257 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SWISVAL7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 31.7282 | 0.2751 | 175.0624 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SWISVAL7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 31.7282 | 0.2751 | 175.0624 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [87TH 7 345.00] TO [STRANGR7 345.00] CKT 1 | 31.7187 | 0.2751 | 175.0756 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [87TH 7 345.00] TO [STRANGR7 345.00] CKT 1 | 31.7187 | 0.2751 | 175.0756 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [87TH 7 345.00] TO [87TH 3 115.00] TO [87TH 1X1 13.800] CKT 1 | 31.746 | 0.2755 | 175.4995 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [87TH 7 345.00] TO [87TH 3 115.00] TO [87TH 1X1 13.800] CKT 1 | 31.746 | 0.2755 | 175.4995 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-009-TAP 345.00] TO [NEOSHO 7 345.00] CKT 1 | 27.8259 | 0.289 | 189.0365 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-009-TAP 345.00] TO [NEOSHO 7 345.00] CKT 1 | 27.8259 | 0.289 | 189.0365 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-009345.00] TO [G17-009XFMR134.500] CKT 1 | 31.7573 | 0.2765 | 176.4589 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-009345.00] TO [G17-009XFMR134.500] CKT 1 | 31.7573 | 0.2765 | 176.4589 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-009345.00] TO [G17-009XFMR234.500] CKT 1 | 31.7596 | 0.2765 | 176.4966 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-009345.00] TO [G17-009XFMR234.500] CKT 1 | 31.7596 | 0.2765 | 176.4966 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CANEYRV7 345.00] TO [CANEYWF7 345.00] CKT 1 | 31.7618 | 0.2754 | 175.4051 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CANEYRV7 345.00] TO [CANEYWF7 345.00] CKT 1 | 31.7618 | 0.2754 | 175.4051 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CANEYRV7 345.00] TO [LATHAMS7 345.00] CKT 1 | 27.6886 | 0.2734 | 173.4157 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CANEYRV7 345.00] TO [LATHAMS7 345.00] CKT 1 | 27.6886 | 0.2734 | 173.4157 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KINGMAN7 345.00] TO [BUFFALO7 345.00] CKT 1 | 31.7684 | 0.2744 | 174.386 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KINGMAN7 345.00] TO [BUFFALO7 345.00] CKT 1 | 31.7684 | 0.2744 | 174.386 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NINN1WF7 345.00] TO [PRATTWF7 345.00] CKT 1 | 31.7582 | 0.2749 | 174.8621 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NINN1WF7 345.00] TO [PRATTWF7 345.00] CKT 1 | 31.7582 | 0.2749 | 174.8621 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NINN1WF7 345.00] TO [N1 LV 1 34.500] TO [N1 WFTX1 13.800] CKT 1 | 31.7546 | 0.275 | 175.0393 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NINN1WF7 345.00] TO [N1 LV 1 34.500] TO [N1 WFTX1 13.800] CKT 1 | 31.7546 | 0.275 | 175.0393 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTON 7 345.00] TO [ROSEHIL7 345.00] CKT 1 | 31.4515 | 0.2743 | 174.2515 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTON 7 345.00] TO [ROSEHIL7 345.00] CKT 1 | 31.4515 | 0.2743 | 174.2515 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTON 7 345.00] TO [BENTON 4 138.00] TO [BENTN1 1 13.800] CKT 1 | 31.7442 | 0.2757 | 175.692 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTON 7 345.00] TO [BENTON 4 138.00] TO [BENTN1 1 13.800] CKT 1 | 31.7442 | 0.2757 | 175.692 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTON 7 345.00] TO [BENTON 4 138.00] TO [BENTN2 1 13.800] CKT 1 | 31.7445 | 0.2757 | 175.6763 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTON 7 345.00] TO [BENTON 4 138.00] TO [BENTN2 1 13.800] CKT 1 | 31.7445 | 0.2757 | 175.6763 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 1 | 31.744 | 0.2753 | 175.3366 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 1 | 31.744 | 0.2753 | 175.3366 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 2 | 31.744 | 0.2753 | 175.3366 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 2 | 31.744 | 0.2753 | 175.3366 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [EVANS N4 138.00] TO [WICH11 1 13.800] CKT 1 | 31.7494 | 0.2755 | 175.4559 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [EVANS N4 138.00] TO [WICH11 1 13.800] CKT 1 | 31.7494 | 0.2755 | 175.4559 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [EVANS N4 138.00] TO [WICH12 1 13.800] CKT 1 | 31.75 | 0.2755 | 175.4593 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [EVANS N4 138.00] TO [WICH12 1 13.800] CKT 1 | 31.75 | 0.2755 | 175.4593 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WOLFCRK7 345.00] TO [WCGS U1 25.000] CKT 1 | 31.2999 | 0.258 | 157.9649 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WOLFCRK7 345.00] TO [WCGS U1 25.000] CKT 1 | 31.2999 | 0.258 | 157.9649 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WOLFCRK7 345.00] TO [ROSEHIL7 345.00] CKT 1 | 31.7101 | 0.2781 | 178.1062 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WOLFCRK7 345.00] TO [ROSEHIL7 345.00] CKT 1 | 31.7101 | 0.2781 | 178.1062 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WOLFCRK7 345.00] TO [WOLFCRK2 69.000] TO [WOLFCRK1 17.000] CKT 1 | 31.736 | 0.2764 | 176.4127 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WOLFCRK7 345.00] TO [WOLFCRK2 69.000] TO [WOLFCRK1 17.000] CKT 1 | 31.736 | 0.2764 | 176.4127 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [VIOLA 7 345.00] TO [RENFROW7 345.00] CKT 1 | 31.6768 | 0.2776 | 177.62 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [VIOLA 7 345.00] TO [RENFROW7 345.00] CKT 1 | 31.6768 | 0.2776 | 177.62 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [VIOLA 7 345.00] TO [G16-153-TAP 345.00] CKT 1 | 31.7704 | 0.2743 | 174.3373 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [VIOLA 7 345.00] TO [G16-153-TAP 345.00] CKT 1 | 31.7704 | 0.2743 | 174.3373 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WAVERLY7 345.00] TO [WAVERTX7 345.00] CKT 1 | 31.7661 | 0.2748 | 174.8013 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WAVERLY7 345.00] TO [WAVERTX7 345.00] CKT 1 | 31.7661 | 0.2748 | 174.8013 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EXPEDITION7 345.00] TO [GEN-2014-001345.00] CKT 1 | 31.7563 | 0.275 | 175.0117 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EXPEDITION7 345.00] TO [GEN-2014-001345.00] CKT 1 | 31.7563 | 0.275 | 175.0117 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N345 1 1 13.800] TO [NEOSHO 7 345.00] TO [NEOSHO 4 138.00] CKT 1 | 30.9164 | 0.2789 | 178.8898 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N345 1 1 13.800] TO [NEOSHO 7 345.00] TO [NEOSHO 4 138.00] CKT 1 | 30.9164 | 0.2789 | 178.8898 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N345 2 1 13.800] TO [NEOSHO 7 345.00] TO [NEOSHO 5 161.00] CKT 1 | 29.9402 | 0.2696 | 169.5743 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N345 2 1 13.800] TO [NEOSHO 7 345.00] TO [NEOSHO 5 161.00] CKT 1 | 29.9402 | 0.2696 | 169.5743 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SWISVAL6 230.00] TO [AUBURN 6 230.00] CKT 1 | 31.7454 | 0.2754 | 175.3707 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SWISVAL6 230.00] TO [AUBURN 6 230.00] CKT 1 | 31.7454 | 0.2754 | 175.3707 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SWISVAL6 230.00] TO [LAWHILL6 230.00] CKT 1 | 31.7421 | 0.2754 | 175.4475 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SWISVAL6 230.00] TO [LAWHILL6 230.00] CKT 1 | 31.7421 | 0.2754 | 175.4475 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SWISVAL6 230.00] TO [TECHILL6 230.00] CKT 1 | 31.7455 | 0.2755 | 175.4715 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SWISVAL6 230.00] TO [TECHILL6 230.00] CKT 1 | 31.7455 | 0.2755 | 175.4715 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SWISVAL6 230.00] TO [MORRIS 6 230.00] CKT 1 | 31.7477 | 0.2754 | 175.4353 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SWISVAL6 230.00] TO [MORRIS 6 230.00] CKT 1 | 31.7477 | 0.2754 | 175.4353 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NMANHT6 230.00] TO [EMANHAT6 230.00] CKT 1 | 31.7467 | 0.2755 | 175.4774 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NMANHT6 230.00] TO [EMANHAT6 230.00] CKT 1 | 31.7467 | 0.2755 | 175.4774 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NMANHT6 230.00] TO [NMANHT3 115.00] TO [NMANHX1 14.400] CKT 1 | 31.7478 | 0.2754 | 175.432 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NMANHT6 230.00] TO [NMANHT3 115.00] TO [NMANHX1 14.400] CKT 1 | 31.7478 | 0.2754 | 175.432 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH 5 161.00] TO [ASB349 5 161.00] CKT 1 | 31.4746 | 0.276 | 175.9974 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH 5 161.00] TO [ASB349 5 161.00] CKT 1 | 31.4746 | 0.276 | 175.9974 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MARMTNW5 161.00] TO [MARMTNE5 161.00] CKT Z1 | 31.3691 | 0.2738 | 173.7586 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MARMTNW5 161.00] TO [MARMTNE5 161.00] CKT Z1 | 31.3691 | 0.2738 | 173.7586 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MARMTNW5 161.00] TO [MARMATN2 69.000] TO [MARMATN1 13.200] CKT 1 | 31.7237 | 0.2759 | 175.8856 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MARMTNW5 161.00] TO [MARMATN2 69.000] TO [MARMATN1 13.200] CKT 1 | 31.7237 | 0.2759 | 175.8856 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FRANKLIN5 161.00] TO [G17-005-TAP 161.00] CKT 1 | 31.6643 | 0.2777 | 177.7456 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FRANKLIN5 161.00] TO [G17-005-TAP 161.00] CKT 1 | 31.6643 | 0.2777 | 177.7456 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FRANKLIN5 161.00] TO [FRANKLIN2 69.000] TO [FRANKLIN1 12.470] CKT 1 | 31.7339 | 0.2754 | 175.3622 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FRANKLIN5 161.00] TO [FRANKLIN2 69.000] TO [FRANKLIN1 12.470] CKT 1 | 31.7339 | 0.2754 | 175.3622 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRESWLN4 138.00] TO [MIDLTNT4 138.00] CKT 1 | 31.7385 | 0.2755 | 175.4886 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRESWLN4 138.00] TO [MIDLTNT4 138.00] CKT 1 | 31.7385 | 0.2755 | 175.4886 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRESWLN4 138.00] TO [SLATECRK4 138.00] CKT 1 | 31.7472 | 0.2752 | 175.2458 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRESWLN4 138.00] TO [SLATECRK4 138.00] CKT 1 | 31.7472 | 0.2752 | 175.2458 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRESWLN4 138.00] TO [CRESWLN2 69.000] TO [CRESW1 1 13.200] CKT 1 | 31.7485 | 0.2754 | 175.4353 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRESWLN4 138.00] TO [CRESWLN2 69.000] TO [CRESW1 1 13.200] CKT 1 | 31.7485 | 0.2754 | 175.4353 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRESWLN4 138.00] TO [CRESWLS2 69.000] TO [CRESW2 1 13.200] CKT 1 | 31.7488 | 0.2754 | 175.422 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRESWLN4 138.00] TO [CRESWLS2 69.000] TO [CRESW2 1 13.200] CKT 1 | 31.7488 | 0.2754 | 175.422 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [OXFORD 4 138.00] TO [SUMNER 4 138.00] CKT 1 | 31.7314 | 0.2756 | 175.6318 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [OXFORD 4 138.00] TO [SUMNER 4 138.00] CKT 1 | 31.7314 | 0.2756 | 175.6318 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TIMBJCT4 138.00] TO [SUMNER 4 138.00] CKT 1 | 31.748 | 0.2755 | 175.4829 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TIMBJCT4 138.00] TO [SUMNER 4 138.00] CKT 1 | 31.748 | 0.2755 | 175.4829 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TIOGA 4 138.00] TO [TIOGA 2 69.000] TO [TIOGA 1 13.200] CKT 1 | 31.5221 | 0.2754 | 175.3872 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TIOGA 4 138.00] TO [TIOGA 2 69.000] TO [TIOGA 1 13.200] CKT 1 | 31.5221 | 0.2754 | 175.3872 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [OTTRCRK4 138.00] TO [BUTLER 4 138.00] CKT 1 | 31.7067 | 0.2753 | 175.2984 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [OTTRCRK4 138.00] TO [BUTLER 4 138.00] CKT 1 | 31.7067 | 0.2753 | 175.2984 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [OTTRCRK4 138.00] TO [OTTRCRK3 115.00] TO [OTTRX1 1 13.800] CKT 1 | 31.7036 | 0.2753 | 175.3188 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [OTTRCRK4 138.00] TO [OTTRCRK3 115.00] TO [OTTRX1 1 13.800] CKT 1 | 31.7036 | 0.2753 | 175.3188 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ALTOONA4 138.00] TO [G17-022-TAP 138.00] CKT 1 | 31.2026 | 0.2766 | 176.585 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ALTOONA4 138.00] TO [G17-022-TAP 138.00] CKT 1 | 31.2026 | 0.2766 | 176.585 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEPARSN4 138.00] TO [G17-022-TAP 138.00] CKT 1 | 31.1563 | 0.2765 | 176.4577 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEPARSN4 138.00] TO [G17-022-TAP 138.00] CKT 1 | 31.1563 | 0.2765 | 176.4577 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TAYLOR 4 138.00] TO [MONTGOM4 138.00] CKT 1 | 31.7249 | 0.2762 | 176.2133 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TAYLOR 4 138.00] TO [MONTGOM4 138.00] CKT 1 | 31.7249 | 0.2762 | 176.2133 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTLEY4 138.00] TO [HALSTD 4 138.00] CKT 1 | 31.7437 | 0.2754 | 175.4389 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTLEY4 138.00] TO [HALSTD 4 138.00] CKT 1 | 31.7437 | 0.2754 | 175.4389 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTLEY4 138.00] TO [WWUPLNT4 138.00] CKT 1 | 31.7474 | 0.2755 | 175.461 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTLEY4 138.00] TO [WWUPLNT4 138.00] CKT 1 | 31.7474 | 0.2755 | 175.461 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHOS4 138.00] TO [TV1MNDV4 138.00] CKT 1 | 31.4167 | 0.2752 | 175.169 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHOS4 138.00] TO [TV1MNDV4 138.00] CKT 1 | 31.4167 | 0.2752 | 175.169 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHON4 138.00] TO [NEOSHON2 69.000] TO [NEC U3 12.000] CKT 1 | 31.7399 | 0.2754 | 175.4086 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHON4 138.00] TO [NEOSHON2 69.000] TO [NEC U3 12.000] CKT 1 | 31.7399 | 0.2754 | 175.4086 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CHISHLM4 138.00] TO [PARKCTY4 138.00] CKT 1 | 31.7418 | 0.2754 | 175.3661 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CHISHLM4 138.00] TO [PARKCTY4 138.00] CKT 1 | 31.7418 | 0.2754 | 175.3661 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CHISHLM4 138.00] TO [17TH 4 138.00] CKT 1 | 31.7445 | 0.2756 | 175.6274 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CHISHLM4 138.00] TO [17TH 4 138.00] CKT 1 | 31.7445 | 0.2756 | 175.6274 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CHISHLM4 138.00] TO [CHISHLM2 69.000] TO [CHISOLM1 13.200] CKT 1 | 31.746 | 0.2756 | 175.553 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CHISHLM4 138.00] TO [CHISHLM2 69.000] TO [CHISOLM1 13.200] CKT 1 | 31.746 | 0.2756 | 175.553 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EVANS S4 138.00] TO [EVANS N4 138.00] CKT Z1 | 31.7483 | 0.2754 | 175.4339 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EVANS S4 138.00] TO [EVANS N4 138.00] CKT Z1 | 31.7483 | 0.2754 | 175.4339 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EVANS S4 138.00] TO [EVANS N4 138.00] CKT Z2 | 31.7483 | 0.2754 | 175.4339 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EVANS S4 138.00] TO [EVANS N4 138.00] CKT Z2 | 31.7483 | 0.2754 | 175.4339 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FARBER 4 138.00] TO [ELPASOE4 138.00] CKT 1 | 31.7265 | 0.2755 | 175.5244 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FARBER 4 138.00] TO [ELPASOE4 138.00] CKT 1 | 31.7265 | 0.2755 | 175.5244 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GILL 4 138.00] TO [GILL W 4 138.00] CKT Z1 | 31.7483 | 0.2754 | 175.4326 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GILL 4 138.00] TO [GILL W 4 138.00] CKT Z1 | 31.7483 | 0.2754 | 175.4326 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GILL 4 138.00] TO [GILL S 4 138.00] CKT Z1 | 31.7483 | 0.2754 | 175.4329 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GILL 4 138.00] TO [GILL S 4 138.00] CKT Z1 | 31.7483 | 0.2754 | 175.4329 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAKERDG4 138.00] TO [HOOVERN4 138.00] CKT 1 | 31.7434 | 0.2759 | 175.8632 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAKERDG4 138.00] TO [HOOVERN4 138.00] CKT 1 | 31.7434 | 0.2759 | 175.8632 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MAIZE 4 138.00] TO [EVANS N4 138.00] CKT 1 | 31.7344 | 0.2758 | 175.8201 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MAIZE 4 138.00] TO [EVANS N4 138.00] CKT 1 | 31.7344 | 0.2758 | 175.8201 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SC10BEL4 138.00] TO [SUMNER 4 138.00] CKT 1 | 31.7281 | 0.2756 | 175.5892 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SC10BEL4 138.00] TO [SUMNER 4 138.00] CKT 1 | 31.7281 | 0.2756 | 175.5892 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SG12COL4 138.00] TO [EVANS N4 138.00] CKT 1 | 31.7433 | 0.2754 | 175.4436 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SG12COL4 138.00] TO [EVANS N4 138.00] CKT 1 | 31.7433 | 0.2754 | 175.4436 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [45TH ST4 138.00] TO [COWSKIN4 138.00] CKT 1 | 31.7425 | 0.276 | 175.9801 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [45TH ST4 138.00] TO [COWSKIN4 138.00] CKT 1 | 31.7425 | 0.276 | 175.9801 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [VIOLA 4 138.00] TO [SUMNER 4 138.00] CKT 1 | 31.746 | 0.2755 | 175.4774 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [VIOLA 4 138.00] TO [SUMNER 4 138.00] CKT 1 | 31.746 | 0.2755 | 175.4774 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [AEC 3 115.00] TO [G17-120-TAP 115.00] CKT 1 | 31.7497 | 0.2753 | 175.2745 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [AEC 3 115.00] TO [G17-120-TAP 115.00] CKT 1 | 31.7497 | 0.2753 | 175.2745 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EABILEN3 115.00] TO [CHAPMAN3 115.00] CKT 1 | 31.7499 | 0.2753 | 175.2793 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EABILEN3 115.00] TO [CHAPMAN3 115.00] CKT 1 | 31.7499 | 0.2753 | 175.2793 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NORTHST3 115.00] TO [SALINA 3 115.00] CKT 1 | 31.7472 | 0.2755 | 175.4571 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NORTHST3 115.00] TO [SALINA 3 115.00] CKT 1 | 31.7472 | 0.2755 | 175.4571 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NORTHVW3 115.00] TO [G17-120-TAP 115.00] CKT 1 | 31.7462 | 0.2756 | 175.5694 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NORTHVW3 115.00] TO [G17-120-TAP 115.00] CKT 1 | 31.7462 | 0.2756 | 175.5694 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 3 115.00] TO [MENTOR 3 115.00] CKT 1 | 31.7486 | 0.2754 | 175.4084 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 3 115.00] TO [MENTOR 3 115.00] CKT 1 | 31.7486 | 0.2754 | 175.4084 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 3 115.00] TO [SO GATE3 115.00] CKT 1 | 31.7481 | 0.2754 | 175.4376 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 3 115.00] TO [SO GATE3 115.00] CKT 1 | 31.7481 | 0.2754 | 175.4376 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 3 115.00] TO [SUMMIT 6 230.00] TO [SUMIT2 1 13.800] CKT 1 | 31.7483 | 0.2754 | 175.4321 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 3 115.00] TO [SUMMIT 6 230.00] TO [SUMIT2 1 13.800] CKT 1 | 31.7483 | 0.2754 | 175.4321 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 3 115.00] TO [SUMMIT 6 230.00] TO [SUMIT3 1 13.800] CKT 1 | 31.7483 | 0.2754 | 175.4314 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 3 115.00] TO [SUMMIT 6 230.00] TO [SUMIT3 1 13.800] CKT 1 | 31.7483 | 0.2754 | 175.4314 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TIMBJCT2 69.000] TO [AKRON 2 69.000] CKT 1 | 31.7471 | 0.2755 | 175.4644 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TIMBJCT2 69.000] TO [AKRON 2 69.000] CKT 1 | 31.7471 | 0.2755 | 175.4644 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TIMBJCT2 69.000] TO [UDALL 2 69.000] CKT 1 | 31.7459 | 0.2754 | 175.4264 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TIMBJCT2 69.000] TO [UDALL 2 69.000] CKT 1 | 31.7459 | 0.2754 | 175.4264 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TIMBJCT2 69.000] TO [WINFLD 2 69.000] CKT 1 | 31.7456 | 0.2755 | 175.5097 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TIMBJCT2 69.000] TO [WINFLD 2 69.000] CKT 1 | 31.7456 | 0.2755 | 175.5097 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ALTOO E2 69.000] TO [NEODJCT2 69.000] CKT 1 | 31.747 | 0.2752 | 175.2142 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ALTOO E2 69.000] TO [NEODJCT2 69.000] CKT 1 | 31.747 | 0.2752 | 175.2142 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ALTOO E2 69.000] TO [RA5HIPR2 69.000] CKT Z1 | 31.7479 | 0.2754 | 175.3812 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ALTOO E2 69.000] TO [RA5HIPR2 69.000] CKT Z1 | 31.7479 | 0.2754 | 175.3812 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ALTOO W2 69.000] TO [STUDBKR2 69.000] CKT 1 | 31.7472 | 0.2751 | 175.1174 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ALTOO W2 69.000] TO [STUDBKR2 69.000] CKT 1 | 31.7472 | 0.2751 | 175.1174 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH N2 69.000] TO [AQUARS 2 69.000] CKT 1 | 31.7482 | 0.2754 | 175.4498 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH N2 69.000] TO [AQUARS 2 69.000] CKT 1 | 31.7482 | 0.2754 | 175.4498 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH N2 69.000] TO [PITNAC 2 69.000] CKT 1 | 31.7472 | 0.2754 | 175.437 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH N2 69.000] TO [PITNAC 2 69.000] CKT 1 | 31.7472 | 0.2754 | 175.437 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH S2 69.000] TO [ROUSE 2 69.000] CKT 1 | 31.748 | 0.2755 | 175.4693 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH S2 69.000] TO [ROUSE 2 69.000] CKT 1 | 31.748 | 0.2755 | 175.4693 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH S2 69.000] TO [SOPITT 2 69.000] CKT 1 | 31.6589 | 0.2764 | 176.3776 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH S2 69.000] TO [SOPITT 2 69.000] CKT 1 | 31.6589 | 0.2764 | 176.3776 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHOS2 69.000] TO [BAKER 2 69.000] CKT 1 | 31.6471 | 0.275 | 174.9551 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHOS2 69.000] TO [BAKER 2 69.000] CKT 1 | 31.6471 | 0.275 | 174.9551 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHOS2 69.000] TO [ORDNJCT2 69.000] CKT 1 | 31.7488 | 0.2757 | 175.6951 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHOS2 69.000] TO [ORDNJCT2 69.000] CKT 1 | 31.7488 | 0.2757 | 175.6951 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHOS2 69.000] TO [CRAWFOR2 69.000] CKT 1 | 31.6272 | 0.2753 | 175.3154 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHOS2 69.000] TO [CRAWFOR2 69.000] CKT 1 | 31.6272 | 0.2753 | 175.3154 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHOS2 69.000] TO [NEOSHON2 69.000] CKT Z1 | 31.741 | 0.2754 | 175.43 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHOS2 69.000] TO [NEOSHON2 69.000] CKT Z1 | 31.741 | 0.2754 | 175.43 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [K1 LV 1 34.500] TO [K1 CLCT1 34.500] CKT 1 | 31.7515 | 0.2752 | 175.2046 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [K1 LV 1 34.500] TO [K1 CLCT1 34.500] CKT 1 | 31.7515 | 0.2752 | 175.2046 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [K2 LV 1 34.500] TO [K2 CLCT1 34.500] CKT 1 | 31.7524 | 0.2752 | 175.2318 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [K2 LV 1 34.500] TO [K2 CLCT1 34.500] CKT 1 | 31.7524 | 0.2752 | 175.2318 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MILAN_GOAB 138.00] TO [CLDWELL4 138.00] CKT 1 | 31.7475 | 0.2754 | 175.4401 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MILAN_GOAB 138.00] TO [CLDWELL4 138.00] CKT 1 | 31.7475 | 0.2754 | 175.4401 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MILAN_GOAB 138.00] TO [MILAN 4 138.00] CKT 1 | 31.7478 | 0.2754 | 175.4455 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MILAN_GOAB 138.00] TO [MILAN 4 138.00] CKT 1 | 31.7478 | 0.2754 | 175.4455 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CONWAY 138.00] TO [MILANTP4 138.00] CKT 1 | 31.7466 | 0.2754 | 175.4276 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CONWAY 138.00] TO [MILANTP4 138.00] CKT 1 | 31.7466 | 0.2754 | 175.4276 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MRWYP16 230.00] TO [MRWYP26 230.00] CKT 1 | 31.7517 | 0.2753 | 175.2769 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MRWYP16 230.00] TO [MRWYP26 230.00] CKT 1 | 31.7517 | 0.2753 | 175.2769 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MRWYP16 230.00] TO [MRWYG11 34.500] TO [MRWYP1T1 13.800] CKT 1 | 31.7516 | 0.2752 | 175.238 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MRWYP16 230.00] TO [MRWYG11 34.500] TO [MRWYP1T1 13.800] CKT 1 | 31.7516 | 0.2752 | 175.238 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FLATRDG4 138.00] TO [FLATRWD4 138.00] CKT 1 | 31.748 | 0.2753 | 175.3312 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FLATRDG4 138.00] TO [FLATRWD4 138.00] CKT 1 | 31.748 | 0.2753 | 175.3312 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FLATRDG4 138.00] TO [HARPER 4 138.00] CKT 1 | 31.7446 | 0.2754 | 175.4414 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FLATRDG4 138.00] TO [HARPER 4 138.00] CKT 1 | 31.7446 | 0.2754 | 175.4414 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FLATRDG4 138.00] TO [BARBER 4 138.00] CKT 1 | 31.7465 | 0.2754 | 175.4035 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FLATRDG4 138.00] TO [BARBER 4 138.00] CKT 1 | 31.7465 | 0.2754 | 175.4035 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ELMCREK6 230.00] TO [ELMCREEK7 345.00] TO [ELMCREEK1 13.800] CKT 1 | 31.7441 | 0.2754 | 175.428 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ELMCREK6 230.00] TO [ELMCREEK7 345.00] TO [ELMCREEK1 13.800] CKT 1 | 31.7441 | 0.2754 | 175.428 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAYNE3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 31.7483 | 0.2754 | 175.4332 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAYNE3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 31.7483 | 0.2754 | 175.4332 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KISMET 3 115.00] TO [CUDAHY 3 115.00] CKT 1 | 31.7472 | 0.2755 | 175.4511 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KISMET 3 115.00] TO [CUDAHY 3 115.00] CKT 1 | 31.7472 | 0.2755 | 175.4511 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CMRIVTP3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 31.7483 | 0.2754 | 175.4275 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CMRIVTP3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 31.7483 | 0.2754 | 175.4275 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CONCRD6 230.00] TO [CONCORD3 115.00] TO [CONCOD-T 13.800] CKT 1 | 31.7441 | 0.2756 | 175.5689 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CONCRD6 230.00] TO [CONCORD3 115.00] TO [CONCOD-T 13.800] CKT 1 | 31.7441 | 0.2756 | 175.5689 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [E-LIBER3 115.00] TO [TXPHSF 3115.00] CKT 1 | 31.7484 | 0.2754 | 175.43 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [E-LIBER3 115.00] TO [TXPHSF 3115.00] CKT 1 | 31.7484 | 0.2754 | 175.43 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [E-LIBER3 115.00] TO [E-PINE 3 115.00] CKT 1 | 31.7471 | 0.2755 | 175.4839 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [E-LIBER3 115.00] TO [E-PINE 3 115.00] CKT 1 | 31.7471 | 0.2755 | 175.4839 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [E-LIBER3 115.00] TO [NATBEEF3 115.00] CKT 1 | 31.7483 | 0.2754 | 175.4306 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [E-LIBER3 115.00] TO [NATBEEF3 115.00] CKT 1 | 31.7483 | 0.2754 | 175.4306 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [E-LIBER3 115.00] TO [E-LIBER1 34.500] TO [ELIB-T 2.4000] CKT 1 | 31.7473 | 0.2755 | 175.4781 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [E-LIBER3 115.00] TO [E-LIBER1 34.500] TO [ELIB-T 2.4000] CKT 1 | 31.7473 | 0.2755 | 175.4781 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NLIB 3 115.00] TO [W-LIBER3 115.00] CKT 1 | 31.7468 | 0.2755 | 175.4966 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NLIB 3 115.00] TO [W-LIBER3 115.00] CKT 1 | 31.7468 | 0.2755 | 175.4966 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NLIB 3 115.00] TO [NATBEEF3 115.00] CKT 1 | 31.7483 | 0.2754 | 175.4333 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NLIB 3 115.00] TO [NATBEEF3 115.00] CKT 1 | 31.7483 | 0.2754 | 175.4333 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NLIB 3 115.00] TO [NLIB 1 34.500] TO [N-LIB-T 13.800] CKT 1 | 31.747 | 0.2755 | 175.4888 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NLIB 3 115.00] TO [NLIB 1 34.500] TO [N-LIB-T 13.800] CKT 1 | 31.747 | 0.2755 | 175.4888 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N-CIMRN3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 31.7481 | 0.2754 | 175.4399 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N-CIMRN3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 31.7481 | 0.2754 | 175.4399 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CIM-PLT 13.800] TO [CIM-PLT3 115.00] CKT 1 | 31.7432 | 0.2756 | 175.6468 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CIM-PLT 13.800] TO [CIM-PLT3 115.00] CKT 1 | 31.7432 | 0.2756 | 175.6468 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [THISTLE7 345.00] CKT 1 | 31.7421 | 0.2755 | 175.4896 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [THISTLE7 345.00] CKT 1 | 31.7421 | 0.2755 | 175.4896 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [THISTLE7 345.00] CKT 2 | 31.7421 | 0.2755 | 175.4896 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [THISTLE7 345.00] CKT 2 | 31.7421 | 0.2755 | 175.4896 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [THISTLE T1 13.800] TO [THISTLE7 345.00] TO [THISTLE4 138.00] CKT 1 | 31.7485 | 0.2754 | 175.4161 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [THISTLE T1 13.800] TO [THISTLE7 345.00] TO [THISTLE4 138.00] CKT 1 | 31.7485 | 0.2754 | 175.4161 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TRANSFORMER 345.00] TO [SUB34.5KVB 34.500] TO [TERTIARYBUS 19.900] CKT 1 | 31.7555 | 0.275 | 174.9783 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TRANSFORMER 345.00] TO [SUB34.5KVB 34.500] TO [TERTIARYBUS 19.900] CKT 1 | 31.7555 | 0.275 | 174.9783 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2011-008345.00] TO [G-2011-008-1345.00] CKT 1 | 31.7514 | 0.2752 | 175.2436 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2011-008345.00] TO [G-2011-008-1345.00] CKT 1 | 31.7514 | 0.2752 | 175.2436 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2011-008345.00] TO [G-2011-008-2345.00] CKT 1 | 31.7512 | 0.2753 | 175.2569 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2011-008345.00] TO [G-2011-008-2345.00] CKT 1 | 31.7512 | 0.2753 | 175.2569 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2011-008345.00] TO [G-2011-008-3345.00] CKT 1 | 31.7531 | 0.2752 | 175.239 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2011-008345.00] TO [G-2011-008-3345.00] CKT 1 | 31.7531 | 0.2752 | 175.239 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MULLNCR7 345.00] TO [HOLT 7 345.00] CKT 1 | 31.7425 | 0.2755 | 175.4849 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MULLNCR7 345.00] TO [HOLT 7 345.00] CKT 1 | 31.7425 | 0.2755 | 175.4849 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [PECULR 7 345.00] TO [PHILL 7 345.00] CKT 1 | 31.6614 | 0.2765 | 176.4611 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [PECULR 7 345.00] TO [PHILL 7 345.00] CKT 1 | 31.6614 | 0.2765 | 176.4611 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [PECULR 7 345.00] TO [PECULR 5 161.00] TO [PECULRT 13.800] CKT 11 | 31.7438 | 0.2756 | 175.6172 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [PECULR 7 345.00] TO [PECULR 5 161.00] TO [PECULRT 13.800] CKT 11 | 31.7438 | 0.2756 | 175.6172 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 7 345.00] TO [G17-183-TAP 345.00] CKT 1 | 31.7452 | 0.2755 | 175.5104 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 7 345.00] TO [G17-183-TAP 345.00] CKT 1 | 31.7452 | 0.2755 | 175.5104 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ARCHIE 5 161.00] TO [G17-108-TAP 161.00] CKT 1 | 31.747 | 0.2755 | 175.5135 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ARCHIE 5 161.00] TO [G17-108-TAP 161.00] CKT 1 | 31.747 | 0.2755 | 175.5135 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WINDSR 5 161.00] TO [5SEDALA 161.00] CKT 1 | 31.7444 | 0.2754 | 175.3659 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WINDSR 5 161.00] TO [5SEDALA 161.00] CKT 1 | 31.7444 | 0.2754 | 175.3659 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HSNVL 5 161.00] TO [5SHARSNV 161.00] CKT 1 | 31.746 | 0.2755 | 175.4853 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HSNVL 5 161.00] TO [5SHARSNV 161.00] CKT 1 | 31.746 | 0.2755 | 175.4853 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HSNVL 5 161.00] TO [PHILL 5 161.00] CKT 1 | 31.7332 | 0.2758 | 175.7999 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HSNVL 5 161.00] TO [PHILL 5 161.00] CKT 1 | 31.7332 | 0.2758 | 175.7999 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HSNVL 5 161.00] TO [HSNVL 2 69.000] CKT 1 | 31.7482 | 0.2754 | 175.4204 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HSNVL 5 161.00] TO [HSNVL 2 69.000] CKT 1 | 31.7482 | 0.2754 | 175.4204 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HSNVL 5 161.00] TO [HSNVL 2 69.000] CKT 2 | 31.7482 | 0.2754 | 175.421 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HSNVL 5 161.00] TO [HSNVL 2 69.000] CKT 2 | 31.7482 | 0.2754 | 175.421 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ADRIAN 5 161.00] TO [5BUTLER 161.00] CKT 1 | 31.7053 | 0.2763 | 176.2545 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ADRIAN 5 161.00] TO [5BUTLER 161.00] CKT 1 | 31.7053 | 0.2763 | 176.2545 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLINTON5 161.00] TO [CLNTN N2 69.000] CKT 1 | 31.7482 | 0.2754 | 175.4413 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLINTON5 161.00] TO [CLNTN N2 69.000] CKT 1 | 31.7482 | 0.2754 | 175.4413 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLINTON5 161.00] TO [CLNTN S2 69.000] CKT 2 | 31.7482 | 0.2754 | 175.4369 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLINTON5 161.00] TO [CLNTN S2 69.000] CKT 2 | 31.7482 | 0.2754 | 175.4369 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 5 161.00] TO [ST JOE_CAP5 161.00] CKT R | 31.7478 | 0.2755 | 175.4734 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 5 161.00] TO [ST JOE_CAP5 161.00] CKT R | 31.7478 | 0.2755 | 175.4734 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 5 161.00] TO [COOK 5 161.00] CKT 1 | 31.7482 | 0.2754 | 175.4278 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 5 161.00] TO [COOK 5 161.00] CKT 1 | 31.7482 | 0.2754 | 175.4278 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 5 161.00] TO [WOODBIN5 161.00] CKT 1 | 31.7483 | 0.2754 | 175.4291 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 5 161.00] TO [WOODBIN5 161.00] CKT 1 | 31.7483 | 0.2754 | 175.4291 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 5 161.00] TO [AVENUECTY 5 161.00] CKT 1 | 31.7469 | 0.2755 | 175.4952 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 5 161.00] TO [AVENUECTY 5 161.00] CKT 1 | 31.7469 | 0.2755 | 175.4952 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP#1 13.800] CKT 1 | 31.7483 | 0.2754 | 175.4319 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP#1 13.800] CKT 1 | 31.7483 | 0.2754 | 175.4319 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP#2 13.800] CKT 1 | 31.7483 | 0.2754 | 175.4319 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP#2 13.800] CKT 1 | 31.7483 | 0.2754 | 175.4319 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP#3 13.800] CKT 1 | 31.7483 | 0.2754 | 175.4319 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP#3 13.800] CKT 1 | 31.7483 | 0.2754 | 175.4319 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP 2 69.000] CKT 1 | 31.7478 | 0.2755 | 175.4533 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP 2 69.000] CKT 1 | 31.7478 | 0.2755 | 175.4533 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [PECULRS5 161.00] CKT 1 | 31.747 | 0.2755 | 175.4872 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [PECULRS5 161.00] CKT 1 | 31.747 | 0.2755 | 175.4872 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EASTOWN7 345.00] TO [EASTOWN5 161.00] TO [EASTOWN1 13.800] CKT 11 | 31.7467 | 0.2755 | 175.4856 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EASTOWN7 345.00] TO [EASTOWN5 161.00] TO [EASTOWN1 13.800] CKT 11 | 31.7467 | 0.2755 | 175.4856 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KETCHEM7 345.00] TO [SIBLEY 7 345.00] CKT 1 | 31.7431 | 0.2755 | 175.4573 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KETCHEM7 345.00] TO [SIBLEY 7 345.00] CKT 1 | 31.7431 | 0.2755 | 175.4573 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KETCHEM7 345.00] TO [OSBORN7 345.00] CKT 1 | 31.7548 | 0.275 | 175.0423 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KETCHEM7 345.00] TO [OSBORN7 345.00] CKT 1 | 31.7548 | 0.275 | 175.0423 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ROCKCK7 345.00] TO [HOLT 7 345.00] CKT 1 | 31.7577 | 0.2749 | 174.8786 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ROCKCK7 345.00] TO [HOLT 7 345.00] CKT 1 | 31.7577 | 0.2749 | 174.8786 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ROCKCK_T1_1 34.500] TO [ROCKCK_P1_1 34.500] CKT 1 | 31.7506 | 0.2753 | 175.2991 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ROCKCK_T1_1 34.500] TO [ROCKCK_P1_1 34.500] CKT 1 | 31.7506 | 0.2753 | 175.2991 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ROCKCK_T2_1 34.500] TO [ROCKCK_P2_1 34.500] CKT 1 | 31.7511 | 0.2753 | 175.2649 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ROCKCK_T2_1 34.500] TO [ROCKCK_P2_1 34.500] CKT 1 | 31.7511 | 0.2753 | 175.2649 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HOLT_REACT7 345.00] TO [HOLT 7 345.00] CKT Z1 | 31.7485 | 0.2754 | 175.4202 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HOLT_REACT7 345.00] TO [HOLT 7 345.00] CKT Z1 | 31.7485 | 0.2754 | 175.4202 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [OUTLAW 345.00] TO [OUTLAW_T2_1 34.500] TO [OUTLAW_TR2_113.800] CKT 1 | 31.7512 | 0.2753 | 175.2581 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [OUTLAW 345.00] TO [OUTLAW_T2_1 34.500] TO [OUTLAW_TR2_113.800] CKT 1 | 31.7512 | 0.2753 | 175.2581 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [OUTLAW 345.00] TO [OUTLAW_T1_1 34.500] TO [OUTLAW_TR1_113.800] CKT 1 | 31.7503 | 0.2753 | 175.3075 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [OUTLAW 345.00] TO [OUTLAW_T1_1 34.500] TO [OUTLAW_TR1_113.800] CKT 1 | 31.7503 | 0.2753 | 175.3075 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [W.GRDNR7 345.00] TO [WGAR T11 13.800] CKT 11 | 31.7303 | 0.2753 | 175.3117 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [W.GRDNR7 345.00] TO [WGAR T11 13.800] CKT 11 | 31.7303 | 0.2753 | 175.3117 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 31.7371 | 0.2757 | 175.7181 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 31.7371 | 0.2757 | 175.7181 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [G17-108-TAP 161.00] CKT 1 | 31.7456 | 0.2756 | 175.6007 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [G17-108-TAP 161.00] CKT 1 | 31.7456 | 0.2756 | 175.6007 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTH 7 345.00] TO [SIBLEY 7 345.00] CKT 1 | 31.7425 | 0.2755 | 175.4522 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTH 7 345.00] TO [SIBLEY 7 345.00] CKT 1 | 31.7425 | 0.2755 | 175.4522 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTH 7 345.00] TO [HAWTHN5 161.00] TO [HAWT T20 13.800] CKT 20 | 31.7486 | 0.2754 | 175.4018 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTH 7 345.00] TO [HAWTHN5 161.00] TO [HAWT T20 13.800] CKT 20 | 31.7486 | 0.2754 | 175.4018 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTH 7 345.00] TO [HAWTHN5 161.00] TO [HAWT T22 13.800] CKT 22 | 31.7474 | 0.2754 | 175.4131 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTH 7 345.00] TO [HAWTHN5 161.00] TO [HAWT T22 13.800] CKT 22 | 31.7474 | 0.2754 | 175.4131 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAW G9 1 13.800] CKT 1 | 31.7558 | 0.2749 | 174.854 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAW G9 1 13.800] CKT 1 | 31.7558 | 0.2749 | 174.854 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [LEEDS 5 161.00] CKT 1 | 31.7469 | 0.2754 | 175.4438 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [LEEDS 5 161.00] CKT 1 | 31.7469 | 0.2754 | 175.4438 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [LEEDS 5 161.00] CKT 2 | 31.747 | 0.2754 | 175.4433 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [LEEDS 5 161.00] CKT 2 | 31.747 | 0.2754 | 175.4433 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTH_B2_1 13.200] CKT 1 | 31.7459 | 0.2756 | 175.575 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTH_B2_1 13.200] CKT 1 | 31.7459 | 0.2756 | 175.575 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [BRMGHAM5 161.00] CKT 1 | 31.7464 | 0.2756 | 175.555 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [BRMGHAM5 161.00] CKT 1 | 31.7464 | 0.2756 | 175.555 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHS_G65 161.00] CKT Z1 | 31.7552 | 0.2749 | 174.8992 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHS_G65 161.00] CKT Z1 | 31.7552 | 0.2749 | 174.8992 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHS_XF5 161.00] CKT Z2 | 31.7482 | 0.2754 | 175.4376 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHS_XF5 161.00] CKT Z2 | 31.7482 | 0.2754 | 175.4376 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHN5 161.00] CKT @1 | 31.7483 | 0.2754 | 175.4332 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHN5 161.00] CKT @1 | 31.7483 | 0.2754 | 175.4332 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHN5 161.00] CKT @2 | 31.7483 | 0.2754 | 175.4332 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHN5 161.00] CKT @2 | 31.7483 | 0.2754 | 175.4332 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 31.6631 | 0.2762 | 176.23 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 31.6631 | 0.2762 | 176.23 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [CRAIG_CAP 5 161.00] CKT R | 31.7467 | 0.2756 | 175.5534 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [CRAIG_CAP 5 161.00] CKT R | 31.7467 | 0.2756 | 175.5534 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [PFLUMM 5 161.00] CKT 1 | 31.7461 | 0.2755 | 175.5245 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [PFLUMM 5 161.00] CKT 1 | 31.7461 | 0.2755 | 175.5245 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [LENEXA 5 161.00] CKT 1 | 31.7469 | 0.2755 | 175.4572 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [LENEXA 5 161.00] CKT 1 | 31.7469 | 0.2755 | 175.4572 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [LENEXA 5 161.00] CKT 2 | 31.7475 | 0.2754 | 175.4475 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [LENEXA 5 161.00] CKT 2 | 31.7475 | 0.2754 | 175.4475 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [COLLEGE5 161.00] CKT 1 | 31.7478 | 0.2754 | 175.4459 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [COLLEGE5 161.00] CKT 1 | 31.7478 | 0.2754 | 175.4459 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NASHUA 7 345.00] TO [G17-183-TAP 345.00] CKT 1 | 31.7472 | 0.2754 | 175.4025 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NASHUA 7 345.00] TO [G17-183-TAP 345.00] CKT 1 | 31.7472 | 0.2754 | 175.4025 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 31.4905 | 0.2771 | 177.1062 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 31.4905 | 0.2771 | 177.1062 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [G17-209-TAP 345.00] CKT 1 | 25.668 | 0.2746 | 174.6103 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [G17-209-TAP 345.00] CKT 1 | 25.668 | 0.2746 | 174.6103 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [STRANGR7 345.00] CKT 1 | 31.7437 | 0.2755 | 175.4743 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [STRANGR7 345.00] CKT 1 | 31.7437 | 0.2755 | 175.4743 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [STRANGR7 345.00] CKT 2 | 31.7442 | 0.2755 | 175.4748 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [STRANGR7 345.00] CKT 2 | 31.7442 | 0.2755 | 175.4748 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [IAT G1 1 24.000] CKT 1 | 31.8076 | 0.2713 | 171.2832 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [IAT G1 1 24.000] CKT 1 | 31.8076 | 0.2713 | 171.2832 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [IAT G2 1 24.500] CKT 1 | 31.806 | 0.2713 | 171.3012 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [IAT G2 1 24.500] CKT 1 | 31.806 | 0.2713 | 171.3012 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [IATAN5 161.00] TO [IATAN 11 14.400] CKT 11 | 31.7469 | 0.2755 | 175.5175 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [IATAN5 161.00] TO [IATAN 11 14.400] CKT 11 | 31.7469 | 0.2755 | 175.5175 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HICKMAN5 161.00] TO [STHTOWN5 161.00] CKT 1 | 31.74 | 0.2754 | 175.4294 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HICKMAN5 161.00] TO [STHTOWN5 161.00] CKT 1 | 31.74 | 0.2754 | 175.4294 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUMILS5 161.00] TO [BLUVLY-161 161.00] CKT 1 | 31.7478 | 0.2754 | 175.444 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUMILS5 161.00] TO [BLUVLY-161 161.00] CKT 1 | 31.7478 | 0.2754 | 175.444 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NASHUA-5 161.00] TO [NASHUA 5 161.00] CKT Z1 | 31.748 | 0.2754 | 175.4466 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NASHUA-5 161.00] TO [NASHUA 5 161.00] CKT Z1 | 31.748 | 0.2754 | 175.4466 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NASHUA-5 161.00] TO [RNRIDGE5 161.00] CKT 1 | 31.7488 | 0.2754 | 175.4038 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NASHUA-5 161.00] TO [RNRIDGE5 161.00] CKT 1 | 31.7488 | 0.2754 | 175.4038 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NASHUA-5 161.00] TO [SHOLCRK5 161.00] CKT 1 | 31.7481 | 0.2754 | 175.4445 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NASHUA-5 161.00] TO [SHOLCRK5 161.00] CKT 1 | 31.7481 | 0.2754 | 175.4445 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CEDRCRK5 161.00] TO [SHWNMSN5 161.00] CKT 1 | 31.746 | 0.2755 | 175.4809 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CEDRCRK5 161.00] TO [SHWNMSN5 161.00] CKT 1 | 31.746 | 0.2755 | 175.4809 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ANTIOCH5 161.00] TO [OXFORD 5 161.00] CKT 1 | 31.7444 | 0.2753 | 175.2671 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ANTIOCH5 161.00] TO [OXFORD 5 161.00] CKT 1 | 31.7444 | 0.2753 | 175.2671 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [REDEL 5 161.00] TO [MARTCIT5 161.00] CKT 1 | 31.7392 | 0.2755 | 175.4743 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [REDEL 5 161.00] TO [MARTCIT5 161.00] CKT 1 | 31.7392 | 0.2755 | 175.4743 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BUCYRUS5 161.00] TO [NLOUISB5 161.00] CKT 1 | 31.7466 | 0.2755 | 175.5284 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BUCYRUS5 161.00] TO [NLOUISB5 161.00] CKT 1 | 31.7466 | 0.2755 | 175.5284 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BUCYRUS5 161.00] TO [WAGSTAF5 161.00] CKT 1 | 31.7235 | 0.2755 | 175.4838 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BUCYRUS5 161.00] TO [WAGSTAF5 161.00] CKT 1 | 31.7235 | 0.2755 | 175.4838 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [PLSTVAL5 161.00] TO [SEOTTWA5 161.00] CKT 1 | 31.739 | 0.2755 | 175.4712 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [PLSTVAL5 161.00] TO [SEOTTWA5 161.00] CKT 1 | 31.739 | 0.2755 | 175.4712 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [PLSTVAL5 161.00] TO [ASG-2018-010161.00] CKT 1 | 31.7528 | 0.2752 | 175.1835 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [PLSTVAL5 161.00] TO [ASG-2018-010161.00] CKT 1 | 31.7528 | 0.2752 | 175.1835 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [PLSTVAL5 161.00] TO [PLSTVAL1 34.500] TO [PLSTVL2_TER17.6210] CKT 2 | 31.747 | 0.2755 | 175.5083 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [PLSTVAL5 161.00] TO [PLSTVAL1 34.500] TO [PLSTVL2_TER17.6210] CKT 2 | 31.747 | 0.2755 | 175.5083 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAKCTYJ2 69.000] TO [LAKCTY 2 69.000] CKT 1 | 31.7482 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAKCTYJ2 69.000] TO [LAKCTY 2 69.000] CKT 1 | 31.7482 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 1 13.800] CKT 1 | 31.7506 | 0.2749 | 174.9319 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 1 13.800] CKT 1 | 31.7506 | 0.2749 | 174.9319 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 2 13.800] CKT 1 | 31.7506 | 0.2749 | 174.9299 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 2 13.800] CKT 1 | 31.7506 | 0.2749 | 174.9299 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 3 13.800] CKT 1 | 31.7505 | 0.2749 | 174.9373 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 3 13.800] CKT 1 | 31.7505 | 0.2749 | 174.9373 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 4 13.800] CKT 1 | 31.7506 | 0.2749 | 174.9301 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 4 13.800] CKT 1 | 31.7506 | 0.2749 | 174.9301 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACKMAN5 161.00] TO [SPRGHL 5 161.00] CKT 1 | 31.7463 | 0.2754 | 175.4184 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACKMAN5 161.00] TO [SPRGHL 5 161.00] CKT 1 | 31.7463 | 0.2754 | 175.4184 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BNSF 5 161.00] TO [MOONLT 5 161.00] CKT 1 | 31.7415 | 0.2758 | 175.8375 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BNSF 5 161.00] TO [MOONLT 5 161.00] CKT 1 | 31.7415 | 0.2758 | 175.8375 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR1 34.500] TO [BALDWINCTY1 34.500] CKT 1 | 31.7482 | 0.2754 | 175.3853 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR1 34.500] TO [BALDWINCTY1 34.500] CKT 1 | 31.7482 | 0.2754 | 175.3853 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE11_7 345.00] TO [LAC11_AQC1 13.800] TO [LAC11_TER1 13.800] CKT 11 | 31.7423 | 0.2756 | 175.5824 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE11_7 345.00] TO [LAC11_AQC1 13.800] TO [LAC11_TER1 13.800] CKT 11 | 31.7423 | 0.2756 | 175.5824 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE22_7 345.00] TO [LAC22_AQC1 13.800] TO [LAC22_TER1 13.800] CKT 22 | 31.7483 | 0.2754 | 175.4313 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE22_7 345.00] TO [LAC22_AQC1 13.800] TO [LAC22_TER1 13.800] CKT 22 | 31.7483 | 0.2754 | 175.4313 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE2 69.000] TO [LAC_LAKE_2 69.000] CKT 1 | 31.7461 | 0.2755 | 175.5146 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE2 69.000] TO [LAC_LAKE_2 69.000] CKT 1 | 31.7461 | 0.2755 | 175.5146 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC3_STAR7 345.00] TO [LAC3_X1 6.9000] CKT X | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC3_STAR7 345.00] TO [LAC3_X1 6.9000] CKT X | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC3_STAR7 345.00] TO [LAC3_Y1 6.9000] CKT Y | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC3_STAR7 345.00] TO [LAC3_Y1 6.9000] CKT Y | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC3_STAR7 345.00] TO [LAC3_Z1 3.9800] CKT Z | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC3_STAR7 345.00] TO [LAC3_Z1 3.9800] CKT Z | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC8_STAR7 345.00] TO [LAC8_X1 6.9000] CKT X | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC8_STAR7 345.00] TO [LAC8_X1 6.9000] CKT X | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC8_STAR7 345.00] TO [LAC8_Y1 6.9000] CKT Y | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC8_STAR7 345.00] TO [LAC8_Y1 6.9000] CKT Y | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC8_STAR7 345.00] TO [LAC8_Z1 4.0000] CKT Z | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC8_STAR7 345.00] TO [LAC8_Z1 4.0000] CKT Z | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RIV4525 161.00] TO [ORO110 5 161.00] CKT 1 | 31.7379 | 0.2751 | 175.1234 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RIV4525 161.00] TO [ORO110 5 161.00] CKT 1 | 31.7379 | 0.2751 | 175.1234 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RIV4525 161.00] TO [STL439 5 161.00] CKT 1 | 31.5955 | 0.2749 | 174.9239 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RIV4525 161.00] TO [STL439 5 161.00] CKT 1 | 31.5955 | 0.2749 | 174.9239 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RIV4525 161.00] TO [RIV452T 5 161.00] CKT 1 | 31.4722 | 0.278 | 177.9933 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RIV4525 161.00] TO [RIV452T 5 161.00] CKT 1 | 31.4722 | 0.278 | 177.9933 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RIV4525 161.00] TO [BAX488 5 161.00] CKT 1 | 31.7035 | 0.2747 | 174.6505 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RIV4525 161.00] TO [BAX488 5 161.00] CKT 1 | 31.7035 | 0.2747 | 174.6505 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RIV4525 161.00] TO [RIV167 2 69.000] TO [RIV452 1 12.500] CKT 1 | 31.7428 | 0.2755 | 175.4975 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RIV4525 161.00] TO [RIV167 2 69.000] TO [RIV452 1 12.500] CKT 1 | 31.7428 | 0.2755 | 175.4975 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CJ 366 5 161.00] TO [ASB349 5 161.00] CKT 1 | 31.7069 | 0.2755 | 175.5427 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CJ 366 5 161.00] TO [ASB349 5 161.00] CKT 1 | 31.7069 | 0.2755 | 175.5427 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CAR395 5 161.00] TO [CARTHAG5 161.00] CKT 1 | 31.6955 | 0.2754 | 175.4444 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CAR395 5 161.00] TO [CARTHAG5 161.00] CKT 1 | 31.6955 | 0.2754 | 175.4444 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FIR417 5 161.00] TO [ORO110 5 161.00] CKT 1 | 31.7109 | 0.2755 | 175.4581 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FIR417 5 161.00] TO [ORO110 5 161.00] CKT 1 | 31.7109 | 0.2755 | 175.4581 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [PUR421 5 161.00] TO [ASB349 5 161.00] CKT 1 | 31.6924 | 0.2755 | 175.4957 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [PUR421 5 161.00] TO [ASB349 5 161.00] CKT 1 | 31.6924 | 0.2755 | 175.4957 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [A1G349 1 13.800] TO [ASB349 5 161.00] CKT 1 | 31.7493 | 0.2752 | 175.2415 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [A1G349 1 13.800] TO [ASB349 5 161.00] CKT 1 | 31.7493 | 0.2752 | 175.2415 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [A2G349 1 13.800] TO [ASB349 5 161.00] CKT 1 | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [A2G349 1 13.800] TO [ASB349 5 161.00] CKT 1 | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB K 69.000] TO [SUB R 69.000] CKT 1 | 31.7483 | 0.2754 | 175.4327 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB K 69.000] TO [SUB R 69.000] CKT 1 | 31.7483 | 0.2754 | 175.4327 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB H 69.000] TO [COURTNY2 69.000] CKT 1 | 31.7482 | 0.2754 | 175.4359 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB H 69.000] TO [COURTNY2 69.000] CKT 1 | 31.7482 | 0.2754 | 175.4359 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB H 69.000] TO [SUGRCK_TP_E269.000] CKT 1 | 31.7482 | 0.2754 | 175.4331 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB H 69.000] TO [SUGRCK_TP_E269.000] CKT 1 | 31.7482 | 0.2754 | 175.4331 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB H 69.000] TO [SUB H-13B1 13.800] CKT H1 | 31.7475 | 0.2754 | 175.4454 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB H 69.000] TO [SUB H-13B1 13.800] CKT H1 | 31.7475 | 0.2754 | 175.4454 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB H 69.000] TO [SUB H-13B2 13.800] CKT H2 | 31.7482 | 0.2754 | 175.423 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB H 69.000] TO [SUB H-13B2 13.800] CKT H2 | 31.7482 | 0.2754 | 175.423 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [BLUVLY-161 161.00] CKT 1 | 31.748 | 0.2754 | 175.4284 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [BLUVLY-161 161.00] CKT 1 | 31.748 | 0.2754 | 175.4284 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [BLUVLY-161 161.00] CKT 2 | 31.748 | 0.2754 | 175.4282 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [BLUVLY-161 161.00] CKT 2 | 31.748 | 0.2754 | 175.4282 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ECKLES-161 161.00] TO [5LEVASY 161.00] CKT 1 | 31.7478 | 0.2754 | 175.4172 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ECKLES-161 161.00] TO [5LEVASY 161.00] CKT 1 | 31.7478 | 0.2754 | 175.4172 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ECKLES-161 161.00] TO [5MOCITYB1 161.00] CKT 1 | 31.7475 | 0.2754 | 175.4283 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ECKLES-161 161.00] TO [5MOCITYB1 161.00] CKT 1 | 31.7475 | 0.2754 | 175.4283 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ECKLES-161 161.00] TO [SIBLEYPL 161.00] CKT 1 | 31.7475 | 0.2754 | 175.4472 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ECKLES-161 161.00] TO [SIBLEYPL 161.00] CKT 1 | 31.7475 | 0.2754 | 175.4472 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB J 69.000] TO [SUB J-13B1 13.800] CKT J1 | 31.7486 | 0.2754 | 175.4126 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB J 69.000] TO [SUB J-13B1 13.800] CKT J1 | 31.7486 | 0.2754 | 175.4126 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB J 69.000] TO [SUB J-13B2 13.800] CKT J2 | 31.7472 | 0.2755 | 175.4828 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB J 69.000] TO [SUB J-13B2 13.800] CKT J2 | 31.7472 | 0.2755 | 175.4828 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB M-161 161.00] TO [BLUVLY-161 161.00] CKT 1 | 31.7476 | 0.2755 | 175.4622 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB M-161 161.00] TO [BLUVLY-161 161.00] CKT 1 | 31.7476 | 0.2755 | 175.4622 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB M 69.000] TO [SHRNKRD 69.000] CKT 1 | 31.7483 | 0.2754 | 175.4318 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB M 69.000] TO [SHRNKRD 69.000] CKT 1 | 31.7483 | 0.2754 | 175.4318 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB P 69.000] TO [SUB I 69.000] CKT 1 | 31.7483 | 0.2754 | 175.4334 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB P 69.000] TO [SUB I 69.000] CKT 1 | 31.7483 | 0.2754 | 175.4334 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G16-046-TAP 345.00] TO [IRONWOOD7 345.00] CKT 1 | 31.7465 | 0.2754 | 175.449 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G16-046-TAP 345.00] TO [IRONWOOD7 345.00] CKT 1 | 31.7465 | 0.2754 | 175.449 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G16-046-TAP 345.00] TO [GEN-2016-046345.00] CKT 1 | 31.7527 | 0.275 | 174.9565 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G16-046-TAP 345.00] TO [GEN-2016-046345.00] CKT 1 | 31.7527 | 0.275 | 174.9565 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-004345.00] TO [G17-004XFMR134.500] CKT 1 | 31.7565 | 0.2749 | 174.9184 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-004345.00] TO [G17-004XFMR134.500] CKT 1 | 31.7565 | 0.2749 | 174.9184 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-004-TAP 345.00] TO [ELMCREEK7 345.00] CKT 1 | 31.7436 | 0.2755 | 175.5202 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-004-TAP 345.00] TO [ELMCREEK7 345.00] CKT 1 | 31.7436 | 0.2755 | 175.5202 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-018345.00] TO [THISTLE7 345.00] CKT 1 | 31.7617 | 0.2746 | 174.6011 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-018345.00] TO [THISTLE7 345.00] CKT 1 | 31.7617 | 0.2746 | 174.6011 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-018XFMR134.500] TO [G17-018-GSU134.500] CKT 1 | 31.7551 | 0.275 | 175.0095 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-018XFMR134.500] TO [G17-018-GSU134.500] CKT 1 | 31.7551 | 0.275 | 175.0095 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-018XFMR234.500] TO [G17-018-GSU234.500] CKT 1 | 31.7551 | 0.275 | 175.0095 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-018XFMR234.500] TO [G17-018-GSU234.500] CKT 1 | 31.7551 | 0.275 | 175.0095 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-068138.00] TO [EVANS N4 138.00] CKT 1 | 31.7571 | 0.2749 | 174.897 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-068138.00] TO [EVANS N4 138.00] CKT 1 | 31.7571 | 0.2749 | 174.897 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-068XFMR134.500] TO [G17-068-GSU134.500] CKT 1 | 31.7571 | 0.2749 | 174.89 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-068XFMR134.500] TO [G17-068-GSU134.500] CKT 1 | 31.7571 | 0.2749 | 174.89 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-082161.00] TO [ASB349 5 161.00] CKT 1 | 31.7422 | 0.2759 | 175.8549 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-082161.00] TO [ASB349 5 161.00] CKT 1 | 31.7422 | 0.2759 | 175.8549 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-082XFMR134.500] TO [G17-082-GSU134.500] CKT 1 | 31.7423 | 0.2758 | 175.8365 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-082XFMR134.500] TO [G17-082-GSU134.500] CKT 1 | 31.7423 | 0.2758 | 175.8365 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [ATCHSN 3 345.00] CKT 1 | 31.7422 | 0.2758 | 175.7808 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [ATCHSN 3 345.00] CKT 1 | 31.7422 | 0.2758 | 175.7808 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [COOPER1G 22.000] CKT 1 | 31.8114 | 0.2715 | 171.4683 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [COOPER1G 22.000] CKT 1 | 31.8114 | 0.2715 | 171.4683 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [MONOLITH 3 345.00] CKT 1 | 31.7458 | 0.2756 | 175.5744 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [MONOLITH 3 345.00] CKT 1 | 31.7458 | 0.2756 | 175.5744 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [COOPER 5 161.00] TO [COOPER T2 913.800] CKT 1 | 31.7484 | 0.2754 | 175.4281 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [COOPER 5 161.00] TO [COOPER T2 913.800] CKT 1 | 31.7484 | 0.2754 | 175.4281 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [COOPER 5 161.00] TO [COOPER T5 913.800] CKT 1 | 31.7484 | 0.2754 | 175.4284 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [COOPER 5 161.00] TO [COOPER T5 913.800] CKT 1 | 31.7484 | 0.2754 | 175.4284 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEBCTY1G 18.000] TO [NC1GA1X9 4.2000] TO [NC1GA1Y9 4.2000] CKT 1 | 31.7462 | 0.2755 | 175.5346 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEBCTY1G 18.000] TO [NC1GA1X9 4.2000] TO [NC1GA1Y9 4.2000] CKT 1 | 31.7462 | 0.2755 | 175.5346 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEBCTY1G 18.000] TO [NC1GA2X9 4.2000] TO [NC1GA2Y9 4.2000] CKT 1 | 31.7462 | 0.2755 | 175.5346 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEBCTY1G 18.000] TO [NC1GA2X9 4.2000] TO [NC1GA2Y9 4.2000] CKT 1 | 31.7462 | 0.2755 | 175.5346 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEBCTY2G 23.000] TO [NC2GA1X9 4.2000] TO [NC2GA1Y9 4.2000] CKT 1 | 31.7473 | 0.2755 | 175.481 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEBCTY2G 23.000] TO [NC2GA1X9 4.2000] TO [NC2GA1Y9 4.2000] CKT 1 | 31.7473 | 0.2755 | 175.481 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEBCTY2G 23.000] TO [NC2GA2X9 13.800] TO [NC2GA2Y9 13.800] CKT 1 | 31.7443 | 0.2757 | 175.6703 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEBCTY2G 23.000] TO [NC2GA2X9 13.800] TO [NC2GA2Y9 13.800] CKT 1 | 31.7443 | 0.2757 | 175.6703 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3456 3 345.00] TO [CBLUFFS3 345.00] CKT 1 | 31.7497 | 0.2753 | 175.3377 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3456 3 345.00] TO [CBLUFFS3 345.00] CKT 1 | 31.7497 | 0.2753 | 175.3377 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3456 3 345.00] TO [S3455 3 345.00] CKT 1 | 31.7485 | 0.2754 | 175.4194 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3456 3 345.00] TO [S3455 3 345.00] CKT 1 | 31.7485 | 0.2754 | 175.4194 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3456 3 345.00] TO [S3459 3 345.00] CKT 1 | 31.7481 | 0.2754 | 175.4484 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3456 3 345.00] TO [S3459 3 345.00] CKT 1 | 31.7481 | 0.2754 | 175.4484 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3456 3 345.00] TO [S1206 5 161.00] TO [S3456T49 13.800] CKT 1 | 31.7484 | 0.2754 | 175.4277 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3456 3 345.00] TO [S1206 5 161.00] TO [S3456T49 13.800] CKT 1 | 31.7484 | 0.2754 | 175.4277 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3458 3 345.00] TO [HOLT 7 345.00] CKT 1 | 31.7384 | 0.2756 | 175.648 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3458 3 345.00] TO [HOLT 7 345.00] CKT 1 | 31.7384 | 0.2756 | 175.648 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3740 3 345.00] TO [CASS 1G 15.000] CKT 1 | 31.7602 | 0.2747 | 174.6909 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3740 3 345.00] TO [CASS 1G 15.000] CKT 1 | 31.7602 | 0.2747 | 174.6909 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3740 3 345.00] TO [CASS 2G 15.000] CKT 1 | 31.7601 | 0.2747 | 174.6937 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3740 3 345.00] TO [CASS 2G 15.000] CKT 1 | 31.7601 | 0.2747 | 174.6937 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3740 3 345.00] TO [S3454 3 345.00] CKT 1 | 31.748 | 0.2754 | 175.4493 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3740 3 345.00] TO [S3454 3 345.00] CKT 1 | 31.748 | 0.2754 | 175.4493 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3740 3 345.00] TO [S3455 3 345.00] CKT 1 | 31.7478 | 0.2755 | 175.4616 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3740 3 345.00] TO [S3455 3 345.00] CKT 1 | 31.7478 | 0.2755 | 175.4616 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3740 3 345.00] TO [GEN-2018-033345.00] CKT 1 | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3740 3 345.00] TO [GEN-2018-033345.00] CKT 1 | 31.7483 | 0.2754 | 175.4324 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [103&ROKEBY3 345.00] TO [MOORE 3 345.00] CKT 1 | 31.7483 | 0.2754 | 175.4339 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [103&ROKEBY3 345.00] TO [MOORE 3 345.00] CKT 1 | 31.7483 | 0.2754 | 175.4339 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [103&ROKEBY3 345.00] TO [WAGENER 3 345.00] CKT 1 | 31.7478 | 0.2755 | 175.4625 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [103&ROKEBY3 345.00] TO [WAGENER 3 345.00] CKT 1 | 31.7478 | 0.2755 | 175.4625 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7SPORTSMAN 345.00] TO [5SPORTSMAN 161.00] CKT 2 | 31.6398 | 0.2756 | 175.6254 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7SPORTSMAN 345.00] TO [5SPORTSMAN 161.00] CKT 2 | 31.6398 | 0.2756 | 175.6254 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IDALIA 5 161.00] TO [2IDALIA 69.000] CKT 2 | 31.7483 | 0.2754 | 175.4337 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IDALIA 5 161.00] TO [2IDALIA 69.000] CKT 2 | 31.7483 | 0.2754 | 175.4337 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [TATONGA7 345.00] CKT 2 | 31.7375 | 0.2761 | 176.1186 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [TATONGA7 345.00] CKT 2 | 31.7375 | 0.2761 | 176.1186 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [G16-003-TAP 345.00] CKT 2 | 31.7425 | 0.2753 | 175.3415 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [G16-003-TAP 345.00] CKT 2 | 31.7425 | 0.2753 | 175.3415 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DGRASSE7 345.00] TO [THISTLE7 345.00] CKT 2 | 31.6549 | 0.2786 | 178.563 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DGRASSE7 345.00] TO [THISTLE7 345.00] CKT 2 | 31.6549 | 0.2786 | 178.563 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 2 | 31.6652 | 0.2743 | 174.3335 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 2 | 31.6652 | 0.2743 | 174.3335 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EVANS S4 138.00] TO [EVANS N4 138.00] CKT Z2 | 31.7291 | 0.2775 | 177.51 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EVANS S4 138.00] TO [EVANS N4 138.00] CKT Z2 | 31.7291 | 0.2775 | 177.51 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [THISTLE7 345.00] CKT 2 | 31.7229 | 0.2755 | 175.5256 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [THISTLE7 345.00] CKT 2 | 31.7229 | 0.2755 | 175.5256 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HSNVL 5 161.00] TO [HSNVL 2 69.000] CKT 2 | 31.7487 | 0.2754 | 175.3877 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HSNVL 5 161.00] TO [HSNVL 2 69.000] CKT 2 | 31.7487 | 0.2754 | 175.3877 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [LEEDS 5 161.00] CKT 2 | 31.7423 | 0.2755 | 175.4805 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [LEEDS 5 161.00] CKT 2 | 31.7423 | 0.2755 | 175.4805 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHN5 161.00] CKT @2 | 31.7452 | 0.2756 | 175.5985 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHN5 161.00] CKT @2 | 31.7452 | 0.2756 | 175.5985 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [LENEXA 5 161.00] CKT 2 | 31.7424 | 0.2755 | 175.5491 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [LENEXA 5 161.00] CKT 2 | 31.7424 | 0.2755 | 175.5491 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [STRANGR7 345.00] CKT 2 | 31.7206 | 0.2756 | 175.6364 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [STRANGR7 345.00] CKT 2 | 31.7206 | 0.2756 | 175.6364 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [BLUVLY-161 161.00] CKT 2 | 31.7485 | 0.2754 | 175.4085 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [BLUVLY-161 161.00] CKT 2 | 31.7485 | 0.2754 | 175.4085 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | Base | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | Base | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7FAIRPT 345.00] TO [ST JOE 7 345.00] CKT 1 | 31.0274 | 0.295 | 195.0011 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7FAIRPT 345.00] TO [ST JOE 7 345.00] CKT 1 | 31.0274 | 0.295 | 195.0011 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7FAIRPT 345.00] TO [COOPER 3 345.00] CKT 1 | 31.0281 | 0.2949 | 194.9491 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7FAIRPT 345.00] TO [COOPER 3 345.00] CKT 1 | 31.0281 | 0.2949 | 194.9491 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [5HOLDENB2 161.00] CKT 1 | 31.0185 | 0.2954 | 195.4084 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [5HOLDENB2 161.00] CKT 1 | 31.0185 | 0.2954 | 195.4084 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [2CLINTN 69.000] CKT 1 | 31.0303 | 0.295 | 194.9599 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [2CLINTN 69.000] CKT 1 | 31.0303 | 0.295 | 194.9599 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [2CLINTN 69.000] CKT 3 | 31.0303 | 0.295 | 194.96 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [2CLINTN 69.000] CKT 3 | 31.0303 | 0.295 | 194.96 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [5OSCEOKCTP 161.00] CKT 1 | 30.9973 | 0.2959 | 195.8551 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [5OSCEOKCTP 161.00] CKT 1 | 30.9973 | 0.2959 | 195.8551 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [TRUMAN 5 161.00] CKT 1 | 31.0207 | 0.2953 | 195.3386 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [TRUMAN 5 161.00] CKT 1 | 31.0207 | 0.2953 | 195.3386 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [WINDSR 5 161.00] CKT 1 | 31.0255 | 0.2949 | 194.8806 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [WINDSR 5 161.00] CKT 1 | 31.0255 | 0.2949 | 194.8806 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [CLINTON5 161.00] CKT Z1 | 31.0297 | 0.295 | 194.9821 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [CLINTON5 161.00] CKT Z1 | 31.0297 | 0.295 | 194.9821 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [N MADRD5 161.00] CKT 1 | 31.0307 | 0.2949 | 194.9446 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [N MADRD5 161.00] CKT 1 | 31.0307 | 0.2949 | 194.9446 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [SIKETAP5 161.00] CKT 1 | 31.0304 | 0.295 | 194.9591 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [SIKETAP5 161.00] CKT 1 | 31.0304 | 0.295 | 194.9591 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7BLACKBERRY 345.00] TO [7SPORTSMAN 345.00] CKT 1 | 29.2523 | 0.3009 | 200.9483 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7BLACKBERRY 345.00] TO [7SPORTSMAN 345.00] CKT 1 | 29.2523 | 0.3009 | 200.9483 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7BLACKBERRY 345.00] TO [7JASPER 345.00] CKT 1 | 28.6691 | 0.2924 | 192.4243 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7BLACKBERRY 345.00] TO [7JASPER 345.00] CKT 1 | 28.6691 | 0.2924 | 192.4243 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7BLACKBERRY 345.00] TO [WOLFCRK7 345.00] CKT 1 | 29.8729 | 0.2998 | 199.8418 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7BLACKBERRY 345.00] TO [WOLFCRK7 345.00] CKT 1 | 29.8729 | 0.2998 | 199.8418 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5MINER 1 161.00] TO [SIKESTN5 161.00] CKT 1 | 31.0302 | 0.295 | 194.973 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5MINER 1 161.00] TO [SIKESTN5 161.00] CKT 1 | 31.0302 | 0.295 | 194.973 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N MADRD5 161.00] TO [KENNETT5 161.00] CKT 1 | 31.0303 | 0.295 | 194.9763 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N MADRD5 161.00] TO [KENNETT5 161.00] CKT 1 | 31.0303 | 0.295 | 194.9763 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N MADRD5 161.00] TO [N MADRD2 69.000] TO [NMA X1 1 13.800] CKT 1 | 31.0306 | 0.2949 | 194.9467 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N MADRD5 161.00] TO [N MADRD2 69.000] TO [NMA X1 1 13.800] CKT 1 | 31.0306 | 0.2949 | 194.9467 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N MADRD5 161.00] TO [N MADRD2 69.000] TO [NMA X2 1 13.800] CKT 1 | 31.0306 | 0.2949 | 194.9465 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N MADRD5 161.00] TO [N MADRD2 69.000] TO [NMA X2 1 13.800] CKT 1 | 31.0306 | 0.2949 | 194.9465 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SIKETAP5 161.00] TO [SIKESTN5 161.00] CKT 1 | 31.0304 | 0.295 | 194.9585 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SIKETAP5 161.00] TO [SIKESTN5 161.00] CKT 1 | 31.0304 | 0.295 | 194.9585 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SIKESTN5 161.00] TO [SIKGEN 1 13.800] CKT 1 | 31.0294 | 0.295 | 195.01 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SIKESTN5 161.00] TO [SIKGEN 1 13.800] CKT 1 | 31.0294 | 0.295 | 195.01 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SIKESTN5 161.00] TO [IDALIA 5 161.00] CKT 1 | 31.0306 | 0.2949 | 194.9473 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SIKESTN5 161.00] TO [IDALIA 5 161.00] CKT 1 | 31.0306 | 0.2949 | 194.9473 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SIKESTN5 161.00] TO [SIKESTN2 69.000] TO [SIK X1 1 13.800] CKT 1 | 31.031 | 0.2949 | 194.9236 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SIKESTN5 161.00] TO [SIKESTN2 69.000] TO [SIK X1 1 13.800] CKT 1 | 31.031 | 0.2949 | 194.9236 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DELAWAR1 13.800] TO [DELWARE4 138.00] TO [DELWARE7 345.00] CKT 1 | 30.9945 | 0.2949 | 194.9442 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DELAWAR1 13.800] TO [DELWARE4 138.00] TO [DELWARE7 345.00] CKT 1 | 30.9945 | 0.2949 | 194.9442 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DELWARE7 345.00] TO [N.E.S.-7 345.00] CKT 1 | 25.6019 | 0.3022 | 202.2081 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DELWARE7 345.00] TO [N.E.S.-7 345.00] CKT 1 | 25.6019 | 0.3022 | 202.2081 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [DGRASSE7 345.00] CKT 1 | 31.0151 | 0.2954 | 195.4336 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [DGRASSE7 345.00] CKT 1 | 31.0151 | 0.2954 | 195.4336 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [DGRASSE7 345.00] CKT 2 | 31.0151 | 0.2954 | 195.434 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [DGRASSE7 345.00] CKT 2 | 31.0151 | 0.2954 | 195.434 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DGRASSE7 345.00] TO [DGRASSE4 138.00] TO [DGRASSE1 13.800] CKT 1 | 31.027 | 0.2951 | 195.0564 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DGRASSE7 345.00] TO [DGRASSE4 138.00] TO [DGRASSE1 13.800] CKT 1 | 31.027 | 0.2951 | 195.0564 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WALKMYR1 13.800] TO [WALKMYR2 69.000] TO [WALKMYR3 115.00] CKT 1 | 31.0293 | 0.295 | 195.0017 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WALKMYR1 13.800] TO [WALKMYR2 69.000] TO [WALKMYR3 115.00] CKT 1 | 31.0293 | 0.295 | 195.0017 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WALKMYR3 115.00] TO [HUGOTON3 115.00] CKT 1 | 31.0303 | 0.295 | 194.9549 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WALKMYR3 115.00] TO [HUGOTON3 115.00] CKT 1 | 31.0303 | 0.295 | 194.9549 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WALKMYR3 115.00] TO [HARBNGR3 115.00] CKT 1 | 31.0298 | 0.295 | 194.9874 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WALKMYR3 115.00] TO [HARBNGR3 115.00] CKT 1 | 31.0298 | 0.295 | 194.9874 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SEWARD-3 115.00] TO [N-CIMRN3 115.00] CKT 1 | 31.0305 | 0.2949 | 194.9493 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SEWARD-3 115.00] TO [N-CIMRN3 115.00] CKT 1 | 31.0305 | 0.2949 | 194.9493 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [CLARKCOUNTY7345.00] CKT 1 | 31.0286 | 0.295 | 194.9568 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [CLARKCOUNTY7345.00] CKT 1 | 31.0286 | 0.295 | 194.9568 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NSES 2X1 13.200] TO [NEOSHO 4 138.00] TO [NEOSHOS2 69.000] CKT 1 | 31.0044 | 0.295 | 195.0313 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NSES 2X1 13.200] TO [NEOSHO 4 138.00] TO [NEOSHOS2 69.000] CKT 1 | 31.0044 | 0.295 | 195.0313 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EEC GT1 13.800] TO [EVANS S4 138.00] CKT 1 | 31.0306 | 0.2949 | 194.9456 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EEC GT1 13.800] TO [EVANS S4 138.00] CKT 1 | 31.0306 | 0.2949 | 194.9456 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EEC GT2 13.800] TO [EVANS S4 138.00] CKT 1 | 31.0306 | 0.2949 | 194.9456 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EEC GT2 13.800] TO [EVANS S4 138.00] CKT 1 | 31.0306 | 0.2949 | 194.9456 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EEC GT3 18.000] TO [EVANS S4 138.00] CKT 1 | 31.0306 | 0.2949 | 194.9464 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EEC GT3 18.000] TO [EVANS S4 138.00] CKT 1 | 31.0306 | 0.2949 | 194.9464 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [SWISVAL7 345.00] CKT 1 | 31.0267 | 0.2952 | 195.1648 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [SWISVAL7 345.00] CKT 1 | 31.0267 | 0.2952 | 195.1648 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EXPEDITION7 345.00] CKT 1 | 30.9913 | 0.2949 | 194.9156 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EXPEDITION7 345.00] CKT 1 | 30.9913 | 0.2949 | 194.9156 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RENO 7 345.00] TO [WICHITA7 345.00] CKT 1 | 30.9909 | 0.2952 | 195.1516 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RENO 7 345.00] TO [WICHITA7 345.00] CKT 1 | 30.9909 | 0.2952 | 195.1516 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 7 345.00] TO [G17-004-TAP 345.00] CKT 1 | 31.029 | 0.295 | 194.953 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 7 345.00] TO [G17-004-TAP 345.00] CKT 1 | 31.029 | 0.295 | 194.953 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SWISVAL7 345.00] TO [SWISVAL6 230.00] TO [SWISV1X1 14.400] CKT 1 | 31.0286 | 0.2949 | 194.8778 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SWISVAL7 345.00] TO [SWISVAL6 230.00] TO [SWISV1X1 14.400] CKT 1 | 31.0286 | 0.2949 | 194.8778 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SWISVAL7 345.00] TO [SWISVAL6 230.00] TO [SWISV2X2 14.400] CKT 2 | 31.0283 | 0.2949 | 194.9433 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SWISVAL7 345.00] TO [SWISVAL6 230.00] TO [SWISV2X2 14.400] CKT 2 | 31.0283 | 0.2949 | 194.9433 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [87TH 7 345.00] TO [CRAIG 7 345.00] CKT 1 | 30.9792 | 0.2952 | 195.1684 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [87TH 7 345.00] TO [CRAIG 7 345.00] CKT 1 | 30.9792 | 0.2952 | 195.1684 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-009-TAP 345.00] TO [GEN-2017-009345.00] CKT 1 | 31.0397 | 0.2988 | 198.7843 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-009-TAP 345.00] TO [GEN-2017-009345.00] CKT 1 | 31.0397 | 0.2988 | 198.7843 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-009-TAP 345.00] TO [CANEYRV7 345.00] CKT 1 | 27.2197 | 0.2996 | 199.623 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-009-TAP 345.00] TO [CANEYRV7 345.00] CKT 1 | 27.2197 | 0.2996 | 199.623 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KINGMAN7 345.00] TO [NINN1WF7 345.00] CKT 1 | 31.0607 | 0.293 | 193.048 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KINGMAN7 345.00] TO [NINN1WF7 345.00] CKT 1 | 31.0607 | 0.293 | 193.048 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KINGMAN7 345.00] TO [K1 LV 1 34.500] TO [K1 WFTX1 13.800] CKT 1 | 31.0377 | 0.2945 | 194.4574 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KINGMAN7 345.00] TO [K1 LV 1 34.500] TO [K1 WFTX1 13.800] CKT 1 | 31.0377 | 0.2945 | 194.4574 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KINGMAN7 345.00] TO [K2 LV 1 34.500] TO [K2 WFTX1 13.800] CKT 1 | 31.038 | 0.2944 | 194.4387 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KINGMAN7 345.00] TO [K2 LV 1 34.500] TO [K2 WFTX1 13.800] CKT 1 | 31.038 | 0.2944 | 194.4387 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTON 7 345.00] TO [WICHITA7 345.00] CKT 1 | 30.7498 | 0.2941 | 194.1436 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTON 7 345.00] TO [WICHITA7 345.00] CKT 1 | 30.7498 | 0.2941 | 194.1436 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTON 7 345.00] TO [WOLFCRK7 345.00] CKT 1 | 31.0161 | 0.2969 | 196.871 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTON 7 345.00] TO [WOLFCRK7 345.00] CKT 1 | 31.0161 | 0.2969 | 196.871 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [VIOLA 7 345.00] CKT 1 | 31.0078 | 0.296 | 195.9815 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [VIOLA 7 345.00] CKT 1 | 31.0078 | 0.296 | 195.9815 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [EXPEDITION7 345.00] CKT 1 | 30.9897 | 0.2953 | 195.2632 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [EXPEDITION7 345.00] CKT 1 | 30.9897 | 0.2953 | 195.2632 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WOLFCRK7 345.00] TO [WAVERLY7 345.00] CKT 1 | 31.0506 | 0.2937 | 193.6694 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WOLFCRK7 345.00] TO [WAVERLY7 345.00] CKT 1 | 31.0506 | 0.2937 | 193.6694 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [VIOLA 7 345.00] TO [VIOLA 4 138.00] TO [VIOLA1X1 13.800] CKT 1 | 31.0296 | 0.295 | 194.988 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [VIOLA 7 345.00] TO [VIOLA 4 138.00] TO [VIOLA1X1 13.800] CKT 1 | 31.0296 | 0.295 | 194.988 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [VIOLA 7 345.00] TO [VIOLA 4 138.00] TO [SCJ1X1 13.800] CKT 2 | 31.0297 | 0.2949 | 194.9216 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [VIOLA 7 345.00] TO [VIOLA 4 138.00] TO [SCJ1X1 13.800] CKT 2 | 31.0297 | 0.2949 | 194.9216 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WAVERLY7 345.00] TO [LACYGNE7 345.00] CKT 1 | 31.0285 | 0.2954 | 195.3928 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WAVERLY7 345.00] TO [LACYGNE7 345.00] CKT 1 | 31.0285 | 0.2954 | 195.3928 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NMANHT6 230.00] TO [ELMCREK6 230.00] CKT 1 | 31.0306 | 0.295 | 194.9564 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NMANHT6 230.00] TO [ELMCREK6 230.00] CKT 1 | 31.0306 | 0.295 | 194.9564 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH 5 161.00] TO [FRANKLIN5 161.00] CKT 1 | 30.9423 | 0.2963 | 196.3309 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH 5 161.00] TO [FRANKLIN5 161.00] CKT 1 | 30.9423 | 0.2963 | 196.3309 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH 5 161.00] TO [LITCH S2 69.000] TO [LITCH1 1 13.200] CKT 1 | 31.0203 | 0.2948 | 194.8325 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH 5 161.00] TO [LITCH S2 69.000] TO [LITCH1 1 13.200] CKT 1 | 31.0203 | 0.2948 | 194.8325 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH 5 161.00] TO [LITCH N2 69.000] TO [LITCH2 1 13.200] CKT 1 | 31.0226 | 0.2951 | 195.061 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH 5 161.00] TO [LITCH N2 69.000] TO [LITCH2 1 13.200] CKT 1 | 31.0226 | 0.2951 | 195.061 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MARMTNW5 161.00] TO [NEOSHO 5 161.00] CKT 1 | 30.5178 | 0.2931 | 193.1253 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MARMTNW5 161.00] TO [NEOSHO 5 161.00] CKT 1 | 30.5178 | 0.2931 | 193.1253 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHO 5 161.00] TO [RIV4525 161.00] CKT 1 | 28.8595 | 0.2846 | 184.6268 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHO 5 161.00] TO [RIV4525 161.00] CKT 1 | 28.8595 | 0.2846 | 184.6268 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHO 5 161.00] TO [NEOSHO 4 138.00] TO [NEOSH4 1 13.200] CKT 1 | 31.0309 | 0.2949 | 194.9367 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHO 5 161.00] TO [NEOSHO 4 138.00] TO [NEOSH4 1 13.200] CKT 1 | 31.0309 | 0.2949 | 194.9367 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHO 5 161.00] TO [NEOSHOS4 138.00] TO [NEOSH5 1 13.200] CKT 1 | 31.0309 | 0.2949 | 194.9281 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHO 5 161.00] TO [NEOSHOS4 138.00] TO [NEOSH5 1 13.200] CKT 1 | 31.0309 | 0.2949 | 194.9281 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRESWLN4 138.00] TO [OXFORD 4 138.00] CKT 1 | 31.0122 | 0.2952 | 195.1962 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRESWLN4 138.00] TO [OXFORD 4 138.00] CKT 1 | 31.0122 | 0.2952 | 195.1962 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TCROCK 4 138.00] TO [TIMBJCT4 138.00] CKT 1 | 31.0278 | 0.295 | 195.0228 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TCROCK 4 138.00] TO [TIMBJCT4 138.00] CKT 1 | 31.0278 | 0.295 | 195.0228 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TIMBJCT4 138.00] TO [TIMBJCT2 69.000] TO [TIMBJCT1 13.200] CKT 1 | 31.029 | 0.295 | 195.0148 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TIMBJCT4 138.00] TO [TIMBJCT2 69.000] TO [TIMBJCT1 13.200] CKT 1 | 31.029 | 0.295 | 195.0148 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TIOGA 4 138.00] TO [ALTOONA4 138.00] CKT 1 | 30.828 | 0.2943 | 194.2719 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TIOGA 4 138.00] TO [ALTOONA4 138.00] CKT 1 | 30.828 | 0.2943 | 194.2719 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [OTTRCRK4 138.00] TO [ALTOONA4 138.00] CKT 1 | 30.8793 | 0.2946 | 194.5892 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [OTTRCRK4 138.00] TO [ALTOONA4 138.00] CKT 1 | 30.8793 | 0.2946 | 194.5892 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ALTOONA4 138.00] TO [TAYLOR 4 138.00] CKT 1 | 31.0079 | 0.2961 | 196.1139 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ALTOONA4 138.00] TO [TAYLOR 4 138.00] CKT 1 | 31.0079 | 0.2961 | 196.1139 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ALTOONA4 138.00] TO [ALTOO W2 69.000] TO [ALTOO1 1 13.200] CKT 1 | 31.0283 | 0.2948 | 194.8138 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ALTOONA4 138.00] TO [ALTOO W2 69.000] TO [ALTOO1 1 13.200] CKT 1 | 31.0283 | 0.2948 | 194.8138 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ALTOONA4 138.00] TO [ALTOO E2 69.000] TO [ALTOO3 1 13.200] CKT 1 | 31.0273 | 0.2953 | 195.2752 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ALTOONA4 138.00] TO [ALTOO E2 69.000] TO [ALTOO3 1 13.200] CKT 1 | 31.0273 | 0.2953 | 195.2752 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEPARSN4 138.00] TO [NEOSHON4 138.00] CKT 1 | 30.5019 | 0.2958 | 195.8493 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEPARSN4 138.00] TO [NEOSHON4 138.00] CKT 1 | 30.5019 | 0.2958 | 195.8493 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTLEY4 138.00] TO [SG12COL4 138.00] CKT 1 | 31.0265 | 0.295 | 194.9984 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTLEY4 138.00] TO [SG12COL4 138.00] CKT 1 | 31.0265 | 0.295 | 194.9984 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHOS4 138.00] TO [NEOSHO 4 138.00] CKT Z1 | 30.9874 | 0.2947 | 194.654 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHOS4 138.00] TO [NEOSHO 4 138.00] CKT Z1 | 30.9874 | 0.2947 | 194.654 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHO 4 138.00] TO [NEOSHON4 138.00] CKT Z1 | 30.7887 | 0.2956 | 195.6225 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHO 4 138.00] TO [NEOSHON4 138.00] CKT Z1 | 30.7887 | 0.2956 | 195.6225 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CHISHLM4 138.00] TO [MAIZE 4 138.00] CKT 1 | 31.0205 | 0.295 | 195.0175 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CHISHLM4 138.00] TO [MAIZE 4 138.00] CKT 1 | 31.0205 | 0.295 | 195.0175 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLEARWT4 138.00] TO [GILL 4 138.00] CKT 1 | 31.027 | 0.295 | 195.0248 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLEARWT4 138.00] TO [GILL 4 138.00] CKT 1 | 31.027 | 0.295 | 195.0248 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLEARWT4 138.00] TO [VIOLA 4 138.00] CKT 1 | 31.0264 | 0.295 | 194.9968 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLEARWT4 138.00] TO [VIOLA 4 138.00] CKT 1 | 31.0264 | 0.295 | 194.9968 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EVANS S4 138.00] TO [LAKERDG4 138.00] CKT 1 | 31.0272 | 0.2953 | 195.2844 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EVANS S4 138.00] TO [LAKERDG4 138.00] CKT 1 | 31.0272 | 0.2953 | 195.2844 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EVANS S4 138.00] TO [45TH ST4 138.00] CKT 1 | 31.027 | 0.2953 | 195.2957 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EVANS S4 138.00] TO [45TH ST4 138.00] CKT 1 | 31.027 | 0.2953 | 195.2957 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FARBER 4 138.00] TO [SC10BEL4 138.00] CKT 1 | 31.0113 | 0.2951 | 195.0718 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FARBER 4 138.00] TO [SC10BEL4 138.00] CKT 1 | 31.0113 | 0.2951 | 195.0718 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GILL 4 138.00] TO [VIOLA 4 138.00] CKT 1 | 31.0263 | 0.295 | 195.019 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GILL 4 138.00] TO [VIOLA 4 138.00] CKT 1 | 31.0263 | 0.295 | 195.019 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [VIOLA 4 138.00] TO [MILAN_GOAB 138.00] CKT 1 | 31.0298 | 0.295 | 194.95 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [VIOLA 4 138.00] TO [MILAN_GOAB 138.00] CKT 1 | 31.0298 | 0.295 | 194.95 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [VIOLA 4 138.00] TO [CONWAY 138.00] CKT 1 | 31.029 | 0.2949 | 194.9296 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [VIOLA 4 138.00] TO [CONWAY 138.00] CKT 1 | 31.029 | 0.2949 | 194.9296 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [AEC 3 115.00] TO [EABILEN3 115.00] CKT 1 | 31.0317 | 0.2949 | 194.9102 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [AEC 3 115.00] TO [EABILEN3 115.00] CKT 1 | 31.0317 | 0.2949 | 194.9102 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [AEC 3 115.00] TO [AEC E1 34.500] CKT 2 | 31.0293 | 0.295 | 194.999 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [AEC 3 115.00] TO [AEC E1 34.500] CKT 2 | 31.0293 | 0.295 | 194.999 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [AEC 3 115.00] TO [AEC W1 34.500] CKT 1 | 31.026 | 0.2951 | 195.1313 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [AEC 3 115.00] TO [AEC W1 34.500] CKT 1 | 31.026 | 0.2951 | 195.1313 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NORTHST3 115.00] TO [NORTHVW3 115.00] CKT 1 | 31.0299 | 0.295 | 194.9561 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NORTHST3 115.00] TO [NORTHVW3 115.00] CKT 1 | 31.0299 | 0.295 | 194.9561 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NORTHVW3 115.00] TO [SUMMIT 3 115.00] CKT 1 | 31.0307 | 0.2949 | 194.9448 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NORTHVW3 115.00] TO [SUMMIT 3 115.00] CKT 1 | 31.0307 | 0.2949 | 194.9448 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH N2 69.000] TO [LITCH S2 69.000] CKT Z1 | 31.0286 | 0.295 | 195.0181 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH N2 69.000] TO [LITCH S2 69.000] CKT Z1 | 31.0286 | 0.295 | 195.0181 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MRWYP16 230.00] TO [ELMCREK6 230.00] CKT 1 | 31.0417 | 0.2943 | 194.2675 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MRWYP16 230.00] TO [ELMCREK6 230.00] CKT 1 | 31.0417 | 0.2943 | 194.2675 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FLATRDG4 138.00] TO [THISTLE4 138.00] CKT 1 | 31.0312 | 0.2949 | 194.9245 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FLATRDG4 138.00] TO [THISTLE4 138.00] CKT 1 | 31.0312 | 0.2949 | 194.9245 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ELMCREK6 230.00] TO [CONCRD6 230.00] CKT 1 | 31.0261 | 0.2951 | 195.0606 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ELMCREK6 230.00] TO [CONCRD6 230.00] CKT 1 | 31.0261 | 0.2951 | 195.0606 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAYNE3 115.00] TO [NLIB 3 115.00] CKT 1 | 31.0304 | 0.2949 | 194.9472 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAYNE3 115.00] TO [NLIB 3 115.00] CKT 1 | 31.0304 | 0.2949 | 194.9472 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KISMET 3 115.00] TO [CMRIVTP3 115.00] CKT 1 | 31.0294 | 0.295 | 194.9628 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KISMET 3 115.00] TO [CMRIVTP3 115.00] CKT 1 | 31.0294 | 0.295 | 194.9628 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CMRIVTP3 115.00] TO [E-LIBER3 115.00] CKT 1 | 31.0306 | 0.2949 | 194.9493 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CMRIVTP3 115.00] TO [E-LIBER3 115.00] CKT 1 | 31.0306 | 0.2949 | 194.9493 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CIM-PLT1 13.800] TO [CIM-PLT 13.800] CKT Z1 | 31.0284 | 0.2951 | 195.0878 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CIM-PLT1 13.800] TO [CIM-PLT 13.800] CKT Z1 | 31.0284 | 0.2951 | 195.0878 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N-CIMRN3 115.00] TO [N-CMRN 1 34.500] TO [N-CMRN-T 13.800] CKT 1 | 31.0302 | 0.295 | 194.9644 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N-CIMRN3 115.00] TO [N-CMRN 1 34.500] TO [N-CMRN-T 13.800] CKT 1 | 31.0302 | 0.295 | 194.9644 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [TRANSFORMER 345.00] CKT 1 | 31.0371 | 0.2945 | 194.5064 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [TRANSFORMER 345.00] CKT 1 | 31.0371 | 0.2945 | 194.5064 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [GEN-2011-008345.00] CKT 1 | 31.0454 | 0.294 | 194.0362 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [GEN-2011-008345.00] CKT 1 | 31.0454 | 0.294 | 194.0362 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [G16-046-TAP 345.00] CKT 1 | 31.0273 | 0.2949 | 194.9243 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [G16-046-TAP 345.00] CKT 1 | 31.0273 | 0.2949 | 194.9243 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MULLNCR7 345.00] TO [MC REAC1 345.00] CKT Z1 | 31.0313 | 0.2949 | 194.9251 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MULLNCR7 345.00] TO [MC REAC1 345.00] CKT Z1 | 31.0313 | 0.2949 | 194.9251 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MULLNCR7 345.00] TO [MC REAC2 345.00] CKT Z1 | 31.0313 | 0.2949 | 194.9251 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MULLNCR7 345.00] TO [MC REAC2 345.00] CKT Z1 | 31.0313 | 0.2949 | 194.9251 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MULLNCR7 345.00] TO [MC REAC3 345.00] CKT Z1 | 31.0312 | 0.2949 | 194.9056 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MULLNCR7 345.00] TO [MC REAC3 345.00] CKT Z1 | 31.0312 | 0.2949 | 194.9056 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MULLNCR7 345.00] TO [KETCHEM7 345.00] CKT 1 | 31.0266 | 0.2946 | 194.6155 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MULLNCR7 345.00] TO [KETCHEM7 345.00] CKT 1 | 31.0266 | 0.2946 | 194.6155 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [PECULR 7 345.00] TO [STILWEL7 345.00] CKT 1 | 30.9199 | 0.2969 | 196.9431 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [PECULR 7 345.00] TO [STILWEL7 345.00] CKT 1 | 30.9199 | 0.2969 | 196.9431 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 7 345.00] TO [EASTOWN7 345.00] CKT 1 | 31.0246 | 0.2952 | 195.2204 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 7 345.00] TO [EASTOWN7 345.00] CKT 1 | 31.0246 | 0.2952 | 195.2204 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 7 345.00] TO [COOPER 3 345.00] CKT 1 | 31.0261 | 0.2949 | 194.8922 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 7 345.00] TO [COOPER 3 345.00] CKT 1 | 31.0261 | 0.2949 | 194.8922 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 7 345.00] TO [ST JOE 5 161.00] TO [STJOE 1T 13.800] CKT 22 | 31.0304 | 0.295 | 194.9548 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 7 345.00] TO [ST JOE 5 161.00] TO [STJOE 1T 13.800] CKT 22 | 31.0304 | 0.295 | 194.9548 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 7 345.00] TO [ST JOE 5 161.00] TO [STJOE 2T 13.800] CKT 33 | 31.0304 | 0.295 | 194.9549 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 7 345.00] TO [ST JOE 5 161.00] TO [STJOE 2T 13.800] CKT 33 | 31.0304 | 0.295 | 194.9549 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ARCHIE 5 161.00] TO [HSNVL 5 161.00] CKT 1 | 31.0191 | 0.295 | 194.9823 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ARCHIE 5 161.00] TO [HSNVL 5 161.00] CKT 1 | 31.0191 | 0.295 | 194.9823 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ARCHIE 5 161.00] TO [ADRIAN 5 161.00] CKT 1 | 30.9788 | 0.2962 | 196.2412 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ARCHIE 5 161.00] TO [ADRIAN 5 161.00] CKT 1 | 30.9788 | 0.2962 | 196.2412 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ARCHIE 5 161.00] TO [S.HARP 5 161.00] CKT 1 | 31.0242 | 0.2953 | 195.346 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ARCHIE 5 161.00] TO [S.HARP 5 161.00] CKT 1 | 31.0242 | 0.2953 | 195.346 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [STILWEL5 161.00] CKT 1 | 31.0288 | 0.295 | 195.0277 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [STILWEL5 161.00] CKT 1 | 31.0288 | 0.295 | 195.0277 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EASTOWN7 345.00] TO [IATAN 7 345.00] CKT 1 | 31.0154 | 0.2957 | 195.7221 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EASTOWN7 345.00] TO [IATAN 7 345.00] CKT 1 | 31.0154 | 0.2957 | 195.7221 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ROCKCK_TR1_113.200] TO [ROCKCK7 345.00] TO [ROCKCK_T1_1 34.500] CKT 1 | 31.0396 | 0.2944 | 194.365 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ROCKCK_TR1_113.200] TO [ROCKCK7 345.00] TO [ROCKCK_T1_1 34.500] CKT 1 | 31.0396 | 0.2944 | 194.365 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ROCKCK_TR2_113.200] TO [ROCKCK7 345.00] TO [ROCKCK_T2_1 34.500] CKT 1 | 31.0393 | 0.2944 | 194.3871 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ROCKCK_TR2_113.200] TO [ROCKCK7 345.00] TO [ROCKCK_T2_1 34.500] CKT 1 | 31.0393 | 0.2944 | 194.3871 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ROCKCK7 345.00] TO [OUTLAW 345.00] CKT 1 | 31.0463 | 0.2939 | 193.8972 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ROCKCK7 345.00] TO [OUTLAW 345.00] CKT 1 | 31.0463 | 0.2939 | 193.8972 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC G1 1 22.000] TO [LACYGNE7 345.00] CKT 1 | 30.6758 | 0.2905 | 190.5158 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC G1 1 22.000] TO [LACYGNE7 345.00] CKT 1 | 30.6758 | 0.2905 | 190.5158 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC G2 1 24.000] TO [LACYGNE7 345.00] CKT 1 | 30.8223 | 0.2859 | 185.9005 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC G2 1 24.000] TO [LACYGNE7 345.00] CKT 1 | 30.8223 | 0.2859 | 185.9005 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [CEDRCRK5 161.00] CKT 1 | 31.0239 | 0.295 | 194.9914 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [CEDRCRK5 161.00] CKT 1 | 31.0239 | 0.295 | 194.9914 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [CEDARNL5 161.00] CKT 1 | 31.0293 | 0.295 | 195.0083 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [CEDARNL5 161.00] CKT 1 | 31.0293 | 0.295 | 195.0083 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [PLSTVAL5 161.00] CKT 1 | 31.0172 | 0.295 | 194.9807 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [PLSTVAL5 161.00] CKT 1 | 31.0172 | 0.295 | 194.9807 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [BULLCRK5 161.00] CKT 1 | 31.0307 | 0.2949 | 194.9444 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [BULLCRK5 161.00] CKT 1 | 31.0307 | 0.2949 | 194.9444 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [BNSF 5 161.00] CKT 1 | 31.0246 | 0.2951 | 195.0979 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [BNSF 5 161.00] CKT 1 | 31.0246 | 0.2951 | 195.0979 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [WGARDNR1 34.500] CKT 7 | 31.0278 | 0.2951 | 195.0708 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [WGARDNR1 34.500] CKT 7 | 31.0278 | 0.2951 | 195.0708 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL7 345.00] TO [LACYGNE7 345.00] CKT 1 | 30.6909 | 0.3011 | 201.0634 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL7 345.00] TO [LACYGNE7 345.00] CKT 1 | 30.6909 | 0.3011 | 201.0634 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL7 345.00] TO [STILWEL5 161.00] TO [STIL T11 13.800] CKT 11 | 31.0218 | 0.2953 | 195.2728 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL7 345.00] TO [STILWEL5 161.00] TO [STIL T11 13.800] CKT 11 | 31.0218 | 0.2953 | 195.2728 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL7 345.00] TO [STILWEL5 161.00] TO [STIL T22 13.800] CKT 22 | 31.0212 | 0.2953 | 195.2926 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL7 345.00] TO [STILWEL5 161.00] TO [STIL T22 13.800] CKT 22 | 31.0212 | 0.2953 | 195.2926 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [HICKMAN5 161.00] CKT 1 | 31.0209 | 0.295 | 194.9939 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [HICKMAN5 161.00] CKT 1 | 31.0209 | 0.295 | 194.9939 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [ANTIOCH5 161.00] CKT 1 | 31.0266 | 0.2949 | 194.8688 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [ANTIOCH5 161.00] CKT 1 | 31.0266 | 0.2949 | 194.8688 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [REDEL 5 161.00] CKT 1 | 31.0198 | 0.295 | 195.0068 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [REDEL 5 161.00] CKT 1 | 31.0198 | 0.295 | 195.0068 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [BUCYRUS5 161.00] CKT 1 | 30.968 | 0.295 | 194.953 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [BUCYRUS5 161.00] CKT 1 | 30.968 | 0.295 | 194.953 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [LACKMAN5 161.00] CKT 1 | 31.0283 | 0.2949 | 194.9468 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [LACKMAN5 161.00] CKT 1 | 31.0283 | 0.2949 | 194.9468 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTH 7 345.00] TO [NASHUA 7 345.00] CKT 1 | 31.0201 | 0.2955 | 195.5153 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTH 7 345.00] TO [NASHUA 7 345.00] CKT 1 | 31.0201 | 0.2955 | 195.5153 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [SUB M-161 161.00] CKT 1 | 31.0292 | 0.295 | 195.0061 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [SUB M-161 161.00] CKT 1 | 31.0292 | 0.295 | 195.0061 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 7 345.00] TO [CRAIG 5 161.00] TO [CRAI T11 13.800] CKT 11 | 31.0273 | 0.2951 | 195.1408 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 7 345.00] TO [CRAIG 5 161.00] TO [CRAI T11 13.800] CKT 11 | 31.0273 | 0.2951 | 195.1408 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 7 345.00] TO [CRAIG 5 161.00] TO [CRAI T22 13.800] CKT 22 | 31.0274 | 0.2951 | 195.1363 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 7 345.00] TO [CRAIG 5 161.00] TO [CRAI T22 13.800] CKT 22 | 31.0274 | 0.2951 | 195.1363 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 7 345.00] TO [CRAIG 5 161.00] TO [CRAI T33 13.800] CKT 33 | 31.0284 | 0.2951 | 195.0651 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 7 345.00] TO [CRAIG 5 161.00] TO [CRAI T33 13.800] CKT 33 | 31.0284 | 0.2951 | 195.0651 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [CEDRCRK5 161.00] CKT 1 | 31.0304 | 0.2949 | 194.9497 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [CEDRCRK5 161.00] CKT 1 | 31.0304 | 0.2949 | 194.9497 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NASHUA 7 345.00] TO [IATAN 7 345.00] CKT 1 | 31.0188 | 0.2958 | 195.7654 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NASHUA 7 345.00] TO [IATAN 7 345.00] CKT 1 | 31.0188 | 0.2958 | 195.7654 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NASHUA 7 345.00] TO [NASHUA-5 161.00] TO [NASH T11 13.800] CKT 11 | 31.0314 | 0.2949 | 194.8978 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NASHUA 7 345.00] TO [NASHUA-5 161.00] TO [NASH T11 13.800] CKT 11 | 31.0314 | 0.2949 | 194.8978 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NASHUA 7 345.00] TO [NASHUA-5 161.00] TO [NASH T12 13.800] CKT 12 | 31.0294 | 0.295 | 195.0302 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NASHUA 7 345.00] TO [NASHUA-5 161.00] TO [NASH T12 13.800] CKT 12 | 31.0294 | 0.295 | 195.0302 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [LACYGNE11_7 345.00] CKT 1 | 31.0239 | 0.2952 | 195.1585 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [LACYGNE11_7 345.00] CKT 1 | 31.0239 | 0.2952 | 195.1585 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [LACYGNE22_7 345.00] CKT 1 | 31.0306 | 0.2949 | 194.9498 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [LACYGNE22_7 345.00] CKT 1 | 31.0306 | 0.2949 | 194.9498 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [LAC3_STAR7 345.00] CKT H | 31.0306 | 0.2949 | 194.9461 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [LAC3_STAR7 345.00] CKT H | 31.0306 | 0.2949 | 194.9461 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [LAC8_STAR7 345.00] CKT H | 31.0306 | 0.2949 | 194.9457 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [LAC8_STAR7 345.00] CKT H | 31.0306 | 0.2949 | 194.9457 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [LACYGNE2 69.000] TO [LACYGN7_TER16.9000] CKT 7 | 31.0273 | 0.2951 | 195.0629 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [LACYGNE2 69.000] TO [LACYGN7_TER16.9000] CKT 7 | 31.0273 | 0.2951 | 195.0629 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUMILS5 161.00] TO [ECKLES-161 161.00] CKT 1 | 31.0306 | 0.2949 | 194.9442 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUMILS5 161.00] TO [ECKLES-161 161.00] CKT 1 | 31.0306 | 0.2949 | 194.9442 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUMILS5 161.00] TO [BLUEMLS2 69.000] TO [BLUMILS_TER112.500] CKT 3 | 31.0297 | 0.295 | 194.9958 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUMILS5 161.00] TO [BLUEMLS2 69.000] TO [BLUMILS_TER112.500] CKT 3 | 31.0297 | 0.295 | 194.9958 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAKCTYJ2 69.000] TO [BLUVLY 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9448 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAKCTYJ2 69.000] TO [BLUVLY 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9448 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CJ 366 5 161.00] TO [FIR417 5 161.00] CKT 1 | 30.989 | 0.295 | 195 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CJ 366 5 161.00] TO [FIR417 5 161.00] CKT 1 | 30.989 | 0.295 | 195 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CAR395 5 161.00] TO [PUR421 5 161.00] CKT 1 | 30.9787 | 0.2951 | 195.0951 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CAR395 5 161.00] TO [PUR421 5 161.00] CKT 1 | 30.9787 | 0.2951 | 195.0951 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB K 69.000] TO [BLUVLY 69.000] CKT 1 | 31.0305 | 0.2949 | 194.9468 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB K 69.000] TO [BLUVLY 69.000] CKT 1 | 31.0305 | 0.2949 | 194.9468 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB H 69.000] TO [BLUVLY 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9462 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB H 69.000] TO [BLUVLY 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9462 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB H 69.000] TO [SUB M 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9457 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB H 69.000] TO [SUB M 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9457 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUVLY 13.8 13.800] TO [BLUVLY 69.000] CKT 1 | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUVLY 13.8 13.800] TO [BLUVLY 69.000] CKT 1 | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [SUB B 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9464 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [SUB B 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9464 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [SUB J 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9466 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [SUB J 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9466 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [SUB P 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9461 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [SUB P 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9461 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB B 69.000] TO [SUB J 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9468 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB B 69.000] TO [SUB J 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9468 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB J 69.000] TO [SUB M 69.000] CKT 1 | 31.0305 | 0.2949 | 194.9477 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB J 69.000] TO [SUB M 69.000] CKT 1 | 31.0305 | 0.2949 | 194.9477 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB M-161 161.00] TO [SUB M 69.000] CKT 1 | 31.0301 | 0.295 | 194.9546 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB M-161 161.00] TO [SUB M 69.000] CKT 1 | 31.0301 | 0.295 | 194.9546 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-004345.00] TO [G17-004-TAP 345.00] CKT 1 | 31.0431 | 0.2942 | 194.1682 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-004345.00] TO [G17-004-TAP 345.00] CKT 1 | 31.0431 | 0.2942 | 194.1682 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-018345.00] TO [G17-018XFMR134.500] CKT 1 | 31.0419 | 0.2942 | 194.1944 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-018345.00] TO [G17-018XFMR134.500] CKT 1 | 31.0419 | 0.2942 | 194.1944 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-018345.00] TO [G17-018XFMR234.500] CKT 1 | 31.0419 | 0.2942 | 194.1944 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-018345.00] TO [G17-018XFMR234.500] CKT 1 | 31.0419 | 0.2942 | 194.1944 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-068138.00] TO [G17-068XFMR134.500] CKT 1 | 31.0457 | 0.294 | 193.9897 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-068138.00] TO [G17-068XFMR134.500] CKT 1 | 31.0457 | 0.294 | 193.9897 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-082161.00] TO [G17-082XFMR134.500] CKT 1 | 31.0266 | 0.2953 | 195.314 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-082161.00] TO [G17-082XFMR134.500] CKT 1 | 31.0266 | 0.2953 | 195.314 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [S3458 3 345.00] CKT 1 | 31.0304 | 0.2949 | 194.9054 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [S3458 3 345.00] CKT 1 | 31.0304 | 0.2949 | 194.9054 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEBCTY1G 18.000] TO [S3458 3 345.00] CKT 1 | 31.0848 | 0.2914 | 191.4131 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEBCTY1G 18.000] TO [S3458 3 345.00] CKT 1 | 31.0848 | 0.2914 | 191.4131 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEBCTY2G 23.000] TO [S3458 3 345.00] CKT 1 | 31.0876 | 0.2911 | 191.1005 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEBCTY2G 23.000] TO [S3458 3 345.00] CKT 1 | 31.0876 | 0.2911 | 191.1005 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3456 3 345.00] TO [S3458 3 345.00] CKT 1 | 31.0267 | 0.2952 | 195.1748 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3456 3 345.00] TO [S3458 3 345.00] CKT 1 | 31.0267 | 0.2952 | 195.1748 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3458 3 345.00] TO [S3740 3 345.00] CKT 1 | 31.0279 | 0.2951 | 195.0955 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3458 3 345.00] TO [S3740 3 345.00] CKT 1 | 31.0279 | 0.2951 | 195.0955 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3458 3 345.00] TO [103&ROKEBY3 345.00] CKT 1 | 31.0302 | 0.295 | 194.9695 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3458 3 345.00] TO [103&ROKEBY3 345.00] CKT 1 | 31.0302 | 0.295 | 194.9695 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7FAIRPT 345.00] TO [5FAIRPTXF3 161.00] CKT 3 | 31.0282 | 0.2951 | 195.0856 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7FAIRPT 345.00] TO [5FAIRPTXF3 161.00] CKT 3 | 31.0282 | 0.2951 | 195.0856 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [G17-108-TAP 161.00] CKT 1 | 31.0097 | 0.2962 | 196.2408 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5CLINTN 161.00] TO [G17-108-TAP 161.00] CKT 1 | 31.0097 | 0.2962 | 196.2408 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5GIBSON 161.00] CKT 1 | 31.0301 | 0.295 | 194.9764 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5GIBSON 161.00] CKT 1 | 31.0301 | 0.295 | 194.9764 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M0 161.00] CKT 1 | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M0 161.00] CKT 1 | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M1 161.00] CKT 1 | 31.0314 | 0.2949 | 194.9009 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M1 161.00] CKT 1 | 31.0314 | 0.2949 | 194.9009 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M2 161.00] CKT 1 | 31.0314 | 0.2949 | 194.9009 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M2 161.00] CKT 1 | 31.0314 | 0.2949 | 194.9009 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M3 161.00] CKT 1 | 31.0314 | 0.2949 | 194.9009 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M3 161.00] CKT 1 | 31.0314 | 0.2949 | 194.9009 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5NEWMADCP 161.00] CKT Z1 | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5NEWMADCP 161.00] CKT Z1 | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5NEWMADXF12 161.00] CKT Z1 | 31.0307 | 0.2949 | 194.9336 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5NEWMADXF12 161.00] CKT Z1 | 31.0307 | 0.2949 | 194.9336 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5NEWMADGSU1 161.00] CKT 1 | 31.0262 | 0.2952 | 195.2244 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5NEWMADGSU1 161.00] CKT 1 | 31.0262 | 0.2952 | 195.2244 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5NMDSU100HS 161.00] CKT 1 | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5NMDSU100HS 161.00] CKT 1 | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5NMDSU200HS 161.00] CKT 1 | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5NMDSU200HS 161.00] CKT 1 | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5PORTAGEVLE 161.00] CKT 1 | 31.0303 | 0.295 | 194.9671 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5PORTAGEVLE 161.00] CKT 1 | 31.0303 | 0.295 | 194.9671 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5TIPTONVL TN161.00] CKT 1 | 31.0325 | 0.2948 | 194.8293 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5NEWMAD 161.00] TO [5TIPTONVL TN161.00] CKT 1 | 31.0325 | 0.2948 | 194.8293 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5HOLDENB2 161.00] TO [1HOLDNG11 13.800] CKT 11 | 31.0313 | 0.2946 | 194.5639 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5HOLDENB2 161.00] TO [1HOLDNG11 13.800] CKT 11 | 31.0313 | 0.2946 | 194.5639 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5HOLDENB2 161.00] TO [1HOLDNG12 13.800] CKT 12 | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5HOLDENB2 161.00] TO [1HOLDNG12 13.800] CKT 12 | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5HOLDENB2 161.00] TO [2HOLDEN 69.000] CKT 1 | 31.0307 | 0.2949 | 194.9462 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5HOLDENB2 161.00] TO [2HOLDEN 69.000] CKT 1 | 31.0307 | 0.2949 | 194.9462 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5HOLDENB2 161.00] TO [5HOLDENB1 161.00] CKT Z1 | 31.0304 | 0.2949 | 194.9482 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5HOLDENB2 161.00] TO [5HOLDENB1 161.00] CKT Z1 | 31.0304 | 0.2949 | 194.9482 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [2CLINTN 69.000] TO [2LINCLN 69.000] CKT 1 | 31.0286 | 0.295 | 194.9759 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [2CLINTN 69.000] TO [2LINCLN 69.000] CKT 1 | 31.0286 | 0.295 | 194.9759 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [2CLINTN 69.000] TO [2GAINES 69.000] CKT 1 | 31.0283 | 0.2951 | 195.0672 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [2CLINTN 69.000] TO [2GAINES 69.000] CKT 1 | 31.0283 | 0.2951 | 195.0672 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [2CLINTN 69.000] TO [2LEETON 69.000] CKT 1 | 31.0305 | 0.2949 | 194.9485 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [2CLINTN 69.000] TO [2LEETON 69.000] CKT 1 | 31.0305 | 0.2949 | 194.9485 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [2CLINTN 69.000] TO [2PIPER 69.000] CKT 1 | 31.0294 | 0.295 | 194.961 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [2CLINTN 69.000] TO [2PIPER 69.000] CKT 1 | 31.0294 | 0.295 | 194.961 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [2CLINTN 69.000] TO [2CLINTNLD 69.000] CKT 1 | 31.0259 | 0.2951 | 195.1046 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [2CLINTN 69.000] TO [2CLINTNLD 69.000] CKT 1 | 31.0259 | 0.2951 | 195.1046 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7BLACKBERRY 345.00] TO [NEOSHO 7 345.00] CKT 1 | 22.8194 | 0.2915 | 191.5345 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7BLACKBERRY 345.00] TO [NEOSHO 7 345.00] CKT 1 | 22.8194 | 0.2915 | 191.5345 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7SPORTSMAN 345.00] TO [5SPORTSMAN 161.00] CKT 1 | 31.0045 | 0.295 | 194.9794 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7SPORTSMAN 345.00] TO [5SPORTSMAN 161.00] CKT 1 | 31.0045 | 0.295 | 194.9794 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7SPORTSMAN 345.00] TO [5SPORTSMAN 161.00] CKT 2 | 31.0045 | 0.295 | 194.9795 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7SPORTSMAN 345.00] TO [5SPORTSMAN 161.00] CKT 2 | 31.0045 | 0.295 | 194.9795 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7SPORTSMAN 345.00] TO [GRDA1 7 345.00] CKT 1 | 30.7728 | 0.2955 | 195.5414 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7SPORTSMAN 345.00] TO [GRDA1 7 345.00] CKT 1 | 30.7728 | 0.2955 | 195.5414 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7JASPER 345.00] TO [7MORGAN 345.00] CKT 1 | 29.3028 | 0.2919 | 191.9313 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7JASPER 345.00] TO [7MORGAN 345.00] CKT 1 | 29.3028 | 0.2919 | 191.9313 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7JASPER 345.00] TO [5JASPER 161.00] CKT 1 | 30.7947 | 0.2954 | 195.3863 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7JASPER 345.00] TO [5JASPER 161.00] CKT 1 | 30.7947 | 0.2954 | 195.3863 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5OSCEOKCTP 161.00] TO [5OSCEOLTP 161.00] CKT 1 | 31.0013 | 0.2955 | 195.4934 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5OSCEOKCTP 161.00] TO [5OSCEOLTP 161.00] CKT 1 | 31.0013 | 0.2955 | 195.4934 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5OSCEOKCTP 161.00] TO [5OSCEOKC 161.00] CKT 1 | 31.0313 | 0.2949 | 194.8757 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5OSCEOKCTP 161.00] TO [5OSCEOKC 161.00] CKT 1 | 31.0313 | 0.2949 | 194.8757 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5MINER 1 161.00] TO [5CHARLSTN 161.00] CKT 1 | 31.0307 | 0.2949 | 194.9437 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5MINER 1 161.00] TO [5CHARLSTN 161.00] CKT 1 | 31.0307 | 0.2949 | 194.9437 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5MINER 1 161.00] TO [5BULLION 161.00] CKT 1 | 31.03 | 0.295 | 194.9876 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5MINER 1 161.00] TO [5BULLION 161.00] CKT 1 | 31.03 | 0.295 | 194.9876 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5MINER 1 161.00] TO [5MINER 2 161.00] CKT Z | 31.0307 | 0.2949 | 194.9435 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [5MINER 1 161.00] TO [5MINER 2 161.00] CKT Z | 31.0307 | 0.2949 | 194.9435 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N MADRD5 161.00] TO [G17-202-TAP 161.00] CKT 1 | 31.0303 | 0.295 | 194.9669 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N MADRD5 161.00] TO [G17-202-TAP 161.00] CKT 1 | 31.0303 | 0.295 | 194.9669 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N MADRD2 69.000] TO [2STJUDEW 69.000] CKT 1 | 31.0305 | 0.295 | 194.95 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N MADRD2 69.000] TO [2STJUDEW 69.000] CKT 1 | 31.0305 | 0.295 | 194.95 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N MADRD2 69.000] TO [2LILBRN 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9458 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N MADRD2 69.000] TO [2LILBRN 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9458 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N MADRD2 69.000] TO [MALDEN 2 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9486 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N MADRD2 69.000] TO [MALDEN 2 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9486 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KENNETT5 161.00] TO [PARAGLD5 161.00] CKT 1 | 31.0301 | 0.295 | 194.9682 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KENNETT5 161.00] TO [PARAGLD5 161.00] CKT 1 | 31.0301 | 0.295 | 194.9682 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KENNETT5 161.00] TO [KENNETT2 69.000] TO [KEN X1 1 13.800] CKT 1 | 31.0306 | 0.2949 | 194.9458 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KENNETT5 161.00] TO [KENNETT2 69.000] TO [KEN X1 1 13.800] CKT 1 | 31.0306 | 0.2949 | 194.9458 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KENNETT5 161.00] TO [KENNETT2 69.000] TO [KEN X2 1 13.800] CKT 1 | 31.0306 | 0.2949 | 194.9457 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KENNETT5 161.00] TO [KENNETT2 69.000] TO [KEN X2 1 13.800] CKT 1 | 31.0306 | 0.2949 | 194.9457 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SIKETAP5 161.00] TO [SIKE SW5 161.00] CKT 1 | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SIKETAP5 161.00] TO [SIKE SW5 161.00] CKT 1 | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SIKESTN5 161.00] TO [G17-202-TAP 161.00] CKT 1 | 31.0304 | 0.295 | 194.9622 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SIKESTN5 161.00] TO [G17-202-TAP 161.00] CKT 1 | 31.0304 | 0.295 | 194.9622 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IDALIA 5 161.00] TO [5ESSEX 161.00] CKT 1 | 31.0299 | 0.295 | 194.9967 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IDALIA 5 161.00] TO [5ESSEX 161.00] CKT 1 | 31.0299 | 0.295 | 194.9967 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IDALIA 5 161.00] TO [2IDALIA 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9462 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IDALIA 5 161.00] TO [2IDALIA 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9462 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IDALIA 5 161.00] TO [2IDALIA 69.000] CKT 2 | 31.0306 | 0.2949 | 194.9462 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IDALIA 5 161.00] TO [2IDALIA 69.000] CKT 2 | 31.0306 | 0.2949 | 194.9462 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IDALIA 5 161.00] TO [ASHRVL5 161.00] CKT 1 | 31.0285 | 0.2951 | 195.0704 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IDALIA 5 161.00] TO [ASHRVL5 161.00] CKT 1 | 31.0285 | 0.2951 | 195.0704 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TRUMAN 5 161.00] TO [5LOSTVALY 161.00] CKT 1 | 31.0074 | 0.2965 | 196.5094 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TRUMAN 5 161.00] TO [5LOSTVALY 161.00] CKT 1 | 31.0074 | 0.2965 | 196.5094 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TRUMAN 5 161.00] TO [TRU123 1 13.800] CKT 1 | 31.0276 | 0.295 | 194.9507 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TRUMAN 5 161.00] TO [TRU123 1 13.800] CKT 1 | 31.0276 | 0.295 | 194.9507 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TRUMAN 5 161.00] TO [TRU456 1 13.800] CKT 1 | 31.0276 | 0.2949 | 194.9493 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TRUMAN 5 161.00] TO [TRU456 1 13.800] CKT 1 | 31.0276 | 0.2949 | 194.9493 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DELWARE4 138.00] TO [FARML 4 138.00] CKT 1 | 30.9941 | 0.295 | 195.0459 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DELWARE4 138.00] TO [FARML 4 138.00] CKT 1 | 30.9941 | 0.295 | 195.0459 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DELWARE7 345.00] TO [NEOSHO 7 345.00] CKT 1 | 25.226 | 0.3046 | 204.5982 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DELWARE7 345.00] TO [NEOSHO 7 345.00] CKT 1 | 25.226 | 0.3046 | 204.5982 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N.E.S.-7 345.00] TO [ONETA--7 345.00] CKT 1 | 30.3797 | 0.2951 | 195.0825 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N.E.S.-7 345.00] TO [ONETA--7 345.00] CKT 1 | 30.3797 | 0.2951 | 195.0825 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N.E.S.-7 345.00] TO [T.NO.--7 345.00] CKT 1 | 30.4511 | 0.2949 | 194.8686 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N.E.S.-7 345.00] TO [T.NO.--7 345.00] CKT 1 | 30.4511 | 0.2949 | 194.8686 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N.E.S.-7 345.00] TO [NES3-1 22.000] CKT 1 | 30.6201 | 0.2975 | 197.4518 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N.E.S.-7 345.00] TO [NES3-1 22.000] CKT 1 | 30.6201 | 0.2975 | 197.4518 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [TATONGA7 345.00] CKT 1 | 31.0272 | 0.2952 | 195.1993 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [TATONGA7 345.00] CKT 1 | 31.0272 | 0.2952 | 195.1993 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [TATONGA7 345.00] CKT 2 | 31.0271 | 0.2952 | 195.2041 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [TATONGA7 345.00] CKT 2 | 31.0271 | 0.2952 | 195.2041 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [G07621119-20345.00] CKT 1 | 31.0307 | 0.295 | 194.9647 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [G07621119-20345.00] CKT 1 | 31.0307 | 0.295 | 194.9647 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [GUTHRIE7 345.00] CKT 1 | 31.0306 | 0.295 | 194.954 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [GUTHRIE7 345.00] CKT 1 | 31.0306 | 0.295 | 194.954 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [BECKHAM7 345.00] CKT 1 | 31.0168 | 0.2955 | 195.4693 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [BECKHAM7 345.00] CKT 1 | 31.0168 | 0.2955 | 195.4693 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [G16-003-TAP 345.00] CKT 1 | 31.0298 | 0.2949 | 194.9348 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [G16-003-TAP 345.00] CKT 1 | 31.0298 | 0.2949 | 194.9348 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [G16-003-TAP 345.00] CKT 2 | 31.0298 | 0.2949 | 194.9348 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [G16-003-TAP 345.00] CKT 2 | 31.0298 | 0.2949 | 194.9348 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [WWRDEHV4 138.00] TO [WWDEHV31 13.800] CKT 1 | 31.0303 | 0.2949 | 194.9339 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [WWRDEHV4 138.00] TO [WWDEHV31 13.800] CKT 1 | 31.0303 | 0.2949 | 194.9339 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [WWRDEHV4 138.00] TO [WWDEHV21 13.800] CKT 2 | 31.0303 | 0.2949 | 194.9261 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [WWRDEHV4 138.00] TO [WWDEHV21 13.800] CKT 2 | 31.0303 | 0.2949 | 194.9261 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DGRASSE7 345.00] TO [THISTLE7 345.00] CKT 1 | 31.0092 | 0.2957 | 195.6704 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DGRASSE7 345.00] TO [THISTLE7 345.00] CKT 1 | 31.0092 | 0.2957 | 195.6704 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DGRASSE7 345.00] TO [THISTLE7 345.00] CKT 2 | 31.0092 | 0.2957 | 195.6703 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DGRASSE7 345.00] TO [THISTLE7 345.00] CKT 2 | 31.0092 | 0.2957 | 195.6703 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DGRASSE4 138.00] TO [KNOBHIL4 138.00] CKT 1 | 31.0303 | 0.295 | 194.9574 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DGRASSE4 138.00] TO [KNOBHIL4 138.00] CKT 1 | 31.0303 | 0.295 | 194.9574 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DGRASSE4 138.00] TO [ROSEVLY4 138.00] CKT 1 | 31.0303 | 0.295 | 194.9574 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DGRASSE4 138.00] TO [ROSEVLY4 138.00] CKT 1 | 31.0303 | 0.295 | 194.9574 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DGRASSE4 138.00] TO [MOORLND4 138.00] CKT 1 | 31.027 | 0.295 | 194.9805 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DGRASSE4 138.00] TO [MOORLND4 138.00] CKT 1 | 31.027 | 0.295 | 194.9805 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WALKMYR2 69.000] TO [NORTH6T2 69.000] CKT 1 | 31.0299 | 0.295 | 194.9759 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WALKMYR2 69.000] TO [NORTH6T2 69.000] CKT 1 | 31.0299 | 0.295 | 194.9759 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WALKMYR2 69.000] TO [WOODS 2 69.000] CKT 1 | 31.0301 | 0.295 | 194.9697 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WALKMYR2 69.000] TO [WOODS 2 69.000] CKT 1 | 31.0301 | 0.295 | 194.9697 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WALKMYR3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 31.0305 | 0.295 | 194.965 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WALKMYR3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 31.0305 | 0.295 | 194.965 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SEWARD-3 115.00] TO [HASKELL3 115.00] CKT 1 | 31.0305 | 0.295 | 194.9505 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SEWARD-3 115.00] TO [HASKELL3 115.00] CKT 1 | 31.0305 | 0.295 | 194.9505 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SEWARD-3 115.00] TO [CMSSWRD2 69.000] TO [SEWARD 1 13.800] CKT 1 | 31.0301 | 0.295 | 194.9703 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SEWARD-3 115.00] TO [CMSSWRD2 69.000] TO [SEWARD 1 13.800] CKT 1 | 31.0301 | 0.295 | 194.9703 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [POSTROCK7 345.00] CKT 1 | 31.0283 | 0.295 | 194.9714 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [POSTROCK7 345.00] CKT 1 | 31.0283 | 0.295 | 194.9714 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [BUCKNER7 345.00] CKT 1 | 31.022 | 0.2947 | 194.6839 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [BUCKNER7 345.00] CKT 1 | 31.022 | 0.2947 | 194.6839 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [IRONWOOD7 345.00] CKT 1 | 31.0279 | 0.295 | 195.0046 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [IRONWOOD7 345.00] CKT 1 | 31.0279 | 0.295 | 195.0046 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [SPRVL 3 115.00] TO [SPRVL-T 13.800] CKT 1 | 31.0307 | 0.2949 | 194.9422 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [SPRVL 3 115.00] TO [SPRVL-T 13.800] CKT 1 | 31.0307 | 0.2949 | 194.9422 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [SPEARVL6 230.00] TO [SPERTER1 13.800] CKT 1 | 31.0311 | 0.2949 | 194.9387 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SPERVIL7 345.00] TO [SPEARVL6 230.00] TO [SPERTER1 13.800] CKT 1 | 31.0311 | 0.2949 | 194.9387 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HUGOTON3 115.00] TO [GRANTTP3 115.00] CKT 1 | 31.0302 | 0.295 | 194.9645 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HUGOTON3 115.00] TO [GRANTTP3 115.00] CKT 1 | 31.0302 | 0.295 | 194.9645 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HUGOTON3 115.00] TO [ABBK 2 115.00] CKT 1 | 31.0299 | 0.295 | 194.9782 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HUGOTON3 115.00] TO [ABBK 2 115.00] CKT 1 | 31.0299 | 0.295 | 194.9782 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HUGOTON3 115.00] TO [HUGOTON2 69.000] TO [HUGOTON1 13.800] CKT 1 | 31.0289 | 0.295 | 195.0175 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HUGOTON3 115.00] TO [HUGOTON2 69.000] TO [HUGOTON1 13.800] CKT 1 | 31.0289 | 0.295 | 195.0175 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HARBNGR3 115.00] TO [HARBNGR7 345.00] TO [HARBNGR-T 13.800] CKT 1 | 31.0297 | 0.295 | 194.9881 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HARBNGR3 115.00] TO [HARBNGR7 345.00] TO [HARBNGR-T 13.800] CKT 1 | 31.0297 | 0.295 | 194.9881 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EEC GT1 13.800] TO [DG TIE 1 4.1600] CKT 1 | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EEC GT1 13.800] TO [DG TIE 1 4.1600] CKT 1 | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EEC GT2 13.800] TO [EEC DG 1 4.1600] CKT 1 | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EEC GT2 13.800] TO [EEC DG 1 4.1600] CKT 1 | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC121 13.800] CKT 1 | 31.0338 | 0.2942 | 194.2026 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC121 13.800] CKT 1 | 31.0338 | 0.2942 | 194.2026 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC341 13.800] CKT 1 | 31.0337 | 0.2942 | 194.2026 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC341 13.800] CKT 1 | 31.0337 | 0.2942 | 194.2026 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC5 1 18.000] CKT 1 | 31.0339 | 0.2935 | 193.5294 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC5 1 18.000] CKT 1 | 31.0339 | 0.2935 | 193.5294 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC6 1 18.000] CKT 1 | 31.0306 | 0.2949 | 194.947 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC6 1 18.000] CKT 1 | 31.0306 | 0.2949 | 194.947 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC7 1 18.000] CKT 1 | 31.0323 | 0.2936 | 193.5779 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC7 1 18.000] CKT 1 | 31.0323 | 0.2936 | 193.5779 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [LANG 7 345.00] CKT 1 | 31.027 | 0.2948 | 194.8331 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [LANG 7 345.00] CKT 1 | 31.027 | 0.2948 | 194.8331 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [MORRIS 7 345.00] CKT 1 | 31.0305 | 0.295 | 195.0366 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [MORRIS 7 345.00] CKT 1 | 31.0305 | 0.295 | 195.0366 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [READWF 7 345.00] CKT 1 | 31.0401 | 0.2943 | 194.3179 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EMPEC 7 345.00] TO [READWF 7 345.00] CKT 1 | 31.0401 | 0.2943 | 194.3179 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RENO 7 345.00] TO [G16-111-TAP 345.00] CKT 1 | 31.012 | 0.2951 | 195.1182 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RENO 7 345.00] TO [G16-111-TAP 345.00] CKT 1 | 31.012 | 0.2951 | 195.1182 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RENO 7 345.00] TO [RENO 3 115.00] TO [RENO 1X1 14.400] CKT 1 | 31.0297 | 0.2949 | 194.8862 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RENO 7 345.00] TO [RENO 3 115.00] TO [RENO 1X1 14.400] CKT 1 | 31.0297 | 0.2949 | 194.8862 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RENO 7 345.00] TO [RENO 3 115.00] TO [RENO 2X1 14.400] CKT 1 | 31.0296 | 0.2949 | 194.8894 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RENO 7 345.00] TO [RENO 3 115.00] TO [RENO 2X1 14.400] CKT 1 | 31.0296 | 0.2949 | 194.8894 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 7 345.00] TO [GEARY 7 345.00] CKT 1 | 31.0267 | 0.295 | 194.9891 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 7 345.00] TO [GEARY 7 345.00] CKT 1 | 31.0267 | 0.295 | 194.9891 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 7 345.00] TO [G16-111-TAP 345.00] CKT 1 | 31.012 | 0.295 | 195.0215 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 7 345.00] TO [G16-111-TAP 345.00] CKT 1 | 31.012 | 0.295 | 195.0215 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 7 345.00] TO [SUMMIT 6 230.00] TO [SUMMIT 1 14.400] CKT 1 | 31.0294 | 0.2949 | 194.8925 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 7 345.00] TO [SUMMIT 6 230.00] TO [SUMMIT 1 14.400] CKT 1 | 31.0294 | 0.2949 | 194.8925 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SWISVAL7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 31.0058 | 0.295 | 195.0021 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SWISVAL7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 31.0058 | 0.295 | 195.0021 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [87TH 7 345.00] TO [STRANGR7 345.00] CKT 1 | 30.989 | 0.295 | 194.9626 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [87TH 7 345.00] TO [STRANGR7 345.00] CKT 1 | 30.989 | 0.295 | 194.9626 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [87TH 7 345.00] TO [87TH 3 115.00] TO [87TH 1X1 13.800] CKT 1 | 31.0284 | 0.295 | 195.0052 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [87TH 7 345.00] TO [87TH 3 115.00] TO [87TH 1X1 13.800] CKT 1 | 31.0284 | 0.295 | 195.0052 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-009-TAP 345.00] TO [NEOSHO 7 345.00] CKT 1 | 27.2491 | 0.3077 | 207.7103 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-009-TAP 345.00] TO [NEOSHO 7 345.00] CKT 1 | 27.2491 | 0.3077 | 207.7103 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-009345.00] TO [G17-009XFMR134.500] CKT 1 | 31.0327 | 0.2964 | 196.4299 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-009345.00] TO [G17-009XFMR134.500] CKT 1 | 31.0327 | 0.2964 | 196.4299 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-009345.00] TO [G17-009XFMR234.500] CKT 1 | 31.0335 | 0.2966 | 196.5623 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-009345.00] TO [G17-009XFMR234.500] CKT 1 | 31.0335 | 0.2966 | 196.5623 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CANEYRV7 345.00] TO [CANEYWF7 345.00] CKT 1 | 31.049 | 0.2946 | 194.6148 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CANEYRV7 345.00] TO [CANEYWF7 345.00] CKT 1 | 31.049 | 0.2946 | 194.6148 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CANEYRV7 345.00] TO [LATHAMS7 345.00] CKT 1 | 27.1226 | 0.2913 | 191.3124 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CANEYRV7 345.00] TO [LATHAMS7 345.00] CKT 1 | 27.1226 | 0.2913 | 191.3124 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KINGMAN7 345.00] TO [BUFFALO7 345.00] CKT 1 | 31.0731 | 0.2924 | 192.3679 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KINGMAN7 345.00] TO [BUFFALO7 345.00] CKT 1 | 31.0731 | 0.2924 | 192.3679 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NINN1WF7 345.00] TO [PRATTWF7 345.00] CKT 1 | 31.0459 | 0.294 | 194.0257 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NINN1WF7 345.00] TO [PRATTWF7 345.00] CKT 1 | 31.0459 | 0.294 | 194.0257 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NINN1WF7 345.00] TO [N1 LV 1 34.500] TO [N1 WFTX1 13.800] CKT 1 | 31.0453 | 0.294 | 193.9881 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NINN1WF7 345.00] TO [N1 LV 1 34.500] TO [N1 WFTX1 13.800] CKT 1 | 31.0453 | 0.294 | 193.9881 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTON 7 345.00] TO [ROSEHIL7 345.00] CKT 1 | 30.7643 | 0.2938 | 193.7577 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTON 7 345.00] TO [ROSEHIL7 345.00] CKT 1 | 30.7643 | 0.2938 | 193.7577 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTON 7 345.00] TO [BENTON 4 138.00] TO [BENTN1 1 13.800] CKT 1 | 31.0297 | 0.2951 | 195.0851 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTON 7 345.00] TO [BENTON 4 138.00] TO [BENTN1 1 13.800] CKT 1 | 31.0297 | 0.2951 | 195.0851 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTON 7 345.00] TO [BENTON 4 138.00] TO [BENTN2 1 13.800] CKT 1 | 31.0297 | 0.2951 | 195.0791 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTON 7 345.00] TO [BENTON 4 138.00] TO [BENTN2 1 13.800] CKT 1 | 31.0297 | 0.2951 | 195.0791 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 1 | 31.0265 | 0.2948 | 194.7913 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 1 | 31.0265 | 0.2948 | 194.7913 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 2 | 31.0265 | 0.2948 | 194.7913 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 2 | 31.0265 | 0.2948 | 194.7913 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [EVANS N4 138.00] TO [WICH11 1 13.800] CKT 1 | 31.0307 | 0.2949 | 194.9427 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [EVANS N4 138.00] TO [WICH11 1 13.800] CKT 1 | 31.0307 | 0.2949 | 194.9427 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [EVANS N4 138.00] TO [WICH12 1 13.800] CKT 1 | 31.0308 | 0.2949 | 194.9396 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [EVANS N4 138.00] TO [WICH12 1 13.800] CKT 1 | 31.0308 | 0.2949 | 194.9396 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WOLFCRK7 345.00] TO [WCGS U1 25.000] CKT 1 | 30.5298 | 0.2763 | 176.2777 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WOLFCRK7 345.00] TO [WCGS U1 25.000] CKT 1 | 30.5298 | 0.2763 | 176.2777 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WOLFCRK7 345.00] TO [ROSEHIL7 345.00] CKT 1 | 31.0026 | 0.2971 | 197.0546 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WOLFCRK7 345.00] TO [ROSEHIL7 345.00] CKT 1 | 31.0026 | 0.2971 | 197.0546 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WOLFCRK7 345.00] TO [WOLFCRK2 69.000] TO [WOLFCRK1 17.000] CKT 1 | 31.0189 | 0.2956 | 195.6482 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WOLFCRK7 345.00] TO [WOLFCRK2 69.000] TO [WOLFCRK1 17.000] CKT 1 | 31.0189 | 0.2956 | 195.6482 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [VIOLA 7 345.00] TO [RENFROW7 345.00] CKT 1 | 30.9315 | 0.2986 | 198.6217 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [VIOLA 7 345.00] TO [RENFROW7 345.00] CKT 1 | 30.9315 | 0.2986 | 198.6217 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [VIOLA 7 345.00] TO [G16-153-TAP 345.00] CKT 1 | 31.082 | 0.2919 | 191.8659 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [VIOLA 7 345.00] TO [G16-153-TAP 345.00] CKT 1 | 31.082 | 0.2919 | 191.8659 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WAVERLY7 345.00] TO [WAVERTX7 345.00] CKT 1 | 31.0622 | 0.2934 | 193.413 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WAVERLY7 345.00] TO [WAVERTX7 345.00] CKT 1 | 31.0622 | 0.2934 | 193.413 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EXPEDITION7 345.00] TO [GEN-2014-001345.00] CKT 1 | 31.0439 | 0.2942 | 194.1866 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EXPEDITION7 345.00] TO [GEN-2014-001345.00] CKT 1 | 31.0439 | 0.2942 | 194.1866 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N345 1 1 13.800] TO [NEOSHO 7 345.00] TO [NEOSHO 4 138.00] CKT 1 | 30.1799 | 0.2898 | 189.7868 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N345 1 1 13.800] TO [NEOSHO 7 345.00] TO [NEOSHO 4 138.00] CKT 1 | 30.1799 | 0.2898 | 189.7868 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N345 2 1 13.800] TO [NEOSHO 7 345.00] TO [NEOSHO 5 161.00] CKT 1 | 29.3571 | 0.292 | 192.0294 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N345 2 1 13.800] TO [NEOSHO 7 345.00] TO [NEOSHO 5 161.00] CKT 1 | 29.3571 | 0.292 | 192.0294 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SWISVAL6 230.00] TO [AUBURN 6 230.00] CKT 1 | 31.0297 | 0.295 | 194.9994 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SWISVAL6 230.00] TO [AUBURN 6 230.00] CKT 1 | 31.0297 | 0.295 | 194.9994 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SWISVAL6 230.00] TO [LAWHILL6 230.00] CKT 1 | 31.0215 | 0.2949 | 194.9099 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SWISVAL6 230.00] TO [LAWHILL6 230.00] CKT 1 | 31.0215 | 0.2949 | 194.9099 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SWISVAL6 230.00] TO [TECHILL6 230.00] CKT 1 | 31.0283 | 0.295 | 194.9869 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SWISVAL6 230.00] TO [TECHILL6 230.00] CKT 1 | 31.0283 | 0.295 | 194.9869 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SWISVAL6 230.00] TO [MORRIS 6 230.00] CKT 1 | 31.0304 | 0.295 | 194.9803 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SWISVAL6 230.00] TO [MORRIS 6 230.00] CKT 1 | 31.0304 | 0.295 | 194.9803 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NMANHT6 230.00] TO [EMANHAT6 230.00] CKT 1 | 31.0304 | 0.2949 | 194.9486 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NMANHT6 230.00] TO [EMANHAT6 230.00] CKT 1 | 31.0304 | 0.2949 | 194.9486 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NMANHT6 230.00] TO [NMANHT3 115.00] TO [NMANHX1 14.400] CKT 1 | 31.0306 | 0.2949 | 194.9455 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NMANHT6 230.00] TO [NMANHT3 115.00] TO [NMANHX1 14.400] CKT 1 | 31.0306 | 0.2949 | 194.9455 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH 5 161.00] TO [ASB349 5 161.00] CKT 1 | 30.7361 | 0.2965 | 196.5353 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH 5 161.00] TO [ASB349 5 161.00] CKT 1 | 30.7361 | 0.2965 | 196.5353 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MARMTNW5 161.00] TO [MARMTNE5 161.00] CKT Z1 | 30.6868 | 0.2935 | 193.462 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MARMTNW5 161.00] TO [MARMTNE5 161.00] CKT Z1 | 30.6868 | 0.2935 | 193.462 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MARMTNW5 161.00] TO [MARMATN2 69.000] TO [MARMATN1 13.200] CKT 1 | 31.0118 | 0.295 | 194.9984 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MARMTNW5 161.00] TO [MARMATN2 69.000] TO [MARMATN1 13.200] CKT 1 | 31.0118 | 0.295 | 194.9984 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FRANKLIN5 161.00] TO [G17-005-TAP 161.00] CKT 1 | 30.9339 | 0.2982 | 198.1675 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FRANKLIN5 161.00] TO [G17-005-TAP 161.00] CKT 1 | 30.9339 | 0.2982 | 198.1675 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FRANKLIN5 161.00] TO [FRANKLIN2 69.000] TO [FRANKLIN1 12.470] CKT 1 | 31.019 | 0.2949 | 194.9493 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FRANKLIN5 161.00] TO [FRANKLIN2 69.000] TO [FRANKLIN1 12.470] CKT 1 | 31.019 | 0.2949 | 194.9493 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRESWLN4 138.00] TO [MIDLTNT4 138.00] CKT 1 | 31.0142 | 0.2952 | 195.2492 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRESWLN4 138.00] TO [MIDLTNT4 138.00] CKT 1 | 31.0142 | 0.2952 | 195.2492 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRESWLN4 138.00] TO [SLATECRK4 138.00] CKT 1 | 31.032 | 0.2946 | 194.5704 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRESWLN4 138.00] TO [SLATECRK4 138.00] CKT 1 | 31.032 | 0.2946 | 194.5704 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRESWLN4 138.00] TO [CRESWLN2 69.000] TO [CRESW1 1 13.200] CKT 1 | 31.0308 | 0.2949 | 194.9362 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRESWLN4 138.00] TO [CRESWLN2 69.000] TO [CRESW1 1 13.200] CKT 1 | 31.0308 | 0.2949 | 194.9362 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRESWLN4 138.00] TO [CRESWLS2 69.000] TO [CRESW2 1 13.200] CKT 1 | 31.0307 | 0.295 | 194.9607 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRESWLN4 138.00] TO [CRESWLS2 69.000] TO [CRESW2 1 13.200] CKT 1 | 31.0307 | 0.295 | 194.9607 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [OXFORD 4 138.00] TO [SUMNER 4 138.00] CKT 1 | 31.012 | 0.2952 | 195.1973 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [OXFORD 4 138.00] TO [SUMNER 4 138.00] CKT 1 | 31.012 | 0.2952 | 195.1973 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TIMBJCT4 138.00] TO [SUMNER 4 138.00] CKT 1 | 31.0302 | 0.295 | 195.033 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TIMBJCT4 138.00] TO [SUMNER 4 138.00] CKT 1 | 31.0302 | 0.295 | 195.033 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TIOGA 4 138.00] TO [TIOGA 2 69.000] TO [TIOGA 1 13.200] CKT 1 | 30.8277 | 0.2942 | 194.1661 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TIOGA 4 138.00] TO [TIOGA 2 69.000] TO [TIOGA 1 13.200] CKT 1 | 30.8277 | 0.2942 | 194.1661 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [OTTRCRK4 138.00] TO [BUTLER 4 138.00] CKT 1 | 30.9859 | 0.2949 | 194.8513 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [OTTRCRK4 138.00] TO [BUTLER 4 138.00] CKT 1 | 30.9859 | 0.2949 | 194.8513 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [OTTRCRK4 138.00] TO [OTTRCRK3 115.00] TO [OTTRX1 1 13.800] CKT 1 | 30.9903 | 0.2947 | 194.7066 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [OTTRCRK4 138.00] TO [OTTRCRK3 115.00] TO [OTTRX1 1 13.800] CKT 1 | 30.9903 | 0.2947 | 194.7066 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ALTOONA4 138.00] TO [G17-022-TAP 138.00] CKT 1 | 30.5387 | 0.2937 | 193.7011 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ALTOONA4 138.00] TO [G17-022-TAP 138.00] CKT 1 | 30.5387 | 0.2937 | 193.7011 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEPARSN4 138.00] TO [G17-022-TAP 138.00] CKT 1 | 30.4918 | 0.2935 | 193.5491 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEPARSN4 138.00] TO [G17-022-TAP 138.00] CKT 1 | 30.4918 | 0.2935 | 193.5491 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TAYLOR 4 138.00] TO [MONTGOM4 138.00] CKT 1 | 31.0095 | 0.2959 | 195.8526 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TAYLOR 4 138.00] TO [MONTGOM4 138.00] CKT 1 | 31.0095 | 0.2959 | 195.8526 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTLEY4 138.00] TO [HALSTD 4 138.00] CKT 1 | 31.0267 | 0.295 | 194.9918 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTLEY4 138.00] TO [HALSTD 4 138.00] CKT 1 | 31.0267 | 0.295 | 194.9918 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTLEY4 138.00] TO [WWUPLNT4 138.00] CKT 1 | 31.0294 | 0.295 | 194.9932 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BENTLEY4 138.00] TO [WWUPLNT4 138.00] CKT 1 | 31.0294 | 0.295 | 194.9932 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHOS4 138.00] TO [TV1MNDV4 138.00] CKT 1 | 30.7358 | 0.2941 | 194.0591 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHOS4 138.00] TO [TV1MNDV4 138.00] CKT 1 | 30.7358 | 0.2941 | 194.0591 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHON4 138.00] TO [NEOSHON2 69.000] TO [NEC U3 12.000] CKT 1 | 31.0228 | 0.2949 | 194.8939 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHON4 138.00] TO [NEOSHON2 69.000] TO [NEC U3 12.000] CKT 1 | 31.0228 | 0.2949 | 194.8939 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CHISHLM4 138.00] TO [PARKCTY4 138.00] CKT 1 | 31.0256 | 0.2948 | 194.8217 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CHISHLM4 138.00] TO [PARKCTY4 138.00] CKT 1 | 31.0256 | 0.2948 | 194.8217 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CHISHLM4 138.00] TO [17TH 4 138.00] CKT 1 | 31.0283 | 0.2951 | 195.06 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CHISHLM4 138.00] TO [17TH 4 138.00] CKT 1 | 31.0283 | 0.2951 | 195.06 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CHISHLM4 138.00] TO [CHISHLM2 69.000] TO [CHISOLM1 13.200] CKT 1 | 31.0296 | 0.295 | 195.0189 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CHISHLM4 138.00] TO [CHISHLM2 69.000] TO [CHISOLM1 13.200] CKT 1 | 31.0296 | 0.295 | 195.0189 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EVANS S4 138.00] TO [EVANS N4 138.00] CKT Z1 | 31.0306 | 0.2949 | 194.9469 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EVANS S4 138.00] TO [EVANS N4 138.00] CKT Z1 | 31.0306 | 0.2949 | 194.9469 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EVANS S4 138.00] TO [EVANS N4 138.00] CKT Z2 | 31.0306 | 0.2949 | 194.9469 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EVANS S4 138.00] TO [EVANS N4 138.00] CKT Z2 | 31.0306 | 0.2949 | 194.9469 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FARBER 4 138.00] TO [ELPASOE4 138.00] CKT 1 | 31.0104 | 0.2951 | 195.0612 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FARBER 4 138.00] TO [ELPASOE4 138.00] CKT 1 | 31.0104 | 0.2951 | 195.0612 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GILL 4 138.00] TO [GILL W 4 138.00] CKT Z1 | 31.0306 | 0.2949 | 194.9461 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GILL 4 138.00] TO [GILL W 4 138.00] CKT Z1 | 31.0306 | 0.2949 | 194.9461 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GILL 4 138.00] TO [GILL S 4 138.00] CKT Z1 | 31.0306 | 0.2949 | 194.9462 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GILL 4 138.00] TO [GILL S 4 138.00] CKT Z1 | 31.0306 | 0.2949 | 194.9462 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAKERDG4 138.00] TO [HOOVERN4 138.00] CKT 1 | 31.0277 | 0.2952 | 195.203 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAKERDG4 138.00] TO [HOOVERN4 138.00] CKT 1 | 31.0277 | 0.2952 | 195.203 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MAIZE 4 138.00] TO [EVANS N4 138.00] CKT 1 | 31.0204 | 0.2951 | 195.0743 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MAIZE 4 138.00] TO [EVANS N4 138.00] CKT 1 | 31.0204 | 0.2951 | 195.0743 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SC10BEL4 138.00] TO [SUMNER 4 138.00] CKT 1 | 31.0115 | 0.2951 | 195.0768 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SC10BEL4 138.00] TO [SUMNER 4 138.00] CKT 1 | 31.0115 | 0.2951 | 195.0768 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SG12COL4 138.00] TO [EVANS N4 138.00] CKT 1 | 31.0264 | 0.295 | 194.999 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SG12COL4 138.00] TO [EVANS N4 138.00] CKT 1 | 31.0264 | 0.295 | 194.999 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [45TH ST4 138.00] TO [COWSKIN4 138.00] CKT 1 | 31.0271 | 0.2953 | 195.2852 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [45TH ST4 138.00] TO [COWSKIN4 138.00] CKT 1 | 31.0271 | 0.2953 | 195.2852 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [VIOLA 4 138.00] TO [SUMNER 4 138.00] CKT 1 | 31.0288 | 0.295 | 194.9627 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [VIOLA 4 138.00] TO [SUMNER 4 138.00] CKT 1 | 31.0288 | 0.295 | 194.9627 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [AEC 3 115.00] TO [G17-120-TAP 115.00] CKT 1 | 31.0314 | 0.2949 | 194.8685 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [AEC 3 115.00] TO [G17-120-TAP 115.00] CKT 1 | 31.0314 | 0.2949 | 194.8685 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EABILEN3 115.00] TO [CHAPMAN3 115.00] CKT 1 | 31.0318 | 0.2949 | 194.9102 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EABILEN3 115.00] TO [CHAPMAN3 115.00] CKT 1 | 31.0318 | 0.2949 | 194.9102 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NORTHST3 115.00] TO [SALINA 3 115.00] CKT 1 | 31.0301 | 0.295 | 194.9544 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NORTHST3 115.00] TO [SALINA 3 115.00] CKT 1 | 31.0301 | 0.295 | 194.9544 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NORTHVW3 115.00] TO [G17-120-TAP 115.00] CKT 1 | 31.0303 | 0.295 | 194.9887 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NORTHVW3 115.00] TO [G17-120-TAP 115.00] CKT 1 | 31.0303 | 0.295 | 194.9887 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 3 115.00] TO [MENTOR 3 115.00] CKT 1 | 31.0305 | 0.2949 | 194.9498 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 3 115.00] TO [MENTOR 3 115.00] CKT 1 | 31.0305 | 0.2949 | 194.9498 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 3 115.00] TO [SO GATE3 115.00] CKT 1 | 31.0305 | 0.2949 | 194.9481 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 3 115.00] TO [SO GATE3 115.00] CKT 1 | 31.0305 | 0.2949 | 194.9481 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 3 115.00] TO [SUMMIT 6 230.00] TO [SUMIT2 1 13.800] CKT 1 | 31.0307 | 0.2949 | 194.9453 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 3 115.00] TO [SUMMIT 6 230.00] TO [SUMIT2 1 13.800] CKT 1 | 31.0307 | 0.2949 | 194.9453 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 3 115.00] TO [SUMMIT 6 230.00] TO [SUMIT3 1 13.800] CKT 1 | 31.0307 | 0.2949 | 194.9453 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUMMIT 3 115.00] TO [SUMMIT 6 230.00] TO [SUMIT3 1 13.800] CKT 1 | 31.0307 | 0.2949 | 194.9453 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TIMBJCT2 69.000] TO [AKRON 2 69.000] CKT 1 | 31.0289 | 0.295 | 194.9998 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TIMBJCT2 69.000] TO [AKRON 2 69.000] CKT 1 | 31.0289 | 0.295 | 194.9998 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TIMBJCT2 69.000] TO [UDALL 2 69.000] CKT 1 | 31.028 | 0.295 | 194.9599 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TIMBJCT2 69.000] TO [UDALL 2 69.000] CKT 1 | 31.028 | 0.295 | 194.9599 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TIMBJCT2 69.000] TO [WINFLD 2 69.000] CKT 1 | 31.0273 | 0.2952 | 195.1654 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TIMBJCT2 69.000] TO [WINFLD 2 69.000] CKT 1 | 31.0273 | 0.2952 | 195.1654 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ALTOO E2 69.000] TO [NEODJCT2 69.000] CKT 1 | 31.0283 | 0.2948 | 194.8031 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ALTOO E2 69.000] TO [NEODJCT2 69.000] CKT 1 | 31.0283 | 0.2948 | 194.8031 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ALTOO E2 69.000] TO [RA5HIPR2 69.000] CKT Z1 | 31.03 | 0.2949 | 194.9001 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ALTOO E2 69.000] TO [RA5HIPR2 69.000] CKT Z1 | 31.03 | 0.2949 | 194.9001 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ALTOO W2 69.000] TO [STUDBKR2 69.000] CKT 1 | 31.0285 | 0.2948 | 194.8186 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ALTOO W2 69.000] TO [STUDBKR2 69.000] CKT 1 | 31.0285 | 0.2948 | 194.8186 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH N2 69.000] TO [AQUARS 2 69.000] CKT 1 | 31.0306 | 0.295 | 194.9573 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH N2 69.000] TO [AQUARS 2 69.000] CKT 1 | 31.0306 | 0.295 | 194.9573 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH N2 69.000] TO [PITNAC 2 69.000] CKT 1 | 31.0293 | 0.2949 | 194.9415 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH N2 69.000] TO [PITNAC 2 69.000] CKT 1 | 31.0293 | 0.2949 | 194.9415 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH S2 69.000] TO [ROUSE 2 69.000] CKT 1 | 31.0306 | 0.295 | 194.9504 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH S2 69.000] TO [ROUSE 2 69.000] CKT 1 | 31.0306 | 0.295 | 194.9504 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH S2 69.000] TO [SOPITT 2 69.000] CKT 1 | 30.9462 | 0.2953 | 195.3146 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LITCH S2 69.000] TO [SOPITT 2 69.000] CKT 1 | 30.9462 | 0.2953 | 195.3146 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHOS2 69.000] TO [BAKER 2 69.000] CKT 1 | 30.9398 | 0.2945 | 194.5303 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHOS2 69.000] TO [BAKER 2 69.000] CKT 1 | 30.9398 | 0.2945 | 194.5303 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHOS2 69.000] TO [ORDNJCT2 69.000] CKT 1 | 31.0282 | 0.2941 | 194.1337 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHOS2 69.000] TO [ORDNJCT2 69.000] CKT 1 | 31.0282 | 0.2941 | 194.1337 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHOS2 69.000] TO [CRAWFOR2 69.000] CKT 1 | 30.92 | 0.295 | 194.9887 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHOS2 69.000] TO [CRAWFOR2 69.000] CKT 1 | 30.92 | 0.295 | 194.9887 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHOS2 69.000] TO [NEOSHON2 69.000] CKT Z1 | 31.0239 | 0.295 | 194.9503 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEOSHOS2 69.000] TO [NEOSHON2 69.000] CKT Z1 | 31.0239 | 0.295 | 194.9503 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [K1 LV 1 34.500] TO [K1 CLCT1 34.500] CKT 1 | 31.0379 | 0.2944 | 194.4275 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [K1 LV 1 34.500] TO [K1 CLCT1 34.500] CKT 1 | 31.0379 | 0.2944 | 194.4275 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [K2 LV 1 34.500] TO [K2 CLCT1 34.500] CKT 1 | 31.038 | 0.2944 | 194.4419 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [K2 LV 1 34.500] TO [K2 CLCT1 34.500] CKT 1 | 31.038 | 0.2944 | 194.4419 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MILAN_GOAB 138.00] TO [CLDWELL4 138.00] CKT 1 | 31.0297 | 0.295 | 194.9545 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MILAN_GOAB 138.00] TO [CLDWELL4 138.00] CKT 1 | 31.0297 | 0.295 | 194.9545 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MILAN_GOAB 138.00] TO [MILAN 4 138.00] CKT 1 | 31.0301 | 0.295 | 194.9662 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MILAN_GOAB 138.00] TO [MILAN 4 138.00] CKT 1 | 31.0301 | 0.295 | 194.9662 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CONWAY 138.00] TO [MILANTP4 138.00] CKT 1 | 31.029 | 0.2949 | 194.9287 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CONWAY 138.00] TO [MILANTP4 138.00] CKT 1 | 31.029 | 0.2949 | 194.9287 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MRWYP16 230.00] TO [MRWYP26 230.00] CKT 1 | 31.0356 | 0.2946 | 194.6421 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MRWYP16 230.00] TO [MRWYP26 230.00] CKT 1 | 31.0356 | 0.2946 | 194.6421 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MRWYP16 230.00] TO [MRWYG11 34.500] TO [MRWYP1T1 13.800] CKT 1 | 31.037 | 0.2945 | 194.535 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MRWYP16 230.00] TO [MRWYG11 34.500] TO [MRWYP1T1 13.800] CKT 1 | 31.037 | 0.2945 | 194.535 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FLATRDG4 138.00] TO [FLATRWD4 138.00] CKT 1 | 31.0317 | 0.2946 | 194.6475 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FLATRDG4 138.00] TO [FLATRWD4 138.00] CKT 1 | 31.0317 | 0.2946 | 194.6475 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FLATRDG4 138.00] TO [HARPER 4 138.00] CKT 1 | 31.0271 | 0.2949 | 194.9024 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FLATRDG4 138.00] TO [HARPER 4 138.00] CKT 1 | 31.0271 | 0.2949 | 194.9024 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FLATRDG4 138.00] TO [BARBER 4 138.00] CKT 1 | 31.0295 | 0.2949 | 194.9383 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FLATRDG4 138.00] TO [BARBER 4 138.00] CKT 1 | 31.0295 | 0.2949 | 194.9383 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ELMCREK6 230.00] TO [ELMCREEK7 345.00] TO [ELMCREEK1 13.800] CKT 1 | 31.0277 | 0.295 | 194.9848 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ELMCREK6 230.00] TO [ELMCREEK7 345.00] TO [ELMCREEK1 13.800] CKT 1 | 31.0277 | 0.295 | 194.9848 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAYNE3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 31.0304 | 0.2949 | 194.9461 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAYNE3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 31.0304 | 0.2949 | 194.9461 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KISMET 3 115.00] TO [CUDAHY 3 115.00] CKT 1 | 31.0291 | 0.295 | 194.9688 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KISMET 3 115.00] TO [CUDAHY 3 115.00] CKT 1 | 31.0291 | 0.295 | 194.9688 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CMRIVTP3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 31.0305 | 0.2949 | 194.9429 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CMRIVTP3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 31.0305 | 0.2949 | 194.9429 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CONCRD6 230.00] TO [CONCORD3 115.00] TO [CONCOD-T 13.800] CKT 1 | 31.0261 | 0.2951 | 195.057 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CONCRD6 230.00] TO [CONCORD3 115.00] TO [CONCOD-T 13.800] CKT 1 | 31.0261 | 0.2951 | 195.057 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [E-LIBER3 115.00] TO [TXPHSF 3115.00] CKT 1 | 31.0306 | 0.2949 | 194.9423 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [E-LIBER3 115.00] TO [TXPHSF 3115.00] CKT 1 | 31.0306 | 0.2949 | 194.9423 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [E-LIBER3 115.00] TO [E-PINE 3 115.00] CKT 1 | 31.0293 | 0.295 | 195.0033 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [E-LIBER3 115.00] TO [E-PINE 3 115.00] CKT 1 | 31.0293 | 0.295 | 195.0033 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [E-LIBER3 115.00] TO [NATBEEF3 115.00] CKT 1 | 31.0306 | 0.2949 | 194.9447 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [E-LIBER3 115.00] TO [NATBEEF3 115.00] CKT 1 | 31.0306 | 0.2949 | 194.9447 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [E-LIBER3 115.00] TO [E-LIBER1 34.500] TO [ELIB-T 2.4000] CKT 1 | 31.0293 | 0.295 | 195.0018 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [E-LIBER3 115.00] TO [E-LIBER1 34.500] TO [ELIB-T 2.4000] CKT 1 | 31.0293 | 0.295 | 195.0018 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NLIB 3 115.00] TO [W-LIBER3 115.00] CKT 1 | 31.0289 | 0.295 | 195.0172 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NLIB 3 115.00] TO [W-LIBER3 115.00] CKT 1 | 31.0289 | 0.295 | 195.0172 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NLIB 3 115.00] TO [NATBEEF3 115.00] CKT 1 | 31.0306 | 0.2949 | 194.9468 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NLIB 3 115.00] TO [NATBEEF3 115.00] CKT 1 | 31.0306 | 0.2949 | 194.9468 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NLIB 3 115.00] TO [NLIB 1 34.500] TO [N-LIB-T 13.800] CKT 1 | 31.0291 | 0.295 | 195.0086 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NLIB 3 115.00] TO [NLIB 1 34.500] TO [N-LIB-T 13.800] CKT 1 | 31.0291 | 0.295 | 195.0086 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N-CIMRN3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 31.0305 | 0.2949 | 194.9481 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [N-CIMRN3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 31.0305 | 0.2949 | 194.9481 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CIM-PLT 13.800] TO [CIM-PLT3 115.00] CKT 1 | 31.0255 | 0.2953 | 195.2692 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CIM-PLT 13.800] TO [CIM-PLT3 115.00] CKT 1 | 31.0255 | 0.2953 | 195.2692 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [THISTLE7 345.00] CKT 1 | 31.0262 | 0.2949 | 194.8796 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [THISTLE7 345.00] CKT 1 | 31.0262 | 0.2949 | 194.8796 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [THISTLE7 345.00] CKT 2 | 31.0262 | 0.2949 | 194.8796 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [THISTLE7 345.00] CKT 2 | 31.0262 | 0.2949 | 194.8796 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [THISTLE T1 13.800] TO [THISTLE7 345.00] TO [THISTLE4 138.00] CKT 1 | 31.0312 | 0.2949 | 194.9239 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [THISTLE T1 13.800] TO [THISTLE7 345.00] TO [THISTLE4 138.00] CKT 1 | 31.0312 | 0.2949 | 194.9239 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TRANSFORMER 345.00] TO [SUB34.5KVB 34.500] TO [TERTIARYBUS 19.900] CKT 1 | 31.0371 | 0.2945 | 194.5064 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [TRANSFORMER 345.00] TO [SUB34.5KVB 34.500] TO [TERTIARYBUS 19.900] CKT 1 | 31.0371 | 0.2945 | 194.5064 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2011-008345.00] TO [G-2011-008-1345.00] CKT 1 | 31.0353 | 0.2946 | 194.6494 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2011-008345.00] TO [G-2011-008-1345.00] CKT 1 | 31.0353 | 0.2946 | 194.6494 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2011-008345.00] TO [G-2011-008-2345.00] CKT 1 | 31.0351 | 0.2947 | 194.6684 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2011-008345.00] TO [G-2011-008-2345.00] CKT 1 | 31.0351 | 0.2947 | 194.6684 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2011-008345.00] TO [G-2011-008-3345.00] CKT 1 | 31.0358 | 0.2947 | 194.656 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2011-008345.00] TO [G-2011-008-3345.00] CKT 1 | 31.0358 | 0.2947 | 194.656 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MULLNCR7 345.00] TO [HOLT 7 345.00] CKT 1 | 31.0245 | 0.2948 | 194.784 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [MULLNCR7 345.00] TO [HOLT 7 345.00] CKT 1 | 31.0245 | 0.2948 | 194.784 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [PECULR 7 345.00] TO [PHILL 7 345.00] CKT 1 | 30.9332 | 0.2963 | 196.2535 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [PECULR 7 345.00] TO [PHILL 7 345.00] CKT 1 | 30.9332 | 0.2963 | 196.2535 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [PECULR 7 345.00] TO [PECULR 5 161.00] TO [PECULRT 13.800] CKT 11 | 31.0249 | 0.2953 | 195.2722 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [PECULR 7 345.00] TO [PECULR 5 161.00] TO [PECULRT 13.800] CKT 11 | 31.0249 | 0.2953 | 195.2722 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 7 345.00] TO [G17-183-TAP 345.00] CKT 1 | 31.0265 | 0.295 | 194.9623 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 7 345.00] TO [G17-183-TAP 345.00] CKT 1 | 31.0265 | 0.295 | 194.9623 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ARCHIE 5 161.00] TO [G17-108-TAP 161.00] CKT 1 | 31.0266 | 0.2952 | 195.1932 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ARCHIE 5 161.00] TO [G17-108-TAP 161.00] CKT 1 | 31.0266 | 0.2952 | 195.1932 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WINDSR 5 161.00] TO [5SEDALA 161.00] CKT 1 | 31.0255 | 0.2949 | 194.8843 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WINDSR 5 161.00] TO [5SEDALA 161.00] CKT 1 | 31.0255 | 0.2949 | 194.8843 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HSNVL 5 161.00] TO [5SHARSNV 161.00] CKT 1 | 31.0286 | 0.2951 | 195.0673 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HSNVL 5 161.00] TO [5SHARSNV 161.00] CKT 1 | 31.0286 | 0.2951 | 195.0673 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HSNVL 5 161.00] TO [PHILL 5 161.00] CKT 1 | 31.0128 | 0.2955 | 195.4915 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HSNVL 5 161.00] TO [PHILL 5 161.00] CKT 1 | 31.0128 | 0.2955 | 195.4915 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HSNVL 5 161.00] TO [HSNVL 2 69.000] CKT 1 | 31.0307 | 0.2949 | 194.931 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HSNVL 5 161.00] TO [HSNVL 2 69.000] CKT 1 | 31.0307 | 0.2949 | 194.931 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HSNVL 5 161.00] TO [HSNVL 2 69.000] CKT 2 | 31.0307 | 0.2949 | 194.9318 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HSNVL 5 161.00] TO [HSNVL 2 69.000] CKT 2 | 31.0307 | 0.2949 | 194.9318 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ADRIAN 5 161.00] TO [5BUTLER 161.00] CKT 1 | 30.981 | 0.296 | 196.0332 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ADRIAN 5 161.00] TO [5BUTLER 161.00] CKT 1 | 30.981 | 0.296 | 196.0332 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLINTON5 161.00] TO [CLNTN N2 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9495 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLINTON5 161.00] TO [CLNTN N2 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9495 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLINTON5 161.00] TO [CLNTN S2 69.000] CKT 2 | 31.0306 | 0.2949 | 194.9485 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLINTON5 161.00] TO [CLNTN S2 69.000] CKT 2 | 31.0306 | 0.2949 | 194.9485 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 5 161.00] TO [ST JOE_CAP5 161.00] CKT R | 31.0297 | 0.295 | 195.0121 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 5 161.00] TO [ST JOE_CAP5 161.00] CKT R | 31.0297 | 0.295 | 195.0121 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 5 161.00] TO [COOK 5 161.00] CKT 1 | 31.0307 | 0.2949 | 194.9436 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 5 161.00] TO [COOK 5 161.00] CKT 1 | 31.0307 | 0.2949 | 194.9436 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 5 161.00] TO [WOODBIN5 161.00] CKT 1 | 31.0307 | 0.2949 | 194.9425 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 5 161.00] TO [WOODBIN5 161.00] CKT 1 | 31.0307 | 0.2949 | 194.9425 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 5 161.00] TO [AVENUECTY 5 161.00] CKT 1 | 31.0296 | 0.295 | 194.9743 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ST JOE 5 161.00] TO [AVENUECTY 5 161.00] CKT 1 | 31.0296 | 0.295 | 194.9743 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP#1 13.800] CKT 1 | 31.0307 | 0.2949 | 194.9454 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP#1 13.800] CKT 1 | 31.0307 | 0.2949 | 194.9454 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP#2 13.800] CKT 1 | 31.0307 | 0.2949 | 194.9454 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP#2 13.800] CKT 1 | 31.0307 | 0.2949 | 194.9454 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP#3 13.800] CKT 1 | 31.0307 | 0.2949 | 194.9454 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP#3 13.800] CKT 1 | 31.0307 | 0.2949 | 194.9454 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP 2 69.000] CKT 1 | 31.0301 | 0.295 | 194.9717 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP 2 69.000] CKT 1 | 31.0301 | 0.295 | 194.9717 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [PECULRS5 161.00] CKT 1 | 31.0281 | 0.2951 | 195.0695 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S.HARP 5 161.00] TO [PECULRS5 161.00] CKT 1 | 31.0281 | 0.2951 | 195.0695 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EASTOWN7 345.00] TO [EASTOWN5 161.00] TO [EASTOWN1 13.800] CKT 11 | 31.0295 | 0.295 | 195.0079 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EASTOWN7 345.00] TO [EASTOWN5 161.00] TO [EASTOWN1 13.800] CKT 11 | 31.0295 | 0.295 | 195.0079 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KETCHEM7 345.00] TO [SIBLEY 7 345.00] CKT 1 | 31.0244 | 0.2948 | 194.8197 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KETCHEM7 345.00] TO [SIBLEY 7 345.00] CKT 1 | 31.0244 | 0.2948 | 194.8197 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KETCHEM7 345.00] TO [OSBORN7 345.00] CKT 1 | 31.0387 | 0.2944 | 194.435 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [KETCHEM7 345.00] TO [OSBORN7 345.00] CKT 1 | 31.0387 | 0.2944 | 194.435 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ROCKCK7 345.00] TO [HOLT 7 345.00] CKT 1 | 31.0638 | 0.2927 | 192.7373 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ROCKCK7 345.00] TO [HOLT 7 345.00] CKT 1 | 31.0638 | 0.2927 | 192.7373 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ROCKCK_T1_1 34.500] TO [ROCKCK_P1_1 34.500] CKT 1 | 31.0396 | 0.2944 | 194.3649 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ROCKCK_T1_1 34.500] TO [ROCKCK_P1_1 34.500] CKT 1 | 31.0396 | 0.2944 | 194.3649 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ROCKCK_T2_1 34.500] TO [ROCKCK_P2_1 34.500] CKT 1 | 31.0392 | 0.2944 | 194.3876 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ROCKCK_T2_1 34.500] TO [ROCKCK_P2_1 34.500] CKT 1 | 31.0392 | 0.2944 | 194.3876 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HOLT_REACT7 345.00] TO [HOLT 7 345.00] CKT Z1 | 31.0311 | 0.2949 | 194.9321 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HOLT_REACT7 345.00] TO [HOLT 7 345.00] CKT Z1 | 31.0311 | 0.2949 | 194.9321 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [OUTLAW 345.00] TO [OUTLAW_T2_1 34.500] TO [OUTLAW_TR2_113.800] CKT 1 | 31.037 | 0.2945 | 194.5222 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [OUTLAW 345.00] TO [OUTLAW_T2_1 34.500] TO [OUTLAW_TR2_113.800] CKT 1 | 31.037 | 0.2945 | 194.5222 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [OUTLAW 345.00] TO [OUTLAW_T1_1 34.500] TO [OUTLAW_TR1_113.800] CKT 1 | 31.0398 | 0.2944 | 194.3517 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [OUTLAW 345.00] TO [OUTLAW_T1_1 34.500] TO [OUTLAW_TR1_113.800] CKT 1 | 31.0398 | 0.2944 | 194.3517 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [W.GRDNR7 345.00] TO [WGAR T11 13.800] CKT 11 | 31.0219 | 0.2953 | 195.3113 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR5 161.00] TO [W.GRDNR7 345.00] TO [WGAR T11 13.800] CKT 11 | 31.0219 | 0.2953 | 195.3113 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 31.023 | 0.2953 | 195.2555 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 31.023 | 0.2953 | 195.2555 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [G17-108-TAP 161.00] CKT 1 | 31.0239 | 0.2954 | 195.3679 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [STILWEL5 161.00] TO [G17-108-TAP 161.00] CKT 1 | 31.0239 | 0.2954 | 195.3679 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTH 7 345.00] TO [SIBLEY 7 345.00] CKT 1 | 31.027 | 0.295 | 194.9813 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTH 7 345.00] TO [SIBLEY 7 345.00] CKT 1 | 31.027 | 0.295 | 194.9813 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTH 7 345.00] TO [HAWTHN5 161.00] TO [HAWT T20 13.800] CKT 20 | 31.0306 | 0.295 | 194.9692 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTH 7 345.00] TO [HAWTHN5 161.00] TO [HAWT T20 13.800] CKT 20 | 31.0306 | 0.295 | 194.9692 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTH 7 345.00] TO [HAWTHN5 161.00] TO [HAWT T22 13.800] CKT 22 | 31.0306 | 0.295 | 194.9627 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTH 7 345.00] TO [HAWTHN5 161.00] TO [HAWT T22 13.800] CKT 22 | 31.0306 | 0.295 | 194.9627 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAW G9 1 13.800] CKT 1 | 31.0306 | 0.2949 | 194.9458 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAW G9 1 13.800] CKT 1 | 31.0306 | 0.2949 | 194.9458 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [LEEDS 5 161.00] CKT 1 | 31.0291 | 0.295 | 194.9635 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [LEEDS 5 161.00] CKT 1 | 31.0291 | 0.295 | 194.9635 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [LEEDS 5 161.00] CKT 2 | 31.0291 | 0.295 | 194.9631 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [LEEDS 5 161.00] CKT 2 | 31.0291 | 0.295 | 194.9631 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTH_B2_1 13.200] CKT 1 | 31.0283 | 0.2951 | 195.0764 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTH_B2_1 13.200] CKT 1 | 31.0283 | 0.2951 | 195.0764 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [BRMGHAM5 161.00] CKT 1 | 31.0289 | 0.295 | 195.043 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [BRMGHAM5 161.00] CKT 1 | 31.0289 | 0.295 | 195.043 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHS_G65 161.00] CKT Z1 | 31.0301 | 0.295 | 194.9745 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHS_G65 161.00] CKT Z1 | 31.0301 | 0.295 | 194.9745 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHS_XF5 161.00] CKT Z2 | 31.0305 | 0.295 | 194.9507 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHS_XF5 161.00] CKT Z2 | 31.0305 | 0.295 | 194.9507 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHN5 161.00] CKT @1 | 31.0306 | 0.2949 | 194.9484 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHN5 161.00] CKT @1 | 31.0306 | 0.2949 | 194.9484 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHN5 161.00] CKT @2 | 31.0306 | 0.2949 | 194.9484 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHN5 161.00] CKT @2 | 31.0306 | 0.2949 | 194.9484 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 30.9431 | 0.296 | 195.9782 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 30.9431 | 0.296 | 195.9782 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [CRAIG_CAP 5 161.00] CKT R | 31.0283 | 0.2952 | 195.1871 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [CRAIG_CAP 5 161.00] CKT R | 31.0283 | 0.2952 | 195.1871 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [PFLUMM 5 161.00] CKT 1 | 31.0278 | 0.2951 | 195.0768 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [PFLUMM 5 161.00] CKT 1 | 31.0278 | 0.2951 | 195.0768 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [LENEXA 5 161.00] CKT 1 | 31.029 | 0.295 | 194.9787 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [LENEXA 5 161.00] CKT 1 | 31.029 | 0.295 | 194.9787 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [LENEXA 5 161.00] CKT 2 | 31.0297 | 0.295 | 194.966 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [LENEXA 5 161.00] CKT 2 | 31.0297 | 0.295 | 194.966 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [COLLEGE5 161.00] CKT 1 | 31.0284 | 0.2951 | 195.0626 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [COLLEGE5 161.00] CKT 1 | 31.0284 | 0.2951 | 195.0626 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NASHUA 7 345.00] TO [G17-183-TAP 345.00] CKT 1 | 31.0265 | 0.295 | 195.0121 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NASHUA 7 345.00] TO [G17-183-TAP 345.00] CKT 1 | 31.0265 | 0.295 | 195.0121 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 30.8018 | 0.2979 | 197.8591 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 30.8018 | 0.2979 | 197.8591 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [G17-209-TAP 345.00] CKT 1 | 25.217 | 0.2884 | 188.4046 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE7 345.00] TO [G17-209-TAP 345.00] CKT 1 | 25.217 | 0.2884 | 188.4046 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [STRANGR7 345.00] CKT 1 | 31.0219 | 0.295 | 194.9521 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [STRANGR7 345.00] CKT 1 | 31.0219 | 0.295 | 194.9521 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [STRANGR7 345.00] CKT 2 | 31.023 | 0.295 | 194.9631 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [STRANGR7 345.00] CKT 2 | 31.023 | 0.295 | 194.9631 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [IAT G1 1 24.000] CKT 1 | 31.0906 | 0.29 | 189.9887 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [IAT G1 1 24.000] CKT 1 | 31.0906 | 0.29 | 189.9887 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [IAT G2 1 24.500] CKT 1 | 31.0846 | 0.2902 | 190.1985 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [IAT G2 1 24.500] CKT 1 | 31.0846 | 0.2902 | 190.1985 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [IATAN5 161.00] TO [IATAN 11 14.400] CKT 11 | 31.0282 | 0.2951 | 195.1123 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [IATAN5 161.00] TO [IATAN 11 14.400] CKT 11 | 31.0282 | 0.2951 | 195.1123 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HICKMAN5 161.00] TO [STHTOWN5 161.00] CKT 1 | 31.0217 | 0.295 | 194.9584 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HICKMAN5 161.00] TO [STHTOWN5 161.00] CKT 1 | 31.0217 | 0.295 | 194.9584 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUMILS5 161.00] TO [BLUVLY-161 161.00] CKT 1 | 31.0304 | 0.295 | 194.9554 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUMILS5 161.00] TO [BLUVLY-161 161.00] CKT 1 | 31.0304 | 0.295 | 194.9554 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NASHUA-5 161.00] TO [NASHUA 5 161.00] CKT Z1 | 31.0303 | 0.295 | 194.9633 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NASHUA-5 161.00] TO [NASHUA 5 161.00] CKT Z1 | 31.0303 | 0.295 | 194.9633 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NASHUA-5 161.00] TO [RNRIDGE5 161.00] CKT 1 | 31.0307 | 0.2949 | 194.9453 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NASHUA-5 161.00] TO [RNRIDGE5 161.00] CKT 1 | 31.0307 | 0.2949 | 194.9453 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NASHUA-5 161.00] TO [SHOLCRK5 161.00] CKT 1 | 31.0295 | 0.295 | 195.0332 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NASHUA-5 161.00] TO [SHOLCRK5 161.00] CKT 1 | 31.0295 | 0.295 | 195.0332 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CEDRCRK5 161.00] TO [SHWNMSN5 161.00] CKT 1 | 31.0275 | 0.295 | 194.9894 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CEDRCRK5 161.00] TO [SHWNMSN5 161.00] CKT 1 | 31.0275 | 0.295 | 194.9894 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ANTIOCH5 161.00] TO [OXFORD 5 161.00] CKT 1 | 31.0267 | 0.2949 | 194.8702 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ANTIOCH5 161.00] TO [OXFORD 5 161.00] CKT 1 | 31.0267 | 0.2949 | 194.8702 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [REDEL 5 161.00] TO [MARTCIT5 161.00] CKT 1 | 31.0201 | 0.295 | 195.0096 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [REDEL 5 161.00] TO [MARTCIT5 161.00] CKT 1 | 31.0201 | 0.295 | 195.0096 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BUCYRUS5 161.00] TO [NLOUISB5 161.00] CKT 1 | 31.0287 | 0.295 | 195.029 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BUCYRUS5 161.00] TO [NLOUISB5 161.00] CKT 1 | 31.0287 | 0.295 | 195.029 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BUCYRUS5 161.00] TO [WAGSTAF5 161.00] CKT 1 | 30.9654 | 0.2949 | 194.9262 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BUCYRUS5 161.00] TO [WAGSTAF5 161.00] CKT 1 | 30.9654 | 0.2949 | 194.9262 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [PLSTVAL5 161.00] TO [SEOTTWA5 161.00] CKT 1 | 31.018 | 0.295 | 194.989 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [PLSTVAL5 161.00] TO [SEOTTWA5 161.00] CKT 1 | 31.018 | 0.295 | 194.989 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [PLSTVAL5 161.00] TO [ASG-2018-010161.00] CKT 1 | 31.0358 | 0.2947 | 194.6946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [PLSTVAL5 161.00] TO [ASG-2018-010161.00] CKT 1 | 31.0358 | 0.2947 | 194.6946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [PLSTVAL5 161.00] TO [PLSTVAL1 34.500] TO [PLSTVL2_TER17.6210] CKT 2 | 31.0293 | 0.295 | 195.0041 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [PLSTVAL5 161.00] TO [PLSTVAL1 34.500] TO [PLSTVL2_TER17.6210] CKT 2 | 31.0293 | 0.295 | 195.0041 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAKCTYJ2 69.000] TO [LAKCTY 2 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9455 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAKCTYJ2 69.000] TO [LAKCTY 2 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9455 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 1 13.800] CKT 1 | 31.0306 | 0.2949 | 194.9455 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 1 13.800] CKT 1 | 31.0306 | 0.2949 | 194.9455 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 2 13.800] CKT 1 | 31.0306 | 0.2949 | 194.9455 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 2 13.800] CKT 1 | 31.0306 | 0.2949 | 194.9455 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 3 13.800] CKT 1 | 31.0306 | 0.2949 | 194.9455 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 3 13.800] CKT 1 | 31.0306 | 0.2949 | 194.9455 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 4 13.800] CKT 1 | 31.0306 | 0.2949 | 194.9455 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 4 13.800] CKT 1 | 31.0306 | 0.2949 | 194.9455 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACKMAN5 161.00] TO [SPRGHL 5 161.00] CKT 1 | 31.0283 | 0.2949 | 194.948 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACKMAN5 161.00] TO [SPRGHL 5 161.00] CKT 1 | 31.0283 | 0.2949 | 194.948 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BNSF 5 161.00] TO [MOONLT 5 161.00] CKT 1 | 31.025 | 0.2951 | 195.0756 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BNSF 5 161.00] TO [MOONLT 5 161.00] CKT 1 | 31.025 | 0.2951 | 195.0756 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR1 34.500] TO [BALDWINCTY1 34.500] CKT 1 | 31.0306 | 0.2949 | 194.9466 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WGARDNR1 34.500] TO [BALDWINCTY1 34.500] CKT 1 | 31.0306 | 0.2949 | 194.9466 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE11_7 345.00] TO [LAC11_AQC1 13.800] TO [LAC11_TER1 13.800] CKT 11 | 31.024 | 0.2952 | 195.1541 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE11_7 345.00] TO [LAC11_AQC1 13.800] TO [LAC11_TER1 13.800] CKT 11 | 31.024 | 0.2952 | 195.1541 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE22_7 345.00] TO [LAC22_AQC1 13.800] TO [LAC22_TER1 13.800] CKT 22 | 31.0306 | 0.2949 | 194.9451 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE22_7 345.00] TO [LAC22_AQC1 13.800] TO [LAC22_TER1 13.800] CKT 22 | 31.0306 | 0.2949 | 194.9451 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE2 69.000] TO [LAC_LAKE_2 69.000] CKT 1 | 31.028 | 0.2951 | 195.0537 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LACYGNE2 69.000] TO [LAC_LAKE_2 69.000] CKT 1 | 31.028 | 0.2951 | 195.0537 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC3_STAR7 345.00] TO [LAC3_X1 6.9000] CKT X | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC3_STAR7 345.00] TO [LAC3_X1 6.9000] CKT X | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC3_STAR7 345.00] TO [LAC3_Y1 6.9000] CKT Y | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC3_STAR7 345.00] TO [LAC3_Y1 6.9000] CKT Y | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC3_STAR7 345.00] TO [LAC3_Z1 3.9800] CKT Z | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC3_STAR7 345.00] TO [LAC3_Z1 3.9800] CKT Z | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC8_STAR7 345.00] TO [LAC8_X1 6.9000] CKT X | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC8_STAR7 345.00] TO [LAC8_X1 6.9000] CKT X | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC8_STAR7 345.00] TO [LAC8_Y1 6.9000] CKT Y | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC8_STAR7 345.00] TO [LAC8_Y1 6.9000] CKT Y | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC8_STAR7 345.00] TO [LAC8_Z1 4.0000] CKT Z | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [LAC8_STAR7 345.00] TO [LAC8_Z1 4.0000] CKT Z | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RIV4525 161.00] TO [ORO110 5 161.00] CKT 1 | 31.0256 | 0.2946 | 194.5783 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RIV4525 161.00] TO [ORO110 5 161.00] CKT 1 | 31.0256 | 0.2946 | 194.5783 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RIV4525 161.00] TO [STL439 5 161.00] CKT 1 | 30.8923 | 0.2943 | 194.2758 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RIV4525 161.00] TO [STL439 5 161.00] CKT 1 | 30.8923 | 0.2943 | 194.2758 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RIV4525 161.00] TO [RIV452T 5 161.00] CKT 1 | 30.7287 | 0.2982 | 198.1701 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RIV4525 161.00] TO [RIV452T 5 161.00] CKT 1 | 30.7287 | 0.2982 | 198.1701 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RIV4525 161.00] TO [BAX488 5 161.00] CKT 1 | 30.9744 | 0.294 | 194.0445 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RIV4525 161.00] TO [BAX488 5 161.00] CKT 1 | 30.9744 | 0.294 | 194.0445 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RIV4525 161.00] TO [RIV167 2 69.000] TO [RIV452 1 12.500] CKT 1 | 31.0246 | 0.2951 | 195.0964 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [RIV4525 161.00] TO [RIV167 2 69.000] TO [RIV452 1 12.500] CKT 1 | 31.0246 | 0.2951 | 195.0964 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CJ 366 5 161.00] TO [ASB349 5 161.00] CKT 1 | 30.9857 | 0.2951 | 195.1032 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CJ 366 5 161.00] TO [ASB349 5 161.00] CKT 1 | 30.9857 | 0.2951 | 195.1032 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CAR395 5 161.00] TO [CARTHAG5 161.00] CKT 1 | 30.9809 | 0.295 | 195.0251 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CAR395 5 161.00] TO [CARTHAG5 161.00] CKT 1 | 30.9809 | 0.295 | 195.0251 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FIR417 5 161.00] TO [ORO110 5 161.00] CKT 1 | 30.9922 | 0.2949 | 194.9345 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [FIR417 5 161.00] TO [ORO110 5 161.00] CKT 1 | 30.9922 | 0.2949 | 194.9345 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [PUR421 5 161.00] TO [ASB349 5 161.00] CKT 1 | 30.9769 | 0.2952 | 195.1582 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [PUR421 5 161.00] TO [ASB349 5 161.00] CKT 1 | 30.9769 | 0.2952 | 195.1582 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [A1G349 1 13.800] TO [ASB349 5 161.00] CKT 1 | 31.0319 | 0.2947 | 194.6906 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [A1G349 1 13.800] TO [ASB349 5 161.00] CKT 1 | 31.0319 | 0.2947 | 194.6906 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [A2G349 1 13.800] TO [ASB349 5 161.00] CKT 1 | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [A2G349 1 13.800] TO [ASB349 5 161.00] CKT 1 | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB K 69.000] TO [SUB R 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9465 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB K 69.000] TO [SUB R 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9465 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB H 69.000] TO [COURTNY2 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9497 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB H 69.000] TO [COURTNY2 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9497 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB H 69.000] TO [SUGRCK_TP_E269.000] CKT 1 | 31.0306 | 0.2949 | 194.9469 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB H 69.000] TO [SUGRCK_TP_E269.000] CKT 1 | 31.0306 | 0.2949 | 194.9469 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB H 69.000] TO [SUB H-13B1 13.800] CKT H1 | 31.0293 | 0.295 | 195.0151 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB H 69.000] TO [SUB H-13B1 13.800] CKT H1 | 31.0293 | 0.295 | 195.0151 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB H 69.000] TO [SUB H-13B2 13.800] CKT H2 | 31.0297 | 0.295 | 194.9572 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB H 69.000] TO [SUB H-13B2 13.800] CKT H2 | 31.0297 | 0.295 | 194.9572 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [BLUVLY-161 161.00] CKT 1 | 31.0303 | 0.2949 | 194.9493 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [BLUVLY-161 161.00] CKT 1 | 31.0303 | 0.2949 | 194.9493 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [BLUVLY-161 161.00] CKT 2 | 31.0303 | 0.2949 | 194.9495 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [BLUVLY-161 161.00] CKT 2 | 31.0303 | 0.2949 | 194.9495 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ECKLES-161 161.00] TO [5LEVASY 161.00] CKT 1 | 31.0286 | 0.295 | 195.0466 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ECKLES-161 161.00] TO [5LEVASY 161.00] CKT 1 | 31.0286 | 0.295 | 195.0466 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ECKLES-161 161.00] TO [5MOCITYB1 161.00] CKT 1 | 31.0296 | 0.2949 | 194.9388 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ECKLES-161 161.00] TO [5MOCITYB1 161.00] CKT 1 | 31.0296 | 0.2949 | 194.9388 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ECKLES-161 161.00] TO [SIBLEYPL 161.00] CKT 1 | 31.0295 | 0.295 | 194.9731 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [ECKLES-161 161.00] TO [SIBLEYPL 161.00] CKT 1 | 31.0295 | 0.295 | 194.9731 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB J 69.000] TO [SUB J-13B1 13.800] CKT J1 | 31.0297 | 0.295 | 194.9965 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB J 69.000] TO [SUB J-13B1 13.800] CKT J1 | 31.0297 | 0.295 | 194.9965 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB J 69.000] TO [SUB J-13B2 13.800] CKT J2 | 31.0291 | 0.295 | 195.0226 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB J 69.000] TO [SUB J-13B2 13.800] CKT J2 | 31.0291 | 0.295 | 195.0226 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB M-161 161.00] TO [BLUVLY-161 161.00] CKT 1 | 31.0301 | 0.295 | 194.9724 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB M-161 161.00] TO [BLUVLY-161 161.00] CKT 1 | 31.0301 | 0.295 | 194.9724 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB M 69.000] TO [SHRNKRD 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9471 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB M 69.000] TO [SHRNKRD 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9471 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB P 69.000] TO [SUB I 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9462 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [SUB P 69.000] TO [SUB I 69.000] CKT 1 | 31.0306 | 0.2949 | 194.9462 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G16-046-TAP 345.00] TO [IRONWOOD7 345.00] CKT 1 | 31.0292 | 0.295 | 194.95 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G16-046-TAP 345.00] TO [IRONWOOD7 345.00] CKT 1 | 31.0292 | 0.295 | 194.95 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G16-046-TAP 345.00] TO [GEN-2016-046345.00] CKT 1 | 31.0413 | 0.2939 | 193.8926 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G16-046-TAP 345.00] TO [GEN-2016-046345.00] CKT 1 | 31.0413 | 0.2939 | 193.8926 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-004345.00] TO [G17-004XFMR134.500] CKT 1 | 31.0431 | 0.2942 | 194.1625 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-004345.00] TO [G17-004XFMR134.500] CKT 1 | 31.0431 | 0.2942 | 194.1625 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-004-TAP 345.00] TO [ELMCREEK7 345.00] CKT 1 | 31.0286 | 0.295 | 194.9808 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-004-TAP 345.00] TO [ELMCREEK7 345.00] CKT 1 | 31.0286 | 0.295 | 194.9808 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-018345.00] TO [THISTLE7 345.00] CKT 1 | 31.0529 | 0.2935 | 193.4588 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-018345.00] TO [THISTLE7 345.00] CKT 1 | 31.0529 | 0.2935 | 193.4588 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-018XFMR134.500] TO [G17-018-GSU134.500] CKT 1 | 31.0419 | 0.2942 | 194.1943 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-018XFMR134.500] TO [G17-018-GSU134.500] CKT 1 | 31.0419 | 0.2942 | 194.1943 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-018XFMR234.500] TO [G17-018-GSU234.500] CKT 1 | 31.0419 | 0.2942 | 194.1943 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-018XFMR234.500] TO [G17-018-GSU234.500] CKT 1 | 31.0419 | 0.2942 | 194.1943 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-068138.00] TO [EVANS N4 138.00] CKT 1 | 31.0456 | 0.294 | 193.9966 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-068138.00] TO [EVANS N4 138.00] CKT 1 | 31.0456 | 0.294 | 193.9966 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-068XFMR134.500] TO [G17-068-GSU134.500] CKT 1 | 31.0456 | 0.294 | 193.9899 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-068XFMR134.500] TO [G17-068-GSU134.500] CKT 1 | 31.0456 | 0.294 | 193.9899 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-082161.00] TO [ASB349 5 161.00] CKT 1 | 31.0265 | 0.2953 | 195.3381 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [GEN-2017-082161.00] TO [ASB349 5 161.00] CKT 1 | 31.0265 | 0.2953 | 195.3381 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-082XFMR134.500] TO [G17-082-GSU134.500] CKT 1 | 31.0266 | 0.2953 | 195.3139 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [G17-082XFMR134.500] TO [G17-082-GSU134.500] CKT 1 | 31.0266 | 0.2953 | 195.3139 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [ATCHSN 3 345.00] CKT 1 | 31.0212 | 0.2955 | 195.5193 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [ATCHSN 3 345.00] CKT 1 | 31.0212 | 0.2955 | 195.5193 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [COOPER1G 22.000] CKT 1 | 31.1014 | 0.2903 | 190.2669 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [COOPER1G 22.000] CKT 1 | 31.1014 | 0.2903 | 190.2669 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [MONOLITH 3 345.00] CKT 1 | 31.0294 | 0.295 | 194.9931 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [MONOLITH 3 345.00] CKT 1 | 31.0294 | 0.295 | 194.9931 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [COOPER 5 161.00] TO [COOPER T2 913.800] CKT 1 | 31.0308 | 0.2949 | 194.938 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [COOPER 5 161.00] TO [COOPER T2 913.800] CKT 1 | 31.0308 | 0.2949 | 194.938 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [COOPER 5 161.00] TO [COOPER T5 913.800] CKT 1 | 31.0308 | 0.2949 | 194.9386 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [COOPER 3 345.00] TO [COOPER 5 161.00] TO [COOPER T5 913.800] CKT 1 | 31.0308 | 0.2949 | 194.9386 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEBCTY1G 18.000] TO [NC1GA1X9 4.2000] TO [NC1GA1Y9 4.2000] CKT 1 | 31.0279 | 0.2951 | 195.0704 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEBCTY1G 18.000] TO [NC1GA1X9 4.2000] TO [NC1GA1Y9 4.2000] CKT 1 | 31.0279 | 0.2951 | 195.0704 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEBCTY1G 18.000] TO [NC1GA2X9 4.2000] TO [NC1GA2Y9 4.2000] CKT 1 | 31.0279 | 0.2951 | 195.0703 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEBCTY1G 18.000] TO [NC1GA2X9 4.2000] TO [NC1GA2Y9 4.2000] CKT 1 | 31.0279 | 0.2951 | 195.0703 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEBCTY2G 23.000] TO [NC2GA1X9 4.2000] TO [NC2GA1Y9 4.2000] CKT 1 | 31.0294 | 0.295 | 195.0052 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEBCTY2G 23.000] TO [NC2GA1X9 4.2000] TO [NC2GA1Y9 4.2000] CKT 1 | 31.0294 | 0.295 | 195.0052 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEBCTY2G 23.000] TO [NC2GA2X9 13.800] TO [NC2GA2Y9 13.800] CKT 1 | 31.0262 | 0.2952 | 195.2343 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [NEBCTY2G 23.000] TO [NC2GA2X9 13.800] TO [NC2GA2Y9 13.800] CKT 1 | 31.0262 | 0.2952 | 195.2343 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3456 3 345.00] TO [CBLUFFS3 345.00] CKT 1 | 31.0315 | 0.2949 | 194.8811 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3456 3 345.00] TO [CBLUFFS3 345.00] CKT 1 | 31.0315 | 0.2949 | 194.8811 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3456 3 345.00] TO [S3455 3 345.00] CKT 1 | 31.0307 | 0.2949 | 194.9413 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3456 3 345.00] TO [S3455 3 345.00] CKT 1 | 31.0307 | 0.2949 | 194.9413 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3456 3 345.00] TO [S3459 3 345.00] CKT 1 | 31.0304 | 0.295 | 194.964 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3456 3 345.00] TO [S3459 3 345.00] CKT 1 | 31.0304 | 0.295 | 194.964 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3456 3 345.00] TO [S1206 5 161.00] TO [S3456T49 13.800] CKT 1 | 31.0307 | 0.2949 | 194.9395 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3456 3 345.00] TO [S1206 5 161.00] TO [S3456T49 13.800] CKT 1 | 31.0307 | 0.2949 | 194.9395 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3458 3 345.00] TO [HOLT 7 345.00] CKT 1 | 31.0145 | 0.2953 | 195.2995 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3458 3 345.00] TO [HOLT 7 345.00] CKT 1 | 31.0145 | 0.2953 | 195.2995 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3740 3 345.00] TO [CASS 1G 15.000] CKT 1 | 31.0442 | 0.2941 | 194.0711 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3740 3 345.00] TO [CASS 1G 15.000] CKT 1 | 31.0442 | 0.2941 | 194.0711 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3740 3 345.00] TO [CASS 2G 15.000] CKT 1 | 31.0442 | 0.2941 | 194.0744 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3740 3 345.00] TO [CASS 2G 15.000] CKT 1 | 31.0442 | 0.2941 | 194.0744 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3740 3 345.00] TO [S3454 3 345.00] CKT 1 | 31.0303 | 0.295 | 194.9646 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3740 3 345.00] TO [S3454 3 345.00] CKT 1 | 31.0303 | 0.295 | 194.9646 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3740 3 345.00] TO [S3455 3 345.00] CKT 1 | 31.03 | 0.295 | 194.9871 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3740 3 345.00] TO [S3455 3 345.00] CKT 1 | 31.03 | 0.295 | 194.9871 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3740 3 345.00] TO [GEN-2018-033345.00] CKT 1 | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [S3740 3 345.00] TO [GEN-2018-033345.00] CKT 1 | 31.0306 | 0.2949 | 194.946 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [103&ROKEBY3 345.00] TO [MOORE 3 345.00] CKT 1 | 31.0303 | 0.295 | 194.9552 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [103&ROKEBY3 345.00] TO [MOORE 3 345.00] CKT 1 | 31.0303 | 0.295 | 194.9552 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [103&ROKEBY3 345.00] TO [WAGENER 3 345.00] CKT 1 | 31.0298 | 0.295 | 194.9975 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [103&ROKEBY3 345.00] TO [WAGENER 3 345.00] CKT 1 | 31.0298 | 0.295 | 194.9975 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7SPORTSMAN 345.00] TO [5SPORTSMAN 161.00] CKT 2 | 30.9158 | 0.2951 | 195.1045 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [7SPORTSMAN 345.00] TO [5SPORTSMAN 161.00] CKT 2 | 30.9158 | 0.2951 | 195.1045 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IDALIA 5 161.00] TO [2IDALIA 69.000] CKT 2 | 31.0306 | 0.2949 | 194.9491 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IDALIA 5 161.00] TO [2IDALIA 69.000] CKT 2 | 31.0306 | 0.2949 | 194.9491 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [TATONGA7 345.00] CKT 2 | 31.0109 | 0.2963 | 196.2893 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [TATONGA7 345.00] CKT 2 | 31.0109 | 0.2963 | 196.2893 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [G16-003-TAP 345.00] CKT 2 | 31.0209 | 0.295 | 194.9688 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WWRDEHV7 345.00] TO [G16-003-TAP 345.00] CKT 2 | 31.0209 | 0.295 | 194.9688 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DGRASSE7 345.00] TO [THISTLE7 345.00] CKT 2 | 30.9121 | 0.2992 | 199.2213 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [DGRASSE7 345.00] TO [THISTLE7 345.00] CKT 2 | 30.9121 | 0.2992 | 199.2213 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 2 | 30.9515 | 0.2927 | 192.6867 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 2 | 30.9515 | 0.2927 | 192.6867 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EVANS S4 138.00] TO [EVANS N4 138.00] CKT Z2 | 31.0204 | 0.2961 | 196.0652 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [EVANS S4 138.00] TO [EVANS N4 138.00] CKT Z2 | 31.0204 | 0.2961 | 196.0652 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [THISTLE7 345.00] CKT 2 | 31.0136 | 0.2944 | 194.4047 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [THISTLE7 345.00] CKT 2 | 31.0136 | 0.2944 | 194.4047 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HSNVL 5 161.00] TO [HSNVL 2 69.000] CKT 2 | 31.0312 | 0.2949 | 194.8951 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HSNVL 5 161.00] TO [HSNVL 2 69.000] CKT 2 | 31.0312 | 0.2949 | 194.8951 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [LEEDS 5 161.00] CKT 2 | 31.0241 | 0.295 | 195.0199 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [LEEDS 5 161.00] CKT 2 | 31.0241 | 0.295 | 195.0199 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHN5 161.00] CKT @2 | 31.0239 | 0.2953 | 195.3128 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHN5 161.00] CKT @2 | 31.0239 | 0.2953 | 195.3128 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [LENEXA 5 161.00] CKT 2 | 31.0237 | 0.2951 | 195.0982 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [CRAIG 5 161.00] TO [LENEXA 5 161.00] CKT 2 | 31.0237 | 0.2951 | 195.0982 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [STRANGR7 345.00] CKT 2 | 30.9782 | 0.2947 | 194.7063 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [IATAN 7 345.00] TO [STRANGR7 345.00] CKT 2 | 30.9782 | 0.2947 | 194.7063 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [BLUVLY-161 161.00] CKT 2 | 31.0296 | 0.295 | 194.952 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-032 | Neosho 345kV Substation | OPEN LINE FROM [BLUVLY 69.000] TO [BLUVLY-161 161.00] CKT 2 | 31.0296 | 0.295 | 194.952 | 154.74 | 175.5 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | GEN-2018-052 | Roadrunner 115kV Substation | OPEN LINE FROM [RDRNNER_TR1113.200] TO [RDRUNNER 7345.00] TO [RDRUNNER 3115.00] CKT 1 | 6.3261 | 13.1427 | 13042.7415 | 70 | 75 | PASS | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | GEN-2018-052 | Roadrunner 115kV Substation | OPEN LINE FROM [RDRNNER_TR1113.200] TO [RDRUNNER 7345.00] TO [RDRUNNER 3115.00] CKT 1 | 6.2445 | 13.1348 | 13034.8293 | 70 | 75 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | GEN-2018-055 | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | OPEN LINE FROM [L.E.S.-7 345.00] TO [G17-171-TAP 345.00] CKT 1 | 8.1551 | 2.7726 | 2672.6372 | 252 | 280 | PASS | PASS
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | GEN-2018-055 | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | OPEN LINE FROM [L.E.S.-7 345.00] TO [G17-171-TAP 345.00] CKT 1 | 8.0398 | 2.5805 | 2480.488 | 252 | 280 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | Base | 8.5371 | 34.4843 | 34384.2826 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [7FAIRPT 345.00] TO [ST JOE 7 345.00] CKT 1 | 8.5364 | 34.4707 | 34370.6674 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [7FAIRPT 345.00] TO [COOPER 3 345.00] CKT 1 | 8.537 | 34.4837 | 34383.7087 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5CLINTN 161.00] TO [5HOLDENB2 161.00] CKT 1 | 8.5368 | 34.4767 | 34376.6715 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5CLINTN 161.00] TO [2CLINTN 69.000] CKT 1 | 8.537 | 34.4838 | 34383.7976 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5CLINTN 161.00] TO [2CLINTN 69.000] CKT 3 | 8.537 | 34.4838 | 34383.796 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5CLINTN 161.00] TO [5OSCEOKCTP 161.00] CKT 1 | 8.5366 | 34.4685 | 34368.4781 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5CLINTN 161.00] TO [TRUMAN 5 161.00] CKT 1 | 8.5368 | 34.4802 | 34380.1627 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5CLINTN 161.00] TO [WINDSR 5 161.00] CKT 1 | 8.537 | 34.4854 | 34385.4082 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5CLINTN 161.00] TO [CLINTON5 161.00] CKT Z1 | 8.5371 | 34.4849 | 34384.8548 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5NEWMAD 161.00] TO [N MADRD5 161.00] CKT 1 | 8.5371 | 34.4845 | 34384.5211 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5NEWMAD 161.00] TO [SIKETAP5 161.00] CKT 1 | 8.537 | 34.4829 | 34382.8934 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [7BLACKBERRY 345.00] TO [7SPORTSMAN 345.00] CKT 1 | 8.526 | 34.4704 | 34370.4273 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [7BLACKBERRY 345.00] TO [7JASPER 345.00] CKT 1 | 8.5185 | 34.5262 | 34426.1734 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [7BLACKBERRY 345.00] TO [WOLFCRK7 345.00] CKT 1 | 8.5084 | 34.1855 | 34085.4824 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5MINER 1 161.00] TO [SIKESTN5 161.00] CKT 1 | 8.537 | 34.483 | 34383.0337 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [N MADRD5 161.00] TO [KENNETT5 161.00] CKT 1 | 8.5369 | 34.4804 | 34380.3776 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [N MADRD5 161.00] TO [N MADRD2 69.000] TO [NMA X1 1 13.800] CKT 1 | 8.5371 | 34.4843 | 34384.3443 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [N MADRD5 161.00] TO [N MADRD2 69.000] TO [NMA X2 1 13.800] CKT 1 | 8.5371 | 34.4843 | 34384.3271 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SIKETAP5 161.00] TO [SIKESTN5 161.00] CKT 1 | 8.537 | 34.4829 | 34382.893 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SIKESTN5 161.00] TO [SIKGEN 1 13.800] CKT 1 | 8.5374 | 34.4963 | 34396.3027 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SIKESTN5 161.00] TO [IDALIA 5 161.00] CKT 1 | 8.5371 | 34.4849 | 34384.9282 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SIKESTN5 161.00] TO [SIKESTN2 69.000] TO [SIK X1 1 13.800] CKT 1 | 8.5369 | 34.4797 | 34379.7193 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [DELAWAR1 13.800] TO [DELWARE4 138.00] TO [DELWARE7 345.00] CKT 1 | 8.5368 | 34.476 | 34376.0015 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [DELWARE7 345.00] TO [N.E.S.-7 345.00] CKT 1 | 8.523 | 34.4661 | 34366.102 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WWRDEHV7 345.00] TO [DGRASSE7 345.00] CKT 1 | 8.486 | 34.5373 | 34437.2746 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WWRDEHV7 345.00] TO [DGRASSE7 345.00] CKT 2 | 8.486 | 34.5368 | 34436.8411 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [DGRASSE7 345.00] TO [DGRASSE4 138.00] TO [DGRASSE1 13.800] CKT 1 | 8.5262 | 34.5184 | 34418.3831 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WALKMYR1 13.800] TO [WALKMYR2 69.000] TO [WALKMYR3 115.00] CKT 1 | 8.5369 | 34.4823 | 34382.3059 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WALKMYR3 115.00] TO [HUGOTON3 115.00] CKT 1 | 8.5364 | 34.4832 | 34383.1759 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WALKMYR3 115.00] TO [HARBNGR3 115.00] CKT 1 | 8.5366 | 34.4785 | 34378.5286 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SEWARD-3 115.00] TO [N-CIMRN3 115.00] CKT 1 | 8.5366 | 34.4822 | 34382.1537 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SPERVIL7 345.00] TO [CLARKCOUNTY7345.00] CKT 1 | 8.5248 | 34.4535 | 34353.5325 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NSES 2X1 13.200] TO [NEOSHO 4 138.00] TO [NEOSHOS2 69.000] CKT 1 | 8.5369 | 34.4834 | 34383.4318 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EEC GT1 13.800] TO [EVANS S4 138.00] CKT 1 | 8.537 | 34.4876 | 34387.5834 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EEC GT2 13.800] TO [EVANS S4 138.00] CKT 1 | 8.537 | 34.4873 | 34387.3353 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EEC GT3 18.000] TO [EVANS S4 138.00] CKT 1 | 8.537 | 34.4848 | 34384.7818 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EMPEC 7 345.00] TO [SWISVAL7 345.00] CKT 1 | 8.4798 | 34.4209 | 34320.9453 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EMPEC 7 345.00] TO [EXPEDITION7 345.00] CKT 1 | 8.0753 | 35.4544 | 35354.364 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [RENO 7 345.00] TO [WICHITA7 345.00] CKT 1 | 8.2424 | 34.692 | 34591.968 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUMMIT 7 345.00] TO [G17-004-TAP 345.00] CKT 1 | 8.5082 | 34.3968 | 34296.7681 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SWISVAL7 345.00] TO [SWISVAL6 230.00] TO [SWISV1X1 14.400] CKT 1 | 8.5368 | 34.4825 | 34382.5268 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SWISVAL7 345.00] TO [SWISVAL6 230.00] TO [SWISV2X2 14.400] CKT 2 | 8.5368 | 34.4826 | 34382.5675 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [87TH 7 345.00] TO [CRAIG 7 345.00] CKT 1 | 8.5359 | 34.4668 | 34366.774 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [G17-009-TAP 345.00] TO [GEN-2017-009345.00] CKT 1 | 8.5367 | 34.4645 | 34364.5372 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [G17-009-TAP 345.00] TO [CANEYRV7 345.00] CKT 1 | 8.3402 | 34.9148 | 34814.7756 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [KINGMAN7 345.00] TO [NINN1WF7 345.00] CKT 1 | 8.5411 | 34.6429 | 34542.8802 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [KINGMAN7 345.00] TO [K1 LV 1 34.500] TO [K1 WFTX1 13.800] CKT 1 | 8.5355 | 34.5608 | 34460.8057 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [KINGMAN7 345.00] TO [K2 LV 1 34.500] TO [K2 WFTX1 13.800] CKT 1 | 8.5358 | 34.5259 | 34425.8784 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BENTON 7 345.00] TO [WICHITA7 345.00] CKT 1 | 8.2807 | 33.9686 | 33868.6416 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BENTON 7 345.00] TO [WOLFCRK7 345.00] CKT 1 | 8.2955 | 34.8052 | 34705.2229 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WICHITA7 345.00] TO [VIOLA 7 345.00] CKT 1 | 8.4223 | 33.8397 | 33739.7416 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WICHITA7 345.00] TO [EXPEDITION7 345.00] CKT 1 | 8.0829 | 35.1334 | 35033.3544 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WOLFCRK7 345.00] TO [WAVERLY7 345.00] CKT 1 | 8.4809 | 34.6072 | 34507.1885 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [VIOLA 7 345.00] TO [VIOLA 4 138.00] TO [VIOLA1X1 13.800] CKT 1 | 8.5206 | 34.4512 | 34351.2312 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [VIOLA 7 345.00] TO [VIOLA 4 138.00] TO [SCJ1X1 13.800] CKT 2 | 8.5194 | 34.5161 | 34416.0888 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WAVERLY7 345.00] TO [LACYGNE7 345.00] CKT 1 | 8.4779 | 34.6056 | 34505.636 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NMANHT6 230.00] TO [ELMCREK6 230.00] CKT 1 | 8.5216 | 34.4988 | 34398.81 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LITCH 5 161.00] TO [FRANKLIN5 161.00] CKT 1 | 8.5362 | 34.4752 | 34375.1651 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LITCH 5 161.00] TO [LITCH S2 69.000] TO [LITCH1 1 13.200] CKT 1 | 8.537 | 34.4814 | 34381.4174 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LITCH 5 161.00] TO [LITCH N2 69.000] TO [LITCH2 1 13.200] CKT 1 | 8.537 | 34.4866 | 34386.563 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [MARMTNW5 161.00] TO [NEOSHO 5 161.00] CKT 1 | 8.5357 | 34.4963 | 34396.318 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEOSHO 5 161.00] TO [RIV4525 161.00] CKT 1 | 8.5281 | 34.5435 | 34443.513 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEOSHO 5 161.00] TO [NEOSHO 4 138.00] TO [NEOSH4 1 13.200] CKT 1 | 8.537 | 34.4842 | 34384.229 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEOSHO 5 161.00] TO [NEOSHOS4 138.00] TO [NEOSH5 1 13.200] CKT 1 | 8.5369 | 34.4842 | 34384.2062 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRESWLN4 138.00] TO [OXFORD 4 138.00] CKT 1 | 8.4864 | 34.4708 | 34370.783 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [TCROCK 4 138.00] TO [TIMBJCT4 138.00] CKT 1 | 8.5356 | 34.5249 | 34424.9466 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [TIMBJCT4 138.00] TO [TIMBJCT2 69.000] TO [TIMBJCT1 13.200] CKT 1 | 8.5348 | 34.4524 | 34352.4004 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [TIOGA 4 138.00] TO [ALTOONA4 138.00] CKT 1 | 8.5327 | 34.5018 | 34401.7592 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [OTTRCRK4 138.00] TO [ALTOONA4 138.00] CKT 1 | 8.4886 | 34.5571 | 34457.1015 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ALTOONA4 138.00] TO [TAYLOR 4 138.00] CKT 1 | 8.5335 | 34.496 | 34396.0417 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ALTOONA4 138.00] TO [ALTOO W2 69.000] TO [ALTOO1 1 13.200] CKT 1 | 8.5369 | 34.476 | 34376.0357 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ALTOONA4 138.00] TO [ALTOO E2 69.000] TO [ALTOO3 1 13.200] CKT 1 | 8.5369 | 34.4821 | 34382.1298 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEPARSN4 138.00] TO [NEOSHON4 138.00] CKT 1 | 8.5341 | 34.5028 | 34402.7707 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BENTLEY4 138.00] TO [SG12COL4 138.00] CKT 1 | 8.2305 | 34.3496 | 34249.6035 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEOSHOS4 138.00] TO [NEOSHO 4 138.00] CKT Z1 | 8.5366 | 34.4836 | 34383.6194 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEOSHO 4 138.00] TO [NEOSHON4 138.00] CKT Z1 | 8.5363 | 34.4945 | 34394.5233 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CHISHLM4 138.00] TO [MAIZE 4 138.00] CKT 1 | 7.7322 | 33.856 | 33756.0008 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CLEARWT4 138.00] TO [GILL 4 138.00] CKT 1 | 8.4619 | 34.4519 | 34351.8853 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CLEARWT4 138.00] TO [VIOLA 4 138.00] CKT 1 | 8.4603 | 34.5292 | 34429.2363 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EVANS S4 138.00] TO [LAKERDG4 138.00] CKT 1 | 8.1145 | 33.4378 | 33337.767 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EVANS S4 138.00] TO [45TH ST4 138.00] CKT 1 | 8.1122 | 33.6103 | 33510.3027 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [FARBER 4 138.00] TO [SC10BEL4 138.00] CKT 1 | 8.509 | 34.4622 | 34362.169 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GILL 4 138.00] TO [VIOLA 4 138.00] CKT 1 | 8.4621 | 34.4867 | 34386.7286 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [VIOLA 4 138.00] TO [MILAN_GOAB 138.00] CKT 1 | 8.5326 | 34.4937 | 34393.7253 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [VIOLA 4 138.00] TO [CONWAY 138.00] CKT 1 | 8.5266 | 34.5011 | 34401.1083 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [AEC 3 115.00] TO [EABILEN3 115.00] CKT 1 | 8.5328 | 34.5868 | 34486.7764 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [AEC 3 115.00] TO [AEC E1 34.500] CKT 2 | 8.5363 | 34.4776 | 34377.6055 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [AEC 3 115.00] TO [AEC W1 34.500] CKT 1 | 8.5353 | 34.4731 | 34373.0501 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NORTHST3 115.00] TO [NORTHVW3 115.00] CKT 1 | 8.5368 | 34.5046 | 34404.5947 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NORTHVW3 115.00] TO [SUMMIT 3 115.00] CKT 1 | 8.5359 | 34.4905 | 34390.4864 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LITCH N2 69.000] TO [LITCH S2 69.000] CKT Z1 | 8.5371 | 34.4855 | 34385.493 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [MRWYP16 230.00] TO [ELMCREK6 230.00] CKT 1 | 8.5382 | 34.5463 | 34446.3271 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [FLATRDG4 138.00] TO [THISTLE4 138.00] CKT 1 | 8.5371 | 34.4715 | 34371.4834 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ELMCREK6 230.00] TO [CONCRD6 230.00] CKT 1 | 8.5276 | 34.4234 | 34323.4175 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAYNE3 115.00] TO [NLIB 3 115.00] CKT 1 | 8.537 | 34.4821 | 34382.1455 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [KISMET 3 115.00] TO [CMRIVTP3 115.00] CKT 1 | 8.5332 | 34.4808 | 34380.7912 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CMRIVTP3 115.00] TO [E-LIBER3 115.00] CKT 1 | 8.5368 | 34.481 | 34380.9757 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CIM-PLT1 13.800] TO [CIM-PLT 13.800] CKT Z1 | 8.5367 | 34.4768 | 34376.8224 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [N-CIMRN3 115.00] TO [N-CMRN 1 34.500] TO [N-CMRN-T 13.800] CKT 1 | 8.537 | 34.4838 | 34383.8111 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [TRANSFORMER 345.00] CKT 1 | 8.5393 | 34.5735 | 34473.4546 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [GEN-2011-008345.00] CKT 1 | 8.5421 | 34.5819 | 34481.9227 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [G16-046-TAP 345.00] CKT 1 | 8.5179 | 34.4708 | 34370.81 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [MULLNCR7 345.00] TO [MC REAC1 345.00] CKT Z1 | 8.5372 | 34.4845 | 34384.5473 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [MULLNCR7 345.00] TO [MC REAC2 345.00] CKT Z1 | 8.5372 | 34.4845 | 34384.5473 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [MULLNCR7 345.00] TO [MC REAC3 345.00] CKT Z1 | 8.5371 | 34.4848 | 34384.8393 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [MULLNCR7 345.00] TO [KETCHEM7 345.00] CKT 1 | 8.5369 | 34.4871 | 34387.0733 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [PECULR 7 345.00] TO [STILWEL7 345.00] CKT 1 | 8.532 | 34.4635 | 34363.4775 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ST JOE 7 345.00] TO [EASTOWN7 345.00] CKT 1 | 8.536 | 34.4589 | 34358.9139 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ST JOE 7 345.00] TO [COOPER 3 345.00] CKT 1 | 8.5367 | 34.4784 | 34378.3925 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ST JOE 7 345.00] TO [ST JOE 5 161.00] TO [STJOE 1T 13.800] CKT 22 | 8.537 | 34.484 | 34384.0364 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ST JOE 7 345.00] TO [ST JOE 5 161.00] TO [STJOE 2T 13.800] CKT 33 | 8.537 | 34.4841 | 34384.0569 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ARCHIE 5 161.00] TO [HSNVL 5 161.00] CKT 1 | 8.5369 | 34.4828 | 34382.8251 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ARCHIE 5 161.00] TO [ADRIAN 5 161.00] CKT 1 | 8.5363 | 34.4601 | 34360.1181 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ARCHIE 5 161.00] TO [S.HARP 5 161.00] CKT 1 | 8.5367 | 34.4784 | 34378.3858 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S.HARP 5 161.00] TO [STILWEL5 161.00] CKT 1 | 8.537 | 34.4832 | 34383.1568 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EASTOWN7 345.00] TO [IATAN 7 345.00] CKT 1 | 8.5348 | 34.424 | 34323.9576 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ROCKCK_TR1_113.200] TO [ROCKCK7 345.00] TO [ROCKCK_T1_1 34.500] CKT 1 | 8.5374 | 34.4922 | 34392.1526 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ROCKCK_TR2_113.200] TO [ROCKCK7 345.00] TO [ROCKCK_T2_1 34.500] CKT 1 | 8.5376 | 34.4945 | 34394.5261 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ROCKCK7 345.00] TO [OUTLAW 345.00] CKT 1 | 8.5376 | 34.5032 | 34403.2474 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LAC G1 1 22.000] TO [LACYGNE7 345.00] CKT 1 | 8.5322 | 34.7374 | 34637.3658 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LAC G2 1 24.000] TO [LACYGNE7 345.00] CKT 1 | 8.5346 | 34.7456 | 34645.5774 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WGARDNR5 161.00] TO [CEDRCRK5 161.00] CKT 1 | 8.5368 | 34.4812 | 34381.2435 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WGARDNR5 161.00] TO [CEDARNL5 161.00] CKT 1 | 8.5369 | 34.4802 | 34380.1968 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WGARDNR5 161.00] TO [PLSTVAL5 161.00] CKT 1 | 8.5369 | 34.4798 | 34379.8043 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WGARDNR5 161.00] TO [BULLCRK5 161.00] CKT 1 | 8.5384 | 34.6041 | 34504.1292 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WGARDNR5 161.00] TO [BNSF 5 161.00] CKT 1 | 8.5368 | 34.4778 | 34377.7856 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WGARDNR5 161.00] TO [WGARDNR1 34.500] CKT 7 | 8.5367 | 34.4762 | 34376.1813 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [STILWEL7 345.00] TO [LACYGNE7 345.00] CKT 1 | 8.534 | 34.5069 | 34406.9161 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [STILWEL7 345.00] TO [STILWEL5 161.00] TO [STIL T11 13.800] CKT 11 | 8.5365 | 34.4805 | 34380.4506 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [STILWEL7 345.00] TO [STILWEL5 161.00] TO [STIL T22 13.800] CKT 22 | 8.5364 | 34.4801 | 34380.1496 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [STILWEL5 161.00] TO [HICKMAN5 161.00] CKT 1 | 8.5368 | 34.486 | 34385.9983 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [STILWEL5 161.00] TO [ANTIOCH5 161.00] CKT 1 | 8.5372 | 34.4907 | 34390.6754 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [STILWEL5 161.00] TO [REDEL 5 161.00] CKT 1 | 8.5367 | 34.4844 | 34384.422 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [STILWEL5 161.00] TO [BUCYRUS5 161.00] CKT 1 | 8.537 | 34.4805 | 34380.5346 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [STILWEL5 161.00] TO [LACKMAN5 161.00] CKT 1 | 8.5371 | 34.4854 | 34385.3753 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTH 7 345.00] TO [NASHUA 7 345.00] CKT 1 | 8.5364 | 34.4637 | 34363.7257 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTHS5 161.00] TO [SUB M-161 161.00] CKT 1 | 8.537 | 34.482 | 34381.9963 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRAIG 7 345.00] TO [CRAIG 5 161.00] TO [CRAI T11 13.800] CKT 11 | 8.5365 | 34.4773 | 34377.3238 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRAIG 7 345.00] TO [CRAIG 5 161.00] TO [CRAI T22 13.800] CKT 22 | 8.5365 | 34.4774 | 34377.4256 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRAIG 7 345.00] TO [CRAIG 5 161.00] TO [CRAI T33 13.800] CKT 33 | 8.5366 | 34.4806 | 34380.6154 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRAIG 5 161.00] TO [CEDRCRK5 161.00] CKT 1 | 8.537 | 34.4841 | 34384.1359 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NASHUA 7 345.00] TO [IATAN 7 345.00] CKT 1 | 8.5355 | 34.438 | 34338.0397 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NASHUA 7 345.00] TO [NASHUA-5 161.00] TO [NASH T11 13.800] CKT 11 | 8.5371 | 34.4831 | 34383.1121 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NASHUA 7 345.00] TO [NASHUA-5 161.00] TO [NASH T12 13.800] CKT 12 | 8.537 | 34.4831 | 34383.1391 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LACYGNE7 345.00] TO [LACYGNE11_7 345.00] CKT 1 | 8.5364 | 34.4709 | 34370.9142 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LACYGNE7 345.00] TO [LACYGNE22_7 345.00] CKT 1 | 8.5371 | 34.4842 | 34384.2446 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LACYGNE7 345.00] TO [LAC3_STAR7 345.00] CKT H | 8.5371 | 34.4843 | 34384.2615 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LACYGNE7 345.00] TO [LAC8_STAR7 345.00] CKT H | 8.5371 | 34.4843 | 34384.2779 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LACYGNE7 345.00] TO [LACYGNE2 69.000] TO [LACYGN7_TER16.9000] CKT 7 | 8.5368 | 34.4792 | 34379.1606 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BLUMILS5 161.00] TO [ECKLES-161 161.00] CKT 1 | 8.5371 | 34.4843 | 34384.2527 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BLUMILS5 161.00] TO [BLUEMLS2 69.000] TO [BLUMILS_TER112.500] CKT 3 | 8.5369 | 34.481 | 34381.017 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LAKCTYJ2 69.000] TO [BLUVLY 69.000] CKT 1 | 8.5371 | 34.4842 | 34384.2379 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CJ 366 5 161.00] TO [FIR417 5 161.00] CKT 1 | 8.5368 | 34.4838 | 34383.8157 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CAR395 5 161.00] TO [PUR421 5 161.00] CKT 1 | 8.5367 | 34.4826 | 34382.5928 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB K 69.000] TO [BLUVLY 69.000] CKT 1 | 8.5371 | 34.4844 | 34384.431 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB H 69.000] TO [BLUVLY 69.000] CKT 1 | 8.5371 | 34.4843 | 34384.276 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB H 69.000] TO [SUB M 69.000] CKT 1 | 8.5371 | 34.4843 | 34384.3165 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BLUVLY 13.8 13.800] TO [BLUVLY 69.000] CKT 1 | 8.5371 | 34.4843 | 34384.2829 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BLUVLY 69.000] TO [SUB B 69.000] CKT 1 | 8.5371 | 34.4843 | 34384.307 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BLUVLY 69.000] TO [SUB J 69.000] CKT 1 | 8.5371 | 34.4843 | 34384.2944 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BLUVLY 69.000] TO [SUB P 69.000] CKT 1 | 8.5371 | 34.4844 | 34384.3748 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB B 69.000] TO [SUB J 69.000] CKT 1 | 8.537 | 34.4843 | 34384.3409 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB J 69.000] TO [SUB M 69.000] CKT 1 | 8.5371 | 34.4844 | 34384.3914 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB M-161 161.00] TO [SUB M 69.000] CKT 1 | 8.537 | 34.4843 | 34384.2577 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GEN-2017-004345.00] TO [G17-004-TAP 345.00] CKT 1 | 8.5387 | 34.515 | 34414.9576 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GEN-2017-018345.00] TO [G17-018XFMR134.500] CKT 1 | 8.538 | 34.5092 | 34409.2053 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GEN-2017-018345.00] TO [G17-018XFMR234.500] CKT 1 | 8.538 | 34.5092 | 34409.2053 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GEN-2017-068138.00] TO [G17-068XFMR134.500] CKT 1 | 8.5417 | 34.8519 | 34751.9366 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GEN-2017-082161.00] TO [G17-082XFMR134.500] CKT 1 | 8.537 | 34.4828 | 34382.8447 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [COOPER 3 345.00] TO [S3458 3 345.00] CKT 1 | 8.5369 | 34.4819 | 34381.8877 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEBCTY1G 18.000] TO [S3458 3 345.00] CKT 1 | 8.543 | 34.6841 | 34584.1016 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEBCTY2G 23.000] TO [S3458 3 345.00] CKT 1 | 8.5433 | 34.6935 | 34593.5071 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S3456 3 345.00] TO [S3458 3 345.00] CKT 1 | 8.5368 | 34.4766 | 34376.5975 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S3458 3 345.00] TO [S3740 3 345.00] CKT 1 | 8.5369 | 34.4787 | 34378.6616 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S3458 3 345.00] TO [103&ROKEBY3 345.00] CKT 1 | 8.5369 | 34.478 | 34378.0136 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [7FAIRPT 345.00] TO [5FAIRPTXF3 161.00] CKT 3 | 8.5366 | 34.4728 | 34372.805 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5CLINTN 161.00] TO [G17-108-TAP 161.00] CKT 1 | 8.5358 | 34.4501 | 34350.1213 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5NEWMAD 161.00] TO [5GIBSON 161.00] CKT 1 | 8.5371 | 34.4841 | 34384.1454 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M0 161.00] CKT 1 | 8.5371 | 34.4843 | 34384.2829 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M1 161.00] CKT 1 | 8.5369 | 34.48 | 34379.9766 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M2 161.00] CKT 1 | 8.5369 | 34.48 | 34379.9754 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M3 161.00] CKT 1 | 8.5369 | 34.48 | 34379.9766 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5NEWMAD 161.00] TO [5NEWMADCP 161.00] CKT Z1 | 8.5371 | 34.4843 | 34384.2858 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5NEWMAD 161.00] TO [5NEWMADXF12 161.00] CKT Z1 | 8.537 | 34.4836 | 34383.6364 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5NEWMAD 161.00] TO [5NEWMADGSU1 161.00] CKT 1 | 8.5378 | 34.5081 | 34408.0529 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5NEWMAD 161.00] TO [5NMDSU100HS 161.00] CKT 1 | 8.5371 | 34.4843 | 34384.2829 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5NEWMAD 161.00] TO [5NMDSU200HS 161.00] CKT 1 | 8.5371 | 34.4843 | 34384.2829 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5NEWMAD 161.00] TO [5PORTAGEVLE 161.00] CKT 1 | 8.537 | 34.4824 | 34382.3986 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5NEWMAD 161.00] TO [5TIPTONVL TN161.00] CKT 1 | 8.5368 | 34.4748 | 34374.8098 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5HOLDENB2 161.00] TO [1HOLDNG11 13.800] CKT 11 | 8.538 | 34.5196 | 34419.59 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5HOLDENB2 161.00] TO [1HOLDNG12 13.800] CKT 12 | 8.5371 | 34.4842 | 34384.2495 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5HOLDENB2 161.00] TO [2HOLDEN 69.000] CKT 1 | 8.5371 | 34.4846 | 34384.5657 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5HOLDENB2 161.00] TO [5HOLDENB1 161.00] CKT Z1 | 8.5371 | 34.4865 | 34386.4625 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [2CLINTN 69.000] TO [2LINCLN 69.000] CKT 1 | 8.537 | 34.4838 | 34383.8008 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [2CLINTN 69.000] TO [2GAINES 69.000] CKT 1 | 8.537 | 34.4823 | 34382.2868 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [2CLINTN 69.000] TO [2LEETON 69.000] CKT 1 | 8.537 | 34.4842 | 34384.1682 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [2CLINTN 69.000] TO [2PIPER 69.000] CKT 1 | 8.537 | 34.4843 | 34384.2589 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [2CLINTN 69.000] TO [2CLINTNLD 69.000] CKT 1 | 8.537 | 34.482 | 34382.0411 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [7BLACKBERRY 345.00] TO [NEOSHO 7 345.00] CKT 1 | 8.529 | 34.5388 | 34438.8405 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [7SPORTSMAN 345.00] TO [5SPORTSMAN 161.00] CKT 1 | 8.5368 | 34.4864 | 34386.4016 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [7SPORTSMAN 345.00] TO [5SPORTSMAN 161.00] CKT 2 | 8.5368 | 34.4864 | 34386.401 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [7SPORTSMAN 345.00] TO [GRDA1 7 345.00] CKT 1 | 8.5348 | 34.4401 | 34340.1157 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [7JASPER 345.00] TO [7MORGAN 345.00] CKT 1 | 8.5233 | 34.5035 | 34403.5347 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [7JASPER 345.00] TO [5JASPER 161.00] CKT 1 | 8.5357 | 34.4962 | 34396.1704 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5OSCEOKCTP 161.00] TO [5OSCEOLTP 161.00] CKT 1 | 8.5365 | 34.4726 | 34372.5808 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5OSCEOKCTP 161.00] TO [5OSCEOKC 161.00] CKT 1 | 8.537 | 34.483 | 34383.0247 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5MINER 1 161.00] TO [5CHARLSTN 161.00] CKT 1 | 8.537 | 34.4832 | 34383.1696 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5MINER 1 161.00] TO [5BULLION 161.00] CKT 1 | 8.537 | 34.4818 | 34381.784 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5MINER 1 161.00] TO [5MINER 2 161.00] CKT Z | 8.537 | 34.4833 | 34383.321 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [N MADRD5 161.00] TO [G17-202-TAP 161.00] CKT 1 | 8.537 | 34.4815 | 34381.4923 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [N MADRD2 69.000] TO [2STJUDEW 69.000] CKT 1 | 8.5371 | 34.4844 | 34384.4376 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [N MADRD2 69.000] TO [2LILBRN 69.000] CKT 1 | 8.5371 | 34.4845 | 34384.4626 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [N MADRD2 69.000] TO [MALDEN 2 69.000] CKT 1 | 8.5371 | 34.4839 | 34383.9148 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [KENNETT5 161.00] TO [PARAGLD5 161.00] CKT 1 | 8.537 | 34.481 | 34381.0224 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [KENNETT5 161.00] TO [KENNETT2 69.000] TO [KEN X1 1 13.800] CKT 1 | 8.5371 | 34.4843 | 34384.3227 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [KENNETT5 161.00] TO [KENNETT2 69.000] TO [KEN X2 1 13.800] CKT 1 | 8.5371 | 34.4843 | 34384.324 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SIKETAP5 161.00] TO [SIKE SW5 161.00] CKT 1 | 8.5371 | 34.4843 | 34384.2829 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SIKESTN5 161.00] TO [G17-202-TAP 161.00] CKT 1 | 8.537 | 34.4833 | 34383.2761 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [IDALIA 5 161.00] TO [5ESSEX 161.00] CKT 1 | 8.537 | 34.4834 | 34383.4125 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [IDALIA 5 161.00] TO [2IDALIA 69.000] CKT 1 | 8.5371 | 34.4843 | 34384.3221 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [IDALIA 5 161.00] TO [2IDALIA 69.000] CKT 2 | 8.5371 | 34.4843 | 34384.3153 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [IDALIA 5 161.00] TO [ASHRVL5 161.00] CKT 1 | 8.537 | 34.4835 | 34383.4921 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [TRUMAN 5 161.00] TO [5LOSTVALY 161.00] CKT 1 | 8.5363 | 34.4585 | 34358.4507 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [TRUMAN 5 161.00] TO [TRU123 1 13.800] CKT 1 | 8.5376 | 34.5033 | 34403.3476 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [TRUMAN 5 161.00] TO [TRU456 1 13.800] CKT 1 | 8.5376 | 34.5034 | 34403.3613 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [DELWARE4 138.00] TO [FARML 4 138.00] CKT 1 | 8.5368 | 34.4747 | 34374.7293 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [DELWARE7 345.00] TO [NEOSHO 7 345.00] CKT 1 | 8.5207 | 34.4169 | 34316.8761 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [N.E.S.-7 345.00] TO [ONETA--7 345.00] CKT 1 | 8.5325 | 34.4723 | 34372.3401 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [N.E.S.-7 345.00] TO [T.NO.--7 345.00] CKT 1 | 8.5359 | 34.4456 | 34345.6366 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [N.E.S.-7 345.00] TO [NES3-1 22.000] CKT 1 | 8.5306 | 34.3959 | 34295.8751 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WWRDEHV7 345.00] TO [TATONGA7 345.00] CKT 1 | 8.5306 | 34.448 | 34348.0417 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WWRDEHV7 345.00] TO [TATONGA7 345.00] CKT 2 | 8.5305 | 34.4482 | 34348.1591 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WWRDEHV7 345.00] TO [G07621119-20345.00] CKT 1 | 8.5372 | 34.4642 | 34364.1724 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WWRDEHV7 345.00] TO [GUTHRIE7 345.00] CKT 1 | 8.5371 | 34.4776 | 34377.6183 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WWRDEHV7 345.00] TO [BECKHAM7 345.00] CKT 1 | 8.5109 | 34.4952 | 34395.1794 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WWRDEHV7 345.00] TO [G16-003-TAP 345.00] CKT 1 | 8.5354 | 34.5158 | 34415.8444 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WWRDEHV7 345.00] TO [G16-003-TAP 345.00] CKT 2 | 8.5354 | 34.5159 | 34415.8755 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WWRDEHV7 345.00] TO [WWRDEHV4 138.00] TO [WWDEHV31 13.800] CKT 1 | 8.536 | 34.4982 | 34398.2493 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WWRDEHV7 345.00] TO [WWRDEHV4 138.00] TO [WWDEHV21 13.800] CKT 2 | 8.5359 | 34.5071 | 34407.1124 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [DGRASSE7 345.00] TO [THISTLE7 345.00] CKT 1 | 8.4675 | 34.5473 | 34447.2848 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [DGRASSE7 345.00] TO [THISTLE7 345.00] CKT 2 | 8.4675 | 34.5474 | 34447.4363 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [DGRASSE4 138.00] TO [KNOBHIL4 138.00] CKT 1 | 8.5368 | 34.4761 | 34376.1494 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [DGRASSE4 138.00] TO [ROSEVLY4 138.00] CKT 1 | 8.5368 | 34.4759 | 34375.9434 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [DGRASSE4 138.00] TO [MOORLND4 138.00] CKT 1 | 8.5236 | 34.4882 | 34388.1597 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WALKMYR2 69.000] TO [NORTH6T2 69.000] CKT 1 | 8.5369 | 34.4837 | 34383.7164 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WALKMYR2 69.000] TO [WOODS 2 69.000] CKT 1 | 8.537 | 34.4839 | 34383.9451 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WALKMYR3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 8.5372 | 34.4791 | 34379.1468 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SEWARD-3 115.00] TO [HASKELL3 115.00] CKT 1 | 8.5366 | 34.4815 | 34381.4703 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SEWARD-3 115.00] TO [CMSSWRD2 69.000] TO [SEWARD 1 13.800] CKT 1 | 8.537 | 34.4834 | 34383.4384 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SPERVIL7 345.00] TO [POSTROCK7 345.00] CKT 1 | 8.5243 | 34.4674 | 34367.3952 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SPERVIL7 345.00] TO [BUCKNER7 345.00] CKT 1 | 8.484 | 34.5953 | 34495.2818 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SPERVIL7 345.00] TO [IRONWOOD7 345.00] CKT 1 | 8.5264 | 34.4685 | 34368.5196 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SPERVIL7 345.00] TO [SPRVL 3 115.00] TO [SPRVL-T 13.800] CKT 1 | 8.5373 | 34.4871 | 34387.0578 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SPERVIL7 345.00] TO [SPEARVL6 230.00] TO [SPERTER1 13.800] CKT 1 | 8.5386 | 34.4819 | 34381.8541 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HUGOTON3 115.00] TO [GRANTTP3 115.00] CKT 1 | 8.5364 | 34.4776 | 34377.63 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HUGOTON3 115.00] TO [ABBK 2 115.00] CKT 1 | 8.5369 | 34.4834 | 34383.3557 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HUGOTON3 115.00] TO [HUGOTON2 69.000] TO [HUGOTON1 13.800] CKT 1 | 8.5367 | 34.4827 | 34382.7306 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HARBNGR3 115.00] TO [HARBNGR7 345.00] TO [HARBNGR-T 13.800] CKT 1 | 8.5366 | 34.4786 | 34378.5505 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EEC GT1 13.800] TO [DG TIE 1 4.1600] CKT 1 | 8.5371 | 34.4843 | 34384.2829 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EEC GT2 13.800] TO [EEC DG 1 4.1600] CKT 1 | 8.5371 | 34.4843 | 34384.2831 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC121 13.800] CKT 1 | 8.5282 | 34.5519 | 34451.9009 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC341 13.800] CKT 1 | 8.5282 | 34.552 | 34451.9569 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC5 1 18.000] CKT 1 | 8.5168 | 34.6125 | 34512.5082 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC6 1 18.000] CKT 1 | 8.5176 | 34.6429 | 34542.8918 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC7 1 18.000] CKT 1 | 8.5371 | 34.4842 | 34384.2021 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EMPEC 7 345.00] TO [LANG 7 345.00] CKT 1 | 8.5335 | 34.4139 | 34313.894 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EMPEC 7 345.00] TO [MORRIS 7 345.00] CKT 1 | 8.5259 | 34.51 | 34409.9874 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EMPEC 7 345.00] TO [READWF 7 345.00] CKT 1 | 8.5386 | 34.5415 | 34441.524 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [RENO 7 345.00] TO [G16-111-TAP 345.00] CKT 1 | 8.2943 | 34.6924 | 34592.3866 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [RENO 7 345.00] TO [RENO 3 115.00] TO [RENO 1X1 14.400] CKT 1 | 8.5358 | 34.5578 | 34457.8334 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [RENO 7 345.00] TO [RENO 3 115.00] TO [RENO 2X1 14.400] CKT 1 | 8.5357 | 34.5528 | 34452.8274 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUMMIT 7 345.00] TO [GEARY 7 345.00] CKT 1 | 8.4404 | 34.7259 | 34625.9191 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUMMIT 7 345.00] TO [G16-111-TAP 345.00] CKT 1 | 8.2961 | 34.91 | 34810.0318 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUMMIT 7 345.00] TO [SUMMIT 6 230.00] TO [SUMMIT 1 14.400] CKT 1 | 8.5338 | 34.5228 | 34422.7728 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SWISVAL7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 8.5046 | 34.4118 | 34311.8265 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [87TH 7 345.00] TO [STRANGR7 345.00] CKT 1 | 8.5358 | 34.4628 | 34362.7599 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [87TH 7 345.00] TO [87TH 3 115.00] TO [87TH 1X1 13.800] CKT 1 | 8.5372 | 34.4886 | 34388.6239 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [G17-009-TAP 345.00] TO [NEOSHO 7 345.00] CKT 1 | 8.336 | 35.2335 | 35133.5465 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GEN-2017-009345.00] TO [G17-009XFMR134.500] CKT 1 | 8.537 | 34.4795 | 34379.4748 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GEN-2017-009345.00] TO [G17-009XFMR234.500] CKT 1 | 8.537 | 34.4798 | 34379.7849 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CANEYRV7 345.00] TO [CANEYWF7 345.00] CKT 1 | 8.5376 | 34.4959 | 34395.8511 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CANEYRV7 345.00] TO [LATHAMS7 345.00] CKT 1 | 8.3422 | 34.9222 | 34822.1795 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [KINGMAN7 345.00] TO [BUFFALO7 345.00] CKT 1 | 8.5388 | 34.4378 | 34337.7984 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NINN1WF7 345.00] TO [PRATTWF7 345.00] CKT 1 | 8.5441 | 34.6848 | 34584.7976 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NINN1WF7 345.00] TO [N1 LV 1 34.500] TO [N1 WFTX1 13.800] CKT 1 | 8.5341 | 34.545 | 34445.0179 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BENTON 7 345.00] TO [ROSEHIL7 345.00] CKT 1 | 8.2833 | 34.4536 | 34353.5918 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BENTON 7 345.00] TO [BENTON 4 138.00] TO [BENTN1 1 13.800] CKT 1 | 8.49 | 34.4935 | 34393.5488 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BENTON 7 345.00] TO [BENTON 4 138.00] TO [BENTN2 1 13.800] CKT 1 | 8.4937 | 34.4873 | 34387.2775 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 1 | 8.4976 | 34.6967 | 34596.6531 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 2 | 8.4976 | 34.6967 | 34596.6531 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WICHITA7 345.00] TO [EVANS N4 138.00] TO [WICH11 1 13.800] CKT 1 | 7.1453 | 35.7964 | 35696.4458 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WICHITA7 345.00] TO [EVANS N4 138.00] TO [WICH12 1 13.800] CKT 1 | 6.8823 | 36.311 | 36211.0209 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WOLFCRK7 345.00] TO [WCGS U1 25.000] CKT 1 | 8.4218 | 35.959 | 35858.9733 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WOLFCRK7 345.00] TO [ROSEHIL7 345.00] CKT 1 | 8.3902 | 34.6004 | 34500.406 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WOLFCRK7 345.00] TO [WOLFCRK2 69.000] TO [WOLFCRK1 17.000] CKT 1 | 8.5344 | 34.4426 | 34342.5685 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [VIOLA 7 345.00] TO [RENFROW7 345.00] CKT 1 | 8.0458 | 34.8776 | 34777.5892 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [VIOLA 7 345.00] TO [G16-153-TAP 345.00] CKT 1 | 8.5425 | 34.3275 | 34227.5443 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WAVERLY7 345.00] TO [WAVERTX7 345.00] CKT 1 | 8.5392 | 34.5018 | 34401.7666 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EXPEDITION7 345.00] TO [GEN-2014-001345.00] CKT 1 | 8.5397 | 34.5039 | 34403.8685 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [N345 1 1 13.800] TO [NEOSHO 7 345.00] TO [NEOSHO 4 138.00] CKT 1 | 8.5361 | 34.4767 | 34376.6733 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [N345 2 1 13.800] TO [NEOSHO 7 345.00] TO [NEOSHO 5 161.00] CKT 1 | 8.5342 | 34.499 | 34399.0254 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SWISVAL6 230.00] TO [AUBURN 6 230.00] CKT 1 | 8.5364 | 34.4749 | 34374.9405 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SWISVAL6 230.00] TO [LAWHILL6 230.00] CKT 1 | 8.5297 | 34.4946 | 34394.5816 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SWISVAL6 230.00] TO [TECHILL6 230.00] CKT 1 | 8.5356 | 34.4733 | 34373.2843 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SWISVAL6 230.00] TO [MORRIS 6 230.00] CKT 1 | 8.5297 | 34.4878 | 34387.7907 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NMANHT6 230.00] TO [EMANHAT6 230.00] CKT 1 | 8.5295 | 34.5089 | 34408.9088 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NMANHT6 230.00] TO [NMANHT3 115.00] TO [NMANHX1 14.400] CKT 1 | 8.5367 | 34.4823 | 34382.2815 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LITCH 5 161.00] TO [ASB349 5 161.00] CKT 1 | 8.5355 | 34.4801 | 34380.1446 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [MARMTNW5 161.00] TO [MARMTNE5 161.00] CKT Z1 | 8.5353 | 34.49 | 34389.9702 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [MARMTNW5 161.00] TO [MARMATN2 69.000] TO [MARMATN1 13.200] CKT 1 | 8.5364 | 34.4756 | 34375.5806 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [FRANKLIN5 161.00] TO [G17-005-TAP 161.00] CKT 1 | 8.5358 | 34.4572 | 34357.1706 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [FRANKLIN5 161.00] TO [FRANKLIN2 69.000] TO [FRANKLIN1 12.470] CKT 1 | 8.537 | 34.4848 | 34384.7733 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRESWLN4 138.00] TO [MIDLTNT4 138.00] CKT 1 | 8.4819 | 34.6947 | 34594.6742 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRESWLN4 138.00] TO [SLATECRK4 138.00] CKT 1 | 8.5201 | 34.496 | 34395.9709 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRESWLN4 138.00] TO [CRESWLN2 69.000] TO [CRESW1 1 13.200] CKT 1 | 8.5368 | 34.478 | 34377.9935 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRESWLN4 138.00] TO [CRESWLS2 69.000] TO [CRESW2 1 13.200] CKT 1 | 8.5372 | 34.4867 | 34386.6533 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [OXFORD 4 138.00] TO [SUMNER 4 138.00] CKT 1 | 8.4859 | 34.4731 | 34373.052 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [TIMBJCT4 138.00] TO [SUMNER 4 138.00] CKT 1 | 8.5356 | 34.4431 | 34343.0896 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [TIOGA 4 138.00] TO [TIOGA 2 69.000] TO [TIOGA 1 13.200] CKT 1 | 8.5328 | 34.5038 | 34403.8271 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [OTTRCRK4 138.00] TO [BUTLER 4 138.00] CKT 1 | 8.4671 | 34.5624 | 34462.3815 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [OTTRCRK4 138.00] TO [OTTRCRK3 115.00] TO [OTTRX1 1 13.800] CKT 1 | 8.531 | 34.4692 | 34369.1625 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ALTOONA4 138.00] TO [G17-022-TAP 138.00] CKT 1 | 8.5329 | 34.4627 | 34362.6716 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEPARSN4 138.00] TO [G17-022-TAP 138.00] CKT 1 | 8.5341 | 34.4871 | 34387.0514 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [TAYLOR 4 138.00] TO [MONTGOM4 138.00] CKT 1 | 8.5336 | 34.4967 | 34396.6754 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BENTLEY4 138.00] TO [HALSTD 4 138.00] CKT 1 | 8.2317 | 34.4055 | 34305.5424 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BENTLEY4 138.00] TO [WWUPLNT4 138.00] CKT 1 | 8.5352 | 34.4691 | 34369.0926 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEOSHOS4 138.00] TO [TV1MNDV4 138.00] CKT 1 | 8.5363 | 34.4644 | 34364.4022 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEOSHON4 138.00] TO [NEOSHON2 69.000] TO [NEC U3 12.000] CKT 1 | 8.537 | 34.4844 | 34384.3985 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CHISHLM4 138.00] TO [PARKCTY4 138.00] CKT 1 | 8.2014 | 34.6926 | 34592.6235 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CHISHLM4 138.00] TO [17TH 4 138.00] CKT 1 | 8.4684 | 34.2216 | 34121.6433 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CHISHLM4 138.00] TO [CHISHLM2 69.000] TO [CHISOLM1 13.200] CKT 1 | 8.5325 | 34.2863 | 34186.3057 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EVANS S4 138.00] TO [EVANS N4 138.00] CKT Z1 | 8.5359 | 34.4811 | 34381.0853 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EVANS S4 138.00] TO [EVANS N4 138.00] CKT Z2 | 8.5359 | 34.4811 | 34381.0853 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [FARBER 4 138.00] TO [ELPASOE4 138.00] CKT 1 | 8.5073 | 34.5066 | 34406.5852 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GILL 4 138.00] TO [GILL W 4 138.00] CKT Z1 | 8.5363 | 34.4845 | 34384.4769 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GILL 4 138.00] TO [GILL S 4 138.00] CKT Z1 | 8.5371 | 34.4839 | 34383.9266 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LAKERDG4 138.00] TO [HOOVERN4 138.00] CKT 1 | 8.1258 | 33.697 | 33597.0307 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [MAIZE 4 138.00] TO [EVANS N4 138.00] CKT 1 | 7.7211 | 33.7385 | 33638.4703 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SC10BEL4 138.00] TO [SUMNER 4 138.00] CKT 1 | 8.5095 | 34.4492 | 34349.1775 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SG12COL4 138.00] TO [EVANS N4 138.00] CKT 1 | 8.2297 | 34.3366 | 34236.5914 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [45TH ST4 138.00] TO [COWSKIN4 138.00] CKT 1 | 8.1131 | 33.6652 | 33565.25 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [VIOLA 4 138.00] TO [SUMNER 4 138.00] CKT 1 | 8.5332 | 34.4479 | 34347.8653 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [AEC 3 115.00] TO [G17-120-TAP 115.00] CKT 1 | 8.5307 | 34.5565 | 34456.4584 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EABILEN3 115.00] TO [CHAPMAN3 115.00] CKT 1 | 8.5334 | 34.5912 | 34491.1551 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NORTHST3 115.00] TO [SALINA 3 115.00] CKT 1 | 8.536 | 34.455 | 34354.9519 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NORTHVW3 115.00] TO [G17-120-TAP 115.00] CKT 1 | 8.5315 | 34.4311 | 34331.1077 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUMMIT 3 115.00] TO [MENTOR 3 115.00] CKT 1 | 8.5372 | 34.5202 | 34420.1976 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUMMIT 3 115.00] TO [SO GATE3 115.00] CKT 1 | 8.5369 | 34.4727 | 34372.7329 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUMMIT 3 115.00] TO [SUMMIT 6 230.00] TO [SUMIT2 1 13.800] CKT 1 | 8.5372 | 34.4828 | 34382.8083 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUMMIT 3 115.00] TO [SUMMIT 6 230.00] TO [SUMIT3 1 13.800] CKT 1 | 8.5372 | 34.482 | 34381.9601 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [TIMBJCT2 69.000] TO [AKRON 2 69.000] CKT 1 | 8.5361 | 34.5013 | 34401.3294 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [TIMBJCT2 69.000] TO [UDALL 2 69.000] CKT 1 | 8.5357 | 34.4955 | 34395.4981 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [TIMBJCT2 69.000] TO [WINFLD 2 69.000] CKT 1 | 8.5332 | 34.4267 | 34326.748 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ALTOO E2 69.000] TO [NEODJCT2 69.000] CKT 1 | 8.5371 | 34.4902 | 34390.2177 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ALTOO E2 69.000] TO [RA5HIPR2 69.000] CKT Z1 | 8.5371 | 34.4858 | 34385.7836 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ALTOO W2 69.000] TO [STUDBKR2 69.000] CKT 1 | 8.5372 | 34.492 | 34392.0365 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LITCH N2 69.000] TO [AQUARS 2 69.000] CKT 1 | 8.5371 | 34.4842 | 34384.2117 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LITCH N2 69.000] TO [PITNAC 2 69.000] CKT 1 | 8.5371 | 34.4843 | 34384.2812 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LITCH S2 69.000] TO [ROUSE 2 69.000] CKT 1 | 8.5371 | 34.4841 | 34384.1468 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LITCH S2 69.000] TO [SOPITT 2 69.000] CKT 1 | 8.5366 | 34.48 | 34380.0317 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEOSHOS2 69.000] TO [BAKER 2 69.000] CKT 1 | 8.5367 | 34.488 | 34388.0175 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEOSHOS2 69.000] TO [ORDNJCT2 69.000] CKT 1 | 8.537 | 34.4828 | 34382.836 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEOSHOS2 69.000] TO [CRAWFOR2 69.000] CKT 1 | 8.5365 | 34.4857 | 34385.6876 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEOSHOS2 69.000] TO [NEOSHON2 69.000] CKT Z1 | 8.537 | 34.4843 | 34384.3348 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [K1 LV 1 34.500] TO [K1 CLCT1 34.500] CKT 1 | 8.5352 | 34.5608 | 34460.8327 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [K2 LV 1 34.500] TO [K2 CLCT1 34.500] CKT 1 | 8.5361 | 34.5258 | 34425.771 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [MILAN_GOAB 138.00] TO [CLDWELL4 138.00] CKT 1 | 8.5328 | 34.4864 | 34386.4395 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [MILAN_GOAB 138.00] TO [MILAN 4 138.00] CKT 1 | 8.5366 | 34.491 | 34390.9975 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CONWAY 138.00] TO [MILANTP4 138.00] CKT 1 | 8.5268 | 34.5002 | 34400.1821 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [MRWYP16 230.00] TO [MRWYP26 230.00] CKT 1 | 8.5379 | 34.5114 | 34411.3747 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [MRWYP16 230.00] TO [MRWYG11 34.500] TO [MRWYP1T1 13.800] CKT 1 | 8.5378 | 34.5217 | 34421.6762 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [FLATRDG4 138.00] TO [FLATRWD4 138.00] CKT 1 | 8.5228 | 34.4956 | 34395.5832 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [FLATRDG4 138.00] TO [HARPER 4 138.00] CKT 1 | 8.5143 | 34.5197 | 34419.6684 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [FLATRDG4 138.00] TO [BARBER 4 138.00] CKT 1 | 8.5302 | 34.4717 | 34371.6952 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ELMCREK6 230.00] TO [ELMCREEK7 345.00] TO [ELMCREEK1 13.800] CKT 1 | 8.5067 | 34.5515 | 34451.5219 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAYNE3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 8.537 | 34.4814 | 34381.3779 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [KISMET 3 115.00] TO [CUDAHY 3 115.00] CKT 1 | 8.533 | 34.4788 | 34378.7708 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CMRIVTP3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 8.5367 | 34.4864 | 34386.3758 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CONCRD6 230.00] TO [CONCORD3 115.00] TO [CONCOD-T 13.800] CKT 1 | 8.5276 | 34.4275 | 34327.5459 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [E-LIBER3 115.00] TO [TXPHSF 3115.00] CKT 1 | 8.5369 | 34.4843 | 34384.3466 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [E-LIBER3 115.00] TO [E-PINE 3 115.00] CKT 1 | 8.5368 | 34.4822 | 34382.2412 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [E-LIBER3 115.00] TO [NATBEEF3 115.00] CKT 1 | 8.5371 | 34.4844 | 34384.433 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [E-LIBER3 115.00] TO [E-LIBER1 34.500] TO [ELIB-T 2.4000] CKT 1 | 8.5368 | 34.4827 | 34382.7103 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NLIB 3 115.00] TO [W-LIBER3 115.00] CKT 1 | 8.5367 | 34.4809 | 34380.8867 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NLIB 3 115.00] TO [NATBEEF3 115.00] CKT 1 | 8.537 | 34.4837 | 34383.7429 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NLIB 3 115.00] TO [NLIB 1 34.500] TO [N-LIB-T 13.800] CKT 1 | 8.5367 | 34.4825 | 34382.5216 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [N-CIMRN3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 8.5365 | 34.483 | 34383.0119 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CIM-PLT 13.800] TO [CIM-PLT3 115.00] CKT 1 | 8.5357 | 34.4733 | 34373.3106 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [THISTLE7 345.00] CKT 1 | 8.506 | 34.5155 | 34415.5115 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [THISTLE7 345.00] CKT 2 | 8.506 | 34.5155 | 34415.5115 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [THISTLE T1 13.800] TO [THISTLE7 345.00] TO [THISTLE4 138.00] CKT 1 | 8.5371 | 34.4723 | 34372.3379 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [TRANSFORMER 345.00] TO [SUB34.5KVB 34.500] TO [TERTIARYBUS 19.900] CKT 1 | 8.5393 | 34.5735 | 34473.4604 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GEN-2011-008345.00] TO [G-2011-008-1345.00] CKT 1 | 8.5382 | 34.5328 | 34432.8214 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GEN-2011-008345.00] TO [G-2011-008-2345.00] CKT 1 | 8.5378 | 34.5093 | 34409.3025 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GEN-2011-008345.00] TO [G-2011-008-3345.00] CKT 1 | 8.5407 | 34.5138 | 34413.8205 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [MULLNCR7 345.00] TO [HOLT 7 345.00] CKT 1 | 8.5369 | 34.4856 | 34385.5635 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [PECULR 7 345.00] TO [PHILL 7 345.00] CKT 1 | 8.5332 | 34.4758 | 34375.8322 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [PECULR 7 345.00] TO [PECULR 5 161.00] TO [PECULRT 13.800] CKT 11 | 8.5367 | 34.4793 | 34379.3267 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ST JOE 7 345.00] TO [G17-183-TAP 345.00] CKT 1 | 8.537 | 34.4835 | 34383.4662 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ARCHIE 5 161.00] TO [G17-108-TAP 161.00] CKT 1 | 8.537 | 34.4827 | 34382.6687 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WINDSR 5 161.00] TO [5SEDALA 161.00] CKT 1 | 8.537 | 34.4853 | 34385.3106 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HSNVL 5 161.00] TO [5SHARSNV 161.00] CKT 1 | 8.5369 | 34.482 | 34382.0405 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HSNVL 5 161.00] TO [PHILL 5 161.00] CKT 1 | 8.5367 | 34.476 | 34375.9955 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HSNVL 5 161.00] TO [HSNVL 2 69.000] CKT 1 | 8.537 | 34.4845 | 34384.5498 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HSNVL 5 161.00] TO [HSNVL 2 69.000] CKT 2 | 8.537 | 34.4846 | 34384.5525 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ADRIAN 5 161.00] TO [5BUTLER 161.00] CKT 1 | 8.5364 | 34.4635 | 34363.4672 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CLINTON5 161.00] TO [CLNTN N2 69.000] CKT 1 | 8.5371 | 34.4842 | 34384.2334 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CLINTON5 161.00] TO [CLNTN S2 69.000] CKT 2 | 8.5371 | 34.4842 | 34384.227 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ST JOE 5 161.00] TO [ST JOE_CAP5 161.00] CKT R | 8.537 | 34.4826 | 34382.641 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ST JOE 5 161.00] TO [COOK 5 161.00] CKT 1 | 8.537 | 34.4847 | 34384.6868 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ST JOE 5 161.00] TO [WOODBIN5 161.00] CKT 1 | 8.5371 | 34.4846 | 34384.6119 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ST JOE 5 161.00] TO [AVENUECTY 5 161.00] CKT 1 | 8.5368 | 34.4809 | 34380.9491 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP#1 13.800] CKT 1 | 8.5371 | 34.4843 | 34384.2799 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP#2 13.800] CKT 1 | 8.5371 | 34.4843 | 34384.2799 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP#3 13.800] CKT 1 | 8.5371 | 34.4843 | 34384.2799 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP 2 69.000] CKT 1 | 8.537 | 34.4838 | 34383.8208 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S.HARP 5 161.00] TO [PECULRS5 161.00] CKT 1 | 8.5369 | 34.4826 | 34382.5827 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EASTOWN7 345.00] TO [EASTOWN5 161.00] TO [EASTOWN1 13.800] CKT 11 | 8.5368 | 34.4813 | 34381.2934 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [KETCHEM7 345.00] TO [SIBLEY 7 345.00] CKT 1 | 8.537 | 34.488 | 34387.9853 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [KETCHEM7 345.00] TO [OSBORN7 345.00] CKT 1 | 8.5379 | 34.5132 | 34413.1924 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ROCKCK7 345.00] TO [HOLT 7 345.00] CKT 1 | 8.5382 | 34.5216 | 34421.6026 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ROCKCK_T1_1 34.500] TO [ROCKCK_P1_1 34.500] CKT 1 | 8.5373 | 34.4926 | 34392.63 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ROCKCK_T2_1 34.500] TO [ROCKCK_P2_1 34.500] CKT 1 | 8.5374 | 34.495 | 34394.9991 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HOLT_REACT7 345.00] TO [HOLT 7 345.00] CKT Z1 | 8.5371 | 34.4845 | 34384.5201 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [OUTLAW 345.00] TO [OUTLAW_T2_1 34.500] TO [OUTLAW_TR2_113.800] CKT 1 | 8.5374 | 34.4955 | 34395.5315 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [OUTLAW 345.00] TO [OUTLAW_T1_1 34.500] TO [OUTLAW_TR1_113.800] CKT 1 | 8.5373 | 34.4921 | 34392.1166 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WGARDNR5 161.00] TO [W.GRDNR7 345.00] TO [WGAR T11 13.800] CKT 11 | 8.534 | 34.4835 | 34383.4802 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [STILWEL7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 8.5341 | 34.4507 | 34350.7324 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [STILWEL5 161.00] TO [G17-108-TAP 161.00] CKT 1 | 8.5368 | 34.4799 | 34379.8585 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTH 7 345.00] TO [SIBLEY 7 345.00] CKT 1 | 8.5369 | 34.4821 | 34382.0504 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTH 7 345.00] TO [HAWTHN5 161.00] TO [HAWT T20 13.800] CKT 20 | 8.5371 | 34.4853 | 34385.2675 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTH 7 345.00] TO [HAWTHN5 161.00] TO [HAWT T22 13.800] CKT 22 | 8.5368 | 34.4849 | 34384.8942 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTHS5 161.00] TO [HAW G9 1 13.800] CKT 1 | 8.5381 | 34.5261 | 34426.0523 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTHS5 161.00] TO [LEEDS 5 161.00] CKT 1 | 8.537 | 34.4849 | 34384.9008 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTHS5 161.00] TO [LEEDS 5 161.00] CKT 2 | 8.537 | 34.4849 | 34384.8626 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTH_B2_1 13.200] CKT 1 | 8.5367 | 34.4748 | 34374.8304 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTHS5 161.00] TO [BRMGHAM5 161.00] CKT 1 | 8.5369 | 34.4796 | 34379.5654 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHS_G65 161.00] CKT Z1 | 8.5381 | 34.524 | 34423.9645 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHS_XF5 161.00] CKT Z2 | 8.537 | 34.4841 | 34384.0624 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHN5 161.00] CKT @1 | 8.5371 | 34.4842 | 34384.2439 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHN5 161.00] CKT @2 | 8.5371 | 34.4842 | 34384.2439 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRAIG 7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 8.5323 | 34.4844 | 34384.3828 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRAIG 5 161.00] TO [CRAIG_CAP 5 161.00] CKT R | 8.537 | 34.4822 | 34382.2314 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRAIG 5 161.00] TO [PFLUMM 5 161.00] CKT 1 | 8.5367 | 34.4806 | 34380.6496 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRAIG 5 161.00] TO [LENEXA 5 161.00] CKT 1 | 8.5369 | 34.4834 | 34383.4414 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRAIG 5 161.00] TO [LENEXA 5 161.00] CKT 2 | 8.537 | 34.4838 | 34383.7715 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRAIG 5 161.00] TO [COLLEGE5 161.00] CKT 1 | 8.537 | 34.4821 | 34382.1198 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NASHUA 7 345.00] TO [G17-183-TAP 345.00] CKT 1 | 8.5371 | 34.4865 | 34386.5028 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LACYGNE7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 8.5377 | 34.5208 | 34420.7914 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LACYGNE7 345.00] TO [G17-209-TAP 345.00] CKT 1 | 8.5261 | 34.3747 | 34274.7461 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [IATAN 7 345.00] TO [STRANGR7 345.00] CKT 1 | 8.5354 | 34.485 | 34384.9595 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [IATAN 7 345.00] TO [STRANGR7 345.00] CKT 2 | 8.5356 | 34.4847 | 34384.6865 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [IATAN 7 345.00] TO [IAT G1 1 24.000] CKT 1 | 8.5438 | 34.7667 | 34666.7132 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [IATAN 7 345.00] TO [IAT G2 1 24.500] CKT 1 | 8.5438 | 34.7726 | 34672.5961 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [IATAN 7 345.00] TO [IATAN5 161.00] TO [IATAN 11 14.400] CKT 11 | 8.5368 | 34.4765 | 34376.4939 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HICKMAN5 161.00] TO [STHTOWN5 161.00] CKT 1 | 8.5368 | 34.4856 | 34385.6294 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BLUMILS5 161.00] TO [BLUVLY-161 161.00] CKT 1 | 8.537 | 34.4838 | 34383.7811 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NASHUA-5 161.00] TO [NASHUA 5 161.00] CKT Z1 | 8.537 | 34.4833 | 34383.255 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NASHUA-5 161.00] TO [RNRIDGE5 161.00] CKT 1 | 8.5371 | 34.4857 | 34385.7334 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NASHUA-5 161.00] TO [SHOLCRK5 161.00] CKT 1 | 8.537 | 34.4833 | 34383.3239 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CEDRCRK5 161.00] TO [SHWNMSN5 161.00] CKT 1 | 8.5369 | 34.4833 | 34383.264 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ANTIOCH5 161.00] TO [OXFORD 5 161.00] CKT 1 | 8.5372 | 34.4894 | 34389.4 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [REDEL 5 161.00] TO [MARTCIT5 161.00] CKT 1 | 8.5367 | 34.4844 | 34384.3884 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BUCYRUS5 161.00] TO [NLOUISB5 161.00] CKT 1 | 8.5368 | 34.4785 | 34378.5304 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BUCYRUS5 161.00] TO [WAGSTAF5 161.00] CKT 1 | 8.537 | 34.4835 | 34383.5289 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [PLSTVAL5 161.00] TO [SEOTTWA5 161.00] CKT 1 | 8.5368 | 34.4767 | 34376.6749 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [PLSTVAL5 161.00] TO [ASG-2018-010161.00] CKT 1 | 8.5375 | 34.4987 | 34398.7114 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [PLSTVAL5 161.00] TO [PLSTVAL1 34.500] TO [PLSTVL2_TER17.6210] CKT 2 | 8.5369 | 34.4803 | 34380.2989 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LAKCTYJ2 69.000] TO [LAKCTY 2 69.000] CKT 1 | 8.5371 | 34.4843 | 34384.3478 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 1 13.800] CKT 1 | 8.5375 | 34.5156 | 34415.6201 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 2 13.800] CKT 1 | 8.5375 | 34.5157 | 34415.7347 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 3 13.800] CKT 1 | 8.5375 | 34.5153 | 34415.2933 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 4 13.800] CKT 1 | 8.5375 | 34.5157 | 34415.7253 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LACKMAN5 161.00] TO [SPRGHL 5 161.00] CKT 1 | 8.5371 | 34.485 | 34384.9662 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BNSF 5 161.00] TO [MOONLT 5 161.00] CKT 1 | 8.5369 | 34.4782 | 34378.2196 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WGARDNR1 34.500] TO [BALDWINCTY1 34.500] CKT 1 | 8.5371 | 34.4874 | 34387.3945 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LACYGNE11_7 345.00] TO [LAC11_AQC1 13.800] TO [LAC11_TER1 13.800] CKT 11 | 8.5364 | 34.4709 | 34370.9363 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LACYGNE22_7 345.00] TO [LAC22_AQC1 13.800] TO [LAC22_TER1 13.800] CKT 22 | 8.5371 | 34.4843 | 34384.2668 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LACYGNE2 69.000] TO [LAC_LAKE_2 69.000] CKT 1 | 8.5369 | 34.4791 | 34379.1237 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LAC3_STAR7 345.00] TO [LAC3_X1 6.9000] CKT X | 8.5371 | 34.4843 | 34384.2829 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LAC3_STAR7 345.00] TO [LAC3_Y1 6.9000] CKT Y | 8.5371 | 34.4843 | 34384.2829 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LAC3_STAR7 345.00] TO [LAC3_Z1 3.9800] CKT Z | 8.5371 | 34.4843 | 34384.2829 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LAC8_STAR7 345.00] TO [LAC8_X1 6.9000] CKT X | 8.5371 | 34.4843 | 34384.2829 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LAC8_STAR7 345.00] TO [LAC8_Y1 6.9000] CKT Y | 8.5371 | 34.4843 | 34384.2829 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LAC8_STAR7 345.00] TO [LAC8_Z1 4.0000] CKT Z | 8.5371 | 34.4843 | 34384.2829 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [RIV4525 161.00] TO [ORO110 5 161.00] CKT 1 | 8.5371 | 34.4884 | 34388.3757 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [RIV4525 161.00] TO [STL439 5 161.00] CKT 1 | 8.5364 | 34.4892 | 34389.2064 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [RIV4525 161.00] TO [RIV452T 5 161.00] CKT 1 | 8.5356 | 34.4721 | 34372.1058 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [RIV4525 161.00] TO [BAX488 5 161.00] CKT 1 | 8.5367 | 34.4759 | 34375.9189 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [RIV4525 161.00] TO [RIV167 2 69.000] TO [RIV452 1 12.500] CKT 1 | 8.537 | 34.4835 | 34383.5177 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CJ 366 5 161.00] TO [ASB349 5 161.00] CKT 1 | 8.5368 | 34.4829 | 34382.916 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CAR395 5 161.00] TO [CARTHAG5 161.00] CKT 1 | 8.5367 | 34.4831 | 34383.1113 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [FIR417 5 161.00] TO [ORO110 5 161.00] CKT 1 | 8.5369 | 34.4846 | 34384.5529 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [PUR421 5 161.00] TO [ASB349 5 161.00] CKT 1 | 8.5366 | 34.4823 | 34382.2789 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [A1G349 1 13.800] TO [ASB349 5 161.00] CKT 1 | 8.5371 | 34.4851 | 34385.0803 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [A2G349 1 13.800] TO [ASB349 5 161.00] CKT 1 | 8.5371 | 34.4843 | 34384.2829 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB K 69.000] TO [SUB R 69.000] CKT 1 | 8.5371 | 34.4843 | 34384.2729 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB H 69.000] TO [COURTNY2 69.000] CKT 1 | 8.5371 | 34.4843 | 34384.2747 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB H 69.000] TO [SUGRCK_TP_E269.000] CKT 1 | 8.5371 | 34.4843 | 34384.2701 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB H 69.000] TO [SUB H-13B1 13.800] CKT H1 | 8.537 | 34.4841 | 34384.067 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB H 69.000] TO [SUB H-13B2 13.800] CKT H2 | 8.5371 | 34.4856 | 34385.6193 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BLUVLY 69.000] TO [BLUVLY-161 161.00] CKT 1 | 8.537 | 34.4844 | 34384.4454 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BLUVLY 69.000] TO [BLUVLY-161 161.00] CKT 2 | 8.537 | 34.4845 | 34384.4574 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ECKLES-161 161.00] TO [5LEVASY 161.00] CKT 1 | 8.5371 | 34.4843 | 34384.2699 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ECKLES-161 161.00] TO [5MOCITYB1 161.00] CKT 1 | 8.5371 | 34.4846 | 34384.6387 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ECKLES-161 161.00] TO [SIBLEYPL 161.00] CKT 1 | 8.537 | 34.4841 | 34384.1235 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB J 69.000] TO [SUB J-13B1 13.800] CKT J1 | 8.5371 | 34.4853 | 34385.3132 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB J 69.000] TO [SUB J-13B2 13.800] CKT J2 | 8.5369 | 34.4811 | 34381.1154 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB M-161 161.00] TO [BLUVLY-161 161.00] CKT 1 | 8.537 | 34.483 | 34382.992 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB M 69.000] TO [SHRNKRD 69.000] CKT 1 | 8.5371 | 34.4843 | 34384.3238 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB P 69.000] TO [SUB I 69.000] CKT 1 | 8.5371 | 34.4843 | 34384.2632 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [G16-046-TAP 345.00] TO [IRONWOOD7 345.00] CKT 1 | 8.5283 | 34.4732 | 34373.2395 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [G16-046-TAP 345.00] TO [GEN-2016-046345.00] CKT 1 | 8.5191 | 34.5258 | 34425.8179 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GEN-2017-004345.00] TO [G17-004XFMR134.500] CKT 1 | 8.5387 | 34.5221 | 34422.0506 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [G17-004-TAP 345.00] TO [ELMCREEK7 345.00] CKT 1 | 8.5085 | 34.4548 | 34354.8393 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GEN-2017-018345.00] TO [THISTLE7 345.00] CKT 1 | 8.5389 | 34.5291 | 34429.1287 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [G17-018XFMR134.500] TO [G17-018-GSU134.500] CKT 1 | 8.538 | 34.5092 | 34409.2053 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [G17-018XFMR234.500] TO [G17-018-GSU234.500] CKT 1 | 8.538 | 34.5092 | 34409.2053 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GEN-2017-068138.00] TO [EVANS N4 138.00] CKT 1 | 8.5425 | 34.821 | 34721.0303 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [G17-068XFMR134.500] TO [G17-068-GSU134.500] CKT 1 | 8.5417 | 34.8519 | 34751.9347 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GEN-2017-082161.00] TO [ASB349 5 161.00] CKT 1 | 8.537 | 34.4827 | 34382.7275 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [G17-082XFMR134.500] TO [G17-082-GSU134.500] CKT 1 | 8.537 | 34.4828 | 34382.8422 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [COOPER 3 345.00] TO [ATCHSN 3 345.00] CKT 1 | 8.5364 | 34.4658 | 34365.7743 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [COOPER 3 345.00] TO [COOPER1G 22.000] CKT 1 | 8.545 | 34.7552 | 34655.1904 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [COOPER 3 345.00] TO [MONOLITH 3 345.00] CKT 1 | 8.5368 | 34.4716 | 34371.6022 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [COOPER 3 345.00] TO [COOPER 5 161.00] TO [COOPER T2 913.800] CKT 1 | 8.5371 | 34.4849 | 34384.9373 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [COOPER 3 345.00] TO [COOPER 5 161.00] TO [COOPER T5 913.800] CKT 1 | 8.5371 | 34.4849 | 34384.8925 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEBCTY1G 18.000] TO [NC1GA1X9 4.2000] TO [NC1GA1Y9 4.2000] CKT 1 | 8.5367 | 34.4777 | 34377.6556 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEBCTY1G 18.000] TO [NC1GA2X9 4.2000] TO [NC1GA2Y9 4.2000] CKT 1 | 8.5367 | 34.4777 | 34377.655 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEBCTY2G 23.000] TO [NC2GA1X9 4.2000] TO [NC2GA1Y9 4.2000] CKT 1 | 8.5369 | 34.4811 | 34381.1337 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEBCTY2G 23.000] TO [NC2GA2X9 13.800] TO [NC2GA2Y9 13.800] CKT 1 | 8.5366 | 34.4673 | 34367.2717 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S3456 3 345.00] TO [CBLUFFS3 345.00] CKT 1 | 8.5372 | 34.4883 | 34388.3139 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S3456 3 345.00] TO [S3455 3 345.00] CKT 1 | 8.5371 | 34.4843 | 34384.2902 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S3456 3 345.00] TO [S3459 3 345.00] CKT 1 | 8.537 | 34.4834 | 34383.4291 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S3456 3 345.00] TO [S1206 5 161.00] TO [S3456T49 13.800] CKT 1 | 8.5371 | 34.4848 | 34384.8169 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S3458 3 345.00] TO [HOLT 7 345.00] CKT 1 | 8.5367 | 34.48 | 34380.0294 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S3740 3 345.00] TO [CASS 1G 15.000] CKT 1 | 8.5386 | 34.5355 | 34435.5329 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S3740 3 345.00] TO [CASS 2G 15.000] CKT 1 | 8.5386 | 34.5353 | 34435.3404 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S3740 3 345.00] TO [S3454 3 345.00] CKT 1 | 8.537 | 34.4833 | 34383.2576 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S3740 3 345.00] TO [S3455 3 345.00] CKT 1 | 8.537 | 34.483 | 34383.035 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S3740 3 345.00] TO [GEN-2018-033345.00] CKT 1 | 8.5371 | 34.4843 | 34384.2758 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [103&ROKEBY3 345.00] TO [MOORE 3 345.00] CKT 1 | 8.5369 | 34.4832 | 34383.1527 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [103&ROKEBY3 345.00] TO [WAGENER 3 345.00] CKT 1 | 8.537 | 34.4832 | 34383.1575 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [7SPORTSMAN 345.00] TO [5SPORTSMAN 161.00] CKT 2 | 8.5362 | 34.4966 | 34396.5739 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [IDALIA 5 161.00] TO [2IDALIA 69.000] CKT 2 | 8.5371 | 34.4845 | 34384.5367 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WWRDEHV7 345.00] TO [TATONGA7 345.00] CKT 2 | 8.5045 | 34.3799 | 34279.9085 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WWRDEHV7 345.00] TO [G16-003-TAP 345.00] CKT 2 | 8.5165 | 34.6374 | 34537.3944 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [DGRASSE7 345.00] TO [THISTLE7 345.00] CKT 2 | 8.197 | 34.666 | 34566.0381 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 2 | 7.9001 | 36.9878 | 36887.7968 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EVANS S4 138.00] TO [EVANS N4 138.00] CKT Z2 | 7.3766 | 32.2338 | 32133.8167 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [THISTLE7 345.00] CKT 2 | 8.4064 | 34.7786 | 34678.5579 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HSNVL 5 161.00] TO [HSNVL 2 69.000] CKT 2 | 8.5371 | 34.4856 | 34385.5922 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTHS5 161.00] TO [LEEDS 5 161.00] CKT 2 | 8.537 | 34.487 | 34387.0202 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHN5 161.00] CKT @2 | 8.5369 | 34.4787 | 34378.6887 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRAIG 5 161.00] TO [LENEXA 5 161.00] CKT 2 | 8.5364 | 34.4798 | 34379.8036 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [IATAN 7 345.00] TO [STRANGR7 345.00] CKT 2 | 8.5269 | 34.4917 | 34391.6805 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25SP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BLUVLY 69.000] TO [BLUVLY-161 161.00] CKT 2 | 8.5371 | 34.4853 | 34385.3449 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | Base | 8.2332 | 32.8693 | 32769.2974 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [7FAIRPT 345.00] TO [ST JOE 7 345.00] CKT 1 | 8.2325 | 32.8684 | 32768.3704 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [7FAIRPT 345.00] TO [COOPER 3 345.00] CKT 1 | 8.2327 | 32.8667 | 32766.6759 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5CLINTN 161.00] TO [5HOLDENB2 161.00] CKT 1 | 8.2329 | 32.8605 | 32760.4879 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5CLINTN 161.00] TO [2CLINTN 69.000] CKT 1 | 8.2332 | 32.8689 | 32768.9113 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5CLINTN 161.00] TO [2CLINTN 69.000] CKT 3 | 8.2332 | 32.8689 | 32768.9097 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5CLINTN 161.00] TO [5OSCEOKCTP 161.00] CKT 1 | 8.2328 | 32.8565 | 32756.5419 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5CLINTN 161.00] TO [TRUMAN 5 161.00] CKT 1 | 8.2328 | 32.8627 | 32762.7283 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5CLINTN 161.00] TO [WINDSR 5 161.00] CKT 1 | 8.2331 | 32.8704 | 32770.3511 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5CLINTN 161.00] TO [CLINTON5 161.00] CKT Z1 | 8.2331 | 32.8694 | 32769.3853 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5NEWMAD 161.00] TO [N MADRD5 161.00] CKT 1 | 8.2332 | 32.8696 | 32769.6147 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5NEWMAD 161.00] TO [SIKETAP5 161.00] CKT 1 | 8.2332 | 32.8682 | 32768.1747 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [7BLACKBERRY 345.00] TO [7SPORTSMAN 345.00] CKT 1 | 8.2209 | 32.8599 | 32759.8893 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [7BLACKBERRY 345.00] TO [7JASPER 345.00] CKT 1 | 8.2128 | 32.8804 | 32780.4325 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [7BLACKBERRY 345.00] TO [WOLFCRK7 345.00] CKT 1 | 8.201 | 32.4942 | 32394.1935 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5MINER 1 161.00] TO [SIKESTN5 161.00] CKT 1 | 8.2332 | 32.8677 | 32767.6927 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [N MADRD5 161.00] TO [KENNETT5 161.00] CKT 1 | 8.2331 | 32.8664 | 32766.435 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [N MADRD5 161.00] TO [N MADRD2 69.000] TO [NMA X1 1 13.800] CKT 1 | 8.2332 | 32.8693 | 32769.3474 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [N MADRD5 161.00] TO [N MADRD2 69.000] TO [NMA X2 1 13.800] CKT 1 | 8.2332 | 32.8693 | 32769.3355 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SIKETAP5 161.00] TO [SIKESTN5 161.00] CKT 1 | 8.2332 | 32.8682 | 32768.1728 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SIKESTN5 161.00] TO [SIKGEN 1 13.800] CKT 1 | 8.2335 | 32.8792 | 32779.2022 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SIKESTN5 161.00] TO [IDALIA 5 161.00] CKT 1 | 8.2332 | 32.8697 | 32769.7426 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SIKESTN5 161.00] TO [SIKESTN2 69.000] TO [SIK X1 1 13.800] CKT 1 | 8.2331 | 32.8656 | 32765.6203 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [DELAWAR1 13.800] TO [DELWARE4 138.00] TO [DELWARE7 345.00] CKT 1 | 8.2329 | 32.853 | 32753.0211 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [DELWARE7 345.00] TO [N.E.S.-7 345.00] CKT 1 | 8.217 | 32.8412 | 32741.1574 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WWRDEHV7 345.00] TO [DGRASSE7 345.00] CKT 1 | 8.1783 | 32.8652 | 32765.1819 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WWRDEHV7 345.00] TO [DGRASSE7 345.00] CKT 2 | 8.1783 | 32.8647 | 32764.7003 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [DGRASSE7 345.00] TO [DGRASSE4 138.00] TO [DGRASSE1 13.800] CKT 1 | 8.2213 | 32.8979 | 32797.8844 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WALKMYR1 13.800] TO [WALKMYR2 69.000] TO [WALKMYR3 115.00] CKT 1 | 8.233 | 32.8657 | 32765.7299 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WALKMYR3 115.00] TO [HUGOTON3 115.00] CKT 1 | 8.2328 | 32.8665 | 32766.4983 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WALKMYR3 115.00] TO [HARBNGR3 115.00] CKT 1 | 8.2328 | 32.8574 | 32757.3911 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SEWARD-3 115.00] TO [N-CIMRN3 115.00] CKT 1 | 8.2328 | 32.8685 | 32768.4605 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SPERVIL7 345.00] TO [CLARKCOUNTY7345.00] CKT 1 | 8.2224 | 32.8369 | 32736.9098 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NSES 2X1 13.200] TO [NEOSHO 4 138.00] TO [NEOSHOS2 69.000] CKT 1 | 8.2331 | 32.8688 | 32768.8037 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EEC GT1 13.800] TO [EVANS S4 138.00] CKT 1 | 8.2331 | 32.8724 | 32772.3769 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EEC GT2 13.800] TO [EVANS S4 138.00] CKT 1 | 8.2331 | 32.8721 | 32772.1399 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EEC GT3 18.000] TO [EVANS S4 138.00] CKT 1 | 8.2332 | 32.8697 | 32769.7198 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EMPEC 7 345.00] TO [SWISVAL7 345.00] CKT 1 | 8.174 | 32.787 | 32686.9742 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EMPEC 7 345.00] TO [EXPEDITION7 345.00] CKT 1 | 7.8011 | 33.3977 | 33297.6963 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [RENO 7 345.00] TO [WICHITA7 345.00] CKT 1 | 8.0013 | 32.8193 | 32719.3436 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUMMIT 7 345.00] TO [G17-004-TAP 345.00] CKT 1 | 8.2127 | 32.8387 | 32738.7218 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SWISVAL7 345.00] TO [SWISVAL6 230.00] TO [SWISV1X1 14.400] CKT 1 | 8.2329 | 32.8752 | 32775.2115 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SWISVAL7 345.00] TO [SWISVAL6 230.00] TO [SWISV2X2 14.400] CKT 2 | 8.2333 | 32.8679 | 32767.944 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [87TH 7 345.00] TO [CRAIG 7 345.00] CKT 1 | 8.233 | 32.865 | 32764.9896 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [G17-009-TAP 345.00] TO [GEN-2017-009345.00] CKT 1 | 8.2328 | 32.8439 | 32743.9039 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [G17-009-TAP 345.00] TO [CANEYRV7 345.00] CKT 1 | 8.0291 | 33.1578 | 33057.7531 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [KINGMAN7 345.00] TO [NINN1WF7 345.00] CKT 1 | 8.2405 | 33.0572 | 32957.1607 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [KINGMAN7 345.00] TO [K1 LV 1 34.500] TO [K1 WFTX1 13.800] CKT 1 | 8.2317 | 32.9517 | 32851.7253 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [KINGMAN7 345.00] TO [K2 LV 1 34.500] TO [K2 WFTX1 13.800] CKT 1 | 8.2331 | 32.9424 | 32842.4493 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BENTON 7 345.00] TO [WICHITA7 345.00] CKT 1 | 7.9633 | 32.6865 | 32586.4996 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BENTON 7 345.00] TO [WOLFCRK7 345.00] CKT 1 | 7.9784 | 32.9707 | 32870.6835 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WICHITA7 345.00] TO [VIOLA 7 345.00] CKT 1 | 8.1259 | 32.4152 | 32315.2487 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WICHITA7 345.00] TO [EXPEDITION7 345.00] CKT 1 | 7.8095 | 33.0772 | 32977.2295 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WOLFCRK7 345.00] TO [WAVERLY7 345.00] CKT 1 | 8.1795 | 32.8855 | 32785.5305 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [VIOLA 7 345.00] TO [VIOLA 4 138.00] TO [VIOLA1X1 13.800] CKT 1 | 8.2166 | 32.8156 | 32715.6479 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [VIOLA 7 345.00] TO [VIOLA 4 138.00] TO [SCJ1X1 13.800] CKT 2 | 8.2148 | 32.9317 | 32831.6791 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WAVERLY7 345.00] TO [LACYGNE7 345.00] CKT 1 | 8.1752 | 32.8507 | 32750.6693 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NMANHT6 230.00] TO [ELMCREK6 230.00] CKT 1 | 8.2234 | 32.852 | 32752.0227 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LITCH 5 161.00] TO [FRANKLIN5 161.00] CKT 1 | 8.2321 | 32.8567 | 32756.7468 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LITCH 5 161.00] TO [LITCH S2 69.000] TO [LITCH1 1 13.200] CKT 1 | 8.2332 | 32.87 | 32770.0124 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LITCH 5 161.00] TO [LITCH N2 69.000] TO [LITCH2 1 13.200] CKT 1 | 8.2332 | 32.8687 | 32768.7024 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [MARMTNW5 161.00] TO [NEOSHO 5 161.00] CKT 1 | 8.2322 | 32.8793 | 32779.2597 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEOSHO 5 161.00] TO [RIV4525 161.00] CKT 1 | 8.2227 | 32.9226 | 32822.5789 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEOSHO 5 161.00] TO [NEOSHO 4 138.00] TO [NEOSH4 1 13.200] CKT 1 | 8.2331 | 32.8707 | 32770.6596 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEOSHO 5 161.00] TO [NEOSHOS4 138.00] TO [NEOSH5 1 13.200] CKT 1 | 8.233 | 32.8717 | 32771.6815 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRESWLN4 138.00] TO [OXFORD 4 138.00] CKT 1 | 8.1826 | 32.8402 | 32740.1807 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [TCROCK 4 138.00] TO [TIMBJCT4 138.00] CKT 1 | 8.2314 | 32.9072 | 32807.2191 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [TIMBJCT4 138.00] TO [TIMBJCT2 69.000] TO [TIMBJCT1 13.200] CKT 1 | 8.2312 | 32.8238 | 32723.7842 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [TIOGA 4 138.00] TO [ALTOONA4 138.00] CKT 1 | 8.2286 | 32.8906 | 32790.5703 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [OTTRCRK4 138.00] TO [ALTOONA4 138.00] CKT 1 | 8.1794 | 32.9119 | 32811.9201 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ALTOONA4 138.00] TO [TAYLOR 4 138.00] CKT 1 | 8.2297 | 32.8891 | 32789.0586 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ALTOONA4 138.00] TO [ALTOO W2 69.000] TO [ALTOO1 1 13.200] CKT 1 | 8.2332 | 32.8741 | 32774.1171 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ALTOONA4 138.00] TO [ALTOO E2 69.000] TO [ALTOO3 1 13.200] CKT 1 | 8.233 | 32.8656 | 32765.5644 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEPARSN4 138.00] TO [NEOSHON4 138.00] CKT 1 | 8.2296 | 32.8755 | 32775.542 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BENTLEY4 138.00] TO [SG12COL4 138.00] CKT 1 | 7.9576 | 32.6945 | 32594.4702 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEOSHOS4 138.00] TO [NEOSHO 4 138.00] CKT Z1 | 8.2328 | 32.8709 | 32770.9482 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEOSHO 4 138.00] TO [NEOSHON4 138.00] CKT Z1 | 8.2323 | 32.8725 | 32772.5485 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CHISHLM4 138.00] TO [MAIZE 4 138.00] CKT 1 | 7.473 | 32.4593 | 32359.2513 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CLEARWT4 138.00] TO [GILL 4 138.00] CKT 1 | 8.159 | 32.8017 | 32701.6827 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CLEARWT4 138.00] TO [VIOLA 4 138.00] CKT 1 | 8.1572 | 32.8831 | 32783.0822 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EVANS S4 138.00] TO [LAKERDG4 138.00] CKT 1 | 7.8417 | 32.3483 | 32248.3471 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EVANS S4 138.00] TO [45TH ST4 138.00] CKT 1 | 7.8391 | 32.4126 | 32312.6419 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [FARBER 4 138.00] TO [SC10BEL4 138.00] CKT 1 | 8.2079 | 32.8136 | 32713.5767 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GILL 4 138.00] TO [VIOLA 4 138.00] CKT 1 | 8.158 | 32.8409 | 32740.9438 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [VIOLA 4 138.00] TO [MILAN_GOAB 138.00] CKT 1 | 8.2289 | 32.8709 | 32770.9116 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [VIOLA 4 138.00] TO [CONWAY 138.00] CKT 1 | 8.2234 | 32.8811 | 32781.0692 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [AEC 3 115.00] TO [EABILEN3 115.00] CKT 1 | 8.2293 | 32.8008 | 32700.7789 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [AEC 3 115.00] TO [AEC E1 34.500] CKT 2 | 8.2327 | 32.8655 | 32765.5226 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [AEC 3 115.00] TO [AEC W1 34.500] CKT 1 | 8.2312 | 32.8617 | 32761.6701 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NORTHST3 115.00] TO [NORTHVW3 115.00] CKT 1 | 8.2326 | 32.8552 | 32755.2127 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NORTHVW3 115.00] TO [SUMMIT 3 115.00] CKT 1 | 8.2327 | 32.8728 | 32772.8364 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LITCH N2 69.000] TO [LITCH S2 69.000] CKT Z1 | 8.2332 | 32.8689 | 32768.9209 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [MRWYP16 230.00] TO [ELMCREK6 230.00] CKT 1 | 8.2352 | 32.9283 | 32828.2576 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [FLATRDG4 138.00] TO [THISTLE4 138.00] CKT 1 | 8.2337 | 32.8854 | 32785.427 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ELMCREK6 230.00] TO [CONCRD6 230.00] CKT 1 | 8.2246 | 32.8538 | 32753.7502 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAYNE3 115.00] TO [NLIB 3 115.00] CKT 1 | 8.233 | 32.8679 | 32767.9158 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [KISMET 3 115.00] TO [CMRIVTP3 115.00] CKT 1 | 8.2284 | 32.8633 | 32763.3211 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CMRIVTP3 115.00] TO [E-LIBER3 115.00] CKT 1 | 8.2329 | 32.8668 | 32766.7765 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CIM-PLT1 13.800] TO [CIM-PLT 13.800] CKT Z1 | 8.2327 | 32.8584 | 32758.4029 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [N-CIMRN3 115.00] TO [N-CMRN 1 34.500] TO [N-CMRN-T 13.800] CKT 1 | 8.2331 | 32.8683 | 32768.3173 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [TRANSFORMER 345.00] CKT 1 | 8.2352 | 32.9425 | 32842.4648 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [GEN-2011-008345.00] CKT 1 | 8.2403 | 32.9866 | 32886.567 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [G16-046-TAP 345.00] CKT 1 | 8.2149 | 32.8527 | 32752.747 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [MULLNCR7 345.00] TO [MC REAC1 345.00] CKT Z1 | 8.2333 | 32.8697 | 32769.7005 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [MULLNCR7 345.00] TO [MC REAC2 345.00] CKT Z1 | 8.2333 | 32.8697 | 32769.7005 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [MULLNCR7 345.00] TO [MC REAC3 345.00] CKT Z1 | 8.2332 | 32.8701 | 32770.1045 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [MULLNCR7 345.00] TO [KETCHEM7 345.00] CKT 1 | 8.2324 | 32.8635 | 32763.5416 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [PECULR 7 345.00] TO [STILWEL7 345.00] CKT 1 | 8.2265 | 32.8511 | 32751.0912 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ST JOE 7 345.00] TO [EASTOWN7 345.00] CKT 1 | 8.2319 | 32.8628 | 32762.785 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ST JOE 7 345.00] TO [COOPER 3 345.00] CKT 1 | 8.2322 | 32.8679 | 32767.9343 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ST JOE 7 345.00] TO [ST JOE 5 161.00] TO [STJOE 1T 13.800] CKT 22 | 8.2332 | 32.869 | 32768.9952 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ST JOE 7 345.00] TO [ST JOE 5 161.00] TO [STJOE 2T 13.800] CKT 33 | 8.2332 | 32.869 | 32769.008 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ARCHIE 5 161.00] TO [HSNVL 5 161.00] CKT 1 | 8.233 | 32.8676 | 32767.6219 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ARCHIE 5 161.00] TO [ADRIAN 5 161.00] CKT 1 | 8.2325 | 32.8496 | 32749.6106 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ARCHIE 5 161.00] TO [S.HARP 5 161.00] CKT 1 | 8.2326 | 32.8623 | 32762.2975 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S.HARP 5 161.00] TO [STILWEL5 161.00] CKT 1 | 8.233 | 32.8682 | 32768.2182 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EASTOWN7 345.00] TO [IATAN 7 345.00] CKT 1 | 8.2307 | 32.8519 | 32751.9003 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ROCKCK_TR1_113.200] TO [ROCKCK7 345.00] TO [ROCKCK_T1_1 34.500] CKT 1 | 8.234 | 32.8968 | 32796.7952 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ROCKCK_TR2_113.200] TO [ROCKCK7 345.00] TO [ROCKCK_T2_1 34.500] CKT 1 | 8.234 | 32.8959 | 32795.922 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ROCKCK7 345.00] TO [OUTLAW 345.00] CKT 1 | 8.2347 | 32.915 | 32814.959 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LAC G1 1 22.000] TO [LACYGNE7 345.00] CKT 1 | 8.2222 | 33.0766 | 32976.6072 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LAC G2 1 24.000] TO [LACYGNE7 345.00] CKT 1 | 8.2254 | 33.0825 | 32982.5093 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WGARDNR5 161.00] TO [CEDRCRK5 161.00] CKT 1 | 8.2328 | 32.8688 | 32768.8191 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WGARDNR5 161.00] TO [CEDARNL5 161.00] CKT 1 | 8.2331 | 32.867 | 32766.9525 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WGARDNR5 161.00] TO [PLSTVAL5 161.00] CKT 1 | 8.2331 | 32.8676 | 32767.6047 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WGARDNR5 161.00] TO [BULLCRK5 161.00] CKT 1 | 8.2332 | 32.8693 | 32769.3198 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WGARDNR5 161.00] TO [BNSF 5 161.00] CKT 1 | 8.2327 | 32.8669 | 32766.9218 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WGARDNR5 161.00] TO [WGARDNR1 34.500] CKT 7 | 8.233 | 32.8642 | 32764.1559 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [STILWEL7 345.00] TO [LACYGNE7 345.00] CKT 1 | 8.2307 | 32.8326 | 32732.5769 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [STILWEL7 345.00] TO [STILWEL5 161.00] TO [STIL T11 13.800] CKT 11 | 8.2326 | 32.8637 | 32763.7434 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [STILWEL7 345.00] TO [STILWEL5 161.00] TO [STIL T22 13.800] CKT 22 | 8.2326 | 32.8633 | 32763.3281 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [STILWEL5 161.00] TO [HICKMAN5 161.00] CKT 1 | 8.2329 | 32.8696 | 32769.5971 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [STILWEL5 161.00] TO [ANTIOCH5 161.00] CKT 1 | 8.2334 | 32.8701 | 32770.1328 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [STILWEL5 161.00] TO [REDEL 5 161.00] CKT 1 | 8.2326 | 32.8693 | 32769.2572 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [STILWEL5 161.00] TO [BUCYRUS5 161.00] CKT 1 | 8.233 | 32.8646 | 32764.5796 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [STILWEL5 161.00] TO [LACKMAN5 161.00] CKT 1 | 8.2332 | 32.8689 | 32768.8835 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTH 7 345.00] TO [NASHUA 7 345.00] CKT 1 | 8.2325 | 32.8514 | 32751.3723 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTHS5 161.00] TO [SUB M-161 161.00] CKT 1 | 8.2331 | 32.8681 | 32768.1303 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRAIG 7 345.00] TO [CRAIG 5 161.00] TO [CRAI T11 13.800] CKT 11 | 8.2326 | 32.8641 | 32764.1006 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRAIG 7 345.00] TO [CRAIG 5 161.00] TO [CRAI T22 13.800] CKT 22 | 8.2326 | 32.8642 | 32764.21 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRAIG 7 345.00] TO [CRAIG 5 161.00] TO [CRAI T33 13.800] CKT 33 | 8.2327 | 32.8671 | 32767.1186 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRAIG 5 161.00] TO [CEDRCRK5 161.00] CKT 1 | 8.2332 | 32.8691 | 32769.1154 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NASHUA 7 345.00] TO [IATAN 7 345.00] CKT 1 | 8.2317 | 32.8425 | 32742.5129 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NASHUA 7 345.00] TO [NASHUA-5 161.00] TO [NASH T11 13.800] CKT 11 | 8.2332 | 32.8682 | 32768.1903 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NASHUA 7 345.00] TO [NASHUA-5 161.00] TO [NASH T12 13.800] CKT 12 | 8.2331 | 32.8672 | 32767.2287 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LACYGNE7 345.00] TO [LACYGNE11_7 345.00] CKT 1 | 8.2327 | 32.8589 | 32758.8778 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LACYGNE7 345.00] TO [LACYGNE22_7 345.00] CKT 1 | 8.2332 | 32.8693 | 32769.2604 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LACYGNE7 345.00] TO [LAC3_STAR7 345.00] CKT H | 8.2332 | 32.8693 | 32769.2852 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LACYGNE7 345.00] TO [LAC8_STAR7 345.00] CKT H | 8.2332 | 32.8693 | 32769.2982 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LACYGNE7 345.00] TO [LACYGNE2 69.000] TO [LACYGN7_TER16.9000] CKT 7 | 8.233 | 32.8653 | 32765.3372 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BLUMILS5 161.00] TO [ECKLES-161 161.00] CKT 1 | 8.2332 | 32.8694 | 32769.3524 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BLUMILS5 161.00] TO [BLUEMLS2 69.000] TO [BLUMILS_TER112.500] CKT 3 | 8.2332 | 32.8671 | 32767.0766 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LAKCTYJ2 69.000] TO [BLUVLY 69.000] CKT 1 | 8.2332 | 32.8694 | 32769.3574 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CJ 366 5 161.00] TO [FIR417 5 161.00] CKT 1 | 8.2329 | 32.8689 | 32768.8849 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CAR395 5 161.00] TO [PUR421 5 161.00] CKT 1 | 8.2328 | 32.8673 | 32767.3295 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB K 69.000] TO [BLUVLY 69.000] CKT 1 | 8.2332 | 32.8693 | 32769.318 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB H 69.000] TO [BLUVLY 69.000] CKT 1 | 8.2332 | 32.8693 | 32769.2969 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB H 69.000] TO [SUB M 69.000] CKT 1 | 8.2332 | 32.8693 | 32769.3111 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BLUVLY 13.8 13.800] TO [BLUVLY 69.000] CKT 1 | 8.2332 | 32.8693 | 32769.2974 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BLUVLY 69.000] TO [SUB B 69.000] CKT 1 | 8.2332 | 32.8693 | 32769.2934 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BLUVLY 69.000] TO [SUB J 69.000] CKT 1 | 8.2332 | 32.8693 | 32769.2879 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BLUVLY 69.000] TO [SUB P 69.000] CKT 1 | 8.2332 | 32.8693 | 32769.3114 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB B 69.000] TO [SUB J 69.000] CKT 1 | 8.2332 | 32.8693 | 32769.2927 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB J 69.000] TO [SUB M 69.000] CKT 1 | 8.2332 | 32.8693 | 32769.2838 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB M-161 161.00] TO [SUB M 69.000] CKT 1 | 8.2331 | 32.8692 | 32769.1999 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GEN-2017-004345.00] TO [G17-004-TAP 345.00] CKT 1 | 8.2349 | 32.8885 | 32788.5415 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GEN-2017-018345.00] TO [G17-018XFMR134.500] CKT 1 | 8.235 | 32.9167 | 32816.6779 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GEN-2017-018345.00] TO [G17-018XFMR234.500] CKT 1 | 8.235 | 32.9167 | 32816.6779 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GEN-2017-068138.00] TO [G17-068XFMR134.500] CKT 1 | 8.2402 | 33.2344 | 33134.3506 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GEN-2017-082161.00] TO [G17-082XFMR134.500] CKT 1 | 8.2332 | 32.8682 | 32768.1915 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [COOPER 3 345.00] TO [S3458 3 345.00] CKT 1 | 8.2329 | 32.8701 | 32770.0958 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEBCTY1G 18.000] TO [S3458 3 345.00] CKT 1 | 8.2386 | 33.0423 | 32942.2716 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEBCTY2G 23.000] TO [S3458 3 345.00] CKT 1 | 8.2389 | 33.051 | 32950.999 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S3456 3 345.00] TO [S3458 3 345.00] CKT 1 | 8.233 | 32.8668 | 32766.7714 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S3458 3 345.00] TO [S3740 3 345.00] CKT 1 | 8.2331 | 32.8689 | 32768.8564 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S3458 3 345.00] TO [103&ROKEBY3 345.00] CKT 1 | 8.2334 | 32.8762 | 32776.1804 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [7FAIRPT 345.00] TO [5FAIRPTXF3 161.00] CKT 3 | 8.2329 | 32.8648 | 32764.7706 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5CLINTN 161.00] TO [G17-108-TAP 161.00] CKT 1 | 8.2319 | 32.8466 | 32746.5915 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5NEWMAD 161.00] TO [5GIBSON 161.00] CKT 1 | 8.2332 | 32.8689 | 32768.9404 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M0 161.00] CKT 1 | 8.2332 | 32.8693 | 32769.2974 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M1 161.00] CKT 1 | 8.2331 | 32.8659 | 32765.8641 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M2 161.00] CKT 1 | 8.2331 | 32.8659 | 32765.8641 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5NEWMAD 161.00] TO [5M7M3 161.00] CKT 1 | 8.2331 | 32.8659 | 32765.8641 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5NEWMAD 161.00] TO [5NEWMADCP 161.00] CKT Z1 | 8.2332 | 32.8693 | 32769.2987 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5NEWMAD 161.00] TO [5NEWMADXF12 161.00] CKT Z1 | 8.2332 | 32.8688 | 32768.7729 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5NEWMAD 161.00] TO [5NEWMADGSU1 161.00] CKT 1 | 8.2338 | 32.8885 | 32788.5281 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5NEWMAD 161.00] TO [5NMDSU100HS 161.00] CKT 1 | 8.2332 | 32.8693 | 32769.2974 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5NEWMAD 161.00] TO [5NMDSU200HS 161.00] CKT 1 | 8.2332 | 32.8693 | 32769.2974 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5NEWMAD 161.00] TO [5PORTAGEVLE 161.00] CKT 1 | 8.2332 | 32.8678 | 32767.7638 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5NEWMAD 161.00] TO [5TIPTONVL TN161.00] CKT 1 | 8.233 | 32.862 | 32762.004 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5HOLDENB2 161.00] TO [1HOLDNG11 13.800] CKT 11 | 8.2339 | 32.8957 | 32795.6514 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5HOLDENB2 161.00] TO [1HOLDNG12 13.800] CKT 12 | 8.2332 | 32.8693 | 32769.2785 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5HOLDENB2 161.00] TO [2HOLDEN 69.000] CKT 1 | 8.2332 | 32.8695 | 32769.4632 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5HOLDENB2 161.00] TO [5HOLDENB1 161.00] CKT Z1 | 8.2332 | 32.8689 | 32768.9107 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [2CLINTN 69.000] TO [2LINCLN 69.000] CKT 1 | 8.2331 | 32.8689 | 32768.933 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [2CLINTN 69.000] TO [2GAINES 69.000] CKT 1 | 8.2331 | 32.8673 | 32767.3182 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [2CLINTN 69.000] TO [2LEETON 69.000] CKT 1 | 8.2332 | 32.8691 | 32769.1177 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [2CLINTN 69.000] TO [2PIPER 69.000] CKT 1 | 8.2332 | 32.8693 | 32769.2535 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [2CLINTN 69.000] TO [2CLINTNLD 69.000] CKT 1 | 8.2331 | 32.8674 | 32767.3588 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [7BLACKBERRY 345.00] TO [NEOSHO 7 345.00] CKT 1 | 8.2243 | 32.933 | 32833.0354 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [7SPORTSMAN 345.00] TO [5SPORTSMAN 161.00] CKT 1 | 8.2329 | 32.8713 | 32771.2706 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [7SPORTSMAN 345.00] TO [5SPORTSMAN 161.00] CKT 2 | 8.2329 | 32.8713 | 32771.2702 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [7SPORTSMAN 345.00] TO [GRDA1 7 345.00] CKT 1 | 8.231 | 32.8278 | 32727.7959 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [7JASPER 345.00] TO [7MORGAN 345.00] CKT 1 | 8.2176 | 32.8727 | 32772.7172 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [7JASPER 345.00] TO [5JASPER 161.00] CKT 1 | 8.2319 | 32.8757 | 32775.6742 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5OSCEOKCTP 161.00] TO [5OSCEOLTP 161.00] CKT 1 | 8.2329 | 32.8605 | 32760.5246 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5OSCEOKCTP 161.00] TO [5OSCEOKC 161.00] CKT 1 | 8.2332 | 32.8684 | 32768.3645 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5MINER 1 161.00] TO [5CHARLSTN 161.00] CKT 1 | 8.2332 | 32.8687 | 32768.6707 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5MINER 1 161.00] TO [5BULLION 161.00] CKT 1 | 8.2331 | 32.8668 | 32766.8371 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [5MINER 1 161.00] TO [5MINER 2 161.00] CKT Z | 8.2332 | 32.8686 | 32768.6094 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [N MADRD5 161.00] TO [G17-202-TAP 161.00] CKT 1 | 8.2332 | 32.8674 | 32767.4386 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [N MADRD2 69.000] TO [2STJUDEW 69.000] CKT 1 | 8.2332 | 32.8694 | 32769.383 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [N MADRD2 69.000] TO [2LILBRN 69.000] CKT 1 | 8.2332 | 32.8694 | 32769.3914 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [N MADRD2 69.000] TO [MALDEN 2 69.000] CKT 1 | 8.2332 | 32.869 | 32769.0233 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [KENNETT5 161.00] TO [PARAGLD5 161.00] CKT 1 | 8.2331 | 32.8671 | 32767.0873 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [KENNETT5 161.00] TO [KENNETT2 69.000] TO [KEN X1 1 13.800] CKT 1 | 8.2332 | 32.8693 | 32769.3359 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [KENNETT5 161.00] TO [KENNETT2 69.000] TO [KEN X2 1 13.800] CKT 1 | 8.2332 | 32.8693 | 32769.3367 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SIKETAP5 161.00] TO [SIKE SW5 161.00] CKT 1 | 8.2332 | 32.8693 | 32769.2974 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SIKESTN5 161.00] TO [G17-202-TAP 161.00] CKT 1 | 8.2332 | 32.8678 | 32767.8213 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [IDALIA 5 161.00] TO [5ESSEX 161.00] CKT 1 | 8.2332 | 32.8682 | 32768.1552 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [IDALIA 5 161.00] TO [2IDALIA 69.000] CKT 1 | 8.2332 | 32.8693 | 32769.3308 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [IDALIA 5 161.00] TO [2IDALIA 69.000] CKT 2 | 8.2332 | 32.8693 | 32769.3236 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [IDALIA 5 161.00] TO [ASHRVL5 161.00] CKT 1 | 8.2332 | 32.868 | 32767.9897 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [TRUMAN 5 161.00] TO [5LOSTVALY 161.00] CKT 1 | 8.2324 | 32.8465 | 32746.5233 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [TRUMAN 5 161.00] TO [TRU123 1 13.800] CKT 1 | 8.2335 | 32.8822 | 32782.2062 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [TRUMAN 5 161.00] TO [TRU456 1 13.800] CKT 1 | 8.2335 | 32.8822 | 32782.2118 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [DELWARE4 138.00] TO [FARML 4 138.00] CKT 1 | 8.2329 | 32.8517 | 32751.6907 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [DELWARE7 345.00] TO [NEOSHO 7 345.00] CKT 1 | 8.2162 | 32.8007 | 32700.7343 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [N.E.S.-7 345.00] TO [ONETA--7 345.00] CKT 1 | 8.2284 | 32.8549 | 32754.9347 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [N.E.S.-7 345.00] TO [T.NO.--7 345.00] CKT 1 | 8.2324 | 32.8473 | 32747.265 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [N.E.S.-7 345.00] TO [NES3-1 22.000] CKT 1 | 8.2253 | 32.7909 | 32690.9427 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WWRDEHV7 345.00] TO [TATONGA7 345.00] CKT 1 | 8.2261 | 32.8105 | 32710.4572 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WWRDEHV7 345.00] TO [TATONGA7 345.00] CKT 2 | 8.226 | 32.8099 | 32709.8598 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WWRDEHV7 345.00] TO [G07621119-20345.00] CKT 1 | 8.2335 | 32.8496 | 32749.6046 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WWRDEHV7 345.00] TO [GUTHRIE7 345.00] CKT 1 | 8.2333 | 32.8635 | 32763.4831 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WWRDEHV7 345.00] TO [BECKHAM7 345.00] CKT 1 | 8.2042 | 32.8495 | 32749.5065 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WWRDEHV7 345.00] TO [G16-003-TAP 345.00] CKT 1 | 8.231 | 32.8886 | 32788.6218 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WWRDEHV7 345.00] TO [G16-003-TAP 345.00] CKT 2 | 8.231 | 32.8886 | 32788.6316 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WWRDEHV7 345.00] TO [WWRDEHV4 138.00] TO [WWDEHV31 13.800] CKT 1 | 8.2318 | 32.8803 | 32780.3483 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WWRDEHV7 345.00] TO [WWRDEHV4 138.00] TO [WWDEHV21 13.800] CKT 2 | 8.2316 | 32.8876 | 32787.6376 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [DGRASSE7 345.00] TO [THISTLE7 345.00] CKT 1 | 8.1587 | 32.8609 | 32760.9046 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [DGRASSE7 345.00] TO [THISTLE7 345.00] CKT 2 | 8.1587 | 32.8611 | 32761.05 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [DGRASSE4 138.00] TO [KNOBHIL4 138.00] CKT 1 | 8.233 | 32.8619 | 32761.8577 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [DGRASSE4 138.00] TO [ROSEVLY4 138.00] CKT 1 | 8.233 | 32.8625 | 32762.549 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [DGRASSE4 138.00] TO [MOORLND4 138.00] CKT 1 | 8.2182 | 32.8649 | 32764.9363 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WALKMYR2 69.000] TO [NORTH6T2 69.000] CKT 1 | 8.2331 | 32.868 | 32768.0034 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WALKMYR2 69.000] TO [WOODS 2 69.000] CKT 1 | 8.2331 | 32.8684 | 32768.3663 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WALKMYR3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 8.2332 | 32.8629 | 32762.8843 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SEWARD-3 115.00] TO [HASKELL3 115.00] CKT 1 | 8.2328 | 32.8681 | 32768.1163 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SEWARD-3 115.00] TO [CMSSWRD2 69.000] TO [SEWARD 1 13.800] CKT 1 | 8.2331 | 32.8679 | 32767.9025 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SPERVIL7 345.00] TO [POSTROCK7 345.00] CKT 1 | 8.2209 | 32.8216 | 32721.6437 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SPERVIL7 345.00] TO [BUCKNER7 345.00] CKT 1 | 8.1754 | 33.0063 | 32906.2754 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SPERVIL7 345.00] TO [IRONWOOD7 345.00] CKT 1 | 8.2233 | 32.8405 | 32740.4887 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SPERVIL7 345.00] TO [SPRVL 3 115.00] TO [SPRVL-T 13.800] CKT 1 | 8.2336 | 32.8771 | 32777.0546 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SPERVIL7 345.00] TO [SPEARVL6 230.00] TO [SPERTER1 13.800] CKT 1 | 8.2341 | 32.8681 | 32768.0555 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HUGOTON3 115.00] TO [GRANTTP3 115.00] CKT 1 | 8.2327 | 32.8631 | 32763.0907 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HUGOTON3 115.00] TO [ABBK 2 115.00] CKT 1 | 8.233 | 32.8676 | 32767.6314 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HUGOTON3 115.00] TO [HUGOTON2 69.000] TO [HUGOTON1 13.800] CKT 1 | 8.2328 | 32.8662 | 32766.207 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HARBNGR3 115.00] TO [HARBNGR7 345.00] TO [HARBNGR-T 13.800] CKT 1 | 8.2327 | 32.8574 | 32757.387 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EEC GT1 13.800] TO [DG TIE 1 4.1600] CKT 1 | 8.2332 | 32.8693 | 32769.2976 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EEC GT2 13.800] TO [EEC DG 1 4.1600] CKT 1 | 8.2332 | 32.8693 | 32769.2976 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC121 13.800] CKT 1 | 8.2189 | 32.932 | 32831.9871 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC341 13.800] CKT 1 | 8.2189 | 32.932 | 32832.0454 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC5 1 18.000] CKT 1 | 8.2011 | 32.9956 | 32895.5837 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC6 1 18.000] CKT 1 | 8.2332 | 32.8692 | 32769.2472 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EMPEC 7 345.00] TO [EMPEC7 1 18.000] CKT 1 | 8.2009 | 32.9889 | 32888.859 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EMPEC 7 345.00] TO [LANG 7 345.00] CKT 1 | 8.2283 | 32.8727 | 32772.7275 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EMPEC 7 345.00] TO [MORRIS 7 345.00] CKT 1 | 8.235 | 32.8466 | 32746.5974 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EMPEC 7 345.00] TO [READWF 7 345.00] CKT 1 | 8.2344 | 32.9115 | 32811.4888 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [RENO 7 345.00] TO [G16-111-TAP 345.00] CKT 1 | 8.0424 | 32.8837 | 32783.6946 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [RENO 7 345.00] TO [RENO 3 115.00] TO [RENO 1X1 14.400] CKT 1 | 8.2317 | 32.9693 | 32869.3387 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [RENO 7 345.00] TO [RENO 3 115.00] TO [RENO 2X1 14.400] CKT 1 | 8.2318 | 32.9651 | 32865.1263 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUMMIT 7 345.00] TO [GEARY 7 345.00] CKT 1 | 8.1622 | 32.9546 | 32854.6063 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUMMIT 7 345.00] TO [G16-111-TAP 345.00] CKT 1 | 8.0413 | 33.0054 | 32905.416 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUMMIT 7 345.00] TO [SUMMIT 6 230.00] TO [SUMMIT 1 14.400] CKT 1 | 8.2275 | 32.9351 | 32835.1274 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SWISVAL7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 8.1822 | 32.8403 | 32740.3354 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [87TH 7 345.00] TO [STRANGR7 345.00] CKT 1 | 8.233 | 32.8623 | 32762.2545 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [87TH 7 345.00] TO [87TH 3 115.00] TO [87TH 1X1 13.800] CKT 1 | 8.2333 | 32.8706 | 32770.6371 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [G17-009-TAP 345.00] TO [NEOSHO 7 345.00] CKT 1 | 8.0222 | 33.3929 | 33292.9039 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GEN-2017-009345.00] TO [G17-009XFMR134.500] CKT 1 | 8.233 | 32.8603 | 32760.3213 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GEN-2017-009345.00] TO [G17-009XFMR234.500] CKT 1 | 8.233 | 32.8597 | 32759.6954 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CANEYRV7 345.00] TO [CANEYWF7 345.00] CKT 1 | 8.2331 | 32.8504 | 32750.3643 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CANEYRV7 345.00] TO [LATHAMS7 345.00] CKT 1 | 8.0306 | 33.1266 | 33026.6099 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [KINGMAN7 345.00] TO [BUFFALO7 345.00] CKT 1 | 8.2376 | 32.815 | 32715.0299 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NINN1WF7 345.00] TO [PRATTWF7 345.00] CKT 1 | 8.242 | 33.0738 | 32973.7989 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NINN1WF7 345.00] TO [N1 LV 1 34.500] TO [N1 WFTX1 13.800] CKT 1 | 8.2316 | 32.9589 | 32858.8722 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BENTON 7 345.00] TO [ROSEHIL7 345.00] CKT 1 | 7.9746 | 32.841 | 32741.0129 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BENTON 7 345.00] TO [BENTON 4 138.00] TO [BENTN1 1 13.800] CKT 1 | 8.187 | 32.7673 | 32667.3181 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BENTON 7 345.00] TO [BENTON 4 138.00] TO [BENTN2 1 13.800] CKT 1 | 8.1905 | 32.7713 | 32671.2632 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 1 | 8.1937 | 33.0328 | 32932.7985 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 2 | 8.1937 | 33.0328 | 32932.7985 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WICHITA7 345.00] TO [EVANS N4 138.00] TO [WICH11 1 13.800] CKT 1 | 6.9085 | 33.5769 | 33476.8601 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WICHITA7 345.00] TO [EVANS N4 138.00] TO [WICH12 1 13.800] CKT 1 | 6.6565 | 33.9082 | 33808.2163 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WOLFCRK7 345.00] TO [WCGS U1 25.000] CKT 1 | 8.0934 | 33.9345 | 33834.502 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WOLFCRK7 345.00] TO [ROSEHIL7 345.00] CKT 1 | 8.0785 | 32.863 | 32762.9949 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WOLFCRK7 345.00] TO [WOLFCRK2 69.000] TO [WOLFCRK1 17.000] CKT 1 | 8.2306 | 32.8382 | 32738.2431 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [VIOLA 7 345.00] TO [RENFROW7 345.00] CKT 1 | 7.7215 | 32.8025 | 32702.5078 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [VIOLA 7 345.00] TO [G16-153-TAP 345.00] CKT 1 | 8.2438 | 32.7855 | 32685.5276 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WAVERLY7 345.00] TO [WAVERTX7 345.00] CKT 1 | 8.2361 | 32.8999 | 32799.9401 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EXPEDITION7 345.00] TO [GEN-2014-001345.00] CKT 1 | 8.2362 | 32.8747 | 32774.6973 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [N345 1 1 13.800] TO [NEOSHO 7 345.00] TO [NEOSHO 4 138.00] CKT 1 | 8.2324 | 32.8828 | 32782.7665 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [N345 2 1 13.800] TO [NEOSHO 7 345.00] TO [NEOSHO 5 161.00] CKT 1 | 8.2303 | 32.8728 | 32772.7818 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SWISVAL6 230.00] TO [AUBURN 6 230.00] CKT 1 | 8.2324 | 32.8734 | 32773.4153 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SWISVAL6 230.00] TO [LAWHILL6 230.00] CKT 1 | 8.221 | 32.8872 | 32787.1677 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SWISVAL6 230.00] TO [TECHILL6 230.00] CKT 1 | 8.2324 | 32.8589 | 32758.9275 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SWISVAL6 230.00] TO [MORRIS 6 230.00] CKT 1 | 8.2231 | 32.8703 | 32770.3114 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NMANHT6 230.00] TO [EMANHAT6 230.00] CKT 1 | 8.2289 | 32.8743 | 32774.3399 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NMANHT6 230.00] TO [NMANHT3 115.00] TO [NMANHX1 14.400] CKT 1 | 8.2332 | 32.8685 | 32768.5417 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LITCH 5 161.00] TO [ASB349 5 161.00] CKT 1 | 8.2306 | 32.8547 | 32754.7264 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [MARMTNW5 161.00] TO [MARMTNE5 161.00] CKT Z1 | 8.232 | 32.8769 | 32776.9165 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [MARMTNW5 161.00] TO [MARMATN2 69.000] TO [MARMATN1 13.200] CKT 1 | 8.233 | 32.8669 | 32766.8711 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [FRANKLIN5 161.00] TO [G17-005-TAP 161.00] CKT 1 | 8.2315 | 32.8417 | 32741.7321 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [FRANKLIN5 161.00] TO [FRANKLIN2 69.000] TO [FRANKLIN1 12.470] CKT 1 | 8.2332 | 32.8693 | 32769.3054 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRESWLN4 138.00] TO [MIDLTNT4 138.00] CKT 1 | 8.1666 | 32.9732 | 32873.1827 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRESWLN4 138.00] TO [SLATECRK4 138.00] CKT 1 | 8.2147 | 32.7609 | 32660.9377 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRESWLN4 138.00] TO [CRESWLN2 69.000] TO [CRESW1 1 13.200] CKT 1 | 8.2322 | 32.8782 | 32778.1525 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRESWLN4 138.00] TO [CRESWLS2 69.000] TO [CRESW2 1 13.200] CKT 1 | 8.2326 | 32.842 | 32742.0191 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [OXFORD 4 138.00] TO [SUMNER 4 138.00] CKT 1 | 8.1822 | 32.8435 | 32743.4982 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [TIMBJCT4 138.00] TO [SUMNER 4 138.00] CKT 1 | 8.2322 | 32.79 | 32689.9606 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [TIOGA 4 138.00] TO [TIOGA 2 69.000] TO [TIOGA 1 13.200] CKT 1 | 8.2286 | 32.8928 | 32792.7788 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [OTTRCRK4 138.00] TO [BUTLER 4 138.00] CKT 1 | 8.1621 | 32.9257 | 32825.7436 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [OTTRCRK4 138.00] TO [OTTRCRK3 115.00] TO [OTTRX1 1 13.800] CKT 1 | 8.2289 | 32.8829 | 32782.8916 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ALTOONA4 138.00] TO [G17-022-TAP 138.00] CKT 1 | 8.2279 | 32.8133 | 32713.2544 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEPARSN4 138.00] TO [G17-022-TAP 138.00] CKT 1 | 8.2295 | 32.8497 | 32749.7095 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [TAYLOR 4 138.00] TO [MONTGOM4 138.00] CKT 1 | 8.2297 | 32.8903 | 32790.3104 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BENTLEY4 138.00] TO [HALSTD 4 138.00] CKT 1 | 7.9582 | 32.741 | 32640.9651 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BENTLEY4 138.00] TO [WWUPLNT4 138.00] CKT 1 | 8.2318 | 32.8512 | 32751.153 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEOSHOS4 138.00] TO [TV1MNDV4 138.00] CKT 1 | 8.2327 | 32.8558 | 32755.762 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEOSHON4 138.00] TO [NEOSHON2 69.000] TO [NEC U3 12.000] CKT 1 | 8.2332 | 32.8695 | 32769.5345 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CHISHLM4 138.00] TO [PARKCTY4 138.00] CKT 1 | 7.9112 | 32.867 | 32766.9822 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CHISHLM4 138.00] TO [17TH 4 138.00] CKT 1 | 8.1695 | 32.7289 | 32628.9183 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CHISHLM4 138.00] TO [CHISHLM2 69.000] TO [CHISOLM1 13.200] CKT 1 | 8.2288 | 32.7879 | 32687.9487 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EVANS S4 138.00] TO [EVANS N4 138.00] CKT Z1 | 8.2321 | 32.8677 | 32767.6668 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EVANS S4 138.00] TO [EVANS N4 138.00] CKT Z2 | 8.2321 | 32.8677 | 32767.6668 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [FARBER 4 138.00] TO [ELPASOE4 138.00] CKT 1 | 8.2073 | 32.831 | 32731.0244 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GILL 4 138.00] TO [GILL W 4 138.00] CKT Z1 | 8.2324 | 32.8692 | 32769.1536 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GILL 4 138.00] TO [GILL S 4 138.00] CKT Z1 | 8.2332 | 32.8691 | 32769.0816 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LAKERDG4 138.00] TO [HOOVERN4 138.00] CKT 1 | 7.8482 | 32.4865 | 32386.4938 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [MAIZE 4 138.00] TO [EVANS N4 138.00] CKT 1 | 7.4666 | 32.3898 | 32289.815 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SC10BEL4 138.00] TO [SUMNER 4 138.00] CKT 1 | 8.2082 | 32.803 | 32703.0418 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SG12COL4 138.00] TO [EVANS N4 138.00] CKT 1 | 7.9571 | 32.6841 | 32584.1187 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [45TH ST4 138.00] TO [COWSKIN4 138.00] CKT 1 | 7.8401 | 32.4406 | 32340.6354 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [VIOLA 4 138.00] TO [SUMNER 4 138.00] CKT 1 | 8.2302 | 32.8379 | 32737.9231 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [AEC 3 115.00] TO [G17-120-TAP 115.00] CKT 1 | 8.2257 | 32.8442 | 32744.2491 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EABILEN3 115.00] TO [CHAPMAN3 115.00] CKT 1 | 8.2298 | 32.8047 | 32704.7432 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NORTHST3 115.00] TO [SALINA 3 115.00] CKT 1 | 8.2327 | 32.8581 | 32758.1064 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NORTHVW3 115.00] TO [G17-120-TAP 115.00] CKT 1 | 8.23 | 32.8612 | 32761.164 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUMMIT 3 115.00] TO [MENTOR 3 115.00] CKT 1 | 8.2333 | 32.862 | 32762.0377 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUMMIT 3 115.00] TO [SO GATE3 115.00] CKT 1 | 8.2332 | 32.8642 | 32764.1841 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUMMIT 3 115.00] TO [SUMMIT 6 230.00] TO [SUMIT2 1 13.800] CKT 1 | 8.2335 | 32.8702 | 32770.2188 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUMMIT 3 115.00] TO [SUMMIT 6 230.00] TO [SUMIT3 1 13.800] CKT 1 | 8.2335 | 32.8692 | 32769.1842 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [TIMBJCT2 69.000] TO [AKRON 2 69.000] CKT 1 | 8.2323 | 32.8854 | 32785.3911 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [TIMBJCT2 69.000] TO [UDALL 2 69.000] CKT 1 | 8.2319 | 32.8683 | 32768.2628 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [TIMBJCT2 69.000] TO [WINFLD 2 69.000] CKT 1 | 8.23 | 32.7027 | 32602.6556 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ALTOO E2 69.000] TO [NEODJCT2 69.000] CKT 1 | 8.2332 | 32.8743 | 32774.3419 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ALTOO E2 69.000] TO [RA5HIPR2 69.000] CKT Z1 | 8.2332 | 32.8708 | 32770.8128 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ALTOO W2 69.000] TO [STUDBKR2 69.000] CKT 1 | 8.2332 | 32.8738 | 32773.8061 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LITCH N2 69.000] TO [AQUARS 2 69.000] CKT 1 | 8.2332 | 32.8692 | 32769.2483 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LITCH N2 69.000] TO [PITNAC 2 69.000] CKT 1 | 8.2332 | 32.8693 | 32769.3295 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LITCH S2 69.000] TO [ROUSE 2 69.000] CKT 1 | 8.2332 | 32.8693 | 32769.2885 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LITCH S2 69.000] TO [SOPITT 2 69.000] CKT 1 | 8.2328 | 32.8684 | 32768.3927 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEOSHOS2 69.000] TO [BAKER 2 69.000] CKT 1 | 8.2328 | 32.8719 | 32771.9252 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEOSHOS2 69.000] TO [ORDNJCT2 69.000] CKT 1 | 8.2332 | 32.8739 | 32773.8509 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEOSHOS2 69.000] TO [CRAWFOR2 69.000] CKT 1 | 8.2327 | 32.8694 | 32769.4278 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEOSHOS2 69.000] TO [NEOSHON2 69.000] CKT Z1 | 8.2332 | 32.8693 | 32769.2906 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [K1 LV 1 34.500] TO [K1 CLCT1 34.500] CKT 1 | 8.2317 | 32.9517 | 32851.6889 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [K2 LV 1 34.500] TO [K2 CLCT1 34.500] CKT 1 | 8.2331 | 32.9425 | 32842.4888 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [MILAN_GOAB 138.00] TO [CLDWELL4 138.00] CKT 1 | 8.2289 | 32.8644 | 32764.4432 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [MILAN_GOAB 138.00] TO [MILAN 4 138.00] CKT 1 | 8.2329 | 32.8717 | 32771.7104 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CONWAY 138.00] TO [MILANTP4 138.00] CKT 1 | 8.2235 | 32.8816 | 32781.5977 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [MRWYP16 230.00] TO [MRWYP26 230.00] CKT 1 | 8.2343 | 32.897 | 32797.0216 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [MRWYP16 230.00] TO [MRWYG11 34.500] TO [MRWYP1T1 13.800] CKT 1 | 8.2343 | 32.9064 | 32806.3714 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [FLATRDG4 138.00] TO [FLATRWD4 138.00] CKT 1 | 8.2174 | 32.8938 | 32793.7782 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [FLATRDG4 138.00] TO [HARPER 4 138.00] CKT 1 | 8.2105 | 32.9093 | 32809.3233 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [FLATRDG4 138.00] TO [BARBER 4 138.00] CKT 1 | 8.2292 | 32.8656 | 32765.5547 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ELMCREK6 230.00] TO [ELMCREEK7 345.00] TO [ELMCREEK1 13.800] CKT 1 | 8.2114 | 32.8789 | 32778.9348 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAYNE3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 8.233 | 32.8676 | 32767.5777 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [KISMET 3 115.00] TO [CUDAHY 3 115.00] CKT 1 | 8.2282 | 32.8618 | 32761.8028 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CMRIVTP3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 8.2327 | 32.87 | 32769.9915 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CONCRD6 230.00] TO [CONCORD3 115.00] TO [CONCOD-T 13.800] CKT 1 | 8.2245 | 32.858 | 32757.9798 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [E-LIBER3 115.00] TO [TXPHSF 3115.00] CKT 1 | 8.2328 | 32.8708 | 32770.7643 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [E-LIBER3 115.00] TO [E-PINE 3 115.00] CKT 1 | 8.2329 | 32.8659 | 32765.8859 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [E-LIBER3 115.00] TO [NATBEEF3 115.00] CKT 1 | 8.2332 | 32.8695 | 32769.546 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [E-LIBER3 115.00] TO [E-LIBER1 34.500] TO [ELIB-T 2.4000] CKT 1 | 8.2328 | 32.8657 | 32765.7483 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NLIB 3 115.00] TO [W-LIBER3 115.00] CKT 1 | 8.2328 | 32.8646 | 32764.5788 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NLIB 3 115.00] TO [NATBEEF3 115.00] CKT 1 | 8.2332 | 32.8689 | 32768.8839 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NLIB 3 115.00] TO [NLIB 1 34.500] TO [N-LIB-T 13.800] CKT 1 | 8.2328 | 32.8659 | 32765.9206 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [N-CIMRN3 115.00] TO [CIM-PLT3 115.00] CKT 1 | 8.2328 | 32.8689 | 32768.8881 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CIM-PLT 13.800] TO [CIM-PLT3 115.00] CKT 1 | 8.2318 | 32.8475 | 32747.5396 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [THISTLE7 345.00] CKT 1 | 8.2045 | 32.8747 | 32774.6844 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [THISTLE7 345.00] CKT 2 | 8.2045 | 32.8747 | 32774.6844 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [THISTLE T1 13.800] TO [THISTLE7 345.00] TO [THISTLE4 138.00] CKT 1 | 8.2337 | 32.8863 | 32786.2874 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [TRANSFORMER 345.00] TO [SUB34.5KVB 34.500] TO [TERTIARYBUS 19.900] CKT 1 | 8.2352 | 32.9425 | 32842.4701 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GEN-2011-008345.00] TO [G-2011-008-1345.00] CKT 1 | 8.2349 | 32.9243 | 32824.3005 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GEN-2011-008345.00] TO [G-2011-008-2345.00] CKT 1 | 8.2344 | 32.9004 | 32800.4004 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GEN-2011-008345.00] TO [G-2011-008-3345.00] CKT 1 | 8.2375 | 32.9076 | 32807.5584 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [MULLNCR7 345.00] TO [HOLT 7 345.00] CKT 1 | 8.2324 | 32.8608 | 32760.8235 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [PECULR 7 345.00] TO [PHILL 7 345.00] CKT 1 | 8.2278 | 32.8622 | 32762.1823 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [PECULR 7 345.00] TO [PECULR 5 161.00] TO [PECULRT 13.800] CKT 11 | 8.2328 | 32.864 | 32763.9647 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ST JOE 7 345.00] TO [G17-183-TAP 345.00] CKT 1 | 8.233 | 32.8672 | 32767.227 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ARCHIE 5 161.00] TO [G17-108-TAP 161.00] CKT 1 | 8.233 | 32.8649 | 32764.8536 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WINDSR 5 161.00] TO [5SEDALA 161.00] CKT 1 | 8.2331 | 32.8703 | 32770.2685 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HSNVL 5 161.00] TO [5SHARSNV 161.00] CKT 1 | 8.2331 | 32.8673 | 32767.2919 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HSNVL 5 161.00] TO [PHILL 5 161.00] CKT 1 | 8.2329 | 32.8611 | 32761.1141 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HSNVL 5 161.00] TO [HSNVL 2 69.000] CKT 1 | 8.2332 | 32.8694 | 32769.4267 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HSNVL 5 161.00] TO [HSNVL 2 69.000] CKT 2 | 8.2332 | 32.8694 | 32769.4253 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ADRIAN 5 161.00] TO [5BUTLER 161.00] CKT 1 | 8.2326 | 32.8519 | 32751.8802 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CLINTON5 161.00] TO [CLNTN N2 69.000] CKT 1 | 8.2332 | 32.8693 | 32769.304 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CLINTON5 161.00] TO [CLNTN S2 69.000] CKT 2 | 8.2332 | 32.8693 | 32769.2518 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ST JOE 5 161.00] TO [ST JOE_CAP5 161.00] CKT R | 8.2332 | 32.8666 | 32766.6125 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ST JOE 5 161.00] TO [COOK 5 161.00] CKT 1 | 8.2332 | 32.8691 | 32769.1101 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ST JOE 5 161.00] TO [WOODBIN5 161.00] CKT 1 | 8.2332 | 32.8692 | 32769.1573 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ST JOE 5 161.00] TO [AVENUECTY 5 161.00] CKT 1 | 8.233 | 32.8692 | 32769.2025 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP#1 13.800] CKT 1 | 8.2332 | 32.8693 | 32769.3034 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP#2 13.800] CKT 1 | 8.2332 | 32.8693 | 32769.3034 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP#3 13.800] CKT 1 | 8.2332 | 32.8693 | 32769.3034 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S.HARP 5 161.00] TO [S.HARP 2 69.000] CKT 1 | 8.2332 | 32.8689 | 32768.8859 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S.HARP 5 161.00] TO [PECULRS5 161.00] CKT 1 | 8.233 | 32.867 | 32767.0186 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EASTOWN7 345.00] TO [EASTOWN5 161.00] TO [EASTOWN1 13.800] CKT 11 | 8.2331 | 32.868 | 32767.9874 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [KETCHEM7 345.00] TO [SIBLEY 7 345.00] CKT 1 | 8.2323 | 32.8561 | 32756.086 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [KETCHEM7 345.00] TO [OSBORN7 345.00] CKT 1 | 8.234 | 32.8943 | 32794.2752 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ROCKCK7 345.00] TO [HOLT 7 345.00] CKT 1 | 8.2363 | 32.9665 | 32866.5307 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ROCKCK_T1_1 34.500] TO [ROCKCK_P1_1 34.500] CKT 1 | 8.234 | 32.8968 | 32796.8135 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ROCKCK_T2_1 34.500] TO [ROCKCK_P2_1 34.500] CKT 1 | 8.234 | 32.8959 | 32795.9456 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HOLT_REACT7 345.00] TO [HOLT 7 345.00] CKT Z1 | 8.2333 | 32.8696 | 32769.5962 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [OUTLAW 345.00] TO [OUTLAW_T2_1 34.500] TO [OUTLAW_TR2_113.800] CKT 1 | 8.2338 | 32.8877 | 32787.7257 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [OUTLAW 345.00] TO [OUTLAW_T1_1 34.500] TO [OUTLAW_TR1_113.800] CKT 1 | 8.234 | 32.897 | 32796.9566 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WGARDNR5 161.00] TO [W.GRDNR7 345.00] TO [WGAR T11 13.800] CKT 11 | 8.2312 | 32.8589 | 32758.9235 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [STILWEL7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 8.2279 | 32.8574 | 32757.3876 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [STILWEL5 161.00] TO [G17-108-TAP 161.00] CKT 1 | 8.2327 | 32.8626 | 32762.5715 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTH 7 345.00] TO [SIBLEY 7 345.00] CKT 1 | 8.2332 | 32.868 | 32768.0198 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTH 7 345.00] TO [HAWTHN5 161.00] TO [HAWT T20 13.800] CKT 20 | 8.2332 | 32.8684 | 32768.3555 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTH 7 345.00] TO [HAWTHN5 161.00] TO [HAWT T22 13.800] CKT 22 | 8.2332 | 32.8687 | 32768.6713 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTHS5 161.00] TO [HAW G9 1 13.800] CKT 1 | 8.2332 | 32.8693 | 32769.2925 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTHS5 161.00] TO [LEEDS 5 161.00] CKT 1 | 8.2332 | 32.8694 | 32769.3943 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTHS5 161.00] TO [LEEDS 5 161.00] CKT 2 | 8.2332 | 32.8694 | 32769.3834 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTH_B2_1 13.200] CKT 1 | 8.233 | 32.863 | 32762.9548 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTHS5 161.00] TO [BRMGHAM5 161.00] CKT 1 | 8.2331 | 32.8675 | 32767.5277 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHS_G65 161.00] CKT Z1 | 8.2332 | 32.8681 | 32768.1089 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHS_XF5 161.00] CKT Z2 | 8.2332 | 32.8692 | 32769.1991 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHN5 161.00] CKT @1 | 8.2332 | 32.8693 | 32769.2574 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHN5 161.00] CKT @2 | 8.2332 | 32.8693 | 32769.2574 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRAIG 7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 8.2288 | 32.8613 | 32761.299 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRAIG 5 161.00] TO [CRAIG_CAP 5 161.00] CKT R | 8.2333 | 32.8648 | 32764.8051 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRAIG 5 161.00] TO [PFLUMM 5 161.00] CKT 1 | 8.2328 | 32.8672 | 32767.1557 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRAIG 5 161.00] TO [LENEXA 5 161.00] CKT 1 | 8.233 | 32.8689 | 32768.8612 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRAIG 5 161.00] TO [LENEXA 5 161.00] CKT 2 | 8.2331 | 32.869 | 32769.0055 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRAIG 5 161.00] TO [COLLEGE5 161.00] CKT 1 | 8.2332 | 32.8675 | 32767.4836 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NASHUA 7 345.00] TO [G17-183-TAP 345.00] CKT 1 | 8.233 | 32.8619 | 32761.8954 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LACYGNE7 345.00] TO [W.GRDNR7 345.00] CKT 1 | 8.234 | 32.87 | 32769.9988 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LACYGNE7 345.00] TO [G17-209-TAP 345.00] CKT 1 | 8.2236 | 32.7828 | 32682.8065 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [IATAN 7 345.00] TO [STRANGR7 345.00] CKT 1 | 8.2278 | 32.8745 | 32774.5083 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [IATAN 7 345.00] TO [STRANGR7 345.00] CKT 2 | 8.2286 | 32.8735 | 32773.5214 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [IATAN 7 345.00] TO [IAT G1 1 24.000] CKT 1 | 8.2344 | 33.0747 | 32974.7349 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [IATAN 7 345.00] TO [IAT G2 1 24.500] CKT 1 | 8.2334 | 33.0659 | 32965.8682 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [IATAN 7 345.00] TO [IATAN5 161.00] TO [IATAN 11 14.400] CKT 11 | 8.233 | 32.8646 | 32764.608 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HICKMAN5 161.00] TO [STHTOWN5 161.00] CKT 1 | 8.2329 | 32.8698 | 32769.8115 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BLUMILS5 161.00] TO [BLUVLY-161 161.00] CKT 1 | 8.2332 | 32.8691 | 32769.1465 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NASHUA-5 161.00] TO [NASHUA 5 161.00] CKT Z1 | 8.2332 | 32.8684 | 32768.4447 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NASHUA-5 161.00] TO [RNRIDGE5 161.00] CKT 1 | 8.2332 | 32.869 | 32768.9998 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NASHUA-5 161.00] TO [SHOLCRK5 161.00] CKT 1 | 8.2331 | 32.8671 | 32767.145 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CEDRCRK5 161.00] TO [SHWNMSN5 161.00] CKT 1 | 8.2329 | 32.8689 | 32768.9176 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ANTIOCH5 161.00] TO [OXFORD 5 161.00] CKT 1 | 8.2333 | 32.87 | 32770.0133 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [REDEL 5 161.00] TO [MARTCIT5 161.00] CKT 1 | 8.2326 | 32.8693 | 32769.2906 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BUCYRUS5 161.00] TO [NLOUISB5 161.00] CKT 1 | 8.2331 | 32.866 | 32765.9737 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BUCYRUS5 161.00] TO [WAGSTAF5 161.00] CKT 1 | 8.2331 | 32.8667 | 32766.6654 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [PLSTVAL5 161.00] TO [SEOTTWA5 161.00] CKT 1 | 8.233 | 32.8657 | 32765.703 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [PLSTVAL5 161.00] TO [ASG-2018-010161.00] CKT 1 | 8.2335 | 32.8788 | 32778.817 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [PLSTVAL5 161.00] TO [PLSTVAL1 34.500] TO [PLSTVL2_TER17.6210] CKT 2 | 8.2331 | 32.8671 | 32767.0905 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LAKCTYJ2 69.000] TO [LAKCTY 2 69.000] CKT 1 | 8.2332 | 32.8693 | 32769.328 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 1 13.800] CKT 1 | 8.2332 | 32.8693 | 32769.3031 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 2 13.800] CKT 1 | 8.2332 | 32.8693 | 32769.3031 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 3 13.800] CKT 1 | 8.2332 | 32.8693 | 32769.3031 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BULLCRK5 161.00] TO [WG CT 4 13.800] CKT 1 | 8.2332 | 32.8693 | 32769.3031 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LACKMAN5 161.00] TO [SPRGHL 5 161.00] CKT 1 | 8.2331 | 32.8688 | 32768.7813 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BNSF 5 161.00] TO [MOONLT 5 161.00] CKT 1 | 8.2327 | 32.8673 | 32767.2845 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WGARDNR1 34.500] TO [BALDWINCTY1 34.500] CKT 1 | 8.2332 | 32.8693 | 32769.2696 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LACYGNE11_7 345.00] TO [LAC11_AQC1 13.800] TO [LAC11_TER1 13.800] CKT 11 | 8.2327 | 32.8589 | 32758.9086 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LACYGNE22_7 345.00] TO [LAC22_AQC1 13.800] TO [LAC22_TER1 13.800] CKT 22 | 8.2332 | 32.8693 | 32769.2908 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LACYGNE2 69.000] TO [LAC_LAKE_2 69.000] CKT 1 | 8.233 | 32.8653 | 32765.3275 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LAC3_STAR7 345.00] TO [LAC3_X1 6.9000] CKT X | 8.2332 | 32.8693 | 32769.2974 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LAC3_STAR7 345.00] TO [LAC3_Y1 6.9000] CKT Y | 8.2332 | 32.8693 | 32769.2974 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LAC3_STAR7 345.00] TO [LAC3_Z1 3.9800] CKT Z | 8.2332 | 32.8693 | 32769.2974 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LAC8_STAR7 345.00] TO [LAC8_X1 6.9000] CKT X | 8.2332 | 32.8693 | 32769.2974 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LAC8_STAR7 345.00] TO [LAC8_Y1 6.9000] CKT Y | 8.2332 | 32.8693 | 32769.2974 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [LAC8_STAR7 345.00] TO [LAC8_Z1 4.0000] CKT Z | 8.2332 | 32.8693 | 32769.2974 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [RIV4525 161.00] TO [ORO110 5 161.00] CKT 1 | 8.2333 | 32.8734 | 32773.3673 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [RIV4525 161.00] TO [STL439 5 161.00] CKT 1 | 8.2326 | 32.8746 | 32774.6497 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [RIV4525 161.00] TO [RIV452T 5 161.00] CKT 1 | 8.2312 | 32.8545 | 32754.4604 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [RIV4525 161.00] TO [BAX488 5 161.00] CKT 1 | 8.233 | 32.8687 | 32768.7176 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [RIV4525 161.00] TO [RIV167 2 69.000] TO [RIV452 1 12.500] CKT 1 | 8.2332 | 32.8682 | 32768.2195 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CJ 366 5 161.00] TO [ASB349 5 161.00] CKT 1 | 8.2328 | 32.8677 | 32767.6725 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CAR395 5 161.00] TO [CARTHAG5 161.00] CKT 1 | 8.2328 | 32.8679 | 32767.9309 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [FIR417 5 161.00] TO [ORO110 5 161.00] CKT 1 | 8.2329 | 32.8697 | 32769.6952 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [PUR421 5 161.00] TO [ASB349 5 161.00] CKT 1 | 8.2328 | 32.8668 | 32766.842 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [A1G349 1 13.800] TO [ASB349 5 161.00] CKT 1 | 8.2332 | 32.8704 | 32770.442 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [A2G349 1 13.800] TO [ASB349 5 161.00] CKT 1 | 8.2332 | 32.8693 | 32769.2974 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB K 69.000] TO [SUB R 69.000] CKT 1 | 8.2332 | 32.8693 | 32769.2878 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB H 69.000] TO [COURTNY2 69.000] CKT 1 | 8.2332 | 32.8692 | 32769.2297 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB H 69.000] TO [SUGRCK_TP_E269.000] CKT 1 | 8.2332 | 32.8693 | 32769.2775 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB H 69.000] TO [SUB H-13B1 13.800] CKT H1 | 8.2331 | 32.8665 | 32766.5171 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB H 69.000] TO [SUB H-13B2 13.800] CKT H2 | 8.2331 | 32.8694 | 32769.3673 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BLUVLY 69.000] TO [BLUVLY-161 161.00] CKT 1 | 8.2331 | 32.8693 | 32769.2698 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BLUVLY 69.000] TO [BLUVLY-161 161.00] CKT 2 | 8.2331 | 32.8693 | 32769.2688 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ECKLES-161 161.00] TO [5LEVASY 161.00] CKT 1 | 8.233 | 32.8662 | 32766.2097 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ECKLES-161 161.00] TO [5MOCITYB1 161.00] CKT 1 | 8.2332 | 32.8694 | 32769.418 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [ECKLES-161 161.00] TO [SIBLEYPL 161.00] CKT 1 | 8.2331 | 32.869 | 32768.9773 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB J 69.000] TO [SUB J-13B1 13.800] CKT J1 | 8.2331 | 32.8673 | 32767.2659 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB J 69.000] TO [SUB J-13B2 13.800] CKT J2 | 8.2331 | 32.8663 | 32766.2538 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB M-161 161.00] TO [BLUVLY-161 161.00] CKT 1 | 8.2332 | 32.8688 | 32768.7574 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB M 69.000] TO [SHRNKRD 69.000] CKT 1 | 8.2332 | 32.8693 | 32769.2886 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [SUB P 69.000] TO [SUB I 69.000] CKT 1 | 8.2332 | 32.8693 | 32769.2929 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [G16-046-TAP 345.00] TO [IRONWOOD7 345.00] CKT 1 | 8.2259 | 32.8561 | 32756.1189 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [G16-046-TAP 345.00] TO [GEN-2016-046345.00] CKT 1 | 8.2127 | 32.9646 | 32864.5895 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GEN-2017-004345.00] TO [G17-004XFMR134.500] CKT 1 | 8.2349 | 32.8955 | 32795.5396 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [G17-004-TAP 345.00] TO [ELMCREEK7 345.00] CKT 1 | 8.2133 | 32.8867 | 32786.7263 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GEN-2017-018345.00] TO [THISTLE7 345.00] CKT 1 | 8.2365 | 32.959 | 32858.9977 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [G17-018XFMR134.500] TO [G17-018-GSU134.500] CKT 1 | 8.235 | 32.9167 | 32816.6799 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [G17-018XFMR234.500] TO [G17-018-GSU234.500] CKT 1 | 8.235 | 32.9167 | 32816.6799 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GEN-2017-068138.00] TO [EVANS N4 138.00] CKT 1 | 8.241 | 33.2053 | 33105.2811 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [G17-068XFMR134.500] TO [G17-068-GSU134.500] CKT 1 | 8.2402 | 33.2344 | 33134.3506 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [GEN-2017-082161.00] TO [ASB349 5 161.00] CKT 1 | 8.2332 | 32.8681 | 32768.0698 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [G17-082XFMR134.500] TO [G17-082-GSU134.500] CKT 1 | 8.2332 | 32.8682 | 32768.1915 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [COOPER 3 345.00] TO [ATCHSN 3 345.00] CKT 1 | 8.2325 | 32.8563 | 32756.3054 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [COOPER 3 345.00] TO [COOPER1G 22.000] CKT 1 | 8.2398 | 33.0916 | 32991.5775 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [COOPER 3 345.00] TO [MONOLITH 3 345.00] CKT 1 | 8.2334 | 32.8745 | 32774.4666 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [COOPER 3 345.00] TO [COOPER 5 161.00] TO [COOPER T2 913.800] CKT 1 | 8.2332 | 32.8697 | 32769.6979 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [COOPER 3 345.00] TO [COOPER 5 161.00] TO [COOPER T5 913.800] CKT 1 | 8.2332 | 32.8697 | 32769.6673 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEBCTY1G 18.000] TO [NC1GA1X9 4.2000] TO [NC1GA1Y9 4.2000] CKT 1 | 8.2329 | 32.8635 | 32763.4871 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEBCTY1G 18.000] TO [NC1GA2X9 4.2000] TO [NC1GA2Y9 4.2000] CKT 1 | 8.2329 | 32.8635 | 32763.4867 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEBCTY2G 23.000] TO [NC2GA1X9 4.2000] TO [NC2GA1Y9 4.2000] CKT 1 | 8.2331 | 32.8665 | 32766.5319 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [NEBCTY2G 23.000] TO [NC2GA2X9 13.800] TO [NC2GA2Y9 13.800] CKT 1 | 8.2328 | 32.8545 | 32754.4906 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S3456 3 345.00] TO [CBLUFFS3 345.00] CKT 1 | 8.2332 | 32.8715 | 32771.5177 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S3456 3 345.00] TO [S3455 3 345.00] CKT 1 | 8.2332 | 32.8692 | 32769.21 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S3456 3 345.00] TO [S3459 3 345.00] CKT 1 | 8.2332 | 32.8697 | 32769.6555 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S3456 3 345.00] TO [S1206 5 161.00] TO [S3456T49 13.800] CKT 1 | 8.2332 | 32.8696 | 32769.6309 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S3458 3 345.00] TO [HOLT 7 345.00] CKT 1 | 8.2327 | 32.8727 | 32772.6652 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S3740 3 345.00] TO [CASS 1G 15.000] CKT 1 | 8.2346 | 32.9151 | 32815.1365 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S3740 3 345.00] TO [CASS 2G 15.000] CKT 1 | 8.2346 | 32.915 | 32814.9603 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S3740 3 345.00] TO [S3454 3 345.00] CKT 1 | 8.2332 | 32.8697 | 32769.7045 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S3740 3 345.00] TO [S3455 3 345.00] CKT 1 | 8.2332 | 32.8689 | 32768.9123 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [S3740 3 345.00] TO [GEN-2018-033345.00] CKT 1 | 8.2332 | 32.8693 | 32769.2955 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [103&ROKEBY3 345.00] TO [MOORE 3 345.00] CKT 1 | 8.2328 | 32.8677 | 32767.7078 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [103&ROKEBY3 345.00] TO [WAGENER 3 345.00] CKT 1 | 8.2331 | 32.8675 | 32767.5489 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [7SPORTSMAN 345.00] TO [5SPORTSMAN 161.00] CKT 2 | 8.232 | 32.8798 | 32779.8222 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [IDALIA 5 161.00] TO [2IDALIA 69.000] CKT 2 | 8.2332 | 32.8695 | 32769.4912 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WWRDEHV7 345.00] TO [TATONGA7 345.00] CKT 2 | 8.1964 | 32.6417 | 32541.7474 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WWRDEHV7 345.00] TO [G16-003-TAP 345.00] CKT 2 | 8.2084 | 32.9223 | 32822.2682 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [DGRASSE7 345.00] TO [THISTLE7 345.00] CKT 2 | 7.865 | 32.6652 | 32565.231 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 2 | 7.5964 | 34.7015 | 34601.4803 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [EVANS S4 138.00] TO [EVANS N4 138.00] CKT Z2 | 7.1574 | 31.7461 | 31646.057 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CLARKCOUNTY7345.00] TO [THISTLE7 345.00] CKT 2 | 8.1117 | 33.1097 | 33009.6881 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HSNVL 5 161.00] TO [HSNVL 2 69.000] CKT 2 | 8.2332 | 32.8698 | 32769.845 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTHS5 161.00] TO [LEEDS 5 161.00] CKT 2 | 8.233 | 32.8698 | 32769.7764 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [HAWTHS5 161.00] TO [HAWTHN5 161.00] CKT @2 | 8.2332 | 32.8634 | 32763.4074 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [CRAIG 5 161.00] TO [LENEXA 5 161.00] CKT 2 | 8.2322 | 32.8671 | 32767.1109 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [IATAN 7 345.00] TO [STRANGR7 345.00] CKT 2 | 8.1987 | 32.9199 | 32819.8659 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 03 CENTRAL | 25WP | GEN-2018-057 | Gordon Evans 138kV | OPEN LINE FROM [BLUVLY 69.000] TO [BLUVLY-161 161.00] CKT 2 | 8.233 | 32.8694 | 32769.3678 | 203.4 | 226 | PASS | PASS
DISIS-2018-001-2 | 02 NEBRASKA | 25SP | GEN-2018-060 | Axtell-Post Rock 345 kV | OPEN LINE FROM [AXTELL 3 345.00] TO [SWEET W3 345.00] CKT 1 | 9.7299 | 2.5188 | 2418.8245 | 50 | 50 | PASS | PASS
DISIS-2018-001-2 | 02 NEBRASKA | 25SP | GEN-2018-060 | Axtell-Post Rock 345 kV | OPEN LINE FROM [POSTROCK7 345.00] TO [G16-050-TAP 345.00] CKT 1 | 8.5881 | 2.4399 | 2339.8894 | 50 | 50 | PASS | PASS
DISIS-2018-001-2 | 02 NEBRASKA | 25SP | GEN-2018-060 | Axtell-Post Rock 345 kV | OPEN LINE FROM [AXTELL 3 345.00] TO [G16-050-TAP 345.00] CKT 1 | 3.9114 | 2.118 | 2018.0401 | 50 | 50 | FAIL | PASS
DISIS-2018-001-2 | 02 NEBRASKA | 25WP | GEN-2018-060 | Axtell-Post Rock 345 kV | OPEN LINE FROM [AXTELL 3 345.00] TO [SWEET W3 345.00] CKT 1 | 9.4945 | 2.6471 | 2547.0755 | 50 | 50 | PASS | PASS
DISIS-2018-001-2 | 02 NEBRASKA | 25WP | GEN-2018-060 | Axtell-Post Rock 345 kV | OPEN LINE FROM [POSTROCK7 345.00] TO [G16-050-TAP 345.00] CKT 1 | 8.3759 | 2.5112 | 2411.2475 | 50 | 50 | PASS | PASS
DISIS-2018-001-2 | 02 NEBRASKA | 25WP | GEN-2018-060 | Axtell-Post Rock 345 kV | OPEN LINE FROM [AXTELL 3 345.00] TO [G16-050-TAP 345.00] CKT 1 | 3.8661 | 2.0473 | 1947.3436 | 50 | 50 | FAIL | PASS

## WSCR
Study Name | GROUP | SEASON | Contingency | WSCR_value | POI 1 Gen 1 | POI 1 Gen 2 | POI 1 Gen 3 | POI 1 Gen 4 | POI 1 Gen 5 | POI 2 Gen 1 | POI 2 Gen 2 | POI 2 Gen 3 | POI 3 Gen 1 | POI 3 Gen 2 | POI 3 Gen 3 | POI 4 Gen 1 | POI 4 Gen 2 | POI 5 Gen 1 | POI 6 Gen 1 | POI 7 Gen 1 | POI 8 Gen 1 | PASS/FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | Base | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [MALLARD7 115.00] TO [LOGAN___-BE7115.00] CKT 1 | 3.7673 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [WASHBRN4 230.00] TO [LELAND_O-BE4230.00] CKT 1 | 2.6475 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 |  | GEN-2017-175 | [8 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [RASMUSN-ER4 230.00] TO [RASMUSN-ER8 69.000] CKT 1 | 2.656 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 |  | GEN-2017-175 | [8 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [SW.MINOT-CP7115.00] TO [SW.MNOT1-CP941.600] CKT 1 | 3.8968 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [SW.MINOT-CP7115.00] TO [SW.MNOT2-CP941.600] CKT 2 | 2.6553 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 |  | GEN-2017-175 | [8 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [SW.MINOT-CP7115.00] TO [BERTHOLD-CP7115.00] CKT 1 | 3.8351 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [SW.MINOT-CP7115.00] TO [E.RUTHVL-CP7115.00] CKT 1 | 3.8902 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [WHTEARTH-MW7115.00] TO [PLSNTV_T-MW7115.00] CKT 1 | 3.8938 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [PWRSLKTP-MW7115.00] TO [POWERSLK-MW7115.00] CKT 1 | 3.8947 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [PWRSLKTP-MW7115.00] TO [POWERSLK-MW7115.00] CKT 1 | 2.6548 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 |  | GEN-2017-175 | [8 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [PWRSLKTP-MW7115.00] TO [LIBERTY -MW7115.00] CKT 1 | 3.894 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [TIOGA.N_-MW7115.00] TO [W.BANK_T-MW7115.00] CKT 1 | 3.8722 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [MANNINGTAP 869.000] TO [TEMPLTON8 69.000] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [FTRANDL4 230.00] TO [UTICAJC4 230.00] CKT 1 | 3.8969 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [LELAND_O-BE3345.00] TO [GEN-2016-130345.00] CKT 1 | 3.8975 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [LELAND_O-BE3345.00] TO [FINSTAD345 345.00] CKT 1 | 3.4115 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [LELAND_O-BE3345.00] TO [ANTELOPE-BE3345.00] CKT 1 | 3.8941 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [LELAND_O-BE3345.00] TO [ANTELOPE-BE3345.00] CKT 2 | 3.8941 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [LELAND_O-BE3345.00] TO [LELAND_2-BEG20.000] CKT 1 | 3.8585 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [LELAND_O-BE3345.00] TO [LO.LS-GR-BE3345.00] CKT Z | 3.8785 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [LELAND_O-BE3345.00] TO [LO.LS-FT-BE3345.00] CKT Z | 3.8789 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [LELAND_O-BE4230.00] TO [LOGAN___-BE4230.00] CKT 1 | 3.5733 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [NESET___-BE7115.00] TO [NESET___-BE4230.00] TO [NES.KV2A-BE913.800] CKT 1 | 3.8619 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [NRTSHORE-BE4230.00] TO [NESET___-BE4230.00] CKT 1 | 3.846 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [FTRANDL4 230.00] TO [SIOUXCY4 230.00] CKT 1 | 3.8969 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [NRTSHORE-BE7115.00] TO [BROOKBNK-MW7115.00] CKT 1 | 3.8771 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [NRTSHORE-BE7115.00] TO [ROSS -MW7115.00] CKT 1 | 3.8948 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [NRTSHORE-BE7115.00] TO [ROSS -MW7115.00] CKT 1 | 2.6548 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 |  | GEN-2017-175 | [8 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [NRTSHORE-BE7115.00] TO [RATLAKE -MW7115.00] CKT 1 | 3.8968 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [NRTSHORE-BE7115.00] TO [SATTER -MW7115.00] CKT 1 | 3.8775 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [BLAISDEL-BE4230.00] TO [LOGAN___-BE4230.00] CKT 1 | 3.5097 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [BLAISDEL-BE7115.00] TO [BERTHOLD-CP7115.00] CKT 1 | 3.8773 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [BLAISDEL-BE7115.00] TO [PALERMO -MW7115.00] CKT 1 | 3.8887 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [BLAISDEL-BE7115.00] TO [BLAISDEL-MW7115.00] CKT 1 | 3.886 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [LOGAN___-BE7115.00] TO [LOGAN___-BE4230.00] TO [LGN.KW1A-BE913.800] CKT 1 | 3.708 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [BASIN___-BE4230.00] TO [GEN-2016-004230.00] CKT 1 | 3.8905 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [UTICAJC4 230.00] TO [PRVLNG16 230.00] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [BASIN___-BE4230.00] TO [BASIN___-BE7115.00] TO [BAL.KY1A-BE913.800] CKT 1 | 2.6554 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 |  | GEN-2017-175 | [8 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [BASIN___-BE4230.00] TO [BASIN___-BE7115.00] TO [BAL.KY1A-BE913.800] CKT 1 | 2.1729 | GEN-2017-222 |  |  |  |  | GEN-2017-215 | GEN-2017-214 |  | GEN-2018-010 | GEN-2017-048 |  | GEN-2017-175 | [5 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [TANDE___-BE3345.00] TO [FINSTAD345 345.00] CKT 1 | 3.591 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [TANDE___-BE3345.00] TO [BURKE___-PP3345.00] CKT 1 | 3.9085 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [TANDE___-BE3345.00] TO [TN.LS-JD-BE3345.00] CKT Z | 3.465 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [TANDE___-BE3345.00] TO [TRADEWND-UA3345.00] CKT 1 | 3.9115 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [TANDE___-BE4230.00] TO [NESET___-BE4230.00] CKT 1 | 3.0107 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [WHEELOCK-BE4230.00] TO [WILISTN4 230.00] CKT 1 | 3.6341 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [WHEELOCK-BE4230.00] TO [WHEELOCK-BE7115.00] TO [WEL.T1__-BE913.800] CKT 1 | 3.8864 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [J6BOYER_-NI869.000] TO [K335AMAI-NI869.000] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [J6BOYER_-NI869.000] TO [K307DENI-NI869.000] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [UTICAJC4 230.00] TO [RASMUSN-ER4 230.00] CKT 1 | 3.8969 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [J6BOYER_-NI869.000] TO [K306SCHL-NI869.000] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [J6BOYER_-NI869.000] TO [J12_____-NI869.000] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [TIOGA4 4 230.00] TO [NESET___-BE4230.00] CKT Z | 2.7639 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [TIOGA4 7 115.00] TO [STANLEY7 115.00] CKT 1 | 3.8767 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [TIOGA4 7 115.00] TO [TIOGA7 7 115.00] CKT 1 | 3.8373 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [BDV 4230.00] TO [BDX 4230.00] CKT 1 & 2 | 3.3109 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [FTRANDL4 230.00] TO [FTRANDL7 115.00] CKT 1 & 2 | 3.8969 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [LELAND_O-BE3345.00] TO [ANTELOPE-BE3345.00] CKT 1 & 2 | 3.8822 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [UTICAJC4 230.00] TO [UTICAJC7 115.00] TO [UTICAJC9 13.200] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [SIOUXCY2 230.00] TO [SIOUXCY4 230.00] CKT Z1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [DENISON5 161.00] TO [EXIRA 5 161.00] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [SIOUXCY4 230.00] TO [RASMUSN-ER4 230.00] CKT 1 | 3.8969 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [SIOUXCY4 230.00] TO [RASMUSN-ER4 230.00] CKT 1 | 2.5836 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 |  | GEN-2017-175 | [8 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [DENISON8 69.000] TO [MANNINGTAP 869.000] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [GRE-STANTON4230.00] TO [LELAND_O-BE4230.00] CKT 1 | 3.8744 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [DENISON8 69.000] TO [DENISONWEST869.000] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [DENISON8 69.000] TO [DENSOUMAIN8 69.000] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [DENISON8 69.000] TO [J6BOYER_-NI869.000] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [SW.MINOT-CP7115.00] TO [LOGAN___-BE7115.00] CKT 1 | 3.8789 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [HESS GAS-MW7115.00] TO [TIOGA.N_-MW7115.00] CKT Z | 3.8966 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [HESS GAS-MW7115.00] TO [NESET___-BE7115.00] CKT 1 | 3.8961 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [WHTEARTH-MW7115.00] TO [NESET___-BE7115.00] CKT 1 | 3.8934 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [PWRSLKTP-MW7115.00] TO [NESET___-BE7115.00] CKT 1 | 2.6533 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 |  | GEN-2017-175 | [8 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [TIOGA.N_-MW7115.00] TO [NESET___-BE7115.00] CKT 1 | 3.8959 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [DENISONWEST869.000] TO [DENSOUMAIN8 69.000] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [TWIN CH4 230.00] TO [SIOUXCY4 230.00] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [LELAND_O-BE3345.00] TO [LELAND_O-BE4230.00] TO [LO.KU1A_-BE913.800] CKT 1 | 3.8916 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [LELAND_O-BE3345.00] TO [LELAND_O-BE4230.00] TO [LO.KVA2_-BE913.800] CKT 1 | 3.8919 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [LELAND_O-BE4230.00] TO [LELAND_1-BEG22.000] CKT 1 | 3.8731 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [LELAND_O-BE4230.00] TO [BASIN___-BE4230.00] CKT 1 | 3.8899 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [NESET___-BE7115.00] TO [TIOGA4 7 115.00] CKT 1 | 3.8988 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [NRTSHORE-BE4230.00] TO [NRTSHORE-BE7115.00] TO [NRTSHORE-BE913.800] CKT 1 | 3.8429 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [BLAISDEL-BE4230.00] TO [TIOGA4 4 230.00] CKT 1 | 3.526 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [BLAISDEL-BE4230.00] TO [BLAISDEL-BE7115.00] TO [BLS.T1__-BE913.800] CKT 1 | 3.8729 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [BLAISDEL-BE4230.00] TO [BLAISDEL-BE7115.00] TO [BLS.T1__-BE913.800] CKT 1 | 2.6427 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 |  | GEN-2017-175 | [8 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [TANDE___-BE3345.00] TO [TANDE___-BE4230.00] TO [TND.KU3A-BE913.800] CKT 1 | 3.0106 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [WHEELOCK-BE4230.00] TO [TIOGA4 4 230.00] CKT 1 | 3.5704 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [SIOUXC39 13.800] TO [SIOUXCY4 230.00] TO [SIOUXCY5 161.00] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [TIOGA4 4 230.00] TO [BDV 4230.00] CKT 1 | 3.3174 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [TIOGA4 4 230.00] TO [TIOGA4 7 115.00] TO [TIOGA4 9 13.800] CKT 1 | 3.8618 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [MALLARD7 115.00] TO [SOURIS 7 115.00] CKT 1 | 2.6168 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 |  | GEN-2017-175 | [8 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [MALLARD7 115.00] TO [NELSON 7 115.00] CKT 1 | 3.8649 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [MALLARD7 115.00] TO [RUGBY 7 115.00] CKT 1 | 3.8768 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [MALLARD7 115.00] TO [MALLARD1-CP941.600] CKT 1 | 3.8967 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [MALLARD7 115.00] TO [MALLARD1-CP941.600] CKT 1 | 2.6559 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 |  | GEN-2017-175 | [8 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [MALLARD7 115.00] TO [MALLARD2-CP941.600] CKT 1 | 2.6558 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 |  | GEN-2017-175 | [8 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [MALLARD7 115.00] TO [MALLARD2-CP941.600] CKT 1 | 3.8966 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [MALLARD7 115.00] TO [E.RUTHVL-CP7115.00] CKT 1 | 3.8958 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [GRE-STANTON4230.00] TO [GRE-COAL CR4230.00] CKT 1 | 3.8955 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [GRE-STANTON4230.00] TO [GRE-COAL TP4230.00] CKT 1 | 3.8966 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [SIOUXC49 13.800] TO [SIOUXCY4 230.00] TO [SIOUXCY5 161.00] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [GRE-STANTON4230.00] TO [SQBUTTE4 230.00] CKT 1 | 3.8931 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [TWIN CH4 230.00] TO [WAKEFIELD 4230.00] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [TWIN CH4 230.00] TO [TWIN CH7 115.00] TO [TWIN CH T4 913.800] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [TWIN CH4 230.00] TO [TWIN CH7 115.00] TO [TWIN CH T6 913.800] CKT 2 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [VFODNES4 230.00] TO [G17-175TAP 230.00] CKT 1 | 3.8969 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [GARRISN4 230.00] TO [JAMESTN4 230.00] CKT 1 | 3.8928 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [GARRISN4 230.00] TO [GARISN1G 13.800] CKT 1 | 3.892 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [GARRISN4 230.00] TO [GARISN2G 13.800] CKT 1 | 3.892 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [GARRISN4 230.00] TO [GARISN3G 13.800] CKT 1 | 3.892 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [GARRISN4 230.00] TO [HILKEN 4 230.00] CKT 1 | 3.8937 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [VFODNES4 230.00] TO [SIOUXFL4 230.00] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [GARRISN4 230.00] TO [GARRISN7 115.00] TO [GARRISON 9 13.800] CKT 1 | 3.8839 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [WASHBRN4 230.00] TO [WASHBRN9 41.800] CKT 1 | 3.8968 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [WASHBRN4 230.00] TO [WASHBRN9 41.800] CKT 1 | 2.656 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 |  | GEN-2017-175 | [8 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [WASHBRN4 230.00] TO [BISMARK4 230.00] CKT 1 | 3.8821 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [FTRANDL4 230.00] TO [MEADOWGROVE4230.00] CKT 1 | 3.8969 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [FTRANDL4 230.00] TO [FTTHOMP4 230.00] CKT 1 | 3.8966 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [FTRANDL4 230.00] TO [FTRANDL7 115.00] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [FTRANDL4 230.00] TO [FTRANDL7 115.00] CKT 2 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [FTRANDL4 230.00] TO [FTRDL34G 13.800] CKT 1 | 3.8969 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [FTRANDL4 230.00] TO [FTRDL56G 13.800] CKT 1 | 3.8969 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [FTRANDL4 230.00] TO [FTRDL78G 13.800] CKT 1 | 3.8969 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [VFODNES4 230.00] TO [VFODNES-ER8 69.000] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [FTRANDL4 230.00] TO [LAKPLAT-ER4 230.00] CKT 1 | 3.8966 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [SIOUXFL4 230.00] TO [SPLT RK4 230.00] CKT 1 | 3.8969 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [SIOUXFL4 230.00] TO [HANLON 4 230.00] CKT 1 | 3.8968 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [SIOUXFL4 230.00] TO [LETCHER4 230.00] CKT 1 | 3.8968 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [SIOUXFL4 230.00] TO [PAHOJA__-BE4230.00] CKT 1 | 3.8969 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [SIOUXFL4 230.00] TO [SIOUXFL7 115.00] TO [SIOUXF19 13.200] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [SIOUXFL4 230.00] TO [SIOUXFL7 115.00] TO [SIOUXF29 13.200] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [UTICAJC4 230.00] TO [G17-175TAP 230.00] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [UTICAJC4 230.00] TO [G17-175TAP 230.00] CKT 1 | 2.3754 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 |  | GEN-2017-175 | [8 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [SIOUXCY2 230.00] TO [EAGLE___-NI4230.00] CKT 1 | 3.8969 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [SIOUXCY2 230.00] TO [SIOUXCY3 345.00] TO [SIOUXC19 13.800] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [VFODNES4 230.00] TO [VFODNES-ER7 115.00] TO [VFODNES1-ER912.500] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [SIOUXCY2 230.00] TO [SIOUXCY3 345.00] TO [SIOUXC29 13.800] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [DENISON5 161.00] TO [DENISON4 230.00] TO [DENISON 9 13.800] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [SIOUXCY4 230.00] TO [DENISON4 230.00] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [SIOUXCY5 161.00] TO [PLYMOTH5 161.00] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [SIOUXCY5 161.00] TO [SPENCER5 161.00] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [SIOUXCY5 161.00] TO [SIOUXCY8 69.000] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [DENISON8 69.000] TO [DENISON4 230.00] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [DENISON8 69.000] TO [DENISON4 230.00] CKT 2 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [EXIRA 5 161.00] TO [ANTA TP5 161.00] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [EXIRA 5 161.00] TO [EXIRA 1G 13.800] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [GARRISN4 230.00] TO [LELAND_O-BE4230.00] CKT 1 | 3.887 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [EXIRA 5 161.00] TO [EXIRA 2G 13.800] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [EXIRA 5 161.00] TO [EXIRA 3G 13.800] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [UTICAJC7 115.00] TO [FREEMAN-ER7 115.00] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [UTICAJC7 115.00] TO [MENNO JCT 7115.00] CKT 1 | 3.8969 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [UTICAJC7 115.00] TO [NAPA JCT 7115.00] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [PRVLNG16 230.00] TO [PRVLNG23 115.00] TO [PRVLNGT21 13.800] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [VFODNES-ER7 115.00] TO [SXFCHCLR-ER7115.00] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [VFODNES-ER7 115.00] TO [BUCKSNRT-ER7115.00] CKT 1 | 2.6559 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 |  | GEN-2017-175 | [8 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [VFODNES-ER7 115.00] TO [SW1109-ER7 115.00] CKT 1 | 2.6559 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 |  | GEN-2017-175 | [8 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25SP | OPEN LINE FROM [VFODNES-ER7 115.00] TO [DAYTON__-ER7115.00] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | Base | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [MALLARD7 115.00] TO [LOGAN___-BE7115.00] CKT 1 | 3.7888 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [WASHBRN4 230.00] TO [LELAND_O-BE4230.00] CKT 1 | 3.9043 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [RASMUSN-ER4 230.00] TO [RASMUSN-ER8 69.000] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [SW.MINOT-CP7115.00] TO [SW.MNOT1-CP941.600] CKT 1 | 3.9194 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [SW.MINOT-CP7115.00] TO [SW.MNOT2-CP941.600] CKT 2 | 3.9169 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [SW.MINOT-CP7115.00] TO [BERTHOLD-CP7115.00] CKT 1 | 3.858 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [SW.MINOT-CP7115.00] TO [E.RUTHVL-CP7115.00] CKT 1 | 3.913 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [WHTEARTH-MW7115.00] TO [PLSNTV_T-MW7115.00] CKT 1 | 3.917 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [PWRSLKTP-MW7115.00] TO [POWERSLK-MW7115.00] CKT 1 | 3.9156 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [PWRSLKTP-MW7115.00] TO [POWERSLK-MW7115.00] CKT 1 | 2.6583 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 |  | GEN-2017-175 | [8 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [PWRSLKTP-MW7115.00] TO [LIBERTY -MW7115.00] CKT 1 | 3.9103 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [TIOGA.N_-MW7115.00] TO [W.BANK_T-MW7115.00] CKT 1 | 3.8925 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [MANNINGTAP 869.000] TO [TEMPLTON8 69.000] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [FTRANDL4 230.00] TO [UTICAJC4 230.00] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [LELAND_O-BE3345.00] TO [GEN-2016-130345.00] CKT 1 | 3.9203 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [LELAND_O-BE3345.00] TO [FINSTAD345 345.00] CKT 1 | 3.4446 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [LELAND_O-BE3345.00] TO [ANTELOPE-BE3345.00] CKT 1 | 3.9163 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [LELAND_O-BE3345.00] TO [ANTELOPE-BE3345.00] CKT 2 | 3.9163 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [LELAND_O-BE3345.00] TO [LELAND_2-BEG20.000] CKT 1 | 3.8843 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [LELAND_O-BE3345.00] TO [LO.LS-GR-BE3345.00] CKT Z | 3.9022 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [LELAND_O-BE3345.00] TO [LO.LS-FT-BE3345.00] CKT Z | 3.903 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [LELAND_O-BE4230.00] TO [LOGAN___-BE4230.00] CKT 1 | 3.6015 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [NESET___-BE7115.00] TO [NESET___-BE4230.00] TO [NES.KV2A-BE913.800] CKT 1 | 3.8845 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [NRTSHORE-BE4230.00] TO [NESET___-BE4230.00] CKT 1 | 3.8681 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [FTRANDL4 230.00] TO [SIOUXCY4 230.00] CKT 1 | 3.9197 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [NRTSHORE-BE7115.00] TO [BROOKBNK-MW7115.00] CKT 1 | 3.901 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [NRTSHORE-BE7115.00] TO [ROSS -MW7115.00] CKT 1 | 3.9155 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [NRTSHORE-BE7115.00] TO [RATLAKE -MW7115.00] CKT 1 | 3.9217 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [NRTSHORE-BE7115.00] TO [SATTER -MW7115.00] CKT 1 | 3.901 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [BLAISDEL-BE4230.00] TO [LOGAN___-BE4230.00] CKT 1 | 3.5318 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [BLAISDEL-BE7115.00] TO [BERTHOLD-CP7115.00] CKT 1 | 3.8994 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [BLAISDEL-BE7115.00] TO [PALERMO -MW7115.00] CKT 1 | 3.9126 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [BLAISDEL-BE7115.00] TO [BLAISDEL-MW7115.00] CKT 1 | 3.9085 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [LOGAN___-BE7115.00] TO [LOGAN___-BE4230.00] TO [LGN.KW1A-BE913.800] CKT 1 | 3.7271 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [BASIN___-BE4230.00] TO [GEN-2016-004230.00] CKT 1 | 3.9138 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [UTICAJC4 230.00] TO [PRVLNG16 230.00] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [BASIN___-BE4230.00] TO [BASIN___-BE7115.00] TO [BAL.KY1A-BE913.800] CKT 1 | 3.919 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [TANDE___-BE3345.00] TO [FINSTAD345 345.00] CKT 1 | 3.6154 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [TANDE___-BE3345.00] TO [BURKE___-PP3345.00] CKT 1 | 3.931 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [TANDE___-BE3345.00] TO [TN.LS-JD-BE3345.00] CKT Z | 3.4748 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [TANDE___-BE3345.00] TO [TRADEWND-UA3345.00] CKT 1 | 3.9305 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [TANDE___-BE4230.00] TO [NESET___-BE4230.00] CKT 1 | 3.021 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [WHEELOCK-BE4230.00] TO [WILISTN4 230.00] CKT 1 | 3.6547 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [WHEELOCK-BE4230.00] TO [WHEELOCK-BE7115.00] TO [WEL.T1__-BE913.800] CKT 1 | 3.9096 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [J6BOYER_-NI869.000] TO [K335AMAI-NI869.000] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [J6BOYER_-NI869.000] TO [K307DENI-NI869.000] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [UTICAJC4 230.00] TO [RASMUSN-ER4 230.00] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [J6BOYER_-NI869.000] TO [K306SCHL-NI869.000] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [J6BOYER_-NI869.000] TO [J12_____-NI869.000] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [TIOGA4 4 230.00] TO [NESET___-BE4230.00] CKT Z | 2.7715 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [TIOGA4 7 115.00] TO [STANLEY7 115.00] CKT 1 | 3.8999 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [TIOGA4 7 115.00] TO [TIOGA7 7 115.00] CKT 1 | 3.8577 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [BDV 4230.00] TO [BDX 4230.00] CKT 1 & 2 | 3.3428 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [FTRANDL4 230.00] TO [FTRANDL7 115.00] CKT 1 & 2 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [LELAND_O-BE3345.00] TO [ANTELOPE-BE3345.00] CKT 1 & 2 | 3.8964 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [UTICAJC4 230.00] TO [UTICAJC7 115.00] TO [UTICAJC9 13.200] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [SIOUXCY2 230.00] TO [SIOUXCY4 230.00] CKT Z1 | 3.9199 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [DENISON5 161.00] TO [EXIRA 5 161.00] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [SIOUXCY4 230.00] TO [RASMUSN-ER4 230.00] CKT 1 | 3.9197 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [DENISON8 69.000] TO [MANNINGTAP 869.000] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [GRE-STANTON4230.00] TO [LELAND_O-BE4230.00] CKT 1 | 2.648 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 |  | GEN-2017-175 | [8 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [GRE-STANTON4230.00] TO [LELAND_O-BE4230.00] CKT 1 | 2.1559 | GEN-2017-222 |  |  |  |  | GEN-2017-215 | GEN-2017-214 |  | GEN-2018-010 | GEN-2017-048 |  | GEN-2017-175 | [5 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [DENISON8 69.000] TO [DENISONWEST869.000] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [DENISON8 69.000] TO [DENSOUMAIN8 69.000] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [DENISON8 69.000] TO [J6BOYER_-NI869.000] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [SW.MINOT-CP7115.00] TO [LOGAN___-BE7115.00] CKT 1 | 3.902 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [HESS GAS-MW7115.00] TO [TIOGA.N_-MW7115.00] CKT Z | 3.9196 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [HESS GAS-MW7115.00] TO [NESET___-BE7115.00] CKT 1 | 3.9188 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [WHTEARTH-MW7115.00] TO [NESET___-BE7115.00] CKT 1 | 3.9162 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [PWRSLKTP-MW7115.00] TO [NESET___-BE7115.00] CKT 1 | 3.9073 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [TIOGA.N_-MW7115.00] TO [NESET___-BE7115.00] CKT 1 | 3.9186 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [DENISONWEST869.000] TO [DENSOUMAIN8 69.000] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [TWIN CH4 230.00] TO [SIOUXCY4 230.00] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [LELAND_O-BE3345.00] TO [LELAND_O-BE4230.00] TO [LO.KU1A_-BE913.800] CKT 1 | 3.9147 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [LELAND_O-BE3345.00] TO [LELAND_O-BE4230.00] TO [LO.KVA2_-BE913.800] CKT 1 | 3.9151 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [LELAND_O-BE4230.00] TO [LELAND_1-BEG22.000] CKT 1 | 3.897 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [LELAND_O-BE4230.00] TO [BASIN___-BE4230.00] CKT 1 | 3.913 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [NESET___-BE7115.00] TO [TIOGA4 7 115.00] CKT 1 | 3.9251 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [NRTSHORE-BE4230.00] TO [NRTSHORE-BE7115.00] TO [NRTSHORE-BE913.800] CKT 1 | 3.8647 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [BLAISDEL-BE4230.00] TO [TIOGA4 4 230.00] CKT 1 | 3.5471 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [BLAISDEL-BE4230.00] TO [BLAISDEL-BE7115.00] TO [BLS.T1__-BE913.800] CKT 1 | 2.6471 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 |  | GEN-2017-175 | [8 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [TANDE___-BE3345.00] TO [TANDE___-BE4230.00] TO [TND.KU3A-BE913.800] CKT 1 | 3.0209 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [WHEELOCK-BE4230.00] TO [TIOGA4 4 230.00] CKT 1 | 3.583 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [SIOUXC39 13.800] TO [SIOUXCY4 230.00] TO [SIOUXCY5 161.00] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [TIOGA4 4 230.00] TO [BDV 4230.00] CKT 1 | 3.3498 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [TIOGA4 4 230.00] TO [TIOGA4 7 115.00] TO [TIOGA4 9 13.800] CKT 1 | 3.8843 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [MALLARD7 115.00] TO [SOURIS 7 115.00] CKT 1 | 3.8493 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [MALLARD7 115.00] TO [NELSON 7 115.00] CKT 1 | 3.8867 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [MALLARD7 115.00] TO [RUGBY 7 115.00] CKT 1 | 3.9004 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [MALLARD7 115.00] TO [MALLARD1-CP941.600] CKT 1 | 3.919 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [MALLARD7 115.00] TO [MALLARD2-CP941.600] CKT 1 | 3.9188 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [MALLARD7 115.00] TO [E.RUTHVL-CP7115.00] CKT 1 | 3.9185 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [GRE-STANTON4230.00] TO [GRE-COAL CR4230.00] CKT 1 | 3.9183 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [GRE-STANTON4230.00] TO [GRE-COAL TP4230.00] CKT 1 | 3.9194 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [SIOUXC49 13.800] TO [SIOUXCY4 230.00] TO [SIOUXCY5 161.00] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [GRE-STANTON4230.00] TO [SQBUTTE4 230.00] CKT 1 | 3.916 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [TWIN CH4 230.00] TO [WAKEFIELD 4230.00] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [TWIN CH4 230.00] TO [TWIN CH7 115.00] TO [TWIN CH T4 913.800] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [TWIN CH4 230.00] TO [TWIN CH7 115.00] TO [TWIN CH T6 913.800] CKT 2 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [VFODNES4 230.00] TO [G17-175TAP 230.00] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [GARRISN4 230.00] TO [JAMESTN4 230.00] CKT 1 | 3.9159 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [GARRISN4 230.00] TO [GARISN1G 13.800] CKT 1 | 3.9149 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [GARRISN4 230.00] TO [GARISN2G 13.800] CKT 1 | 3.9149 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [GARRISN4 230.00] TO [GARISN3G 13.800] CKT 1 | 3.9149 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [GARRISN4 230.00] TO [HILKEN 4 230.00] CKT 1 | 3.9172 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [VFODNES4 230.00] TO [SIOUXFL4 230.00] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [GARRISN4 230.00] TO [GARRISN7 115.00] TO [GARRISON 9 13.800] CKT 1 | 3.9085 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [WASHBRN4 230.00] TO [WASHBRN9 41.800] CKT 1 | 3.9197 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [WASHBRN4 230.00] TO [BISMARK4 230.00] CKT 1 | 2.6522 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 |  | GEN-2017-175 | [8 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [FTRANDL4 230.00] TO [MEADOWGROVE4230.00] CKT 1 | 3.9197 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [FTRANDL4 230.00] TO [FTTHOMP4 230.00] CKT 1 | 3.9195 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [FTRANDL4 230.00] TO [FTRANDL7 115.00] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [FTRANDL4 230.00] TO [FTRANDL7 115.00] CKT 2 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [FTRANDL4 230.00] TO [FTRDL34G 13.800] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [FTRANDL4 230.00] TO [FTRDL56G 13.800] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [FTRANDL4 230.00] TO [FTRDL78G 13.800] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [VFODNES4 230.00] TO [VFODNES-ER8 69.000] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [FTRANDL4 230.00] TO [LAKPLAT-ER4 230.00] CKT 1 | 3.9195 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [SIOUXFL4 230.00] TO [SPLT RK4 230.00] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [SIOUXFL4 230.00] TO [HANLON 4 230.00] CKT 1 | 3.9197 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [SIOUXFL4 230.00] TO [LETCHER4 230.00] CKT 1 | 3.9196 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [SIOUXFL4 230.00] TO [PAHOJA__-BE4230.00] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [SIOUXFL4 230.00] TO [SIOUXFL7 115.00] TO [SIOUXF19 13.200] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [SIOUXFL4 230.00] TO [SIOUXFL7 115.00] TO [SIOUXF29 13.200] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [UTICAJC4 230.00] TO [G17-175TAP 230.00] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [SIOUXCY2 230.00] TO [EAGLE___-NI4230.00] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [SIOUXCY2 230.00] TO [SIOUXCY3 345.00] TO [SIOUXC19 13.800] CKT 1 | 3.9199 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [VFODNES4 230.00] TO [VFODNES-ER7 115.00] TO [VFODNES1-ER912.500] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [SIOUXCY2 230.00] TO [SIOUXCY3 345.00] TO [SIOUXC29 13.800] CKT 1 | 3.9199 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [DENISON5 161.00] TO [DENISON4 230.00] TO [DENISON 9 13.800] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [SIOUXCY4 230.00] TO [DENISON4 230.00] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [SIOUXCY5 161.00] TO [PLYMOTH5 161.00] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [SIOUXCY5 161.00] TO [SPENCER5 161.00] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [SIOUXCY5 161.00] TO [SIOUXCY8 69.000] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [DENISON8 69.000] TO [DENISON4 230.00] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [DENISON8 69.000] TO [DENISON4 230.00] CKT 2 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [EXIRA 5 161.00] TO [ANTA TP5 161.00] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [EXIRA 5 161.00] TO [EXIRA 1G 13.800] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [GARRISN4 230.00] TO [LELAND_O-BE4230.00] CKT 1 | 3.9104 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [EXIRA 5 161.00] TO [EXIRA 2G 13.800] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [EXIRA 5 161.00] TO [EXIRA 3G 13.800] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [UTICAJC7 115.00] TO [FREEMAN-ER7 115.00] CKT 1 | 2.6605 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 |  | GEN-2017-175 | [8 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [UTICAJC7 115.00] TO [MENNO JCT 7115.00] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [UTICAJC7 115.00] TO [NAPA JCT 7115.00] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [PRVLNG16 230.00] TO [PRVLNG23 115.00] TO [PRVLNGT21 13.800] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [VFODNES-ER7 115.00] TO [SXFCHCLR-ER7115.00] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [VFODNES-ER7 115.00] TO [BUCKSNRT-ER7115.00] CKT 1 | 2.6605 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 |  | GEN-2017-175 | [8 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [VFODNES-ER7 115.00] TO [SW1109-ER7 115.00] CKT 1 | 2.6605 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 |  | GEN-2017-175 | [8 empty] | FAIL
DISIS-2018-001-2 | 01 NORTH | 25WP | OPEN LINE FROM [VFODNES-ER7 115.00] TO [DAYTON__-ER7115.00] CKT 1 | 3.9198 | GEN-2017-215 | GEN-2017-214 |  |  |  | GEN-2018-010 | GEN-2017-048 | [10 empty] | FAIL
DISIS-2018-001-2 | 02 NEBRASKA | 25SP | OPEN LINE FROM [POSTROCK7 345.00] TO [G16-050-TAP 345.00] CKT 1 | 2.6392 | GEN-2018-060 | GEN-2016-050 |  |  |  | GEN-2017-144 | GEN-2015-023 |  | GEN-2017-182 | GEN-2017-181 | GEN-2015-088 | GEN-2017-234 | [5 empty] | FAIL
DISIS-2018-001-2 | 02 NEBRASKA | 25SP | OPEN LINE FROM [POSTROCK7 345.00] TO [G16-050-TAP 345.00] CKT 1 | 3.3727 | GEN-2018-060 | GEN-2016-050 |  |  |  | GEN-2017-210 |  |  | GEN-2017-144 | GEN-2015-023 | [7 empty] | FAIL
DISIS-2018-001-2 | 02 NEBRASKA | 25SP | OPEN LINE FROM [POSTROCK7 345.00] TO [G16-050-TAP 345.00] CKT 1 | 3.0952 | GEN-2018-060 | GEN-2016-050 |  |  |  | GEN-2017-144 | GEN-2015-023 |  | GEN-2017-234 | [8 empty] | FAIL
DISIS-2018-001-2 | 02 NEBRASKA | 25SP | OPEN LINE FROM [POSTROCK7 345.00] TO [G16-050-TAP 345.00] CKT 1 | 5.0214 | GEN-2018-060 | GEN-2016-050 |  |  |  | GEN-2017-182 | GEN-2017-181 | GEN-2015-088 | [9 empty] | FAIL
DISIS-2018-001-2 | 02 NEBRASKA | 25SP | OPEN LINE FROM [MOORE 3 345.00] TO [TOBIAS 3345.00] CKT 1 | 2.1799 | GEN-2018-060 | GEN-2016-050 |  |  |  | GEN-2017-182 | GEN-2017-181 | GEN-2015-088 | [9 empty] | FAIL
DISIS-2018-001-2 | 02 NEBRASKA | 25WP | OPEN LINE FROM [POSTROCK7 345.00] TO [G16-050-TAP 345.00] CKT 1 | 3.0301 | GEN-2018-060 | GEN-2016-050 |  |  |  | GEN-2017-144 | GEN-2015-023 |  | GEN-2017-234 | [8 empty] | FAIL
DISIS-2018-001-2 | 02 NEBRASKA | 25WP | OPEN LINE FROM [POSTROCK7 345.00] TO [G16-050-TAP 345.00] CKT 1 | 3.2648 | GEN-2018-060 | GEN-2016-050 |  |  |  | GEN-2017-210 |  |  | GEN-2017-144 | GEN-2015-023 | [7 empty] | FAIL
DISIS-2018-001-2 | 02 NEBRASKA | 25WP | OPEN LINE FROM [POSTROCK7 345.00] TO [G16-050-TAP 345.00] CKT 1 | 4.813 | GEN-2018-060 | GEN-2016-050 |  |  |  | GEN-2017-234 | [11 empty] | FAIL
DISIS-2018-001-2 | 02 NEBRASKA | 25WP | OPEN LINE FROM [POSTROCK7 345.00] TO [G16-050-TAP 345.00] CKT 1 | 4.8362 | GEN-2018-060 | GEN-2016-050 |  |  |  | GEN-2017-182 | GEN-2017-181 | GEN-2015-088 | [9 empty] | FAIL
DISIS-2018-001-2 | 02 NEBRASKA | 25WP | OPEN LINE FROM [MOORE 3 345.00] TO [TOBIAS 3345.00] CKT 1 | 2.1296 | GEN-2018-060 | GEN-2016-050 |  |  |  | GEN-2017-182 | GEN-2017-181 | GEN-2015-088 | [9 empty] | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | OPEN LINE FROM [RENO 7 345.00] TO [WICHITA7 345.00] CKT 1 | 4.3933 | GEN-2017-119 |  |  |  |  | GEN-2018-013 | GEN-2017-120 | [10 empty] | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25SP | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 2 | 2.4744 | GEN-2017-221 | GEN-2017-220 | GEN-2015-090 | GEN-2015-025 | GEN-2015-024 | GEN-2018-049 | GEN-2017-018 | [10 empty] | FAIL
DISIS-2018-001-2 | 03 CENTRAL | 25WP | OPEN LINE FROM [WICHITA7 345.00] TO [BUFFALO7 345.00] CKT 2 | 2.4285 | GEN-2017-221 | GEN-2017-220 | GEN-2015-090 | GEN-2015-025 | GEN-2015-024 | GEN-2018-049 | GEN-2017-018 | [10 empty] | FAIL
DISIS-2018-001-2 | 04 SOUTHEAST | 25SP | OPEN LINE FROM [L.E.S.-7 345.00] TO [G17-171-TAP 345.00] CKT 1 | 3.7945 | GEN-2018-055 |  |  |  |  | GEN-2017-167 |  |  | GEN-2017-173 | GEN-2017-172 | GEN-2017-171 | [6 empty] | FAIL
DISIS-2018-001-2 | 04 SOUTHEAST | 25WP | OPEN LINE FROM [L.E.S.-7 345.00] TO [G17-171-TAP 345.00] CKT 1 | 3.7382 | GEN-2018-055 |  |  |  |  | GEN-2017-167 |  |  | GEN-2017-173 | GEN-2017-172 | GEN-2017-171 | [6 empty] | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | Base | 3.4731 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | Base | 6.1416 | GEN-2017-151 |  |  |  |  | GEN-2018-015 | [11 empty] | PASS
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | Base | 4.6049 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2018-004 |  |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | Base | 3.1175 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [O.K.U.-7 345.00] TO [L.E.S.-7 345.00] CKT 1 | 2.5072 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLSNT_HILL 6230.00] TO [ROOSEVELT 6230.00] CKT 1 | 2.7367 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLSNT_HILL 6230.00] TO [ROOSEVELT 6230.00] CKT 1 | 3.1178 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [NEWHART 6230.00] TO [NEWHART 3115.00] TO [NEWHART_TR2113.200] CKT 2 | 2.7364 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [NEWHART 6230.00] TO [NEWHART 3115.00] TO [NEWHART_TR2113.200] CKT 2 | 3.1175 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [NEWHART 6230.00] TO [NEWHART 3115.00] TO [NEWHART_TR1113.200] CKT 1 | 2.7364 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [NEWHART 6230.00] TO [NEWHART 3115.00] TO [NEWHART_TR1113.200] CKT 1 | 3.1175 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLANT_X 3115.00] TO [MULSHVLY_TP3115.00] CKT 1 | 2.738 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLANT_X 3115.00] TO [MULSHVLY_TP3115.00] CKT 1 | 3.1195 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLANT_X 3115.00] TO [BC-EARTH 3115.00] CKT 1 | 2.7333 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLANT_X 3115.00] TO [BC-EARTH 3115.00] CKT 1 | 3.1147 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLANT_X 3115.00] TO [RKYFORD_TP 3115.00] CKT 1 | 2.7332 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLANT_X 3115.00] TO [RKYFORD_TP 3115.00] CKT 1 | 3.1137 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLANT_X 3115.00] TO [HALE_CNTY 3115.00] CKT 1 | 2.7331 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLANT_X 3115.00] TO [HALE_CNTY 3115.00] CKT 1 | 3.1137 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLANT_X 3115.00] TO [PLANT_X1 113.800] CKT 1 | 2.7364 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLANT_X 3115.00] TO [PLANT_X1 113.800] CKT 1 | 3.1175 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLANT_X 3115.00] TO [PLANT_X2 113.800] CKT 1 | 2.7364 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLANT_X 3115.00] TO [PLANT_X2 113.800] CKT 1 | 3.1175 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLANT_X 3115.00] TO [PLANT_X3 113.800] CKT 1 | 2.7364 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLANT_X 3115.00] TO [PLANT_X3 113.800] CKT 1 | 3.1175 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLANT_X 6230.00] TO [TOLK 6230.00] CKT 1 | 2.6969 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLANT_X 6230.00] TO [TOLK 6230.00] CKT 1 | 3.0731 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [OASIS 6230.00] TO [ROOSEVELT 6230.00] CKT 1 | 2.7343 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [OASIS 6230.00] TO [ROOSEVELT 6230.00] CKT 1 | 3.1149 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLANT_X 6230.00] TO [TOLK 6230.00] CKT 2 | 2.6947 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLANT_X 6230.00] TO [TOLK 6230.00] CKT 2 | 3.0708 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLANT_X 6230.00] TO [G17-146-TAP 230.00] CKT 1 | 2.6383 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLANT_X 6230.00] TO [G17-146-TAP 230.00] CKT 1 | 3.089 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLANT_X 6230.00] TO [G17-146-TAP 230.00] CKT 1 | 3.3374 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TOLK_TR 113.200] TO [TOLK 7345.00] TO [TOLK 6230.00] CKT 1 | 2.7062 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TOLK_TR 113.200] TO [TOLK 7345.00] TO [TOLK 6230.00] CKT 1 | 3.0812 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TOLK_TR 113.200] TO [TOLK 7345.00] TO [TOLK 6230.00] CKT 1 | 3.4313 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TOLK_TR 2 13.200] TO [TOLK 7345.00] TO [TOLK 6230.00] CKT 2 | 2.7062 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TOLK_TR 2 13.200] TO [TOLK 7345.00] TO [TOLK 6230.00] CKT 2 | 3.0812 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TOLK_TR 2 13.200] TO [TOLK 7345.00] TO [TOLK 6230.00] CKT 2 | 3.4313 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TOLK_1 124.000] TO [TOLK 6230.00] CKT 1 | 2.5499 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TOLK_1 124.000] TO [TOLK 6230.00] CKT 1 | 2.8956 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TOLK_2 124.000] TO [TOLK 6230.00] CKT 1 | 2.5469 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TOLK_2 124.000] TO [TOLK 6230.00] CKT 1 | 2.8919 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [BLUECLDPOI 6230.00] TO [BLUECLDCOL 6230.00] CKT 1 | 2.7274 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [BLUECLDPOI 6230.00] TO [BLUECLDCOL 6230.00] CKT 1 | 3.1067 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [NEEDMORE 6230.00] TO [TOLK 6230.00] CKT 1 | 2.6672 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [NEEDMORE 6230.00] TO [TOLK 6230.00] CKT 1 | 3.0344 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [LAMB_CNTY 3115.00] TO [HOCKLEY 3115.00] CKT 1 | 2.7263 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [LAMB_CNTY 3115.00] TO [HOCKLEY 3115.00] CKT 1 | 3.1055 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [LAMB_CNTY 3115.00] TO [LAMB_CNTY 269.000] TO [LAMB_TR1 113.200] CKT 1 | 2.7364 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [LAMB_CNTY 3115.00] TO [LAMB_CNTY 269.000] TO [LAMB_TR1 113.200] CKT 1 | 3.1175 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [ROSEVLT_TR1113.200] TO [ROOSEVELT 6230.00] TO [ROOSEVELT 3115.00] CKT 1 | 2.7352 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [ROSEVLT_TR1113.200] TO [ROOSEVELT 6230.00] TO [ROOSEVELT 3115.00] CKT 1 | 3.1162 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [ROSEVLT_TR1113.200] TO [ROOSEVELT 6230.00] TO [ROOSEVELT 3115.00] CKT 1 | 3.4715 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [LAMB_CNTY 3115.00] TO [LAMB_CNTY 269.000] TO [LAMB_TR2 113.200] CKT 2 | 2.7364 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [LAMB_CNTY 3115.00] TO [LAMB_CNTY 269.000] TO [LAMB_TR2 113.200] CKT 2 | 3.1175 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [LAMB_CNTY 6230.00] TO [TOLK 6230.00] CKT 1 | 2.7248 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [LAMB_CNTY 6230.00] TO [TOLK 6230.00] CKT 1 | 3.1036 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 3115.00] TO [HALE_CNTY 3115.00] CKT 1 | 2.7329 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 3115.00] TO [HALE_CNTY 3115.00] CKT 1 | 3.1135 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 3115.00] TO [FLOYD_CNTY 3115.00] CKT 1 | 2.7358 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 3115.00] TO [FLOYD_CNTY 3115.00] CKT 1 | 3.1168 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 3115.00] TO [STANTON_W 3115.00] CKT 1 | 2.7354 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 3115.00] TO [STANTON_W 3115.00] CKT 1 | 3.1163 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 3115.00] TO [LUBBCK_EST 3115.00] CKT 1 | 2.7342 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 3115.00] TO [LUBBCK_EST 3115.00] CKT 1 | 3.1148 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 3115.00] TO [TUCO_INT2 269.000] TO [TUCO_TR7 113.200] CKT 1 | 2.7355 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 3115.00] TO [TUCO_INT2 269.000] TO [TUCO_TR7 113.200] CKT 1 | 3.1164 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 3115.00] TO [TUCO_INT 269.000] TO [TUCO_TR5 113.200] CKT 2 | 2.7364 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 3115.00] TO [TUCO_INT 269.000] TO [TUCO_TR5 113.200] CKT 2 | 3.1174 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 3115.00] TO [TUCO_INT 269.000] TO [TUCO_TR6 113.200] CKT 1 | 2.7364 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 3115.00] TO [TUCO_INT 269.000] TO [TUCO_TR6 113.200] CKT 1 | 3.1174 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 6230.00] TO [TOLK 6230.00] CKT 1 | 2.6541 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 6230.00] TO [TOLK 6230.00] CKT 1 | 3.0186 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SWISHER 6230.00] TO [NEWHART 6230.00] CKT 1 | 2.7258 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SWISHER 6230.00] TO [NEWHART 6230.00] CKT 1 | 3.1054 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 7345.00] TO [G17-151TAP 345.00] CKT 1 | 4.5891 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2018-004 |  |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 7345.00] TO [G17-151TAP 345.00] CKT 1 | 1.651 | GEN-2017-151 |  |  |  |  | GEN-2018-015 | [11 empty] | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [ANTELOPE_1 6230.00] TO [ANTELOPE_A 113.800] CKT 1 | 2.7296 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [ANTELOPE_1 6230.00] TO [ANTELOPE_A 113.800] CKT 1 | 3.1094 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [ANTELOPE_1 6230.00] TO [ANTELOPE_B 113.800] CKT 1 | 2.7294 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [ANTELOPE_1 6230.00] TO [ANTELOPE_B 113.800] CKT 1 | 3.1091 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [ANTELOPE_1 6230.00] TO [ANTELOPE_C 113.800] CKT 1 | 2.7364 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [ANTELOPE_1 6230.00] TO [ANTELOPE_C 113.800] CKT 1 | 3.1175 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [ELK_CT1 345.00] TO [ELK_1 118.000] CKT 1 | 2.733 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [ELK_CT1 345.00] TO [ELK_2 1 18.000] CKT 1 | 2.7042 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [HALE_WNDCL16230.00] TO [HALEWD_COL1134.500] TO [HALE_WD_TR1113.200] CKT 1 | 2.7373 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [HALE_WNDCL16230.00] TO [HALEWD_COL1134.500] TO [HALE_WD_TR1113.200] CKT 1 | 3.1185 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [HALE_WNDCL16230.00] TO [HALEWD_COL2134.500] TO [HALE_WD_TR2113.200] CKT 1 | 2.7374 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [HALE_WNDCL16230.00] TO [HALEWD_COL2134.500] TO [HALE_WD_TR2113.200] CKT 1 | 3.1186 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [HALE_WNDCL16230.00] TO [HALEWD_COL3134.500] TO [HALE_WD_TR3113.200] CKT 1 | 2.7373 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [HALE_WNDCL16230.00] TO [HALEWD_COL3134.500] TO [HALE_WD_TR3113.200] CKT 1 | 3.1185 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CARLISLE 6230.00] TO [WOLFFORTH 6230.00] CKT 1 | 2.7302 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CARLISLE 6230.00] TO [WOLFFORTH 6230.00] CKT 1 | 3.11 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SWISHER 6230.00] TO [TUCO_INT 6230.00] CKT 1 | 2.7198 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SWISHER 6230.00] TO [TUCO_INT 6230.00] CKT 1 | 3.0985 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SWISHER 6230.00] TO [TUCO_INT 6230.00] CKT 1 | 3.4532 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CARLISLE 6230.00] TO [CARLISLE 3115.00] TO [CRLSLE_TR1 113.200] CKT 1 | 2.7361 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CARLISLE 6230.00] TO [CARLISLE 3115.00] TO [CRLSLE_TR1 113.200] CKT 1 | 3.1171 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [JONES 6230.00] TO [LUBBCK_STH 6230.00] CKT 1 | 2.7353 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [JONES 6230.00] TO [LUBBCK_STH 6230.00] CKT 1 | 3.1162 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [JONES 6230.00] TO [LUBBCK_STH 6230.00] CKT 2 | 2.7353 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [JONES 6230.00] TO [LUBBCK_STH 6230.00] CKT 2 | 3.1162 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [JONES 6230.00] TO [LUBBCK_EST 6230.00] CKT 1 | 2.7357 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [JONES 6230.00] TO [LUBBCK_EST 6230.00] CKT 1 | 3.1166 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [JONES 6230.00] TO [JONES_1 122.000] CKT 1 | 2.7287 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [JONES 6230.00] TO [JONES_1 122.000] CKT 1 | 3.1082 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [JONES 6230.00] TO [JONES_2 122.000] CKT 1 | 2.729 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [JONES 6230.00] TO [JONES_2 122.000] CKT 1 | 3.1087 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [JONES 6230.00] TO [JONES_3 116.500] CKT 1 | 2.7271 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [JONES 6230.00] TO [JONES_3 116.500] CKT 1 | 3.1063 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [JONES 6230.00] TO [JONES_4 116.500] CKT 1 | 2.7298 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [JONES 6230.00] TO [JONES_4 116.500] CKT 1 | 3.1096 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [JONES 6230.00] TO [GRASSLAND 6230.00] CKT 1 | 2.7367 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [JONES 6230.00] TO [GRASSLAND 6230.00] CKT 1 | 3.1179 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SUNDOWN 6230.00] TO [AMOCO_SS 6230.00] CKT 1 | 2.6984 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [NEWHART 6230.00] TO [PLANT_X 6230.00] CKT 1 | 2.7088 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [NEWHART 6230.00] TO [PLANT_X 6230.00] CKT 1 | 3.0845 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SUNDOWN 6230.00] TO [WOLFFORTH 6230.00] CKT 1 | 2.7136 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SUNDOWN 6230.00] TO [WOLFFORTH 6230.00] CKT 1 | 3.0903 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SUNDOWN 6230.00] TO [SUNDOWN 3115.00] TO [SUNDOWN_TR1113.800] CKT 1 | 2.7358 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SUNDOWN 6230.00] TO [SUNDOWN 3115.00] TO [SUNDOWN_TR1113.800] CKT 1 | 3.1167 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [LG-CLAUENE 3115.00] TO [LG-LEVELAND3115.00] CKT 1 | 2.7311 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [LG-CLAUENE 3115.00] TO [LG-LEVELAND3115.00] CKT 1 | 3.1111 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [WOLFFORTH 3115.00] TO [YUMA_INT 3115.00] CKT 1 | 2.734 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [WOLFFORTH 3115.00] TO [YUMA_INT 3115.00] CKT 1 | 3.1145 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [WOLFFORTH 3115.00] TO [WOLFFORTH 6230.00] TO [WOLFRTH_TR1113.200] CKT 1 | 2.7354 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [WOLFFORTH 3115.00] TO [WOLFFORTH 6230.00] TO [WOLFRTH_TR1113.200] CKT 1 | 3.1163 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TERRY_CNTY 269.000] TO [LG-DOCWEBR 269.000] CKT 1 | 2.7353 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TERRY_CNTY 269.000] TO [LG-DOCWEBR 269.000] CKT 1 | 3.1162 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TERRY_CNTY 269.000] TO [LG-BROWNFLD269.000] CKT 1 | 2.7349 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TERRY_CNTY 269.000] TO [LG-BROWNFLD269.000] CKT 1 | 3.1157 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TERRY_CNTY 3115.00] TO [FLATLAND 3115.00] CKT 1 | 2.7112 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TERRY_CNTY 3115.00] TO [FLATLAND 3115.00] CKT 1 | 3.087 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [AMOCOWASSON6230.00] TO [XTO_MAHONEY6230.00] CKT 1 | 2.5825 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [AMOCOWASSON6230.00] TO [XTO_MAHONEY6230.00] CKT 1 | 2.9315 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PRENTICE 3115.00] TO [YOAKUM 3115.00] CKT 1 | 2.733 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PRENTICE 3115.00] TO [YOAKUM 3115.00] CKT 1 | 3.1134 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLANTX_TR1 113.200] TO [PLANT_X 6230.00] TO [PLANT_X 3115.00] CKT 1 | 2.7325 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLANTX_TR1 113.200] TO [PLANT_X 6230.00] TO [PLANT_X 3115.00] CKT 1 | 3.1128 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [YOAKUM 6230.00] TO [AMOCO_SS 6230.00] CKT 1 | 2.6981 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [YOAKUM 6230.00] TO [AMOCO_SS 6230.00] CKT 1 | 3.0715 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [YOAKUM 6230.00] TO [INK_BASIN 6230.00] CKT 1 | 2.6946 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [YOAKUM 6230.00] TO [INK_BASIN 6230.00] CKT 1 | 3.067 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [YOAKUM 6230.00] TO [YOAKUM 3115.00] TO [YOAKUM_TR1 113.200] CKT 1 | 2.732 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [YOAKUM 6230.00] TO [YOAKUM 3115.00] TO [YOAKUM_TR2 113.200] CKT 2 | 2.7321 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [YOAKUM 6230.00] TO [YOAKUM_345 345.00] TO [YOAKUM_TR1 13.200] CKT 1 | 2.6525 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [YOAKUM 6230.00] TO [YOAKUM_345 345.00] TO [YOAKUM_TR1 13.200] CKT 1 | 3.016 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [BRU_SUB 6230.00] TO [XTO_MAHONEY6230.00] CKT 1 | 2.5127 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [BRU_SUB 6230.00] TO [XTO_MAHONEY6230.00] CKT 1 | 2.847 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [DENVER_N 3115.00] TO [EL_PASO 3115.00] CKT 1 | 2.7358 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [DENVER_N 3115.00] TO [EL_PASO 3115.00] CKT 1 | 3.1168 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [DENVER_N 3115.00] TO [HIGGEAST 3115.00] CKT 1 | 2.7302 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [DENVER_N 3115.00] TO [HIGGEAST 3115.00] CKT 1 | 3.11 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [DENVER_N 3115.00] TO [DENVER_CTY 269.000] TO [DNVER_N_TR1113.200] CKT 1 | 2.7364 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [DENVER_N 3115.00] TO [DENVER_CTY 269.000] TO [DNVER_N_TR1113.200] CKT 1 | 3.1174 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MUSTANG 3115.00] TO [SHELL_CO2 3115.00] CKT 1 | 2.7359 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MUSTANG 3115.00] TO [SHELL_CO2 3115.00] CKT 1 | 3.1169 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLANT_X 3115.00] TO [LAMB_CNTY 3115.00] CKT 1 | 2.7347 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLANT_X 3115.00] TO [LAMB_CNTY 3115.00] CKT 1 | 3.1157 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MUSTANG 3115.00] TO [DENVER_S 3115.00] CKT 2 | 2.7361 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MUSTANG 3115.00] TO [DENVER_S 3115.00] CKT 2 | 3.1171 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MUSTANG 3115.00] TO [MUSTANG_1 118.000] CKT 1 | 2.7179 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MUSTANG 3115.00] TO [MUSTANG_1 118.000] CKT 1 | 3.0951 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MUSTANG 3115.00] TO [MUSTANG_2 118.000] CKT 1 | 2.7192 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MUSTANG 3115.00] TO [MUSTANG_2 118.000] CKT 1 | 3.0967 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MUSTANG 3115.00] TO [SEMINOLE 3115.00] CKT 1 | 2.7354 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MUSTANG 3115.00] TO [SEMINOLE 3115.00] CKT 1 | 3.1163 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MUSTANG 3115.00] TO [MUSTANG 6230.00] TO [MUSTANG_TR1113.200] CKT 1 | 2.7166 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MUSTANG 3115.00] TO [MUSTANG 6230.00] TO [MUSTANG_TR1113.200] CKT 1 | 3.0935 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MUSTANG 6230.00] TO [MUSTANG_3 119.000] CKT 1 | 2.7053 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MUSTANG 6230.00] TO [MUSTANG_3 119.000] CKT 1 | 3.0798 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MUSTANG 6230.00] TO [SEMINOLE 6230.00] CKT 1 | 2.7216 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MUSTANG 6230.00] TO [SEMINOLE 6230.00] CKT 1 | 3.0996 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [LG-PLSHILL 3115.00] TO [YOAKUM 3115.00] CKT 1 | 2.7287 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [LG-PLSHILL 3115.00] TO [YOAKUM 3115.00] CKT 1 | 3.1081 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SEAGRAVES 269.000] TO [LG-WELLMAN 269.000] CKT 1 | 2.7363 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SEAGRAVES 269.000] TO [LG-WELLMAN 269.000] CKT 1 | 3.1173 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SEAGRAVES 269.000] TO [MOSS 269.000] CKT 1 | 2.7357 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLANT_X 6230.00] TO [PLANT_X4 120.000] CKT 1 | 2.6571 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLANT_X 6230.00] TO [PLANT_X4 120.000] CKT 1 | 3.0254 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SEAGRAVES 269.000] TO [LG-MC&SMNL+269.000] CKT 1 | 2.7359 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SEAGRAVES 3115.00] TO [FLATLAND 3115.00] CKT 1 | 2.701 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SEAGRAVES 3115.00] TO [FLATLAND 3115.00] CKT 1 | 3.0747 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [DIAMONDBACK269.000] TO [OZRK_MAH02 269.000] CKT 1 | 2.7359 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [DIAMONDBACK269.000] TO [OZRK_MAH02 269.000] CKT 1 | 3.4725 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [DIAMONDBACK269.000] TO [LG-ASHMORE 269.000] CKT 1 | 2.7362 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [DIAMONDBACK269.000] TO [LG-ASHMORE 269.000] CKT 1 | 3.1172 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [DIAMONDBACK269.000] TO [OXY_CEDRLKE269.000] CKT 1 | 2.736 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [DIAMONDBACK269.000] TO [OXY_CEDRLKE269.000] CKT 1 | 3.117 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [DIAMONDBACK3115.00] TO [FLATLAND 3115.00] CKT 1 | 2.7346 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SULPHUR 269.000] TO [ADAIR 269.000] CKT 1 | 2.7356 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SULPHUR 269.000] TO [LG-FOSTER +269.000] CKT 1 | 2.7355 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SULPHUR 3115.00] TO [FLATLAND 3115.00] CKT 1 | 2.7364 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SULPHUR 3115.00] TO [FLATLAND 3115.00] CKT 1 | 3.1175 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SULPHUR 3115.00] TO [FLATLAND 3115.00] CKT 2 | 2.7364 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SULPHUR 3115.00] TO [FLATLAND 3115.00] CKT 2 | 3.1175 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLANT_X 6230.00] TO [SUNDOWN 6230.00] CKT 1 | 2.6965 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLANT_X 6230.00] TO [SUNDOWN 6230.00] CKT 1 | 3.0713 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CROSSROADS 7345.00] TO [SAGA_SCOL 7345.00] CKT 1 | 2.7406 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CROSSROADS 7345.00] TO [SAGA_SCOL 7345.00] CKT 1 | 3.1224 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CROSSROADS 7345.00] TO [RSVLT_CC_E 7345.00] CKT 1 | 2.714 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CROSSROADS 7345.00] TO [RSVLT_CC_E 7345.00] CKT 1 | 3.0907 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CROSSROADS 7345.00] TO [EDDY_CNTY 7345.00] CKT 1 | 2.7291 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CROSSROADS 7345.00] TO [EDDY_CNTY 7345.00] CKT 1 | 3.1087 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [CUNINGHAM1 113.800] CKT 1 | 2.7364 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [CUNINGHAM1 113.800] CKT 1 | 3.1175 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [CUNINGHAM4 113.800] CKT 1 | 2.7284 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [CUNINGHAM4 113.800] CKT 1 | 3.1078 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [BUCKEYE_TP 3115.00] CKT 1 | 2.7364 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [BUCKEYE_TP 3115.00] CKT 1 | 3.1175 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [QUAHADA 3115.00] CKT 1 | 2.7352 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [QUAHADA 3115.00] CKT 1 | 3.116 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [MONUMNT_TP 3115.00] CKT 1 | 2.7287 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [MONUMNT_TP 3115.00] CKT 1 | 3.1082 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [CUNNIGHM_S 6230.00] TO [CUNNHM_TR1 113.200] CKT 1 | 2.7312 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [CUNNIGHM_S 6230.00] TO [CUNNHM_TR1 113.200] CKT 1 | 3.1112 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [HOBBS_INT 3115.00] TO [HOBBS_PLT1 118.000] CKT 1 | 2.7248 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [HOBBS_INT 3115.00] TO [HOBBS_PLT1 118.000] CKT 1 | 3.1034 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [O.K.U.-7 345.00] TO [OKLAUN HVDC7345.00] CKT 1 | 2.7368 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [O.K.U.-7 345.00] TO [OKLAUN HVDC7345.00] CKT 1 | 3.118 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TOLK 7345.00] TO [CROSSROADS 7345.00] CKT 1 | 2.6405 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TOLK 7345.00] TO [CROSSROADS 7345.00] CKT 1 | 3.0032 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [HOBBS_INT 3115.00] TO [HOBBS_PLT2 118.000] CKT 1 | 3.4559 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [HOBBS_INT 3115.00] TO [HOBBS_PLT2 118.000] CKT 1 | 2.7249 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [HOBBS_INT 3115.00] TO [HOBBS_PLT2 118.000] CKT 1 | 3.1035 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [HOBBS_INT 3115.00] TO [LE-WEST_SUB3115.00] CKT 1 | 2.7327 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [HOBBS_INT 3115.00] TO [BENSING 3115.00] CKT 1 | 2.7326 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [HOBBS_INT 3115.00] TO [BENSING 3115.00] CKT 1 | 3.1129 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [HOBBS_INT 3115.00] TO [MILLEN_TPW 3115.00] CKT 1 | 2.7357 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [HOBBS_INT 3115.00] TO [MILLEN_TPW 3115.00] CKT 1 | 3.1166 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [HOBBS_INT 3115.00] TO [HOBBS_INT 6230.00] TO [HOBBS_TR1 113.200] CKT 1 | 2.7314 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [HOBBS_INT 3115.00] TO [HOBBS_INT 6230.00] TO [HOBBS_TR1 113.200] CKT 1 | 3.1114 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [HOBBS_INT 3115.00] TO [HOBBS_INT 6230.00] TO [HOBBS_TR2 113.200] CKT 2 | 2.7289 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [HOBBS_INT 3115.00] TO [HOBBS_INT 6230.00] TO [HOBBS_TR2 113.200] CKT 2 | 3.1084 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [HOBBS_INT 7345.00] TO [HOBBS_INT 6230.00] TO [HOBBS_TR3 113.200] CKT 1 | 2.7146 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [HOBBS_INT 7345.00] TO [HOBBS_INT 6230.00] TO [HOBBS_TR3 113.200] CKT 1 | 3.0913 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [HOBBS_INT 7345.00] TO [HOBBS_INT 6230.00] TO [HOBBS_TR3 113.200] CKT 1 | 3.4431 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [KIOWA 7345.00] TO [EDDY_CNTY 7345.00] CKT 1 | 2.7293 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [KIOWA 7345.00] TO [N_LOVING 7345.00] CKT 1 | 2.7338 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [KIOWA 7345.00] TO [N_LOVING 7345.00] CKT 1 | 3.1143 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [KIOWA 7345.00] TO [KIOWA 3115.00] TO [KIOWA_TR1 113.200] CKT 1 | 2.7342 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [KIOWA 7345.00] TO [KIOWA 3115.00] TO [KIOWA_TR1 113.200] CKT 1 | 3.1148 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [BLUECLDPOI 6230.00] TO [NEEDMORE 6230.00] CKT Z1 | 2.7274 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [BLUECLDPOI 6230.00] TO [NEEDMORE 6230.00] CKT Z1 | 3.1067 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PHANTOM 7345.00] TO [CHINA_DRAW 7345.00] CKT 1 | 2.7346 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PHANTOM 7345.00] TO [CHINA_DRAW 7345.00] CKT 1 | 3.1153 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PHANTOM 7345.00] TO [PHANTOM 3115.00] TO [PHANTOM TR1113.200] CKT 1 | 2.7359 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PHANTOM 7345.00] TO [PHANTOM 3115.00] TO [PHANTOM TR1113.200] CKT 1 | 3.1169 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PHANTOM 7345.00] TO [PHANTOM 3115.00] TO [PHANTOM TR2113.200] CKT 2 | 2.7359 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PHANTOM 7345.00] TO [PHANTOM 3115.00] TO [PHANTOM TR2113.200] CKT 2 | 3.1169 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SAND_DUNES 3115.00] TO [WIPP 3115.00] CKT 1 | 2.7321 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SAND_DUNES 3115.00] TO [WIPP 3115.00] CKT 1 | 3.1123 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [RED_BLUFF 3115.00] TO [RDRUNNER 3115.00] CKT 1 | 2.717 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [RED_BLUFF 3115.00] TO [RDRUNNER 3115.00] CKT 1 | 3.094 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [RDRNNER_TR1113.200] TO [RDRUNNER 7345.00] TO [RDRUNNER 3115.00] CKT 1 | 2.6393 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [RR_SVC_HV 3115.00] TO [RDRUNNER 3115.00] CKT Z1 | 2.7374 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [BATTLE_AXE 3115.00] TO [RDRUNNER 3115.00] CKT 1 | 2.7345 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [BATTLE_AXE 3115.00] TO [RDRUNNER 3115.00] CKT 1 | 3.1152 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [AGAVE_RHILL3115.00] TO [RDRUNNER 3115.00] CKT 1 | 2.7356 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [AGAVE_RHIL23115.00] TO [RDRUNNER 3115.00] CKT 1 | 2.7334 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [AGAVE_RHIL23115.00] TO [RDRUNNER 3115.00] CKT 1 | 3.1138 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [NEEDMORE 6230.00] TO [YOAKUM 6230.00] CKT 1 | 2.6709 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [NEEDMORE 6230.00] TO [YOAKUM 6230.00] CKT 1 | 3.0387 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [WOLFCAMP_TP3115.00] TO [BOPCO_PKRLK3115.00] CKT 1 | 2.7284 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [WOLFCAMP_TP3115.00] TO [BOPCO_PKRLK3115.00] CKT 1 | 3.1078 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [WOLFCAMP_TP3115.00] TO [WOLFCAMP 3115.00] CKT 1 | 2.7358 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [WOLFCAMP_TP3115.00] TO [WOLFCAMP 3115.00] CKT 1 | 3.1167 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CUSTERMTN 3115.00] TO [RDRUNNER 3115.00] CKT 1 | 2.7143 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CUSTERMTN 3115.00] TO [RDRUNNER 3115.00] CKT 1 | 3.0908 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MADDOXG23 3115.00] TO [MADDOX_2 113.800] CKT 1 | 2.7317 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MADDOXG23 3115.00] TO [MADDOX_2 113.800] CKT 1 | 3.1118 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MADDOXG23 3115.00] TO [MADDOX_3 112.500] CKT 1 | 2.7364 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MADDOXG23 3115.00] TO [MADDOX_3 112.500] CKT 1 | 3.1175 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MADDOX 3115.00] TO [G18-004-TAP 115.00] CKT 1 | 2.6433 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PEARLE 3115.00] TO [ENRON_TP 3115.00] CKT 1 | 2.7342 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PEARLE 3115.00] TO [ENRON_TP 3115.00] CKT 1 | 3.1148 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SANGER_SW 3115.00] TO [G18-004-TAP 115.00] CKT 1 | 2.7297 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SANGER_SW 3115.00] TO [G18-004-TAP 115.00] CKT 1 | 3.1094 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SW_4J44 3115.00] TO [OXY_S_HOBBS3115.00] CKT 1 | 2.7361 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SW_4J44 3115.00] TO [OXY_S_HOBBS3115.00] CKT 1 | 3.1171 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SW_4J44 3115.00] TO [W_HOBBS 3115.00] CKT 1 | 2.7361 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SW_4J44 3115.00] TO [W_HOBBS 3115.00] CKT 1 | 3.1171 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [LAMB_TR3 113.200] TO [LAMB_CNTY 6230.00] TO [LAMB_CNTY 3115.00] CKT 1 | 2.7238 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [LAMB_TR3 113.200] TO [LAMB_CNTY 6230.00] TO [LAMB_CNTY 3115.00] CKT 1 | 3.1024 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MONUMENT 3115.00] TO [MONUMENT 112.470] CKT 1 | 2.7358 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MONUMENT 3115.00] TO [MONUMENT 112.470] CKT 1 | 3.1167 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MONUMENT 3115.00] TO [W_HOBBS 3115.00] CKT 1 | 2.7346 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MONUMENT 3115.00] TO [W_HOBBS 3115.00] CKT 1 | 3.1153 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [WHITTEN 3115.00] TO [WARD 3115.00] CKT 1 | 2.7286 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [WHITTEN 3115.00] TO [WARD 3115.00] CKT 1 | 3.1081 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [WHITTEN 3115.00] TO [S_JAL 3115.00] CKT 1 | 2.7288 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [WHITTEN 3115.00] TO [S_JAL 3115.00] CKT 1 | 3.1083 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [OXYPERMIAN 3115.00] TO [OXY_NHU_RCF3115.00] CKT 1 | 2.7298 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [OXYPERMIAN 3115.00] TO [OXY_NHU_RCF3115.00] CKT 1 | 3.1094 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [GEN-2016-121115.00] TO [RDRUNNER 3115.00] CKT 1 | 2.7381 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [GEN-2016-121115.00] TO [RDRUNNER 3115.00] CKT 1 | 3.1195 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [G16-121XFMR134.500] TO [G16-121-GSU134.500] CKT 1 | 2.7381 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [G16-121XFMR134.500] TO [G16-121-GSU134.500] CKT 1 | 3.1195 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [GEN-2017-033345.00] TO [G17-033XFMR134.500] CKT 1 | 2.7366 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [GEN-2017-033345.00] TO [G17-033XFMR134.500] CKT 1 | 3.1177 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [GEN-2017-033345.00] TO [G17-033XFMR234.500] CKT 1 | 2.7367 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [GEN-2017-033345.00] TO [G17-033XFMR234.500] CKT 1 | 3.1178 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [ROOSEVELT 6230.00] TO [TOLK 6230.00] CKT 2 | 2.7154 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [ROOSEVELT 6230.00] TO [TOLK 6230.00] CKT 2 | 3.0927 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_TR3 113.200] TO [TUCO_INT 6230.00] TO [TUCO_INT 3115.00] CKT 2 | 2.7347 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_TR3 113.200] TO [TUCO_INT 6230.00] TO [TUCO_INT 3115.00] CKT 2 | 3.1155 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLANT_X 6230.00] TO [TOLK 6230.00] CKT 2 | 2.5216 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLANT_X 6230.00] TO [TOLK 6230.00] CKT 2 | 2.8777 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [JONES 6230.00] TO [LUBBCK_STH 6230.00] CKT 2 | 2.7232 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [JONES 6230.00] TO [LUBBCK_STH 6230.00] CKT 2 | 3.1018 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SULPHUR 3115.00] TO [FLATLAND 3115.00] CKT 2 | 2.7348 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_SVC 113.000] TO [TUCO_INT 6230.00] CKT 1 | 2.7334 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_SVC 113.000] TO [TUCO_INT 6230.00] CKT 1 | 3.1139 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_TR4 113.200] TO [TUCO_INT 6230.00] TO [TUCO_INT 3115.00] CKT 1 | 2.7346 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_TR4 113.200] TO [TUCO_INT 6230.00] TO [TUCO_INT 3115.00] CKT 1 | 3.1153 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_TR4 113.200] TO [TUCO_INT 6230.00] TO [TUCO_INT 3115.00] CKT 1 | 3.4711 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_TR1 113.200] TO [TUCO_INT 7345.00] TO [TUCO_INT 6230.00] CKT 1 | 2.6974 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_TR1 113.200] TO [TUCO_INT 7345.00] TO [TUCO_INT 6230.00] CKT 1 | 3.0704 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_TR1 113.200] TO [TUCO_INT 7345.00] TO [TUCO_INT 6230.00] CKT 1 | 3.4265 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_TR2 113.200] TO [TUCO_INT 7345.00] TO [TUCO_INT 6230.00] CKT 2 | 2.7052 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_TR2 113.200] TO [TUCO_INT 7345.00] TO [TUCO_INT 6230.00] CKT 2 | 3.0798 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_TR2 113.200] TO [TUCO_INT 7345.00] TO [TUCO_INT 6230.00] CKT 2 | 3.4358 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 6230.00] TO [ANTELOPE_1 6230.00] CKT 1 | 2.7222 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 6230.00] TO [ANTELOPE_1 6230.00] CKT 1 | 3.1005 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [O.K.U.-7 345.00] TO [GEN-2017-033345.00] CKT 1 | 2.7368 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [O.K.U.-7 345.00] TO [GEN-2017-033345.00] CKT 1 | 3.1179 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 6230.00] TO [HALE_WNDCL16230.00] CKT 1 | 3.4758 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 6230.00] TO [HALE_WNDCL16230.00] CKT 1 | 3.1209 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 6230.00] TO [HALE_WNDCL16230.00] CKT 1 | 4.6061 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2018-004 |  |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 6230.00] TO [CARLISLE 6230.00] CKT 1 | 2.7268 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 6230.00] TO [CARLISLE 6230.00] CKT 1 | 3.1058 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 6230.00] TO [JONES 6230.00] CKT 1 | 2.7149 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 6230.00] TO [JONES 6230.00] CKT 1 | 3.0916 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 7345.00] TO [ELK_CT1 345.00] CKT 1 | 2.6992 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 7345.00] TO [ELK_CT1 345.00] CKT 1 | 3.0727 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 7345.00] TO [YOAKUM_345 345.00] CKT 1 | 2.6607 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 7345.00] TO [YOAKUM_345 345.00] CKT 1 | 3.026 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TUCO_INT 7345.00] TO [YOAKUM_345 345.00] CKT 1 | 3.3775 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [LG-CLAUENE 3115.00] TO [TERRY_CNTY 3115.00] CKT 1 | 2.7311 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [LG-CLAUENE 3115.00] TO [TERRY_CNTY 3115.00] CKT 1 | 3.1112 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [WOLFFORTH 3115.00] TO [TERRY_CNTY 3115.00] CKT 1 | 2.7275 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [WOLFFORTH 3115.00] TO [TERRY_CNTY 3115.00] CKT 1 | 3.1067 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TERRY_TR1 113.200] TO [TERRY_CNTY 3115.00] TO [TERRY_CNTY 269.000] CKT 1 | 2.7363 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TERRY_TR1 113.200] TO [TERRY_CNTY 3115.00] TO [TERRY_CNTY 269.000] CKT 1 | 3.1174 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TERRY_TR2 113.200] TO [TERRY_CNTY 3115.00] TO [TERRY_CNTY 269.000] CKT 2 | 2.7363 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TERRY_TR2 113.200] TO [TERRY_CNTY 3115.00] TO [TERRY_CNTY 269.000] CKT 2 | 3.1174 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TERRY_CNTY 3115.00] TO [PRENTICE 3115.00] CKT 1 | 2.7332 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TERRY_CNTY 3115.00] TO [PRENTICE 3115.00] CKT 1 | 3.1136 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [BORDER 7345.00] TO [TUCO_INT 7345.00] CKT 1 | 2.6978 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TERRY_CNTY 3115.00] TO [DENVER_N 3115.00] CKT 1 | 2.7335 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [TERRY_CNTY 3115.00] TO [DENVER_N 3115.00] CKT 1 | 3.114 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [AMOCOWASSON6230.00] TO [MUSTANG 6230.00] CKT 1 | 2.5835 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [AMOCOWASSON6230.00] TO [MUSTANG 6230.00] CKT 1 | 2.9326 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [YOAKUM 6230.00] TO [BRU_SUB 6230.00] CKT 1 | 2.5129 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [YOAKUM 6230.00] TO [BRU_SUB 6230.00] CKT 1 | 2.8473 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [YOAKUM 6230.00] TO [MUSTANG 6230.00] CKT 1 | 2.7315 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [YOAKUM 6230.00] TO [MUSTANG 6230.00] CKT 1 | 3.1116 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [YOAKUM_345 345.00] TO [HOBBS_INT 7345.00] CKT 1 | 2.6913 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [YOAKUM_345 345.00] TO [HOBBS_INT 7345.00] CKT 1 | 3.0629 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [BRU_SUB 6230.00] TO [OXYBRU 6230.00] CKT 1 | 2.7358 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [DENVER_N 3115.00] TO [MUSTANG 3115.00] CKT 1 | 2.736 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [DENVER_N 3115.00] TO [MUSTANG 3115.00] CKT 1 | 3.117 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MUSTANG 3115.00] TO [SEAGRAVES 3115.00] CKT 1 | 2.7213 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MUSTANG 3115.00] TO [SEAGRAVES 3115.00] CKT 1 | 3.0992 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [LG-PLSHILL 3115.00] TO [SEAGRAVES 3115.00] CKT 1 | 2.7286 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [LG-PLSHILL 3115.00] TO [SEAGRAVES 3115.00] CKT 1 | 3.1081 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SEAGRAV_TR1113.200] TO [SEAGRAVES 3115.00] TO [SEAGRAVES 269.000] CKT 1 | 2.735 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SEAGRAV_TR1113.200] TO [SEAGRAVES 3115.00] TO [SEAGRAVES 269.000] CKT 1 | 3.1158 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [POTTER_CO 7345.00] TO [TOLK 7345.00] CKT 1 | 2.6797 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [DIMNDBK_TR1113.200] TO [DIAMONDBACK3115.00] TO [DIAMONDBACK269.000] CKT 1 | 2.7352 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SLPHUR_TR1 113.200] TO [SULPHUR 3115.00] TO [SULPHUR 269.000] CKT 1 | 2.7364 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SLPHUR_TR1 113.200] TO [SULPHUR 3115.00] TO [SULPHUR 269.000] CKT 1 | 3.1175 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SLPHUR_TR2 113.200] TO [SULPHUR 3115.00] TO [SULPHUR 269.000] CKT 2 | 2.7364 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SLPHUR_TR2 113.200] TO [SULPHUR 3115.00] TO [SULPHUR 269.000] CKT 2 | 3.1175 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CROSSROADS 7345.00] TO [HOBBS_INT 7345.00] CKT BA | 2.7268 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CROSSROADS 7345.00] TO [HOBBS_INT 7345.00] CKT BA | 3.1059 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CROSSROADS 7345.00] TO [HOBBS_INT 7345.00] CKT LX | 2.7268 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CROSSROADS 7345.00] TO [HOBBS_INT 7345.00] CKT LX | 3.1059 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [HOBBS_INT 3115.00] CKT 1 | 2.7362 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [HOBBS_INT 3115.00] CKT 2 | 2.7363 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [MADDOX 3115.00] CKT 1 | 2.726 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [MADDOX 3115.00] CKT 1 | 3.1049 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [HOBBS_INT 3115.00] TO [MADDOX 3115.00] CKT 1 | 2.715 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [HOBBS_INT 3115.00] TO [MADDOX 3115.00] CKT 1 | 3.0916 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [HOBBS_INT 3115.00] TO [MADDOX 3115.00] CKT 1 | 3.4435 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [HOBBS_INT 7345.00] TO [KIOWA 7345.00] CKT 1 | 2.7349 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [HOBBS_INT 7345.00] TO [KIOWA 7345.00] CKT 1 | 3.1157 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [BUSHLAND 6230.00] TO [DEAFSMITH 6230.00] CKT 1 | 2.6845 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [HOBBS_INT 7345.00] TO [RDRUNNER 7345.00] CKT UC | 2.7277 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [HOBBS_INT 7345.00] TO [RDRUNNER 7345.00] CKT XA | 2.7277 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [KIOWA 7345.00] TO [RDRUNNER 7345.00] CKT 1 | 2.732 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [KIOWA 7345.00] TO [RDRUNNER 7345.00] CKT 1 | 3.1121 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PHANTOM 7345.00] TO [RDRUNNER 7345.00] CKT 1 | 2.7364 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PHANTOM 7345.00] TO [RDRUNNER 7345.00] CKT 1 | 3.1175 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SAND_DUNES 3115.00] TO [RED_BLUFF 3115.00] CKT 1 | 2.7322 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SAND_DUNES 3115.00] TO [RED_BLUFF 3115.00] CKT 1 | 3.1123 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [RED_BLUFF 3115.00] TO [WOLFCAMP_TP3115.00] CKT 1 | 2.7284 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [RED_BLUFF 3115.00] TO [WOLFCAMP_TP3115.00] CKT 1 | 3.1078 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [RDRUNNR_SVC115.000] TO [RR_SVC_HV 3115.00] CKT 1 | 2.7364 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [RDRUNNR_SVC115.000] TO [RR_SVC_HV 3115.00] CKT 1 | 3.1175 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [AGAVE_RHILL3115.00] TO [OCHOA 3115.00] CKT 1 | 2.7359 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [AGAVE_RHILL3115.00] TO [OCHOA 3115.00] CKT 1 | 3.1169 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CUSTERMTN 3115.00] TO [PONDEROSA 3115.00] CKT 1 | 2.7358 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CUSTERMTN 3115.00] TO [PONDEROSA 3115.00] CKT 1 | 3.1167 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CUSTERMTN 3115.00] TO [WHITTEN 3115.00] CKT 1 | 2.7146 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [CUSTERMTN 3115.00] TO [WHITTEN 3115.00] CKT 1 | 3.0911 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [DFSMTH_EST 3115.00] TO [DEAFSMITH 6230.00] TO [DEFSMTH_TR2113.800] CKT 2 | 2.7333 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [DFSMTH_EST 3115.00] TO [DEAFSMITH 6230.00] TO [DEFSMTH_TR2113.800] CKT 2 | 3.1178 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MADDOX 3115.00] TO [MADDOX_1 113.800] CKT 1 | 2.7205 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MADDOX 3115.00] TO [MADDOX_1 113.800] CKT 1 | 3.0983 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MADDOX 3115.00] TO [PEARLE 3115.00] CKT 1 | 2.7342 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MADDOX 3115.00] TO [PEARLE 3115.00] CKT 1 | 3.1148 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MADDOX 3115.00] TO [MONUMENT 3115.00] CKT 1 | 2.7342 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [MADDOX 3115.00] TO [MONUMENT 3115.00] CKT 1 | 3.1148 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SANGER_SW 3115.00] TO [OXYPERMIAN 3115.00] CKT 1 | 2.7297 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SANGER_SW 3115.00] TO [OXYPERMIAN 3115.00] CKT 1 | 3.1094 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [GEN-2016-121115.00] TO [G16-121XFMR134.500] CKT 1 | 2.7381 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [GEN-2016-121115.00] TO [G16-121XFMR134.500] CKT 1 | 3.1195 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [O.K.U.-7 345.00] TO [G18-015-TAP 345.00] CKT 1 | 2.5318 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [L.E.S.-7 345.00] TO [G16-091-TAP 345.00] CKT 1 | 2.7136 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [L.E.S.-7 345.00] TO [G17-171-TAP 345.00] CKT 1 | 2.7256 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [L.E.S.-7 345.00] TO [L.E.S.-4 138.00] TO [LES#4-1 13.800] CKT 1 | 2.7347 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [L.E.S.-7 345.00] TO [L.E.S.-4 138.00] TO [LES#4-1 13.800] CKT 1 | 3.1155 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [L.E.S.-7 345.00] TO [L.E.S.-4 138.00] TO [LES#5-1 13.800] CKT 2 | 2.7331 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [L.E.S.-7 345.00] TO [L.E.S.-4 138.00] TO [LES#5-1 13.800] CKT 2 | 3.1134 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [DEFSMTH_TR1113.200] TO [DEAFSMITH 6230.00] TO [DFSMTH_WST 3115.00] CKT 1 | 2.7333 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [DEFSMTH_TR1113.200] TO [DEAFSMITH 6230.00] TO [DFSMTH_WST 3115.00] CKT 1 | 3.1178 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [BORDER 7345.00] TO [BECKHAM7 345.00] CKT 1 | 2.6969 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [POTTER_CO 7345.00] TO [HITCHLAND 7345.00] CKT 1 | 2.7172 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [POTTER_CO 7345.00] TO [SPNSPUR_WND7345.00] CKT 1 | 2.7376 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [POTTER_CO 7345.00] TO [SPNSPUR_WND7345.00] CKT 1 | 3.1189 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [POTTER_CO 7345.00] TO [POTTER_CO 6230.00] TO [POTTER_TR 113.200] CKT 1 | 2.7235 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [POTTER_CO 7345.00] TO [POTTER_CO 6230.00] TO [POTTER_TR 113.200] CKT 1 | 3.1026 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [BUSHLAND 6230.00] TO [POTTER_CO 6230.00] CKT 1 | 2.7067 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [BUSHLAND 6230.00] TO [WILDOR2_JUS6230.00] CKT 1 | 2.737 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [BUSHLAND 6230.00] TO [WILDOR2_JUS6230.00] CKT 1 | 3.1185 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [BUSHLAND 6230.00] TO [BUSHLAND 3115.00] TO [BSHLND_TR1 113.200] CKT 1 | 2.7334 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [BUSHLAND 6230.00] TO [BUSHLAND 3115.00] TO [BSHLND_TR1 113.200] CKT 1 | 3.1159 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [DFSMTH_EST 3115.00] TO [TIERABLANCA3115.00] CKT 1 | 2.7333 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [DFSMTH_EST 3115.00] TO [TIERABLANCA3115.00] CKT 1 | 3.1178 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [DFSMTH_WST 3115.00] TO [TIERABLANCA3115.00] CKT 2 | 2.7333 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [DFSMTH_WST 3115.00] TO [TIERABLANCA3115.00] CKT 2 | 3.1177 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [DEAFSMITH 6230.00] TO [G17-146-TAP 230.00] CKT 1 | 2.6498 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLSNT_HILL 6230.00] TO [OASIS 6230.00] CKT 1 | 2.7369 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLSNT_HILL 6230.00] TO [OASIS 6230.00] CKT 1 | 3.1181 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLSNT_HILL 6230.00] TO [PLSNT_HILL 3115.00] TO [PLSNHIL_TR1113.200] CKT 1 | 2.7364 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [PLSNT_HILL 6230.00] TO [PLSNT_HILL 3115.00] TO [PLSNHIL_TR1113.200] CKT 1 | 3.1175 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [OASIS 6230.00] TO [SN_JUAN_TAP6230.00] CKT 1 | 2.7221 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [OASIS 6230.00] TO [SN_JUAN_TAP6230.00] CKT 1 | 3.1006 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [OASIS 6230.00] TO [OASIS 3115.00] TO [OASIS_TR1 113.200] CKT 1 | 2.7368 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [OASIS 6230.00] TO [OASIS 3115.00] TO [OASIS_TR1 113.200] CKT 1 | 3.1181 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [ROOSEVELT 3115.00] TO [CURRY 3115.00] CKT 2 | 2.7353 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [ROOSEVELT 3115.00] TO [CURRY 3115.00] CKT 2 | 3.1164 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [ROOSEVELT 3115.00] TO [PORTALES 3115.00] CKT 1 | 2.7365 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [ROOSEVELT 6230.00] TO [TOLK 6230.00] CKT 1 | 2.7343 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [ROOSEVELT 6230.00] TO [TOLK 6230.00] CKT 1 | 3.115 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [ROOSEVELT 6230.00] TO [TOLK 6230.00] CKT 2 | 2.7344 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [ROOSEVELT 6230.00] TO [TOLK 6230.00] CKT 2 | 3.1151 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SWISHER 6230.00] TO [AMA_SOUTH 6230.00] CKT 1 | 2.7271 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SWISHER 6230.00] TO [AMA_SOUTH 6230.00] CKT 1 | 3.1062 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SWISHER 6230.00] TO [SWISHER 3115.00] TO [SWISHER_TR1113.200] CKT 1 | 2.7367 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [SWISHER 6230.00] TO [SWISHER 3115.00] TO [SWISHER_TR1113.200] CKT 1 | 3.1178 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [NEWHART 6230.00] TO [POTTER_CO 6230.00] CKT 1 | 2.727 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25SP | OPEN LINE FROM [NEWHART 6230.00] TO [POTTER_CO 6230.00] CKT 1 | 3.1062 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | Base | 3.2717 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | Base | 4.3781 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2018-004 |  |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | Base | 5.6469 | GEN-2017-151 |  |  |  |  | GEN-2018-015 | [11 empty] | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | Base | 2.6247 | GEN-2017-239 |  |  |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 |  | GEN-2017-151 |  | GEN-2018-004 | GEN-2018-015 |  |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [O.K.U.-7 345.00] TO [L.E.S.-7 345.00] CKT 1 | 2.3446 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLSNT_HILL 6230.00] TO [ROOSEVELT 6230.00] CKT 1 | 2.5812 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLSNT_HILL 6230.00] TO [ROOSEVELT 6230.00] CKT 1 | 2.9322 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [NEWHART 6230.00] TO [NEWHART 3115.00] TO [NEWHART_TR2113.200] CKT 2 | 2.5807 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [NEWHART 6230.00] TO [NEWHART 3115.00] TO [NEWHART_TR2113.200] CKT 2 | 2.9317 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [NEWHART 6230.00] TO [NEWHART 3115.00] TO [NEWHART_TR1113.200] CKT 1 | 2.5807 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [NEWHART 6230.00] TO [NEWHART 3115.00] TO [NEWHART_TR1113.200] CKT 1 | 2.9317 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLANT_X 3115.00] TO [MULSHVLY_TP3115.00] CKT 1 | 2.5814 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLANT_X 3115.00] TO [MULSHVLY_TP3115.00] CKT 1 | 2.9324 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLANT_X 3115.00] TO [BC-EARTH 3115.00] CKT 1 | 2.578 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLANT_X 3115.00] TO [BC-EARTH 3115.00] CKT 1 | 2.9295 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLANT_X 3115.00] TO [RKYFORD_TP 3115.00] CKT 1 | 2.5781 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLANT_X 3115.00] TO [RKYFORD_TP 3115.00] CKT 1 | 2.9286 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLANT_X 3115.00] TO [HALE_CNTY 3115.00] CKT 1 | 2.578 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLANT_X 3115.00] TO [HALE_CNTY 3115.00] CKT 1 | 2.9285 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLANT_X 3115.00] TO [PLANT_X1 113.800] CKT 1 | 2.5807 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLANT_X 3115.00] TO [PLANT_X1 113.800] CKT 1 | 2.9316 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLANT_X 3115.00] TO [PLANT_X2 113.800] CKT 1 | 2.5807 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLANT_X 3115.00] TO [PLANT_X2 113.800] CKT 1 | 2.9316 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLANT_X 3115.00] TO [PLANT_X3 113.800] CKT 1 | 2.5807 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLANT_X 3115.00] TO [PLANT_X3 113.800] CKT 1 | 2.9316 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLANT_X 6230.00] TO [TOLK 6230.00] CKT 1 | 2.5451 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLANT_X 6230.00] TO [TOLK 6230.00] CKT 1 | 2.8919 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [OASIS 6230.00] TO [ROOSEVELT 6230.00] CKT 1 | 2.579 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [OASIS 6230.00] TO [ROOSEVELT 6230.00] CKT 1 | 2.9295 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLANT_X 6230.00] TO [TOLK 6230.00] CKT 2 | 2.5431 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLANT_X 6230.00] TO [TOLK 6230.00] CKT 2 | 2.8896 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLANT_X 6230.00] TO [G17-146-TAP 230.00] CKT 1 | 2.4866 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLANT_X 6230.00] TO [G17-146-TAP 230.00] CKT 1 | 2.9063 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLANT_X 6230.00] TO [G17-146-TAP 230.00] CKT 1 | 3.1413 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TOLK_TR 113.200] TO [TOLK 7345.00] TO [TOLK 6230.00] CKT 1 | 2.5525 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TOLK_TR 113.200] TO [TOLK 7345.00] TO [TOLK 6230.00] CKT 1 | 2.8977 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TOLK_TR 113.200] TO [TOLK 7345.00] TO [TOLK 6230.00] CKT 1 | 3.2326 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TOLK_TR 2 13.200] TO [TOLK 7345.00] TO [TOLK 6230.00] CKT 2 | 2.5525 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TOLK_TR 2 13.200] TO [TOLK 7345.00] TO [TOLK 6230.00] CKT 2 | 2.8977 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TOLK_TR 2 13.200] TO [TOLK 7345.00] TO [TOLK 6230.00] CKT 2 | 3.2326 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TOLK_1 124.000] TO [TOLK 6230.00] CKT 1 | 2.3937 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TOLK_1 124.000] TO [TOLK 6230.00] CKT 1 | 2.7097 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TOLK_2 124.000] TO [TOLK 6230.00] CKT 1 | 2.3984 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TOLK_2 124.000] TO [TOLK 6230.00] CKT 1 | 2.7149 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TOLK_2 124.000] TO [TOLK 6230.00] CKT 1 | 3.0199 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [BLUECLDPOI 6230.00] TO [BLUECLDCOL 6230.00] CKT 1 | 2.572 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [NEEDMORE 6230.00] TO [TOLK 6230.00] CKT 1 | 2.5162 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [LAMB_CNTY 3115.00] TO [HOCKLEY 3115.00] CKT 1 | 2.5715 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [LAMB_CNTY 3115.00] TO [HOCKLEY 3115.00] CKT 1 | 2.9206 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [LAMB_CNTY 3115.00] TO [LAMB_CNTY 269.000] TO [LAMB_TR1 113.200] CKT 1 | 2.5808 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [LAMB_CNTY 3115.00] TO [LAMB_CNTY 269.000] TO [LAMB_TR1 113.200] CKT 1 | 2.9317 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [LAMB_CNTY 3115.00] TO [LAMB_CNTY 269.000] TO [LAMB_TR1 113.200] CKT 1 | 3.2717 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [ROSEVLT_TR1113.200] TO [ROOSEVELT 6230.00] TO [ROOSEVELT 3115.00] CKT 1 | 2.5801 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [ROSEVLT_TR1113.200] TO [ROOSEVELT 6230.00] TO [ROOSEVELT 3115.00] CKT 1 | 2.931 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [LAMB_CNTY 3115.00] TO [LAMB_CNTY 269.000] TO [LAMB_TR2 113.200] CKT 2 | 2.5808 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [LAMB_CNTY 3115.00] TO [LAMB_CNTY 269.000] TO [LAMB_TR2 113.200] CKT 2 | 2.9317 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [LAMB_CNTY 3115.00] TO [LAMB_CNTY 269.000] TO [LAMB_TR2 113.200] CKT 2 | 3.2717 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [LAMB_CNTY 6230.00] TO [TOLK 6230.00] CKT 1 | 2.5711 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_INT 3115.00] TO [HALE_CNTY 3115.00] CKT 1 | 2.5771 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_INT 3115.00] TO [HALE_CNTY 3115.00] CKT 1 | 2.9275 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_INT 3115.00] TO [HALE_CNTY 3115.00] CKT 1 | 3.2671 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_INT 3115.00] TO [FLOYD_CNTY 3115.00] CKT 1 | 2.5799 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_INT 3115.00] TO [STANTON_W 3115.00] CKT 1 | 2.5795 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_INT 3115.00] TO [STANTON_W 3115.00] CKT 1 | 2.9301 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_INT 3115.00] TO [LUBBCK_EST 3115.00] CKT 1 | 2.5778 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_INT 3115.00] TO [LUBBCK_EST 3115.00] CKT 1 | 2.9282 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_INT 3115.00] TO [TUCO_INT2 269.000] TO [TUCO_TR7 113.200] CKT 1 | 2.5804 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_INT 3115.00] TO [TUCO_INT 269.000] TO [TUCO_TR5 113.200] CKT 2 | 2.5807 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_INT 3115.00] TO [TUCO_INT 269.000] TO [TUCO_TR5 113.200] CKT 2 | 2.9316 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_INT 3115.00] TO [TUCO_INT 269.000] TO [TUCO_TR6 113.200] CKT 1 | 2.5807 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_INT 3115.00] TO [TUCO_INT 269.000] TO [TUCO_TR6 113.200] CKT 1 | 2.9316 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_INT 6230.00] TO [TOLK 6230.00] CKT 1 | 2.5056 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_INT 6230.00] TO [TOLK 6230.00] CKT 1 | 2.8412 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_INT 6230.00] TO [TOLK 6230.00] CKT 1 | 3.1719 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SWISHER 6230.00] TO [NEWHART 6230.00] CKT 1 | 2.5718 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SWISHER 6230.00] TO [NEWHART 6230.00] CKT 1 | 2.9217 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_INT 7345.00] TO [G17-151TAP 345.00] CKT 1 | 4.3536 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2018-004 |  |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_INT 7345.00] TO [G17-151TAP 345.00] CKT 1 | 1.6228 | GEN-2017-151 |  |  |  |  | GEN-2018-015 | [11 empty] | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [ANTELOPE_1 6230.00] TO [ANTELOPE_A 113.800] CKT 1 | 2.5807 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [ANTELOPE_1 6230.00] TO [ANTELOPE_A 113.800] CKT 1 | 2.9316 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [ANTELOPE_1 6230.00] TO [ANTELOPE_B 113.800] CKT 1 | 2.5807 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [ANTELOPE_1 6230.00] TO [ANTELOPE_B 113.800] CKT 1 | 2.9316 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [ANTELOPE_1 6230.00] TO [ANTELOPE_C 113.800] CKT 1 | 2.5807 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [ANTELOPE_1 6230.00] TO [ANTELOPE_C 113.800] CKT 1 | 2.9316 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [ELK_CT1 345.00] TO [ELK_1 118.000] CKT 1 | 2.5807 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [ELK_CT1 345.00] TO [ELK_1 118.000] CKT 1 | 2.9316 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [ELK_CT1 345.00] TO [ELK_2 1 18.000] CKT 1 | 2.5807 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [ELK_CT1 345.00] TO [ELK_2 1 18.000] CKT 1 | 2.9316 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [HALE_WNDCL16230.00] TO [HALEWD_COL1134.500] TO [HALE_WD_TR1113.200] CKT 1 | 2.5817 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [HALE_WNDCL16230.00] TO [HALEWD_COL1134.500] TO [HALE_WD_TR1113.200] CKT 1 | 2.9328 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [HALE_WNDCL16230.00] TO [HALEWD_COL1134.500] TO [HALE_WD_TR1113.200] CKT 1 | 3.2727 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [HALE_WNDCL16230.00] TO [HALEWD_COL2134.500] TO [HALE_WD_TR2113.200] CKT 1 | 2.5818 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [HALE_WNDCL16230.00] TO [HALEWD_COL2134.500] TO [HALE_WD_TR2113.200] CKT 1 | 2.933 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [HALE_WNDCL16230.00] TO [HALEWD_COL2134.500] TO [HALE_WD_TR2113.200] CKT 1 | 3.2728 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [HALE_WNDCL16230.00] TO [HALEWD_COL3134.500] TO [HALE_WD_TR3113.200] CKT 1 | 2.5817 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [HALE_WNDCL16230.00] TO [HALEWD_COL3134.500] TO [HALE_WD_TR3113.200] CKT 1 | 2.9328 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [HALE_WNDCL16230.00] TO [HALEWD_COL3134.500] TO [HALE_WD_TR3113.200] CKT 1 | 3.2726 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CARLISLE 6230.00] TO [WOLFFORTH 6230.00] CKT 1 | 2.5739 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CARLISLE 6230.00] TO [WOLFFORTH 6230.00] CKT 1 | 2.9233 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SWISHER 6230.00] TO [TUCO_INT 6230.00] CKT 1 | 2.5616 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SWISHER 6230.00] TO [TUCO_INT 6230.00] CKT 1 | 2.9094 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SWISHER 6230.00] TO [TUCO_INT 6230.00] CKT 1 | 3.2488 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CARLISLE 6230.00] TO [CARLISLE 3115.00] TO [CRLSLE_TR1 113.200] CKT 1 | 2.5803 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CARLISLE 6230.00] TO [CARLISLE 3115.00] TO [CRLSLE_TR1 113.200] CKT 1 | 2.9311 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CARLISLE 6230.00] TO [CARLISLE 3115.00] TO [CRLSLE_TR1 113.200] CKT 1 | 3.2711 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [JONES 6230.00] TO [LUBBCK_STH 6230.00] CKT 1 | 2.5794 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [JONES 6230.00] TO [LUBBCK_STH 6230.00] CKT 1 | 2.9301 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [JONES 6230.00] TO [LUBBCK_STH 6230.00] CKT 2 | 2.5794 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [JONES 6230.00] TO [LUBBCK_STH 6230.00] CKT 2 | 2.9301 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [JONES 6230.00] TO [LUBBCK_EST 6230.00] CKT 1 | 2.5796 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [JONES 6230.00] TO [JONES_1 122.000] CKT 1 | 2.5699 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [JONES 6230.00] TO [JONES_1 122.000] CKT 1 | 2.9188 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [JONES 6230.00] TO [JONES_2 122.000] CKT 1 | 3.2567 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [JONES 6230.00] TO [JONES_2 122.000] CKT 1 | 2.5708 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [JONES 6230.00] TO [JONES_2 122.000] CKT 1 | 2.9198 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [JONES 6230.00] TO [JONES_3 116.500] CKT 1 | 2.5678 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [JONES 6230.00] TO [JONES_4 116.500] CKT 1 | 2.5714 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [JONES 6230.00] TO [GRASSLAND 6230.00] CKT 1 | 2.5809 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [JONES 6230.00] TO [GRASSLAND 6230.00] CKT 1 | 2.9318 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SUNDOWN 6230.00] TO [AMOCO_SS 6230.00] CKT 1 | 2.5432 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SUNDOWN 6230.00] TO [AMOCO_SS 6230.00] CKT 1 | 2.8866 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [NEWHART 6230.00] TO [PLANT_X 6230.00] CKT 1 | 2.5575 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SUNDOWN 6230.00] TO [WOLFFORTH 6230.00] CKT 1 | 2.5587 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SUNDOWN 6230.00] TO [WOLFFORTH 6230.00] CKT 1 | 2.9054 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SUNDOWN 6230.00] TO [WOLFFORTH 6230.00] CKT 1 | 3.2421 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SUNDOWN 6230.00] TO [SUNDOWN 3115.00] TO [SUNDOWN_TR1113.800] CKT 1 | 2.5795 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [LG-CLAUENE 3115.00] TO [LG-LEVELAND3115.00] CKT 1 | 2.5756 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [LG-CLAUENE 3115.00] TO [LG-LEVELAND3115.00] CKT 1 | 2.9255 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [WOLFFORTH 3115.00] TO [YUMA_INT 3115.00] CKT 1 | 2.5782 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [WOLFFORTH 3115.00] TO [WOLFFORTH 6230.00] TO [WOLFRTH_TR1113.200] CKT 1 | 2.5798 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [WOLFFORTH 3115.00] TO [WOLFFORTH 6230.00] TO [WOLFRTH_TR1113.200] CKT 1 | 2.9305 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TERRY_CNTY 269.000] TO [LG-DOCWEBR 269.000] CKT 1 | 2.5802 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TERRY_CNTY 269.000] TO [LG-BROWNFLD269.000] CKT 1 | 2.58 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TERRY_CNTY 3115.00] TO [FLATLAND 3115.00] CKT 1 | 2.5558 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TERRY_CNTY 3115.00] TO [FLATLAND 3115.00] CKT 1 | 2.9014 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [AMOCOWASSON6230.00] TO [XTO_MAHONEY6230.00] CKT 1 | 2.4542 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PRENTICE 3115.00] TO [YOAKUM 3115.00] CKT 1 | 2.5776 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLANTX_TR1 113.200] TO [PLANT_X 6230.00] TO [PLANT_X 3115.00] CKT 1 | 2.5779 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLANTX_TR1 113.200] TO [PLANT_X 6230.00] TO [PLANT_X 3115.00] CKT 1 | 2.9282 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [YOAKUM 6230.00] TO [AMOCO_SS 6230.00] CKT 1 | 2.5435 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [YOAKUM 6230.00] TO [AMOCO_SS 6230.00] CKT 1 | 2.8869 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [YOAKUM 6230.00] TO [INK_BASIN 6230.00] CKT 1 | 2.5379 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [YOAKUM 6230.00] TO [YOAKUM 3115.00] TO [YOAKUM_TR1 113.200] CKT 1 | 2.5769 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [YOAKUM 6230.00] TO [YOAKUM 3115.00] TO [YOAKUM_TR2 113.200] CKT 2 | 2.5769 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [YOAKUM 6230.00] TO [YOAKUM_345 345.00] TO [YOAKUM_TR1 13.200] CKT 1 | 2.4976 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [BRU_SUB 6230.00] TO [XTO_MAHONEY6230.00] CKT 1 | 2.3737 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [DENVER_N 3115.00] TO [EL_PASO 3115.00] CKT 1 | 2.5802 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [DENVER_N 3115.00] TO [EL_PASO 3115.00] CKT 1 | 2.931 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [DENVER_N 3115.00] TO [HIGGEAST 3115.00] CKT 1 | 2.5746 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [DENVER_N 3115.00] TO [HIGGEAST 3115.00] CKT 1 | 2.9242 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [DENVER_N 3115.00] TO [DENVER_CTY 269.000] TO [DNVER_N_TR1113.200] CKT 1 | 2.5807 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MUSTANG 3115.00] TO [SHELL_CO2 3115.00] CKT 1 | 2.5802 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLANT_X 3115.00] TO [LAMB_CNTY 3115.00] CKT 1 | 2.5792 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLANT_X 3115.00] TO [LAMB_CNTY 3115.00] CKT 1 | 2.9301 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MUSTANG 3115.00] TO [DENVER_S 3115.00] CKT 2 | 2.5804 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MUSTANG 3115.00] TO [MUSTANG_1 118.000] CKT 1 | 3.2414 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MUSTANG 3115.00] TO [MUSTANG_1 118.000] CKT 1 | 4.3281 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2018-004 |  |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MUSTANG 3115.00] TO [MUSTANG_1 118.000] CKT 1 | 5.663 | GEN-2017-151 |  |  |  |  | GEN-2018-015 | [11 empty] | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MUSTANG 3115.00] TO [MUSTANG_1 118.000] CKT 1 | 2.5937 | GEN-2017-239 |  |  |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 |  | GEN-2017-151 |  | GEN-2018-004 | GEN-2018-015 |  |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MUSTANG 3115.00] TO [MUSTANG_2 118.000] CKT 1 | 3.2437 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MUSTANG 3115.00] TO [MUSTANG_2 118.000] CKT 1 | 4.3315 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2018-004 |  |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MUSTANG 3115.00] TO [MUSTANG_2 118.000] CKT 1 | 5.6634 | GEN-2017-151 |  |  |  |  | GEN-2018-015 | [11 empty] | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MUSTANG 3115.00] TO [MUSTANG_2 118.000] CKT 1 | 2.5962 | GEN-2017-239 |  |  |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 |  | GEN-2017-151 |  | GEN-2018-004 | GEN-2018-015 |  |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MUSTANG 3115.00] TO [SEMINOLE 3115.00] CKT 1 | 2.5797 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MUSTANG 3115.00] TO [SEMINOLE 3115.00] CKT 1 | 2.9304 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MUSTANG 3115.00] TO [MUSTANG 6230.00] TO [MUSTANG_TR1113.200] CKT 1 | 3.241 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MUSTANG 3115.00] TO [MUSTANG 6230.00] TO [MUSTANG_TR1113.200] CKT 1 | 2.5585 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MUSTANG 6230.00] TO [MUSTANG_3 119.000] CKT 1 | 3.2215 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MUSTANG 6230.00] TO [MUSTANG_3 119.000] CKT 1 | 4.2963 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2018-004 |  |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MUSTANG 6230.00] TO [MUSTANG_3 119.000] CKT 1 | 2.8893 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MUSTANG 6230.00] TO [MUSTANG_3 119.000] CKT 1 | 2.5695 | GEN-2017-239 |  |  |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 |  | GEN-2017-151 |  | GEN-2018-004 | GEN-2018-015 |  |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MUSTANG 6230.00] TO [SEMINOLE 6230.00] CKT 1 | 2.5659 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MUSTANG 6230.00] TO [SEMINOLE 6230.00] CKT 1 | 2.9137 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [LG-PLSHILL 3115.00] TO [YOAKUM 3115.00] CKT 1 | 2.5731 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [LG-PLSHILL 3115.00] TO [YOAKUM 3115.00] CKT 1 | 2.9224 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SEAGRAVES 269.000] TO [LG-WELLMAN 269.000] CKT 1 | 2.5806 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SEAGRAVES 269.000] TO [MOSS 269.000] CKT 1 | 2.5802 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLANT_X 6230.00] TO [PLANT_X4 120.000] CKT 1 | 2.4994 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLANT_X 6230.00] TO [PLANT_X4 120.000] CKT 1 | 2.8377 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SEAGRAVES 269.000] TO [LG-MC&SMNL+269.000] CKT 1 | 2.5804 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SEAGRAVES 3115.00] TO [FLATLAND 3115.00] CKT 1 | 2.5456 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SEAGRAVES 3115.00] TO [FLATLAND 3115.00] CKT 1 | 2.8892 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [DIAMONDBACK269.000] TO [OZRK_MAH02 269.000] CKT 1 | 2.5803 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [DIAMONDBACK269.000] TO [LG-ASHMORE 269.000] CKT 1 | 2.5807 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [DIAMONDBACK269.000] TO [LG-ASHMORE 269.000] CKT 1 | 2.9316 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [DIAMONDBACK269.000] TO [OXY_CEDRLKE269.000] CKT 1 | 2.5803 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [DIAMONDBACK3115.00] TO [FLATLAND 3115.00] CKT 1 | 3.2704 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [DIAMONDBACK3115.00] TO [FLATLAND 3115.00] CKT 1 | 4.3767 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2018-004 |  |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [DIAMONDBACK3115.00] TO [FLATLAND 3115.00] CKT 1 | 2.5796 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [DIAMONDBACK3115.00] TO [FLATLAND 3115.00] CKT 1 | 2.6229 | GEN-2017-239 |  |  |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 |  | GEN-2017-151 |  | GEN-2018-004 | GEN-2018-015 |  |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SULPHUR 269.000] TO [ADAIR 269.000] CKT 1 | 2.5801 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SULPHUR 269.000] TO [LG-FOSTER +269.000] CKT 1 | 2.5799 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SULPHUR 3115.00] TO [FLATLAND 3115.00] CKT 1 | 2.5807 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SULPHUR 3115.00] TO [FLATLAND 3115.00] CKT 1 | 2.9316 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SULPHUR 3115.00] TO [FLATLAND 3115.00] CKT 2 | 2.5807 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SULPHUR 3115.00] TO [FLATLAND 3115.00] CKT 2 | 2.9316 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLANT_X 6230.00] TO [SUNDOWN 6230.00] CKT 1 | 2.5438 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLANT_X 6230.00] TO [SUNDOWN 6230.00] CKT 1 | 2.889 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CROSSROADS 7345.00] TO [SAGA_SCOL 7345.00] CKT 1 | 2.5864 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CROSSROADS 7345.00] TO [SAGA_SCOL 7345.00] CKT 1 | 2.9384 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CROSSROADS 7345.00] TO [RSVLT_CC_E 7345.00] CKT 1 | 2.557 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CROSSROADS 7345.00] TO [EDDY_CNTY 7345.00] CKT 1 | 2.5737 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CROSSROADS 7345.00] TO [EDDY_CNTY 7345.00] CKT 1 | 2.9232 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [CUNINGHAM1 113.800] CKT 1 | 2.5807 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [CUNINGHAM1 113.800] CKT 1 | 2.9316 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [CUNINGHAM4 113.800] CKT 1 | 2.5723 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [BUCKEYE_TP 3115.00] CKT 1 | 2.5809 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [BUCKEYE_TP 3115.00] CKT 1 | 2.9319 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [BUCKEYE_TP 3115.00] CKT 1 | 3.2718 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [QUAHADA 3115.00] CKT 1 | 2.5795 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [QUAHADA 3115.00] CKT 1 | 2.9301 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [QUAHADA 3115.00] CKT 1 | 3.27 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [MONUMNT_TP 3115.00] CKT 1 | 2.5729 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [MONUMNT_TP 3115.00] CKT 1 | 2.9222 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [MONUMNT_TP 3115.00] CKT 1 | 3.2608 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [CUNNIGHM_S 6230.00] TO [CUNNHM_TR1 113.200] CKT 1 | 2.5757 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [CUNNIGHM_S 6230.00] TO [CUNNHM_TR1 113.200] CKT 1 | 2.9255 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [HOBBS_INT 3115.00] TO [HOBBS_PLT1 118.000] CKT 1 | 2.5691 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [HOBBS_INT 3115.00] TO [HOBBS_PLT1 118.000] CKT 1 | 2.9176 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [O.K.U.-7 345.00] TO [OKLAUN HVDC7345.00] CKT 1 | 2.5818 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TOLK 7345.00] TO [CROSSROADS 7345.00] CKT 1 | 2.4898 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TOLK 7345.00] TO [CROSSROADS 7345.00] CKT 1 | 2.8234 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TOLK 7345.00] TO [CROSSROADS 7345.00] CKT 1 | 3.1454 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [HOBBS_INT 3115.00] TO [HOBBS_PLT2 118.000] CKT 1 | 2.5691 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [HOBBS_INT 3115.00] TO [HOBBS_PLT2 118.000] CKT 1 | 2.9176 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [HOBBS_INT 3115.00] TO [LE-WEST_SUB3115.00] CKT 1 | 2.5771 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [HOBBS_INT 3115.00] TO [BENSING 3115.00] CKT 1 | 2.5768 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [HOBBS_INT 3115.00] TO [MILLEN_TPW 3115.00] CKT 1 | 2.58 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [HOBBS_INT 3115.00] TO [HOBBS_INT 6230.00] TO [HOBBS_TR1 113.200] CKT 1 | 2.5757 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [HOBBS_INT 3115.00] TO [HOBBS_INT 6230.00] TO [HOBBS_TR1 113.200] CKT 1 | 2.9256 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [HOBBS_INT 3115.00] TO [HOBBS_INT 6230.00] TO [HOBBS_TR2 113.200] CKT 2 | 2.5731 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [HOBBS_INT 7345.00] TO [HOBBS_INT 6230.00] TO [HOBBS_TR3 113.200] CKT 1 | 2.5573 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [HOBBS_INT 7345.00] TO [HOBBS_INT 6230.00] TO [HOBBS_TR3 113.200] CKT 1 | 2.9035 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [HOBBS_INT 7345.00] TO [HOBBS_INT 6230.00] TO [HOBBS_TR3 113.200] CKT 1 | 3.2395 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [KIOWA 7345.00] TO [EDDY_CNTY 7345.00] CKT 1 | 2.5739 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [KIOWA 7345.00] TO [N_LOVING 7345.00] CKT 1 | 2.5783 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [KIOWA 7345.00] TO [KIOWA 3115.00] TO [KIOWA_TR1 113.200] CKT 1 | 2.5785 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [KIOWA 7345.00] TO [KIOWA 3115.00] TO [KIOWA_TR1 113.200] CKT 1 | 2.9289 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [BLUECLDPOI 6230.00] TO [NEEDMORE 6230.00] CKT Z1 | 2.572 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PHANTOM 7345.00] TO [CHINA_DRAW 7345.00] CKT 1 | 2.5791 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PHANTOM 7345.00] TO [PHANTOM 3115.00] TO [PHANTOM TR1113.200] CKT 1 | 2.5804 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PHANTOM 7345.00] TO [PHANTOM 3115.00] TO [PHANTOM TR2113.200] CKT 2 | 2.5804 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SAND_DUNES 3115.00] TO [WIPP 3115.00] CKT 1 | 3.2659 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SAND_DUNES 3115.00] TO [WIPP 3115.00] CKT 1 | 2.5765 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SAND_DUNES 3115.00] TO [WIPP 3115.00] CKT 1 | 2.9265 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [RED_BLUFF 3115.00] TO [RDRUNNER 3115.00] CKT 1 | 2.562 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [RDRNNER_TR1113.200] TO [RDRUNNER 7345.00] TO [RDRUNNER 3115.00] CKT 1 | 2.4841 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [RR_SVC_HV 3115.00] TO [RDRUNNER 3115.00] CKT Z1 | 2.5818 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [BATTLE_AXE 3115.00] TO [RDRUNNER 3115.00] CKT 1 | 3.2697 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [BATTLE_AXE 3115.00] TO [RDRUNNER 3115.00] CKT 1 | 2.5789 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [BATTLE_AXE 3115.00] TO [RDRUNNER 3115.00] CKT 1 | 2.9294 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [AGAVE_RHILL3115.00] TO [RDRUNNER 3115.00] CKT 1 | 2.5799 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [AGAVE_RHIL23115.00] TO [RDRUNNER 3115.00] CKT 1 | 3.2679 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [AGAVE_RHIL23115.00] TO [RDRUNNER 3115.00] CKT 1 | 2.5772 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [AGAVE_RHIL23115.00] TO [RDRUNNER 3115.00] CKT 1 | 2.9274 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [NEEDMORE 6230.00] TO [YOAKUM 6230.00] CKT 1 | 2.5191 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [NEEDMORE 6230.00] TO [YOAKUM 6230.00] CKT 1 | 2.8575 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [WOLFCAMP_TP3115.00] TO [BOPCO_PKRLK3115.00] CKT 1 | 3.2611 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [WOLFCAMP_TP3115.00] TO [BOPCO_PKRLK3115.00] CKT 1 | 2.5731 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [WOLFCAMP_TP3115.00] TO [WOLFCAMP 3115.00] CKT 1 | 3.271 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [WOLFCAMP_TP3115.00] TO [WOLFCAMP 3115.00] CKT 1 | 2.58 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CUSTERMTN 3115.00] TO [RDRUNNER 3115.00] CKT 1 | 2.5591 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MADDOXG23 3115.00] TO [MADDOX_2 113.800] CKT 1 | 2.5807 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MADDOXG23 3115.00] TO [MADDOX_2 113.800] CKT 1 | 2.9316 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MADDOXG23 3115.00] TO [MADDOX_3 112.500] CKT 1 | 2.5807 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MADDOXG23 3115.00] TO [MADDOX_3 112.500] CKT 1 | 2.9316 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MADDOX 3115.00] TO [G18-004-TAP 115.00] CKT 1 | 2.4914 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PEARLE 3115.00] TO [ENRON_TP 3115.00] CKT 1 | 2.5784 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PEARLE 3115.00] TO [ENRON_TP 3115.00] CKT 1 | 2.9288 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SANGER_SW 3115.00] TO [G18-004-TAP 115.00] CKT 1 | 2.5742 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SANGER_SW 3115.00] TO [G18-004-TAP 115.00] CKT 1 | 2.9237 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SANGER_SW 3115.00] TO [G18-004-TAP 115.00] CKT 1 | 3.2625 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SW_4J44 3115.00] TO [OXY_S_HOBBS3115.00] CKT 1 | 2.5804 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SW_4J44 3115.00] TO [OXY_S_HOBBS3115.00] CKT 1 | 2.9312 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SW_4J44 3115.00] TO [W_HOBBS 3115.00] CKT 1 | 2.5804 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SW_4J44 3115.00] TO [W_HOBBS 3115.00] CKT 1 | 2.9312 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [LAMB_TR3 113.200] TO [LAMB_CNTY 6230.00] TO [LAMB_CNTY 3115.00] CKT 1 | 2.57 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [LAMB_TR3 113.200] TO [LAMB_CNTY 6230.00] TO [LAMB_CNTY 3115.00] CKT 1 | 2.9188 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MONUMENT 3115.00] TO [MONUMENT 112.470] CKT 1 | 2.5799 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MONUMENT 3115.00] TO [W_HOBBS 3115.00] CKT 1 | 2.5789 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MONUMENT 3115.00] TO [W_HOBBS 3115.00] CKT 1 | 2.9294 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [WHITTEN 3115.00] TO [WARD 3115.00] CKT 1 | 2.5731 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [WHITTEN 3115.00] TO [S_JAL 3115.00] CKT 1 | 2.5732 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [WHITTEN 3115.00] TO [S_JAL 3115.00] CKT 1 | 2.9226 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [OXYPERMIAN 3115.00] TO [OXY_NHU_RCF3115.00] CKT 1 | 2.5741 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [OXYPERMIAN 3115.00] TO [OXY_NHU_RCF3115.00] CKT 1 | 2.9237 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [GEN-2016-121115.00] TO [RDRUNNER 3115.00] CKT 1 | 2.583 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [G16-121XFMR134.500] TO [G16-121-GSU134.500] CKT 1 | 2.583 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [GEN-2017-033345.00] TO [G17-033XFMR134.500] CKT 1 | 3.2717 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [GEN-2017-033345.00] TO [G17-033XFMR134.500] CKT 1 | 4.3781 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2018-004 |  |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [GEN-2017-033345.00] TO [G17-033XFMR134.500] CKT 1 | 5.6484 | GEN-2017-151 |  |  |  |  | GEN-2018-015 | [11 empty] | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [GEN-2017-033345.00] TO [G17-033XFMR134.500] CKT 1 | 2.625 | GEN-2017-239 |  |  |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 |  | GEN-2017-151 |  | GEN-2018-004 | GEN-2018-015 |  |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [GEN-2017-033345.00] TO [G17-033XFMR234.500] CKT 1 | 3.2717 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [GEN-2017-033345.00] TO [G17-033XFMR234.500] CKT 1 | 4.3781 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2018-004 |  |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [GEN-2017-033345.00] TO [G17-033XFMR234.500] CKT 1 | 5.649 | GEN-2017-151 |  |  |  |  | GEN-2018-015 | [11 empty] | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [GEN-2017-033345.00] TO [G17-033XFMR234.500] CKT 1 | 2.6251 | GEN-2017-239 |  |  |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 |  | GEN-2017-151 |  | GEN-2018-004 | GEN-2018-015 |  |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [ROOSEVELT 6230.00] TO [TOLK 6230.00] CKT 2 | 2.5662 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [ROOSEVELT 6230.00] TO [TOLK 6230.00] CKT 2 | 2.9145 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_TR3 113.200] TO [TUCO_INT 6230.00] TO [TUCO_INT 3115.00] CKT 2 | 2.5789 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_TR3 113.200] TO [TUCO_INT 6230.00] TO [TUCO_INT 3115.00] CKT 2 | 2.9294 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLANT_X 6230.00] TO [TOLK 6230.00] CKT 2 | 2.3843 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [JONES 6230.00] TO [LUBBCK_STH 6230.00] CKT 2 | 2.5648 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [JONES 6230.00] TO [LUBBCK_STH 6230.00] CKT 2 | 2.9127 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [JONES 6230.00] TO [LUBBCK_STH 6230.00] CKT 2 | 3.2502 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SULPHUR 3115.00] TO [FLATLAND 3115.00] CKT 2 | 2.5796 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_SVC 113.000] TO [TUCO_INT 6230.00] CKT 1 | 2.5767 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_SVC 113.000] TO [TUCO_INT 6230.00] CKT 1 | 2.9268 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_SVC 113.000] TO [TUCO_INT 6230.00] CKT 1 | 3.2671 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_TR4 113.200] TO [TUCO_INT 6230.00] TO [TUCO_INT 3115.00] CKT 1 | 2.5787 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_TR4 113.200] TO [TUCO_INT 6230.00] TO [TUCO_INT 3115.00] CKT 1 | 2.9292 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_TR1 113.200] TO [TUCO_INT 7345.00] TO [TUCO_INT 6230.00] CKT 1 | 2.5415 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_TR1 113.200] TO [TUCO_INT 7345.00] TO [TUCO_INT 6230.00] CKT 1 | 2.8843 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_TR1 113.200] TO [TUCO_INT 7345.00] TO [TUCO_INT 6230.00] CKT 1 | 3.2255 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_TR2 113.200] TO [TUCO_INT 7345.00] TO [TUCO_INT 6230.00] CKT 2 | 2.5495 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_TR2 113.200] TO [TUCO_INT 7345.00] TO [TUCO_INT 6230.00] CKT 2 | 2.8939 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_INT 6230.00] TO [ANTELOPE_1 6230.00] CKT 1 | 2.5807 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_INT 6230.00] TO [ANTELOPE_1 6230.00] CKT 1 | 2.9316 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [O.K.U.-7 345.00] TO [GEN-2017-033345.00] CKT 1 | 2.581 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [O.K.U.-7 345.00] TO [GEN-2017-033345.00] CKT 1 | 2.9319 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_INT 6230.00] TO [HALE_WNDCL16230.00] CKT 1 | 2.5838 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_INT 6230.00] TO [CARLISLE 6230.00] CKT 1 | 2.5686 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_INT 6230.00] TO [CARLISLE 6230.00] CKT 1 | 2.917 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_INT 6230.00] TO [JONES 6230.00] CKT 1 | 2.5518 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_INT 7345.00] TO [ELK_CT1 345.00] CKT 1 | 2.5807 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_INT 7345.00] TO [YOAKUM_345 345.00] CKT 1 | 2.5004 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_INT 7345.00] TO [YOAKUM_345 345.00] CKT 1 | 2.8345 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TUCO_INT 7345.00] TO [YOAKUM_345 345.00] CKT 1 | 3.1725 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [LG-CLAUENE 3115.00] TO [TERRY_CNTY 3115.00] CKT 1 | 2.5756 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [LG-CLAUENE 3115.00] TO [TERRY_CNTY 3115.00] CKT 1 | 2.9255 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [WOLFFORTH 3115.00] TO [TERRY_CNTY 3115.00] CKT 1 | 2.5716 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [WOLFFORTH 3115.00] TO [TERRY_CNTY 3115.00] CKT 1 | 2.9206 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TERRY_TR1 113.200] TO [TERRY_CNTY 3115.00] TO [TERRY_CNTY 269.000] CKT 1 | 2.5807 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TERRY_TR2 113.200] TO [TERRY_CNTY 3115.00] TO [TERRY_CNTY 269.000] CKT 2 | 2.5807 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TERRY_CNTY 3115.00] TO [PRENTICE 3115.00] CKT 1 | 2.5777 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TERRY_CNTY 3115.00] TO [PRENTICE 3115.00] CKT 1 | 2.9279 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TERRY_CNTY 3115.00] TO [PRENTICE 3115.00] CKT 1 | 3.2674 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [BORDER 7345.00] TO [TUCO_INT 7345.00] CKT 1 | 2.5343 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [BORDER 7345.00] TO [TUCO_INT 7345.00] CKT 1 | 2.8758 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TERRY_CNTY 3115.00] TO [DENVER_N 3115.00] CKT 1 | 2.5777 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [TERRY_CNTY 3115.00] TO [DENVER_N 3115.00] CKT 1 | 2.928 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [AMOCOWASSON6230.00] TO [MUSTANG 6230.00] CKT 1 | 2.4548 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [YOAKUM 6230.00] TO [BRU_SUB 6230.00] CKT 1 | 2.3738 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [YOAKUM 6230.00] TO [MUSTANG 6230.00] CKT 1 | 2.5746 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [YOAKUM_345 345.00] TO [HOBBS_INT 7345.00] CKT 1 | 2.5328 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [YOAKUM_345 345.00] TO [HOBBS_INT 7345.00] CKT 1 | 2.8737 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [YOAKUM_345 345.00] TO [HOBBS_INT 7345.00] CKT 1 | 3.2078 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [BRU_SUB 6230.00] TO [OXYBRU 6230.00] CKT 1 | 2.5801 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [DENVER_N 3115.00] TO [MUSTANG 3115.00] CKT 1 | 2.5804 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MUSTANG 3115.00] TO [SEAGRAVES 3115.00] CKT 1 | 2.5653 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MUSTANG 3115.00] TO [SEAGRAVES 3115.00] CKT 1 | 2.9129 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [LG-PLSHILL 3115.00] TO [SEAGRAVES 3115.00] CKT 1 | 2.5731 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [LG-PLSHILL 3115.00] TO [SEAGRAVES 3115.00] CKT 1 | 2.9224 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SEAGRAV_TR1113.200] TO [SEAGRAVES 3115.00] TO [SEAGRAVES 269.000] CKT 1 | 3.2707 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SEAGRAV_TR1113.200] TO [SEAGRAVES 3115.00] TO [SEAGRAVES 269.000] CKT 1 | 2.5798 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SEAGRAV_TR1113.200] TO [SEAGRAVES 3115.00] TO [SEAGRAVES 269.000] CKT 1 | 4.3773 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2018-004 |  |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SEAGRAV_TR1113.200] TO [SEAGRAVES 3115.00] TO [SEAGRAVES 269.000] CKT 1 | 2.9305 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [POTTER_CO 7345.00] TO [TOLK 7345.00] CKT 1 | 2.5279 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [DIMNDBK_TR1113.200] TO [DIAMONDBACK3115.00] TO [DIAMONDBACK269.000] CKT 1 | 2.5798 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SLPHUR_TR1 113.200] TO [SULPHUR 3115.00] TO [SULPHUR 269.000] CKT 1 | 2.5808 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SLPHUR_TR1 113.200] TO [SULPHUR 3115.00] TO [SULPHUR 269.000] CKT 1 | 2.9317 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SLPHUR_TR2 113.200] TO [SULPHUR 3115.00] TO [SULPHUR 269.000] CKT 2 | 2.5808 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SLPHUR_TR2 113.200] TO [SULPHUR 3115.00] TO [SULPHUR 269.000] CKT 2 | 2.9317 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CROSSROADS 7345.00] TO [HOBBS_INT 7345.00] CKT BA | 2.5718 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CROSSROADS 7345.00] TO [HOBBS_INT 7345.00] CKT BA | 2.9209 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CROSSROADS 7345.00] TO [HOBBS_INT 7345.00] CKT LX | 2.5718 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CROSSROADS 7345.00] TO [HOBBS_INT 7345.00] CKT LX | 2.9209 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [HOBBS_INT 3115.00] CKT 1 | 2.5806 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [HOBBS_INT 3115.00] CKT 1 | 2.9314 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [HOBBS_INT 3115.00] CKT 2 | 2.5806 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [HOBBS_INT 3115.00] CKT 2 | 2.9315 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [MADDOX 3115.00] CKT 1 | 2.5702 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CUNNINHAM 3115.00] TO [MADDOX 3115.00] CKT 1 | 2.9188 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [HOBBS_INT 3115.00] TO [MADDOX 3115.00] CKT 1 | 2.5588 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [HOBBS_INT 3115.00] TO [MADDOX 3115.00] CKT 1 | 2.9051 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [HOBBS_INT 7345.00] TO [KIOWA 7345.00] CKT 1 | 2.5793 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [HOBBS_INT 7345.00] TO [KIOWA 7345.00] CKT 1 | 2.9298 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [BUSHLAND 6230.00] TO [DEAFSMITH 6230.00] CKT 1 | 2.53 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [HOBBS_INT 7345.00] TO [RDRUNNER 7345.00] CKT UC | 2.5722 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [HOBBS_INT 7345.00] TO [RDRUNNER 7345.00] CKT XA | 2.5722 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [KIOWA 7345.00] TO [RDRUNNER 7345.00] CKT 1 | 2.5764 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PHANTOM 7345.00] TO [RDRUNNER 7345.00] CKT 1 | 2.5807 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SAND_DUNES 3115.00] TO [RED_BLUFF 3115.00] CKT 1 | 2.5764 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SAND_DUNES 3115.00] TO [RED_BLUFF 3115.00] CKT 1 | 2.9264 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [RED_BLUFF 3115.00] TO [WOLFCAMP_TP3115.00] CKT 1 | 3.2611 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [RED_BLUFF 3115.00] TO [WOLFCAMP_TP3115.00] CKT 1 | 2.5731 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [RDRUNNR_SVC115.000] TO [RR_SVC_HV 3115.00] CKT 1 | 2.5807 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [RDRUNNR_SVC115.000] TO [RR_SVC_HV 3115.00] CKT 1 | 2.9316 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [AGAVE_RHILL3115.00] TO [OCHOA 3115.00] CKT 1 | 2.5802 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CUSTERMTN 3115.00] TO [PONDEROSA 3115.00] CKT 1 | 3.2709 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CUSTERMTN 3115.00] TO [PONDEROSA 3115.00] CKT 1 | 4.3774 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2018-004 |  |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CUSTERMTN 3115.00] TO [PONDEROSA 3115.00] CKT 1 | 2.5799 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CUSTERMTN 3115.00] TO [PONDEROSA 3115.00] CKT 1 | 2.6235 | GEN-2017-239 |  |  |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 |  | GEN-2017-151 |  | GEN-2018-004 | GEN-2018-015 |  |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [CUSTERMTN 3115.00] TO [WHITTEN 3115.00] CKT 1 | 2.5594 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [DFSMTH_EST 3115.00] TO [DEAFSMITH 6230.00] TO [DEFSMTH_TR2113.800] CKT 2 | 2.5777 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [DFSMTH_EST 3115.00] TO [DEAFSMITH 6230.00] TO [DEFSMTH_TR2113.800] CKT 2 | 2.9318 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MADDOX 3115.00] TO [MADDOX_1 113.800] CKT 1 | 2.565 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MADDOX 3115.00] TO [PEARLE 3115.00] CKT 1 | 2.5786 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MADDOX 3115.00] TO [PEARLE 3115.00] CKT 1 | 2.929 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MADDOX 3115.00] TO [MONUMENT 3115.00] CKT 1 | 2.5788 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [MADDOX 3115.00] TO [MONUMENT 3115.00] CKT 1 | 2.9293 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SANGER_SW 3115.00] TO [OXYPERMIAN 3115.00] CKT 1 | 2.5742 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SANGER_SW 3115.00] TO [OXYPERMIAN 3115.00] CKT 1 | 2.9237 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SANGER_SW 3115.00] TO [OXYPERMIAN 3115.00] CKT 1 | 3.2625 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [GEN-2016-121115.00] TO [G16-121XFMR134.500] CKT 1 | 2.583 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [O.K.U.-7 345.00] TO [G18-015-TAP 345.00] CKT 1 | 2.3769 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [L.E.S.-7 345.00] TO [G16-091-TAP 345.00] CKT 1 | 2.5578 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [L.E.S.-7 345.00] TO [G17-171-TAP 345.00] CKT 1 | 2.5697 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [L.E.S.-7 345.00] TO [L.E.S.-4 138.00] TO [LES#4-1 13.800] CKT 1 | 2.579 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [L.E.S.-7 345.00] TO [L.E.S.-4 138.00] TO [LES#4-1 13.800] CKT 1 | 2.9295 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [L.E.S.-7 345.00] TO [L.E.S.-4 138.00] TO [LES#4-1 13.800] CKT 1 | 3.2707 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [L.E.S.-7 345.00] TO [L.E.S.-4 138.00] TO [LES#5-1 13.800] CKT 2 | 2.5774 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [L.E.S.-7 345.00] TO [L.E.S.-4 138.00] TO [LES#5-1 13.800] CKT 2 | 2.9277 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [L.E.S.-7 345.00] TO [L.E.S.-4 138.00] TO [LES#5-1 13.800] CKT 2 | 3.2698 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [DEFSMTH_TR1113.200] TO [DEAFSMITH 6230.00] TO [DFSMTH_WST 3115.00] CKT 1 | 2.5777 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [DEFSMTH_TR1113.200] TO [DEAFSMITH 6230.00] TO [DFSMTH_WST 3115.00] CKT 1 | 2.9318 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [BORDER 7345.00] TO [BECKHAM7 345.00] CKT 1 | 2.533 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [BORDER 7345.00] TO [BECKHAM7 345.00] CKT 1 | 2.8743 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [POTTER_CO 7345.00] TO [HITCHLAND 7345.00] CKT 1 | 2.5591 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [POTTER_CO 7345.00] TO [SPNSPUR_WND7345.00] CKT 1 | 2.5823 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [POTTER_CO 7345.00] TO [POTTER_CO 6230.00] TO [POTTER_TR 113.200] CKT 1 | 2.5694 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [BUSHLAND 6230.00] TO [POTTER_CO 6230.00] CKT 1 | 2.551 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [BUSHLAND 6230.00] TO [WILDOR2_JUS6230.00] CKT 1 | 2.5817 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [BUSHLAND 6230.00] TO [BUSHLAND 3115.00] TO [BSHLND_TR1 113.200] CKT 1 | 2.578 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [DFSMTH_EST 3115.00] TO [TIERABLANCA3115.00] CKT 1 | 2.5777 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [DFSMTH_EST 3115.00] TO [TIERABLANCA3115.00] CKT 1 | 2.9318 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [DFSMTH_WST 3115.00] TO [TIERABLANCA3115.00] CKT 2 | 2.5777 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [DFSMTH_WST 3115.00] TO [TIERABLANCA3115.00] CKT 2 | 2.9318 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [DEAFSMITH 6230.00] TO [G17-146-TAP 230.00] CKT 1 | 2.498 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLSNT_HILL 6230.00] TO [OASIS 6230.00] CKT 1 | 2.5813 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLSNT_HILL 6230.00] TO [OASIS 6230.00] CKT 1 | 2.9323 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLSNT_HILL 6230.00] TO [PLSNT_HILL 3115.00] TO [PLSNHIL_TR1113.200] CKT 1 | 2.5811 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [PLSNT_HILL 6230.00] TO [PLSNT_HILL 3115.00] TO [PLSNHIL_TR1113.200] CKT 1 | 2.9321 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [OASIS 6230.00] TO [SN_JUAN_TAP6230.00] CKT 1 | 2.5672 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [OASIS 6230.00] TO [SN_JUAN_TAP6230.00] CKT 1 | 2.9157 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [OASIS 6230.00] TO [OASIS 3115.00] TO [OASIS_TR1 113.200] CKT 1 | 2.5811 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [OASIS 6230.00] TO [OASIS 3115.00] TO [OASIS_TR1 113.200] CKT 1 | 2.9322 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [ROOSEVELT 3115.00] TO [CURRY 3115.00] CKT 2 | 2.5803 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [ROOSEVELT 3115.00] TO [CURRY 3115.00] CKT 2 | 2.9312 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [ROOSEVELT 3115.00] TO [PORTALES 3115.00] CKT 1 | 2.5808 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [ROOSEVELT 6230.00] TO [TOLK 6230.00] CKT 1 | 2.5798 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [ROOSEVELT 6230.00] TO [TOLK 6230.00] CKT 1 | 2.9306 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [ROOSEVELT 6230.00] TO [TOLK 6230.00] CKT 2 | 2.5799 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [ROOSEVELT 6230.00] TO [TOLK 6230.00] CKT 2 | 2.9306 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 |  | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SWISHER 6230.00] TO [AMA_SOUTH 6230.00] CKT 1 | 2.5694 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [SWISHER 6230.00] TO [SWISHER 3115.00] TO [SWISHER_TR1113.200] CKT 1 | 2.5805 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL
DISIS-2018-001-2 | 05 SOUTHWEST | 25WP | OPEN LINE FROM [NEWHART 6230.00] TO [POTTER_CO 6230.00] CKT 1 | 2.5704 | GEN-2017-158 |  |  |  |  | GEN-2017-239 |  |  | GEN-2017-187 |  |  | GEN-2018-052 | GEN-2016-121 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | FAIL