03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC121 (532740) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC341 (532741) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.3. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC7 1 (532744) 18.0 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply Fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.2. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.3. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply Fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 b.2. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply Fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.2. MORRIS 6 (532863) 230.0 kV to MORRIS 3 (533305) 115.0 kV to MORRIS2X1 (532890) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 b.4. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 6 (532851) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on UNIONRG6 230.00 (532874) 230 kV Bus a. Apply Fault at the UNIONRG6 230.00 (532874) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.3. UNIONRG6 (532874) 230.0 kV to DVISTA 6 (532875) 230.0 kV Transmission Circuit #1 b.4. UNIONRG6 (532874) 230.0 kV to UNIONRG3 (533359) 115.0 kV to UNIONRG1 (532817) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply Fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit #1 b.2. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 b.3. FRANKLIN5 (532938) 161.0 kV to FRANKLIN2 (533876) 69.0 kV to FRANKLIN1 (533122) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on 17TH 4 138.00 (533064) 138 kV Bus a. Apply Fault at the 17TH 4 138.00 (533064) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANAL 4 (533033) 138.0 kV to FOWLER 4 (533043) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 b.3. FOWLER 4 (533043) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 b.4. 17TH 4 (533064) 138.0 kV to 17TH 2 (533840) 69.0 kV to 17TH 4 1 (533112) 11.3 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply Fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.2. OTTRCRK4 (532997) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.3. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.4. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 b.5. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 b.6. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 b.7. ALTOONA4 (533001) 138.0 kV to ALTOO E2 (533673) 69.0 kV to ALTOO3 1 (533087) 13.2 kV Three Winding #1 b.8. ALTOONA4 (533001) 138.0 kV to ALTOO W2 (533674) 69.0 kV to ALTOO1 1 (533086) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply Fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.2. OTTRCRK4 (532997) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.3. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.4. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 b.5. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.6. ALTOONA4 (533001) 138.0 kV to ALTOO E2 (533673) 69.0 kV to ALTOO3 1 (533087) 13.2 kV Three Winding #1 b.7. ALTOONA4 (533001) 138.0 kV to ALTOO W2 (533674) 69.0 kV to ALTOO1 1 (533086) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on BENTON 4 138.00 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 b.2. BENTON 4 (532986) 138.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 b.2. BENTN1 1 (532821) 13.8 kV to BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on BENTON 4 138.00 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTN1 1 (532821) 13.8 kV to BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV Three Winding #1 b.2. BENTON 4 (532986) 138.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on BENTON 4 138.00 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.2. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.3. BENTON 4 (532986) 138.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.2. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.3. BENTN2 1 (532822) 13.8 kV to BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on BENTON 4 138.00 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTN2 1 (532822) 13.8 kV to BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV Three Winding #1 b.2. BENTON 4 (532986) 138.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on BENTON 4 138.00 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.2. BENTON 4 (532986) 138.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on COWSKIN4 138.00 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 138.00 (533038) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. CENTENN4 (533034) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #1 b.3. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.4. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on COWSKIN4 138.00 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 138.00 (533038) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.3. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.4. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on DEARING4 138.00 (533002) 138 kV Bus a. Apply Fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCOFCTY4 (510378) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.2. NBVILLE4 (510386) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.3. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 b.4. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.5. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.6. DEARING4 (533002) 138.0 kV to DEARING2 (533688) 69.0 kV to DEARING1 (533089) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to WWUPLNT4 (533016) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.5. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.6. WICH11 1 (532829) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.2. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 b.3. WICH11 1 (532829) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to WWUPLNT4 (533016) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.5. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.6. WICH12 1 (532830) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.2. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 b.3. WICH12 1 (532830) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on EVANS S4 138.00 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.2. EVANS S4 (533041) 138.0 kV to EEC GT1 (532723) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on EVANS S4 138.00 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.2. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on LAKERDG4 138.00 (533053) 138 kV Bus a. Apply Fault at the LAKERDG4 138.00 (533053) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EEC DG 1 (532730) 4.2 kV to EEC GT2 (532724) 13.8 kV Two Winding #1 b.2. EVANS S4 (533041) 138.0 kV to EEC GT2 (532724) 13.8 kV Two Winding #1 b.3. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.4. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on EVANS S4 138.00 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.2. EVANS S4 (533041) 138.0 kV to EEC GT2 (532724) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on 45TH ST4 138.00 (533074) 138 kV Bus a. Apply Fault at the 45TH ST4 138.00 (533074) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.3. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on 45TH ST4 138.00 (533074) 138 kV Bus a. Apply Fault at the 45TH ST4 138.00 (533074) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. EVANS S4 (533041) 138.0 kV to EEC GT3 (532725) 18.0 kV Two Winding #1 b.3. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on EVANS S4 138.00 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.2. EVANS S4 (533041) 138.0 kV to EEC GT3 (532725) 18.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply Fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALSTD 4 (533011) 138.0 kV to MOUND 4 (533013) 138.0 kV Transmission Circuit #1 b.2. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.5. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST1 1 (533092) 13.2 kV Three Winding #1 b.6. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST4 1 (533093) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on HOOVERS4 138.00 (533050) 138 kV Bus a. Apply Fault at the HOOVERS4 138.00 (533050) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 4 (533044) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.2. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.3. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.4. HOOVERS4 (533050) 138.0 kV to HOOVERS2 (533806) 69.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on HOOVERN4 138.00 (533049) 138 kV Bus a. Apply Fault at the HOOVERN4 138.00 (533049) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.2. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.3. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.4. HOOVERN4 (533049) 138.0 kV to HOOVERN2 (533805) 69.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply Fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.2. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.3. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 b.4. LIBERTY4 (533003) 138.0 kV to LIBERT-2 (533697) 69.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on GILL W 4 138.00 (533045) 138 kV Bus a. Apply Fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.2. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 b.3. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.4. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 b.5. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.6. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on NOEASTW4 138.00 (533061) 138 kV Bus a. Apply Fault at the NOEASTW4 138.00 (533061) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.2. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.3. NEAST3X1 (533110) 11.3 kV to NOEASTW4 (533061) 138.0 kV to NOEASTW2 (533822) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on NOEASTE4 138.00 (533060) 138 kV Bus a. Apply Fault at the NOEASTE4 138.00 (533060) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.2. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.3. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.4. NEAST5X1 (533111) 13.2 kV to NOEASTE4 (533060) 138.0 kV to NOEASTE2 (533823) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.2. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.3. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.4. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 b.5. NEOSHO 5 (532937) 161.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 b.6. NEOSHO 5 (532937) 161.0 kV to NEOSHOS4 (533020) 138.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 b.7. NEOSHO 5 (532937) 161.0 kV to NEOSHO 4 (533021) 138.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 b.8. NEOSHO 4 (533021) 138.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.10. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.2. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.3. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 b.4. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.5. NEOSHO 5 (532937) 161.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 b.6. NEOSHO 5 (532937) 161.0 kV to NEOSHOS4 (533020) 138.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 b.7. NEOSHO 5 (532937) 161.0 kV to NEOSHO 4 (533021) 138.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 b.2. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 b.3. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 b.4. NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.2. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 b.3. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.4. NEOSHOS4 (533020) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on CHAPMAN3 115.00 (533362) 115 kV Bus a. Apply Fault at the CHAPMAN3 115.00 (533362) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLAYCTR3 (533323) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.2. GEARY 3 (533336) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.3. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.4. AEC 3 (533361) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 b.5. CHAPMAN3 (533362) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on CHAPMAN3 115.00 (533362) 115 kV Bus a. Apply Fault at the CHAPMAN3 115.00 (533362) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLAYCTR3 (533323) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.2. CHAPMAN3 (533362) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on CHAPMAN3 115.00 (533362) 115 kV Bus a. Apply Fault at the CHAPMAN3 115.00 (533362) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NCFOUND3 (533329) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.2. WJCCTY 3 (533342) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.3. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.4. CHAPMAN3 (533362) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on CLAYCTR3 115.00 (533323) 115 kV Bus a. Apply Fault at the CLAYCTR3 115.00 (533323) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLAYCSS3 (533320) 115.0 kV to CLAYCTR3 (533323) 115.0 kV Transmission Circuit #1 b.2. CLAYCTR3 (533323) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.3. AEC 3 (533361) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 b.4. CHAPMAN3 (533362) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on WJCCTYW3 115.00 (533344) 115 kV Bus a. Apply Fault at the WJCCTYW3 115.00 (533344) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NCFOUND3 (533329) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.2. WJCCTY 3 (533342) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.3. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.4. AEC 3 (533361) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 b.5. CHAPMAN3 (533362) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply Fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.2. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.3. ARKVAL 3 (533411) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.4. ARKVALJ3 (533412) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 b.5. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 b.6. CIRCLE 3 (533413) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 b.2. CIRCLE 1 (532892) 13.8 kV to CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC GT 3 (533421) 115.0 kV Transmission Circuit #1 b.2. HEC GT 3 (533421) 115.0 kV to HEC GT2 (532696) 13.8 kV Two Winding #1 b.3. HEC GT 3 (533421) 115.0 kV to HEC GT3 (532697) 13.8 kV Two Winding #1 b.4. HEC GT 3 (533421) 115.0 kV to HEC GT4 (532698) 13.8 kV Two Winding #1 b.5. CIRCLE 1 (532892) 13.8 kV to CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on HEC GT 3 115.00 (533421) 115 kV Bus a. Apply Fault at the HEC GT 3 115.00 (533421) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 b.2. CIRCLE 3 (533413) 115.0 kV to HEC GT 3 (533421) 115.0 kV Transmission Circuit #1 b.3. HEC GT 3 (533421) 115.0 kV to HEC GT2 (532696) 13.8 kV Two Winding #1 b.4. HEC GT 3 (533421) 115.0 kV to HEC GT3 (532697) 13.8 kV Two Winding #1 b.5. HEC GT 3 (533421) 115.0 kV to HEC GT4 (532698) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on CITIES 3 115.00 (533414) 115 kV Bus a. Apply Fault at the CITIES 3 115.00 (533414) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CITIES 3 (533414) 115.0 kV to DAVIS 3 (533415) 115.0 kV Transmission Circuit #1 b.2. CITIES 3 (533414) 115.0 kV to SALTCRK3 (533434) 115.0 kV Transmission Circuit #1 b.3. SALTCRK3 (533434) 115.0 kV to 3 VANBU3 (533435) 115.0 kV Transmission Circuit #1 b.4. CITIES 3 (533414) 115.0 kV to NCTYSVC2 (533505) 69.0 kV to CITIES 1 (533453) 3.9 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on MANVILE3 115.00 (533426) 115 kV Bus a. Apply Fault at the MANVILE3 115.00 (533426) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MANVILE3 (533426) 115.0 kV to MCPHGT4 (532705) 13.8 kV Two Winding #1 b.2. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on MCPHER 3 115.00 (533428) 115 kV Bus a. Apply Fault at the MCPHER 3 115.00 (533428) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCPHER 3 (533428) 115.0 kV to MCPHGT3 (532704) 13.8 kV Two Winding #1 b.2. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on HEC 3 115.00 (533419) 115 kV Bus a. Apply Fault at the HEC 3 115.00 (533419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.2. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.3. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 b.4. HEC 3 (533419) 115.0 kV to 43LORAN (533440) 115.0 kV Transmission Circuit #1 b.5. HEC 3 (533419) 115.0 kV to HEC 2 (533513) 69.0 kV to HEC 1 (533445) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on HEC 3 115.00 (533419) 115 kV Bus a. Apply Fault at the HEC 3 115.00 (533419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 b.2. HEC 3 (533419) 115.0 kV to 43LORAN (533440) 115.0 kV Transmission Circuit #1 b.3. 3 VANBU3 (533435) 115.0 kV to MEADOW 3 (533441) 115.0 kV Transmission Circuit #1 b.4. MEADOW 3 (533441) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 b.5. HEC 3 (533419) 115.0 kV to HEC 2 (533513) 69.0 kV to HEC 1 (533445) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.2. EAST ST3 (533301) 115.0 kV to LANG 3 (533304) 115.0 kV Transmission Circuit #1 b.3. LANG 3 (533304) 115.0 kV to READING3 (533306) 115.0 kV Transmission Circuit #1 b.4. LANG 3 (533304) 115.0 kV to PRAIRIE3 (533307) 115.0 kV Transmission Circuit #1 b.5. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on MOUND 4 138.00 (533013) 138 kV Bus a. Apply Fault at the MOUND 4 138.00 (533013) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.2. WMBROS 3 (533310) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.3. WMBROSJ3 (533311) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 b.4. FLORENC3 (533366) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.5. HILSBOR3 (533369) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.6. SPRGCRK3 (533380) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 b.7. MOUN 2X1 (533097) 7.2 kV to MOUND 4 (533013) 138.0 kV to MOUNDRG3 (533429) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on MOUND 4 138.00 (533013) 138 kV Bus a. Apply Fault at the MOUND 4 138.00 (533013) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 3 (533416) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 b.2. MOUN 2X1 (533097) 7.2 kV to MOUND 4 (533013) 138.0 kV to MOUNDRG3 (533429) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on NORTHVW3 115.00 (533371) 115 kV Bus a. Apply Fault at the NORTHVW3 115.00 (533371) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTHST3 (533370) 115.0 kV to NORTHVW3 (533371) 115.0 kV Transmission Circuit #1 b.2. NORTHST3 (533370) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #1 b.3. NORTHVW3 (533371) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.4. NORTHVW3 (533371) 115.0 kV to G17-120-TAP (760007) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 b.2. RENO 1X1 (532807) 14.4 kV to RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. RENO 2X1 (532810) 14.4 kV to RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on RENO 3 115.00 (533416) 115 kV Bus a. Apply Fault at the RENO 3 115.00 (533416) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 b.2. RENO 3 (533416) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on SALINA 3 115.00 (533376) 115 kV Bus a. Apply Fault at the SALINA 3 115.00 (533376) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAWFRD3 (533364) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #1 b.2. NORTHST3 (533370) 115.0 kV to NORTHVW3 (533371) 115.0 kV Transmission Circuit #1 b.3. NORTHST3 (533370) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTHVW3 (533371) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.2. MENTOR 3 (533374) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.3. SMOKYHLLS3 (533378) 115.0 kV to SO GATE3 (533379) 115.0 kV Transmission Circuit #1 b.4. SO GATE3 (533379) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.5. SUMMIT 3 (533381) 115.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 b.6. SUMMIT 3 (533381) 115.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on TECHILL6 230.00 (532857) 230 kV Bus a. Apply Fault at the TECHILL6 230.00 (532857) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.2. 41CALIF3 (533160) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.3. SHAWNEE3 (533176) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.4. TECHILW3 (533181) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #z1 b.5. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.6. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.7. TECHILE3 (533182) 115.0 kV to INNOVIA1 (533884) 13.8 kV Two Winding #1 b.8. AEC 3 (533361) 115.0 kV to AEC E1 (533886) 34.5 kV Two Winding #2 b.9. AEC E1 (533886) 34.5 kV to AEC GT1 (532681) 13.8 kV Two Winding #1 b.10. AEC E1 (533886) 34.5 kV to AEC W1 (533887) 34.5 kV Transmission Circuit #z1 b.11. TECHILE3 (533182) 115.0 kV to TECHILL6 (532857) 230.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on WEMPORI3 115.00 (533309) 115 kV Bus a. Apply Fault at the WEMPORI3 115.00 (533309) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EAST ST3 (533301) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.2. MORRIS 3 (533305) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.3. PRAIRIE3 (533307) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.4. VAUGHN 3 (533308) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.5. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.6. FLORENC3 (533366) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.7. HILSBOR3 (533369) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.8. SPRGCRK3 (533380) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on WJCCTY 3 115.00 (533342) 115 kV Bus a. Apply Fault at the WJCCTY 3 115.00 (533342) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANZIO 3 (533321) 115.0 kV to WJCCTY 3 (533342) 115.0 kV Transmission Circuit #1 b.2. FT JCT 3 (533328) 115.0 kV to WJCCTY 3 (533342) 115.0 kV Transmission Circuit #1 b.3. NCFOUND3 (533329) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.4. WJCCTY 3 (533342) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.5. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. WMCPHER3 (533438) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. WMCPHER3 (533438) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. LYONS 3 (530620) 115.0 kV to SAXMAN 3 (530711) 115.0 kV Transmission Circuit #1 b.3. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.4. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.5. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on BUTLERS4 138.00 (532989) 138 kV Bus a. Apply Fault at the BUTLERS4 138.00 (532989) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERS4 (532989) 138.0 kV Transmission Circuit #z1 b.2. BUTLER 4 (532987) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.3. BUTLER 4 (532987) 138.0 kV to TIOGA 4 (532996) 138.0 kV Transmission Circuit #1 b.4. BUTLER 4 (532987) 138.0 kV to OTTRCRK4 (532997) 138.0 kV Transmission Circuit #1 b.5. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV Two Winding #1 b.6. BUTLERS4 (532989) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.7. BUTLERS4 (532989) 138.0 kV to BUTLERS2 (533609) 69.0 kV to BUTLER2X (533118) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on HOOVERS4 138.00 (533050) 138 kV Bus a. Apply Fault at the HOOVERS4 138.00 (533050) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.4. HOOVERN4 (533049) 138.0 kV to HOOVERN2 (533805) 69.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 b.5. HOOVERS4 (533050) 138.0 kV to HOOVERS2 (533806) 69.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on NOEASTW4 138.00 (533061) 138 kV Bus a. Apply Fault at the NOEASTW4 138.00 (533061) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.3. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.4. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.5. NOEASTE4 (533060) 138.0 kV to NOEASTE2 (533823) 69.0 kV to NEAST5X1 (533111) 13.2 kV Three Winding #1 b.6. NOEASTW4 (533061) 138.0 kV to NOEASTW2 (533822) 69.0 kV to NEAST3X1 (533110) 11.3 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 b.2. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.3. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 b.4. NEOSHO 4 (533021) 138.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.5. NEOSHO 4 (533021) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 b.6. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 b.7. NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 b.2. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.3. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 b.4. NEOSHOS4 (533020) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 b.5. NEOSHO 4 (533021) 138.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.6. NEOSHO 4 (533021) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 b.7. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on 5THMHILB1 161.00 (300120) 161 kV Bus a. Apply Fault at the 5THMHILB1 161.00 (300120) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5MOBTAP (300126) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on 5NOVELY_SW 161.00 (300106) 161 kV Bus a. Apply Fault at the 5NOVELY_SW 161.00 (300106) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NOVELY_SW (300106) 161.0 kV to 5NEWARK (300363) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on 5ADAIR1 161.00 (344004) 161 kV Bus a. Apply Fault at the 5ADAIR1 161.00 (344004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB3 (300133) 161.0 kV to 5ADAIR1 (344004) 161.0 kV Transmission Circuit #1 b.2. 5ADAIR2 (344001) 161.0 kV to 5ADAIR1 (344004) 161.0 kV Transmission Circuit #z b.3. 5ADAIR1 (344004) 161.0 kV to 2ADAIR 1 (346005) 69.0 kV Two Winding #1 b.4. 4FREDERCK (347084) 138.0 kV to 4MERE_138 (347680) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply Fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 b.2. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.3. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.4. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 b.5. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply Fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.2. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.3. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.4. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on 7ZACHARY 345.00 (344000) 345 kV Bus a. Apply Fault at the 7ZACHARY 345.00 (344000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ZACHARY (344000) 345.0 kV to J1025POI (345438) 345.0 kV Transmission Circuit #1 b.2. 7ZACHARY (344000) 345.0 kV to 5ZACHARY (344010) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on 7ZACHARY 345.00 (344000) 345 kV Bus a. Apply Fault at the 7ZACHARY 345.00 (344000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ZACHARY (344000) 345.0 kV to 7HUGHES (344011) 345.0 kV Transmission Circuit #1 b.2. 7ZACHARY (344000) 345.0 kV to 5ZACHARY (344010) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on 5ADAIR1 161.00 (344004) 161 kV Bus a. Apply Fault at the 5ADAIR1 161.00 (344004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB3 (300133) 161.0 kV to 5ADAIR1 (344004) 161.0 kV Transmission Circuit #1 b.2. 5ADAIR2 (344001) 161.0 kV to 5ADAIR1 (344004) 161.0 kV Transmission Circuit #z b.3. 5ADAIR2 (344001) 161.0 kV to 5ADAIR3 (344006) 161.0 kV Transmission Circuit #z b.4. 5ADAIR2 (344001) 161.0 kV to APANOSE5 (631112) 161.0 kV Transmission Circuit #1 b.5. 5ADAIR1 (344004) 161.0 kV to 2ADAIR 1 (346005) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_129 | Single Phase Fault with Stuck Breaker on 5ADAIR3 161.00 (344006) 161 kV Bus a. Apply Fault at the 5ADAIR3 161.00 (344006) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NOVELY_SW (300106) 161.0 kV to 5ADAIR3 (344006) 161.0 kV Transmission Circuit #1 b.2. 5ADAIR2 (344001) 161.0 kV to 5ADAIR1 (344004) 161.0 kV Transmission Circuit #z b.3. 5ADAIR2 (344001) 161.0 kV to 5ADAIR3 (344006) 161.0 kV Transmission Circuit #z b.4. 5ADAIR2 (344001) 161.0 kV to APANOSE5 (631112) 161.0 kV Transmission Circuit #1 b.5. 5ADAIR3 (344006) 161.0 kV to 5ZACHARY (344010) 161.0 kV Transmission Circuit #1 b.6. 2ADAIR 2 (346006) 69.0 kV to 5ADAIR3 (344006) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_130 | Single Phase Fault with Stuck Breaker on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply Fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.2. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.3. 5MCBAIN T (345071) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.4. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.5. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.6. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z b.7. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 b.8. 5OVERTON 2 (345411) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #2 b.9. 5OVERTON 2 (345411) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_131 | Single Phase Fault with Stuck Breaker on APANOSE5 161.00 (631112) 161 kV Bus a. Apply Fault at the APANOSE5 161.00 (631112) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5ADAIR2 (344001) 161.0 kV to APANOSE5 (631112) 161.0 kV Transmission Circuit #1 b.2. WOODY 5 (631110) 161.0 kV to APANOSE5 (631112) 161.0 kV Transmission Circuit #1 b.3. APANOSE5 (631112) 161.0 kV to APANOSE8 (630033) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_132 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_133 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_134 | Single Phase Fault with Stuck Breaker on HAWTHS_G65 161.00 (543129) 161 kV Bus a. Apply Fault at the HAWTHS_G65 161.00 (543129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT6 1 (542961) 16.8 kV to HAWTHS_G65 (543129) 161.0 kV Two Winding #1 b.2. HAW G9 1 (542967) 13.8 kV to HAWTHS5 (542973) 161.0 kV Two Winding #1 b.3. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_135 | Single Phase Fault with Stuck Breaker on HAWTHS_G65 161.00 (543129) 161 kV Bus a. Apply Fault at the HAWTHS_G65 161.00 (543129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT6 1 (542961) 16.8 kV to HAWTHS_G65 (543129) 161.0 kV Two Winding #1 b.2. HAW G9 1 (542967) 13.8 kV to HAWTHS5 (542973) 161.0 kV Two Winding #1 b.3. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_136 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 b.2. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_137 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAC G2 1 (542956) 24.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 b.2. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_138 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit #1 b.3. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.4. SALSBRY5 (543062) 161.0 kV to Load #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_139 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.3. SALSBRY5 (543062) 161.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_140 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.3. SALSBRY5 (543062) 161.0 kV to Load #1 b.4. SALSBRY5 (543062) 161.0 kV to Load #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_141 | Single Phase Fault with Stuck Breaker on BRUNSWK5 161.00 (543061) 161 kV Bus a. Apply Fault at the BRUNSWK5 161.00 (543061) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit #1 b.2. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.3. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.4. SALSBRY5 (543062) 161.0 kV to Load #2 b.5. SALSBRY5 (543062) 161.0 kV to Load #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_142 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_143 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_144 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_145 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_146 | Single Phase Fault with Stuck Breaker on JOP145 5 161.00 (547470) 161 kV Bus a. Apply Fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 b.2. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.3. JOP145 5 (547470) 161.0 kV to JOP145 2 (547539) 69.0 kV to JOP145 1 (547707) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_147 | Single Phase Fault with Stuck Breaker on JOP389 5 161.00 (547483) 161 kV Bus a. Apply Fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.3. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.4. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 b.5. JOP389 5 (547483) 161.0 kV to JOP389 2 (547592) 69.0 kV to JOP389 1 (547713) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_148 | Single Phase Fault with Stuck Breaker on RIV167 5 161.00 (547502) 161 kV Bus a. Apply Fault at the RIV167 5 161.00 (547502) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.2. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to R12G4531 (547642) 13.8 kV Two Winding #1 b.4. RIV453 5 (547501) 161.0 kV to R13G167 (547643) 13.8 kV Two Winding #1 b.5. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.6. RIV167 5 (547502) 161.0 kV to R10G1671 (547647) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_149 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_150 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_151 | Single Phase Fault with Stuck Breaker on RIV452T 5 161.00 (547503) 161 kV Bus a. Apply Fault at the RIV452T 5 161.00 (547503) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.4. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_152 | Single Phase Fault with Stuck Breaker on RIV452T 5 161.00 (547503) 161 kV Bus a. Apply Fault at the RIV452T 5 161.00 (547503) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.4. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_153 | Single Phase Fault with Stuck Breaker on FIR417 5 161.00 (547490) 161 kV Bus a. Apply Fault at the FIR417 5 161.00 (547490) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 b.3. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_154 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_155 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to T.NO.2-4 (509895) 138.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 b.3. TNO2-1 (509894) 34.5 kV to T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_156 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_157 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_158 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_159 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #1 b.2. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_160 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_161 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.2. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.3. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.4. QUA377 2 (547590) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.5. HOC404 5 (547487) 161.0 kV to HOC404 4 (547486) 138.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.6. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_162 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 b.2. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.3. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.4. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.6. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_163 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 b.2. HAWTHS5 (542973) 161.0 kV to HAWTH_B2_1 (543003) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_164 | Single Phase Fault with Stuck Breaker on NORTON 5 161.00 (543064) 161 kV Bus a. Apply Fault at the NORTON 5 161.00 (543064) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALTABN5 (543059) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.2. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.3. NORTON1 (543123) 34.5 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_165 | Single Phase Fault with Stuck Breaker on HAWTHS_G65 161.00 (543129) 161 kV Bus a. Apply Fault at the HAWTHS_G65 161.00 (543129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT6 1 (542961) 16.8 kV to HAWTHS_G65 (543129) 161.0 kV Two Winding #1 b.2. HAW G9 1 (542967) 13.8 kV to HAWTHS5 (542973) 161.0 kV Two Winding #1 b.3. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_166 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_167 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_168 | Single Phase Fault with Stuck Breaker on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNE5 (532934) 161.0 kV to MARMTNW5 (532935) 161.0 kV Transmission Circuit #z1 b.2. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 b.3. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 b.4. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.5. MARMTNW5 (532935) 161.0 kV to MARMATN2 (533639) 69.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_169 | Single Phase Fault with Stuck Breaker on CORONAD3 115.00 (533394) 115 kV Bus a. Apply Fault at the CORONAD3 115.00 (533394) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MENTOR 3 (533374) 115.0 kV to CORONAD3 (533394) 115.0 kV Transmission Circuit #1 b.2. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_170 | Single Phase Fault with Stuck Breaker on BELAIRE4 138.00 (532988) 138 kV Bus a. Apply Fault at the BELAIRE4 138.00 (532988) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to BELAIRE4 (532988) 138.0 kV Transmission Circuit #1 b.2. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.3. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_171 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.3. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.4. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_172 | Single Phase Fault with Stuck Breaker on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_173 | Single Phase Fault with Stuck Breaker on BENTON 4 138.00 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.3. BENTON 4 (532986) 138.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_174 | Single Phase Fault with Stuck Breaker on BENTON 4 138.00 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.2. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.3. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_175 | Single Phase Fault with Stuck Breaker on WJCCTYW3 115.00 (533344) 115 kV Bus a. Apply Fault at the WJCCTYW3 115.00 (533344) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NCFOUND3 (533329) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.2. GEARY 3 (533336) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.3. WJCCTY 3 (533342) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.4. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_176 | Single Phase Fault with Stuck Breaker on ALLEN 2 69.000 (533621) 69 kV Bus a. Apply Fault at the ALLEN 2 69.000 (533621) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALLEN 2 (533621) 69.0 kV to LEHIGTP2 (533638) 69.0 kV Transmission Circuit #1 b.2. ALLEN 2 (533621) 69.0 kV to MONARCH2 (533641) 69.0 kV Transmission Circuit #1 b.3. ALLEN 2 (533621) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.4. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.5. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_177 | Single Phase Fault with Stuck Breaker on COWSKIN4 138.00 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 138.00 (533038) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.3. COWSKIN2 (533788) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.4. COWSKIN2 (533788) 69.0 kV to SG9STMK2 (533874) 69.0 kV Transmission Circuit #1 b.5. COWSKIN2 (533788) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 b.6. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_178 | Single Phase Fault with Stuck Breaker on DEPAUL 2 69.000 (533759) 69 kV Bus a. Apply Fault at the DEPAUL 2 69.000 (533759) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. DEPAUL 2 (533759) 69.0 kV to PITTSBG2 (533770) 69.0 kV Transmission Circuit #1 b.4. DEPAUL 2 (533759) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 b.5. DEPAUL 2 (533759) 69.0 kV to FRONTEN2 (533775) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_179 | Single Phase Fault with Stuck Breaker on DEARING4 138.00 (533002) 138 kV Bus a. Apply Fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 b.2. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.3. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.4. BEECRK2 (533677) 69.0 kV to DEARING2 (533688) 69.0 kV Transmission Circuit #1 b.5. COFFSUB2 (533683) 69.0 kV to DEARING2 (533688) 69.0 kV Transmission Circuit #1 b.6. DEARING4 (533002) 138.0 kV to DEARING2 (533688) 69.0 kV to DEARING1 (533089) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_180 | Single Phase Fault with Stuck Breaker on FTSCOTT2 69.000 (533635) 69 kV Bus a. Apply Fault at the FTSCOTT2 69.000 (533635) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSCOTT2 (533635) 69.0 kV to SE4DEVO2 (533644) 69.0 kV Transmission Circuit #1 b.2. FTSCOTT2 (533635) 69.0 kV to WARE 2 (533652) 69.0 kV Transmission Circuit #1 b.3. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.4. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 b.5. SE4DEVO2 (533644) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_181 | Single Phase Fault with Stuck Breaker on CRAWFOR2 69.000 (533758) 69 kV Bus a. Apply Fault at the CRAWFOR2 69.000 (533758) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. DEPAUL 2 (533759) 69.0 kV to FRONTEN2 (533775) 69.0 kV Transmission Circuit #1 b.4. GIR JCT2 (533762) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.5. GIR JCT2 (533762) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 b.6. FRONTEN2 (533775) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_182 | Single Phase Fault with Stuck Breaker on HOOVERN4 138.00 (533049) 138 kV Bus a. Apply Fault at the HOOVERN4 138.00 (533049) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERN2 (533805) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #z1 b.4. HOOVERN2 (533805) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.5. HOOVERN2 (533805) 69.0 kV to WATER1 2 (533855) 69.0 kV Transmission Circuit #1 b.6. HOOVERN4 (533049) 138.0 kV to HOOVERN2 (533805) 69.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_183 | Single Phase Fault with Stuck Breaker on HOOVERS4 138.00 (533050) 138 kV Bus a. Apply Fault at the HOOVERS4 138.00 (533050) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.3. HOOVERN2 (533805) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #z1 b.4. HOOVERS2 (533806) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.5. HOOVERS2 (533806) 69.0 kV to TYLER 2 (533847) 69.0 kV Transmission Circuit #1 b.6. HOOVERS2 (533806) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 b.7. HOOVERS4 (533050) 138.0 kV to HOOVERS2 (533806) 69.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_184 | Single Phase Fault with Stuck Breaker on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply Fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.2. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.3. SUNFLRS2 (533670) 69.0 kV to LIBERT-2 (533697) 69.0 kV Transmission Circuit #1 b.4. CHRYJCT2 (533680) 69.0 kV to LIBERT-2 (533697) 69.0 kV Transmission Circuit #1 b.5. LIBERTY4 (533003) 138.0 kV to LIBERT-2 (533697) 69.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_185 | Single Phase Fault with Stuck Breaker on LITCH 5 161.00 (532932) 161 kV Bus a. Apply Fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. LITCH N2 (533765) 69.0 kV to LITCH S2 (533766) 69.0 kV Transmission Circuit #z1 b.4. LITCH S2 (533766) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 b.5. LITCH S2 (533766) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.6. LITCH1 1 (532952) 13.2 kV to LITCH S2 (533766) 69.0 kV to LITCH 5 (532932) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_186 | Single Phase Fault with Stuck Breaker on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.3. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 b.4. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_187 | Single Phase Fault with Stuck Breaker on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALLEN 2 (533621) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.3. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.4. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.5. UN8HUMB2 (533650) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.6. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_188 | Single Phase Fault with Stuck Breaker on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.4. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.5. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.6. NEOSHOS2 (533778) 69.0 kV to NEOSHO 4 (533021) 138.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_189 | Single Phase Fault with Stuck Breaker on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. ORDNCE 2 (533702) 69.0 kV to ORDNJCT2 (533703) 69.0 kV Transmission Circuit #1 b.3. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.4. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.5. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.6. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.7. NEOSHOS2 (533778) 69.0 kV to NEOSHO 4 (533021) 138.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_190 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.2. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.3. NEC U3 (532711) 12.0 kV to NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV Three Winding #1 b.4. NEOSHON2 (533768) 69.0 kV to NEOSHON4 (533022) 138.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_191 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTAMNT2 (533671) 69.0 kV to ALTAMNS2 (533672) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.3. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.4. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.5. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.6. NEOSHON2 (533768) 69.0 kV to NEOSHON4 (533022) 138.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_192 | Single Phase Fault with Stuck Breaker on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.4. GIRARD 2 (533761) 69.0 kV to GIR JCT2 (533762) 69.0 kV Transmission Circuit #1 b.5. GIR JCT2 (533762) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.6. GIR JCT2 (533762) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 b.7. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.8. NEOSHOS2 (533778) 69.0 kV to NEOSHO 4 (533021) 138.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_193 | Single Phase Fault with Stuck Breaker on NOEASTE4 138.00 (533060) 138 kV Bus a. Apply Fault at the NOEASTE4 138.00 (533060) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.3. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.4. MINNEHA2 (533817) 69.0 kV to NOEASTE2 (533823) 69.0 kV Transmission Circuit #1 b.5. NOEASTW2 (533822) 69.0 kV to NOEASTE2 (533823) 69.0 kV Transmission Circuit #z1 b.6. NOEASTE4 (533060) 138.0 kV to NOEASTE2 (533823) 69.0 kV to NEAST5X1 (533111) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_194 | Single Phase Fault with Stuck Breaker on PARSONS2 69.000 (533704) 69 kV Bus a. Apply Fault at the PARSONS2 69.000 (533704) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.3. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_195 | Single Phase Fault with Stuck Breaker on ALTAMNS2 69.000 (533672) 69 kV Bus a. Apply Fault at the ALTAMNS2 69.000 (533672) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.3. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.4. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_196 | Single Phase Fault with Stuck Breaker on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.3. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.4. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.5. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.6. NEOSHON2 (533768) 69.0 kV to NEOSHON4 (533022) 138.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 b.7. NEOSHOS2 (533778) 69.0 kV to NEOSHO 4 (533021) 138.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_197 | Single Phase Fault with Stuck Breaker on MOORLND4 138.00 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 138.00 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORLND4 (520999) 138.0 kV to MORLND1 (520996) 13.8 kV Two Winding #1 b.2. MOORLND2 (520995) 69.0 kV to MOORLND4 (520999) 138.0 kV to MLNDTERT (521180) 2.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_198 | Single Phase Fault with Stuck Breaker on MOORLND4 138.00 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 138.00 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEOCOR4 (514778) 138.0 kV to GLASMTN4 (514788) 138.0 kV Transmission Circuit #1 b.2. GLASMTN4 (514788) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. MOORLND4 (520999) 138.0 kV to MORLND1 (520996) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_199 | Single Phase Fault with Stuck Breaker on MOORLND4 138.00 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 138.00 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 b.2. WINDFRM4 (515785) 138.0 kV to FPLWIND4 (515786) 138.0 kV Transmission Circuit #1 b.3. WINDFRM4 (515785) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.4. MOORLND4 (520999) 138.0 kV to MORLND1 (520996) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_200 | Single Phase Fault with Stuck Breaker on MOORLND4 138.00 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 138.00 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSUPLY4 (520920) 138.0 kV to IODINE 4 (520957) 138.0 kV Transmission Circuit #1 b.2. IODINE 4 (520957) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. MOORLND4 (520999) 138.0 kV to MORLND1 (520996) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_201 | Single Phase Fault with Stuck Breaker on MOORLND4 138.00 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 138.00 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIC4 (520425) 138.0 kV to CDRDLTP4 (520848) 138.0 kV Transmission Circuit #1 b.2. PIC4 (520425) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. CEDRDAL4 (520507) 138.0 kV to CDRDLTP4 (520848) 138.0 kV Transmission Circuit #1 b.4. CDRDLTP4 (520848) 138.0 kV to OKEENE 4 (521016) 138.0 kV Transmission Circuit #1 b.5. MOORLND4 (520999) 138.0 kV to MORLND2 (520997) 18.0 kV Two Winding #1 b.6. MOORLND4 (520999) 138.0 kV to MORLND3 (520998) 18.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_202 | Single Phase Fault with Stuck Breaker on NINMLTP4 138.00 (521128) 138 kV Bus a. Apply Fault at the NINMLTP4 138.00 (521128) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASPEN 4 (520462) 138.0 kV to BEARCAT4 (520500) 138.0 kV Transmission Circuit #1 b.2. ASPEN 4 (520462) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. NINMILE4 (520492) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 b.4. BEARCAT4 (520500) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 b.5. MOORLND4 (520999) 138.0 kV to MORLND2 (520997) 18.0 kV Two Winding #1 b.6. MOORLND4 (520999) 138.0 kV to MORLND3 (520998) 18.0 kV Two Winding #1 b.7. MORWODS4 (521001) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_203 | Single Phase Fault with Stuck Breaker on MOORLND4 138.00 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 138.00 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. NOELSW 4 (520430) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.3. ROSEVLY4 (520436) 138.0 kV to AVARD 4 (520601) 138.0 kV Transmission Circuit #1 b.4. MOORLND4 (520999) 138.0 kV to MORLND1 (520996) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_204 | Single Phase Fault with Stuck Breaker on BAX488 5 161.00 (547729) 161 kV Bus a. Apply Fault at the BAX488 5 161.00 (547729) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.2. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_205 | Single Phase Fault with Stuck Breaker on ATL109 5 161.00 (547466) 161 kV Bus a. Apply Fault at the ATL109 5 161.00 (547466) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTHAG5 (505488) 161.0 kV to ATL109 5 (547466) 161.0 kV Transmission Circuit #1 b.2. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.3. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.4. ATL109 5 (547466) 161.0 kV to ATL109 2 (547533) 69.0 kV to ATL109 1 (547702) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_206 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.3. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 b.4. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 b.5. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.6. ORO110 5 (547467) 161.0 kV to ORO110 2 (547534) 69.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_207 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_208 | Single Phase Fault with Stuck Breaker on BLUVLY 69.000 (548806) 69 kV Bus a. Apply Fault at the BLUVLY 69.000 (548806) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKCTYJ2 (543087) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.2. SUB K (548801) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.3. SUB H (548802) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.4. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #1 b.5. BLUVLY (548806) 69.0 kV to SUB B (548810) 69.0 kV Transmission Circuit #1 b.6. BLUVLY (548806) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 b.7. BLUVLY (548806) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 b.8. BLU VAL 1 (548833) 14.4 kV to BLUVLY (548806) 69.0 kV Two Winding #1 b.9. BLU VAL 2 (548834) 14.4 kV to BLUVLY (548806) 69.0 kV Two Winding #1 b.10. BLU VAL 3 (548835) 13.8 kV to BLUVLY (548806) 69.0 kV Two Winding #1 b.11. BLUVLY (548806) 69.0 kV to Load #T1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_209 | Single Phase Fault with Stuck Breaker on ECKLES-161 161.00 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 161.00 (548808) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOCITYB1 (301563) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.3. BLUMILS5 (543004) 161.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_210 | Single Phase Fault with Stuck Breaker on ECKLES-161 161.00 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 161.00 (548808) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOCITYB1 (301563) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_211 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_212 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_213 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | No | Yes | Yes | Yes | Yes | No | Yes | Non-dampening active power oscillations observed at WCGS U1 (532751) following the fault clearance. Issue is also observed in the base case. The following CQ units were determined to be contingent on the upgrade: - GEN-2018-009 : PTDF of 0.0368 - GEN-2018-032 : PTDF of 0.0882 - GEN-2018-049 : PTDF of 0.0640 - GEN-2018-057 : PTDF of 0.0962 | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_214 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_215 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_216 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_217 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_218 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_219 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_220 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_221 | Single Phase Fault with Stuck Breaker on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply Fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTH_B2_1 (543003) 13.2 kV Two Winding #1 b.2. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 b.3. HAWTHS_XF5 (543130) 161.0 kV to HAWT12_2 (543664) 69.0 kV Two Winding #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_222 | Single Phase Fault with Stuck Breaker on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply Fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 b.3. HAWTHS_XF5 (543130) 161.0 kV to HAWT12_2 (543664) 69.0 kV Two Winding #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_223 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_224 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_225 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 7 (532773) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 b.2. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_226 | Single Phase Fault with Stuck Breaker on OKEENE 4 138.00 (521016) 138 kV Bus a. Apply Fault at the OKEENE 4 138.00 (521016) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIC4 (520425) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. CDRDLTP4 (520848) 138.0 kV to OKEENE 4 (521016) 138.0 kV Transmission Circuit #1 b.3. OKEENE 2 (521015) 69.0 kV to OKEENE 4 (521016) 138.0 kV to OKENTERT (521173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_227 | Single Phase Fault with Stuck Breaker on MOORLND4 138.00 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 138.00 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIC4 (520425) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. CDRDLTP4 (520848) 138.0 kV to OKEENE 4 (521016) 138.0 kV Transmission Circuit #1 b.3. FTSUPLY4 (520920) 138.0 kV to IODINE 4 (520957) 138.0 kV Transmission Circuit #1 b.4. IODINE 4 (520957) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_228 | Single Phase Fault with Stuck Breaker on GLASMTN4 138.00 (514788) 138 kV Bus a. Apply Fault at the GLASMTN4 138.00 (514788) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEOCOR4 (514778) 138.0 kV to GLASMTN4 (514788) 138.0 kV Transmission Circuit #1 b.2. GLASMTN4 (514788) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. ASPEN 4 (520462) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.4. MORWODS4 (521001) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_229 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_230 | Single Phase Fault with Stuck Breaker on ECKLES-161 161.00 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 161.00 (548808) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.3. BLUMILS5 (543004) 161.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_231 | Single Phase Fault with Stuck Breaker on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #2 b.2. BLUVLY (548806) 69.0 kV to Load #T2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_232 | Single Phase Fault with Stuck Breaker on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #2 b.2. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_233 | Single Phase Fault with Stuck Breaker on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #1 b.2. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_234 | Single Phase Fault with Stuck Breaker on SUB M-161 161.00 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 161.00 (548814) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.3. SUB M (548815) 69.0 kV to SUB M-161 (548814) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_235 | Single Phase Fault with Stuck Breaker on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply Fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #2 b.3. BLUEMLS2 (543116) 69.0 kV to BLUMILS5 (543004) 161.0 kV to BLUMILS_TER1 (543117) 12.5 kV Three Winding #3 b.4. BLUMILS_TER1 (543117) 12.5 kV to BLUMILS5 (543004) 161.0 kV to BLUEMLS2 (543116) 69.0 kV Three Winding #3 b.5. BLUMILS_TER1 (543117) 12.5 kV to Load #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_236 | Single Phase Fault with Stuck Breaker on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply Fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #1 b.3. BLUEMLS2 (543116) 69.0 kV to BLUMILS5 (543004) 161.0 kV to BLUMILS_TER1 (543117) 12.5 kV Three Winding #3 b.4. BLUMILS_TER1 (543117) 12.5 kV to BLUMILS5 (543004) 161.0 kV to BLUEMLS2 (543116) 69.0 kV Three Winding #3 b.5. BLUMILS_TER1 (543117) 12.5 kV to Load #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_237 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_238 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #@1 b.2. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #@2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_239 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.3. SALSBRY5 (543062) 161.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_240 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit #1 b.3. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.4. SALSBRY5 (543062) 161.0 kV to Load #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_241 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_242 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | No | Yes | Yes | Yes | Yes | No | Yes | Non-dampening active power oscillations observed at WCGS U1 (532751) following the fault clearance. Issue is also observed in the base case. The following CQ units were determined to be contingent on the upgrade: - GEN-2018-009 : PTDF of 0.0368 - GEN-2018-032 : PTDF of 0.0882 - GEN-2018-049 : PTDF of 0.0640 - GEN-2018-057 : PTDF of 0.0962 | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_243 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_244 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_245 | Single Phase Fault with Stuck Breaker on 87TH 7 345.00 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.3. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_246 | Single Phase Fault with Stuck Breaker on CANEYRV7 345.00 (532780) 345 kV Bus a. Apply Fault at the CANEYRV7 345.00 (532780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.2. CANEYRV7 (532780) 345.0 kV to CANEYWF7 (532781) 345.0 kV Transmission Circuit #1 b.3. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_247 | Single Phase Fault with Stuck Breaker on GEARY 7 345.00 (532767) 345 kV Bus a. Apply Fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 b.3. GEARY 7 (532767) 345.0 kV to GEARY 3 (533336) 115.0 kV to GEARY1X1 (532834) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_248 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_249 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.3. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_250 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_251 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_252 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_253 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_254 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 7 (532773) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 b.2. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_255 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 7 (532773) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_256 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_257 | Single Phase Fault with Stuck Breaker on FTSUPLY4 138.00 (520920) 138 kV Bus a. Apply Fault at the FTSUPLY4 138.00 (520920) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSUPLY4 (520920) 138.0 kV to SLEEPBR4 (520922) 138.0 kV Transmission Circuit #1 b.2. FTSUPLY4 (520920) 138.0 kV to IODINE 4 (520957) 138.0 kV Transmission Circuit #1 b.3. IODINE 4 (520957) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_258 | Single Phase Fault with Stuck Breaker on FTSUPLY4 138.00 (520920) 138 kV Bus a. Apply Fault at the FTSUPLY4 138.00 (520920) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSUPLY4 (520920) 138.0 kV to IODINE 4 (520957) 138.0 kV Transmission Circuit #1 b.2. IODINE 4 (520957) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. FTSUPLY2 (520919) 69.0 kV to FTSUPLY4 (520920) 138.0 kV to FTSUPTERTB (521182) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_259 | Single Phase Fault with Stuck Breaker on ERICK 4 138.00 (520903) 138 kV Bus a. Apply Fault at the ERICK 4 138.00 (520903) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SAYRE--4 (511504) 138.0 kV to ERICK 4 (520903) 138.0 kV Transmission Circuit #1 b.2. BULOJ4 (520402) 138.0 kV to ERICK 4 (520903) 138.0 kV Transmission Circuit #1 b.3. ASPEN 4 (520462) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.4. MORWODS4 (521001) 138.0 kV to MORWOOD4 (521002) 138.0 kV Transmission Circuit #1 b.5. MORWODS4 (521001) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_260 | Single Phase Fault with Stuck Breaker on MORWODS4 138.00 (521001) 138 kV Bus a. Apply Fault at the MORWODS4 138.00 (521001) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASPEN 4 (520462) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. MORWODS4 (521001) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 b.3. MORWODS2 (521000) 69.0 kV to MORWODS4 (521001) 138.0 kV to MRWDTERT (521172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_261 | Single Phase Fault with Stuck Breaker on ROSEVLY4 138.00 (520436) 138 kV Bus a. Apply Fault at the ROSEVLY4 138.00 (520436) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. NOELSW 4 (520430) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.3. NOELSW 4 (520430) 138.0 kV to SALTPLN4 (520437) 138.0 kV Transmission Circuit #1 b.4. CHRKCTY4 (520431) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_262 | Single Phase Fault with Stuck Breaker on NOELSW 4 138.00 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 138.00 (520430) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #2 b.2. NOELSW 4 (520430) 138.0 kV to SALTPLN4 (520437) 138.0 kV Transmission Circuit #1 b.3. CHRKCTY4 (520431) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_263 | Single Phase Fault with Stuck Breaker on NOELSW 4 138.00 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 138.00 (520430) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #1 b.2. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.3. NOELSW 4 (520430) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_264 | Single Phase Fault with Stuck Breaker on OKEENE 4 138.00 (521016) 138 kV Bus a. Apply Fault at the OKEENE 4 138.00 (521016) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIC4 (520425) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. CDRDLTP4 (520848) 138.0 kV to OKEENE 4 (521016) 138.0 kV Transmission Circuit #1 b.3. DOVERSW4 (520882) 138.0 kV to OKEENE 4 (521016) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_265 | Single Phase Fault with Stuck Breaker on OKEENE 4 138.00 (521016) 138 kV Bus a. Apply Fault at the OKEENE 4 138.00 (521016) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIC4 (520425) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. WATNGSW4 (520536) 138.0 kV to OKEENE 4 (521016) 138.0 kV Transmission Circuit #1 b.3. CDRDLTP4 (520848) 138.0 kV to OKEENE 4 (521016) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_266 | Single Phase Fault with Stuck Breaker on MOORLND4 138.00 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 138.00 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORLND4 (520999) 138.0 kV to MORLND3 (520998) 18.0 kV Two Winding #1 b.2. MOORLND2 (520995) 69.0 kV to MOORLND4 (520999) 138.0 kV to MLNDTERT (521180) 2.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_267 | Single Phase Fault with Stuck Breaker on MOORLND4 138.00 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 138.00 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. SEILING4 (520553) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. SEILING4 (520553) 138.0 kV to TALOGA 4 (521065) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_268 | Single Phase Fault with Stuck Breaker on WINDFRM4 138.00 (515785) 138 kV Bus a. Apply Fault at the WINDFRM4 138.00 (515785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 b.2. WINDFRM4 (515785) 138.0 kV to FPLWIND4 (515786) 138.0 kV Transmission Circuit #1 b.3. WINDFRM4 (515785) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.4. ASPEN 4 (520462) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.5. MORWODS4 (521001) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_269 | Single Phase Fault with Stuck Breaker on PIONEER3 115.00 (531391) 115 kV Bus a. Apply Fault at the PIONEER3 115.00 (531391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PUCKET 3 (531375) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.2. HICKOCK3 (531378) 115.0 kV to PIONEER3 (531391) 115.0 kV Transmission Circuit #1 b.3. PIONEER3 (531391) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.4. PIONEER3 (531391) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.5. PIONEER3 (531391) 115.0 kV to ULYSPLT3 (531490) 115.0 kV Transmission Circuit #1 b.6. PK_GOAB3 (531400) 115.0 kV to FLETCHR3 (531420) 115.0 kV Transmission Circuit #1 b.7. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.8. GRANTTP3 (531483) 115.0 kV to GRANT 3 (531484) 115.0 kV Transmission Circuit #1 b.9. PIONEER3 (531391) 115.0 kV to PIONEER2 (531390) 69.0 kV to PIONEER1 (531251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_270 | Single Phase Fault with Stuck Breaker on HARPER 4 138.00 (539668) 138 kV Bus a. Apply Fault at the HARPER 4 138.00 (539668) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit #1 b.2. RAGO 4 (539000) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.3. ANTHONY4 (539001) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.4. ANTHONY4 (539001) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.5. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.6. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.7. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.8. HARPER 4 (539668) 138.0 kV to HARPER 1 (539713) 34.5 kV to HARPER-T (539913) 8.7 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_271 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. SPERTER1 (531468) 13.8 kV to SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV Three Winding #1 b.3. SPERVIL7 (531469) 345.0 kV to SPEARVL6 (539695) 230.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_272 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.2. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_273 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_274 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_275 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #1 b.2. SPERTER1 (531468) 13.8 kV to SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV Three Winding #1 b.3. SPERVIL7 (531469) 345.0 kV to SPEARVL6 (539695) 230.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_276 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERTER1 (531468) 13.8 kV to SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV Three Winding #1 b.2. SPERVIL7 (531469) 345.0 kV to SPEARVL6 (539695) 230.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.3. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_277 | Single Phase Fault with Stuck Breaker on BUCKNER7 345.00 (531501) 345 kV Bus a. Apply Fault at the BUCKNER7 345.00 (531501) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMRRN 7 (531502) 345.0 kV Transmission Circuit #1 b.3. CIMRRN 7 (531502) 345.0 kV to CIMRRN 1 (531503) 34.5 kV Two Winding #1 b.4. CIMRRN 1 (531503) 34.5 kV to CIMARON-GSU1 (531602) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_278 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_279 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_280 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_281 | Single Phase Fault with Stuck Breaker on HOLCOMB3 115.00 (531448) 115 kV Bus a. Apply Fault at the HOLCOMB3 115.00 (531448) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. HOLCGEN1 (531447) 22.0 kV to HOLCOMB3 (531448) 115.0 kV Two Winding #1 b.5. HOLCOMB3 (531448) 115.0 kV to Load #S1 b.6. HOLCOMB3 (531448) 115.0 kV to Load #S2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_282 | Single Phase Fault with Stuck Breaker on N-CIMRN3 115.00 (539749) 115 kV Bus a. Apply Fault at the N-CIMRN3 115.00 (539749) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.2. HAYNE3 (539640) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.3. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.4. N-CIMRN3 (539749) 115.0 kV to N-CMRN 1 (539764) 34.5 kV to N-CMRN-T (539967) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_283 | Single Phase Fault with Stuck Breaker on CUDAHY 3 115.00 (539659) 115 kV Bus a. Apply Fault at the CUDAHY 3 115.00 (539659) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYNE3 (539640) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.2. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.3. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.4. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.5. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.6. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.7. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-T (539906) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_284 | Single Phase Fault with Stuck Breaker on CUDAHY 3 115.00 (539659) 115 kV Bus a. Apply Fault at the CUDAHY 3 115.00 (539659) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.2. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.3. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.4. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.5. CIM-PLT3 (539654) 115.0 kV to CIM-PLT (539780) 13.8 kV Two Winding #1 b.6. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.7. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-T (539906) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_285 | Single Phase Fault with Stuck Breaker on N-CIMRN3 115.00 (539749) 115 kV Bus a. Apply Fault at the N-CIMRN3 115.00 (539749) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.2. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.3. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.4. N-CIMRN3 (539749) 115.0 kV to N-CMRN 1 (539764) 34.5 kV to N-CMRN-T (539967) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_286 | Single Phase Fault with Stuck Breaker on SATATAP3 115.00 (531396) 115 kV Bus a. Apply Fault at the SATATAP3 115.00 (531396) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RUBART 3 (531200) 115.0 kV to SATATAP3 (531396) 115.0 kV Transmission Circuit #1 b.2. RUBART 1 (531201) 13.8 kV to RUBART 3 (531200) 115.0 kV Two Winding #1 b.3. PNTPR-GOAB3 (531203) 115.0 kV to PLSNTPR3 (531204) 115.0 kV Transmission Circuit #1 b.4. PNTPR-GOAB3 (531203) 115.0 kV to PIONTAP3 (531392) 115.0 kV Transmission Circuit #1 b.5. PNTPR-GOAB3 (531203) 115.0 kV to SATATAP3 (531396) 115.0 kV Transmission Circuit #1 b.6. SATATAP3 (531396) 115.0 kV to SATANTA3 (531397) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_287 | Single Phase Fault with Stuck Breaker on 5LEVASY 161.00 (300320) 161 kV Bus a. Apply Fault at the 5LEVASY 161.00 (300320) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 b.2. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.3. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_288 | Single Phase Fault with Stuck Breaker on NORTON 5 161.00 (543064) 161 kV Bus a. Apply Fault at the NORTON 5 161.00 (543064) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NORTON (300105) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #z1 b.2. MALTABN5 (543059) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.3. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.4. NORTON 5 (543064) 161.0 kV to MRSHLJT5 (543072) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_289 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_290 | Single Phase Fault with Stuck Breaker on TEXAS_CNTY 3115.00 (523090) 115 kV Bus a. Apply Fault at the TEXAS_CNTY 3115.00 (523090) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. Y ROAD 3 (522912) 115.0 kV to TEXAS_CNTY 3 (523090) 115.0 kV Transmission Circuit #1 b.2. TC-TXCOUNTY1 (523087) 34.5 kV to TEXAS_CNTY 3 (523090) 115.0 kV Two Winding #1 b.3. TEXAS_CNTY 3 (523090) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #1 b.4. TEXAS_CNTY 3 (523090) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #2 b.5. TEXAS_CNTY 3 (523090) 115.0 kV to TC-MCMURRY 3 (523113) 115.0 kV Transmission Circuit #1 b.6. TEXAS_CNTY 3 (523090) 115.0 kV to GEN-2017-100 (589380) 115.0 kV Transmission Circuit #1 b.7. TXPHSF 3 (523106) 115.0 kV to TEXAS_CNTY 3 (523090) 115.0 kV Transmission Circuit #1 b.8. TXPHSF 3 (523106) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.9. TC-MCMURRY 3 (523113) 115.0 kV to TC-AGGIE 3 (523142) 115.0 kV Transmission Circuit #1 b.10. COLE 3 (523120) 115.0 kV to TC-AGGIE 3 (523142) 115.0 kV Transmission Circuit #1 b.11. TC-TXCN_TR11 (523085) 13.2 kV to TEXAS_CNTY 3 (523090) 115.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV Three Winding #1 b.12. TC-TXCN_TR21 (523086) 13.2 kV to TEXAS_CNTY 3 (523090) 115.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_291 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_292 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_293 | Single Phase Fault with Stuck Breaker on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply Fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. NOVUS_WND 1 (523107) 4.2 kV to NOVUS1 1 (523109) 34.5 kV Two Winding #1 b.3. NOVUS1 1 (523109) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.4. G06-44-2 (560581) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.5. NOVUS1_TR1 1 (523110) 13.8 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV Three Winding #1 b.6. NOVUS1 3 (523111) 115.0 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_294 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.3. HITCHLAND 7 (523097) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_295 | Single Phase Fault with Stuck Breaker on NOBLE_WND 7345.00 (523101) 345 kV Bus a. Apply Fault at the NOBLE_WND 7345.00 (523101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. NOBLE_WND 3 (523103) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.3. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-WT4-1 (523121) 0.6 kV Two Winding #1 b.4. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-LV4-1 (523127) 34.5 kV Transmission Circuit #1 b.5. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-WT2-1 (523123) 0.6 kV Two Winding #1 b.6. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-LV2-1 (523129) 34.5 kV Transmission Circuit #1 b.7. GRPLNS-LV4-1 (523127) 34.5 kV to GRPLNS-GT4-1 (523133) 0.5 kV Two Winding #1 b.8. NBLWND-LV2 1 (523128) 34.5 kV to GRPLNS-HV2-3 (523131) 115.0 kV Two Winding #1 b.9. GRPLNS-LV2-1 (523129) 34.5 kV to GRPLNS-GT2-1 (523132) 0.5 kV Two Winding #1 b.10. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-LV4-1 (523127) 34.5 kV Two Winding #1 b.11. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.12. GRPLNS-HV2-3 (523131) 115.0 kV to GRPLNS-LV2-1 (523129) 34.5 kV Two Winding #1 b.13. NOBLE_TR 1 (523102) 13.8 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV Three Winding #1 b.14. NOBLE_WND 3 (523103) 115.0 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_296 | Single Phase Fault with Stuck Breaker on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply Fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.3. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 b.4. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 b.5. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_297 | Single Phase Fault with Stuck Breaker on FARML 4 138.00 (512734) 138 kV Bus a. Apply Fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY1 (512740) 13.8 kV Three Winding #1 b.4. FARML 4 (512734) 138.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_298 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_299 | Single Phase Fault with Stuck Breaker on PAWN-ED3 115.00 (530622) 115 kV Bus a. Apply Fault at the PAWN-ED3 115.00 (530622) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDWARDS3 (530617) 115.0 kV to PAWN-ED3 (530622) 115.0 kV Transmission Circuit #1 b.2. EDWARDS3 (530617) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.3. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.4. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.5. KINSLEY3 (530619) 115.0 kV to PAWN-ED3 (530622) 115.0 kV Transmission Circuit #1 b.6. PAWNEE 3 (530621) 115.0 kV to PAWN-ED3 (530622) 115.0 kV Transmission Circuit #1 b.7. PAWNEE 3 (530621) 115.0 kV to LARNED3 (530685) 115.0 kV Transmission Circuit #1 b.8. ST JOHN3 (530624) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #z1 b.9. ARKVAL 3 (533411) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.10. ARKVALJ3 (533412) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_300 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.3. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_301 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_302 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_303 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_304 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_305 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_306 | Single Phase Fault with Stuck Breaker on DGRASSE4 138.00 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 138.00 (515853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_307 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_308 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_309 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_310 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_311 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_312 | Single Phase Fault with Stuck Breaker on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply Fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALVAOGE2 (514792) 69.0 kV to KNOBHIL2 (514794) 69.0 kV Transmission Circuit #1 b.2. KNOBHIL2 (514794) 69.0 kV to CZYCRVT2 (515560) 69.0 kV Transmission Circuit #1 b.3. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.4. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #1 b.5. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #2 b.6. KNOBHIL2 (514794) 69.0 kV to KNOBHIL4 (514795) 138.0 kV to KNOBHIL1 (515732) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_313 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_314 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_315 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 b.2. TATONGA7 (515407) 345.0 kV to SLNGWND7 (515582) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_316 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_317 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV31 (515795) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_318 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #2 b.2. WWRDEHV7 (515375) 345.0 kV to GUTHRIE7 (515961) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_319 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_320 | Single Phase Fault with Stuck Breaker on 7KINGDM 345.00 (300043) 345 kV Bus a. Apply Fault at the 7KINGDM 345.00 (300043) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7KINGDM (300043) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 b.2. 7KINGDM (300043) 345.0 kV to 5KINGDMB1 (300090) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_321 | Single Phase Fault with Stuck Breaker on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply Fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MCCRED (300044) 345.0 kV to J1490_POI (44888) 345.0 kV Transmission Circuit #1 b.2. 7MCCRED (300044) 345.0 kV to 7KINGDM (300043) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_322 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 b.2. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_323 | Single Phase Fault with Stuck Breaker on 7THOMHL 345.00 (300049) 345 kV Bus a. Apply Fault at the 7THOMHL 345.00 (300049) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7THOMHL (300049) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 b.2. 7THOMHL (300049) 345.0 kV to 5THOMHLXF4 (301510) 161.0 kV Two Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_324 | Single Phase Fault with Stuck Breaker on 5HIGBEEB1 161.00 (300066) 161 kV Bus a. Apply Fault at the 5HIGBEEB1 161.00 (300066) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HIGBEEB1 (300066) 161.0 kV to 5THMHLB4 (301443) 161.0 kV Transmission Circuit #1 b.2. 5HIGBEEB1 (300066) 161.0 kV to 5HARRSBRG (300953) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_325 | Single Phase Fault with Stuck Breaker on 5CLARK 161.00 (300070) 161 kV Bus a. Apply Fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLARK (300070) 161.0 kV to 5HYDERHL (300793) 161.0 kV Transmission Circuit #1 b.2. 5CLARK (300070) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_326 | Single Phase Fault with Stuck Breaker on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply Fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5GEORGE (300082) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 b.2. 5GEORGE (300082) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_327 | Single Phase Fault with Stuck Breaker on 5NORTON 161.00 (300105) 161 kV Bus a. Apply Fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NORTON (300105) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #z1 b.2. 5NORTON (300105) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_328 | Single Phase Fault with Stuck Breaker on 5THMHILB1 161.00 (300120) 161 kV Bus a. Apply Fault at the 5THMHILB1 161.00 (300120) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5MOBTAP (300126) 161.0 kV Transmission Circuit #1 b.2. 5THMHILB1 (300120) 161.0 kV to 5THMHLB2 (300132) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_329 | Single Phase Fault with Stuck Breaker on 5MOBTAP 161.00 (300126) 161 kV Bus a. Apply Fault at the 5MOBTAP 161.00 (300126) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBTAP (300126) 161.0 kV to 5THMHILB1 (300120) 161.0 kV Transmission Circuit #1 b.2. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_330 | Single Phase Fault with Stuck Breaker on 5THMHLB2 161.00 (300132) 161 kV Bus a. Apply Fault at the 5THMHLB2 161.00 (300132) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB2 (300132) 161.0 kV to 5THMHILB1 (300120) 161.0 kV Transmission Circuit #z1 b.2. 5THMHLB2 (300132) 161.0 kV to 5THMHLB4 (301443) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_331 | Single Phase Fault with Stuck Breaker on 5THMHLB3 161.00 (300133) 161 kV Bus a. Apply Fault at the 5THMHLB3 161.00 (300133) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB3 (300133) 161.0 kV to 5THOMHLXF3 (301506) 161.0 kV Transmission Circuit #1 b.2. 5THMHLB3 (300133) 161.0 kV to 5ADAIR1 (344004) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_332 | Single Phase Fault with Stuck Breaker on 2MALTAJ 69.000 (300536) 69 kV Bus a. Apply Fault at the 2MALTAJ 69.000 (300536) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MALTAJ (300536) 69.0 kV to 2NORTON (300540) 69.0 kV Transmission Circuit #1 b.2. 2MALTAJ (300536) 69.0 kV to 2MARSHL (300537) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_333 | Single Phase Fault with Stuck Breaker on 2NAPTON 69.000 (300538) 69 kV Bus a. Apply Fault at the 2NAPTON 69.000 (300538) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2NAPTON (300538) 69.0 kV to 2NORTON (300540) 69.0 kV Transmission Circuit #1 b.2. 2NAPTON (300538) 69.0 kV to 2PILOTG (300560) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_334 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_335 | Single Phase Fault with Stuck Breaker on 5BUTLER 161.00 (301342) 161 kV Bus a. Apply Fault at the 5BUTLER 161.00 (301342) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BUTLER (301342) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit #1 b.2. 5BUTLER (301342) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_336 | Single Phase Fault with Stuck Breaker on 5THMHLB4 161.00 (301443) 161 kV Bus a. Apply Fault at the 5THMHLB4 161.00 (301443) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB4 (301443) 161.0 kV to 5THOMHLXF4 (301510) 161.0 kV Transmission Circuit #1 b.2. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_337 | Single Phase Fault with Stuck Breaker on 7ZACHARY 345.00 (344000) 345 kV Bus a. Apply Fault at the 7ZACHARY 345.00 (344000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ZACHARY (344000) 345.0 kV to J1025POI (345438) 345.0 kV Transmission Circuit #1 b.2. 7ZACHARY (344000) 345.0 kV to 7HUGHES (344011) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_338 | Single Phase Fault with Stuck Breaker on 7HUGHES 345.00 (344011) 345 kV Bus a. Apply Fault at the 7HUGHES 345.00 (344011) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUGHES (344011) 345.0 kV to 7ZACHARY (344000) 345.0 kV Transmission Circuit #1 b.2. 7HUGHES (344011) 345.0 kV to OTTUMWA3 (631143) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_339 | Single Phase Fault with Stuck Breaker on 5MAURER 2 161.00 (344558) 161 kV Bus a. Apply Fault at the 5MAURER 2 161.00 (344558) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MAURER 2 (344558) 161.0 kV to 5MAURER 1 (344557) 161.0 kV Transmission Circuit #z b.2. 5MAURER 2 (344558) 161.0 kV to 2MAURER (346048) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_340 | Single Phase Fault with Stuck Breaker on 2MEXICO UE 69.000 (345193) 69 kV Bus a. Apply Fault at the 2MEXICO UE 69.000 (345193) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MEXICO UE (345193) 69.0 kV to 2AUDRAIN (346009) 69.0 kV Transmission Circuit #1 b.2. 2MEXICO UE (345193) 69.0 kV to 2LADDONIA (346091) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_341 | Single Phase Fault with Stuck Breaker on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply Fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #2 b.2. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_342 | Single Phase Fault with Stuck Breaker on 7MAYWOOD 345.00 (345435) 345 kV Bus a. Apply Fault at the 7MAYWOOD 345.00 (345435) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MAYWOOD (345435) 345.0 kV to 7HERLEMAN (347010) 345.0 kV Transmission Circuit #1 b.2. 7MAYWOOD (345435) 345.0 kV to J1026 POI (40264) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_343 | Single Phase Fault with Stuck Breaker on 5ADAIR1 161.00 (344004) 161 kV Bus a. Apply Fault at the 5ADAIR1 161.00 (344004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ADAIR 1 (346005) 69.0 kV to 5ADAIR1 (344004) 161.0 kV Two Winding #1 b.2. 2ADAIR 1 (346005) 69.0 kV to 2BRKFLD (346025) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_344 | Single Phase Fault with Stuck Breaker on 2AUDRAIN 69.000 (346009) 69 kV Bus a. Apply Fault at the 2AUDRAIN 69.000 (346009) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2AUDRAIN (346009) 69.0 kV to 2MEXICO UE (345193) 69.0 kV Transmission Circuit #1 b.2. 2AUDRAIN (346009) 69.0 kV to 2GUTHRIE (346063) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_345 | Single Phase Fault with Stuck Breaker on 2BRKFLD 69.000 (346025) 69 kV Bus a. Apply Fault at the 2BRKFLD 69.000 (346025) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2BRKFLD (346025) 69.0 kV to 2ADAIR 1 (346005) 69.0 kV Transmission Circuit #1 b.2. 2BRKFLD (346025) 69.0 kV to 2MARCELIN (346099) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_346 | Single Phase Fault with Stuck Breaker on 2CENTRLIA 69.000 (346032) 69 kV Bus a. Apply Fault at the 2CENTRLIA 69.000 (346032) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2CENTRLIA (346032) 69.0 kV to 2RTE EE (346168) 69.0 kV Transmission Circuit #1 b.2. 2CENTRLIA (346032) 69.0 kV to 2AUDRAIN (346009) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_347 | Single Phase Fault with Stuck Breaker on 5GUTHRIE 1 161.00 (344677) 161 kV Bus a. Apply Fault at the 5GUTHRIE 1 161.00 (344677) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GUTHRIE (346063) 69.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Two Winding #1 b.2. 2GUTHRIE (346063) 69.0 kV to 2NEWBLOOM (346111) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_348 | Single Phase Fault with Stuck Breaker on 2HORNER 69.000 (346067) 69 kV Bus a. Apply Fault at the 2HORNER 69.000 (346067) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2HORNER (346067) 69.0 kV to 2SINNOCK (346142) 69.0 kV Transmission Circuit #1 b.2. 2HORNER (346067) 69.0 kV to 2SPRK TAP (346171) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_349 | Single Phase Fault with Stuck Breaker on 2KINGDCTY 69.000 (346090) 69 kV Bus a. Apply Fault at the 2KINGDCTY 69.000 (346090) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2KINGDCTY (346090) 69.0 kV to 2GUTHRIE (346063) 69.0 kV Transmission Circuit #1 b.2. 2KINGDCTY (346090) 69.0 kV to 2AUBONPAN (346167) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_350 | Single Phase Fault with Stuck Breaker on 2MARCELIN 69.000 (346099) 69 kV Bus a. Apply Fault at the 2MARCELIN 69.000 (346099) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MARCELIN (346099) 69.0 kV to 2ROTH TAP (346170) 69.0 kV Transmission Circuit #1 b.2. 2MARCELIN (346099) 69.0 kV to 2BRKFLD (346025) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_351 | Single Phase Fault with Stuck Breaker on 2SINNOCK 69.000 (346142) 69 kV Bus a. Apply Fault at the 2SINNOCK 69.000 (346142) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2SINNOCK (346142) 69.0 kV to 2HORNER (346067) 69.0 kV Transmission Circuit #1 b.2. 2SINNOCK (346142) 69.0 kV to 2RTE EE (346168) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_352 | Single Phase Fault with Stuck Breaker on SCOFCTY4 138.00 (510378) 138 kV Bus a. Apply Fault at the SCOFCTY4 138.00 (510378) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCOFCTY4 (510378) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.2. SCOFCTY4 (510378) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_353 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_354 | Single Phase Fault with Stuck Breaker on MOORLND4 138.00 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 138.00 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORLND4 (520999) 138.0 kV to ASPEN 4 (520462) 138.0 kV Transmission Circuit #1 b.2. MOORLND4 (520999) 138.0 kV to PIC4 (520425) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_355 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_356 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_357 | Single Phase Fault with Stuck Breaker on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.2. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_358 | Single Phase Fault with Stuck Breaker on HASKELL3 115.00 (531374) 115 kV Bus a. Apply Fault at the HASKELL3 115.00 (531374) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASKELL3 (531374) 115.0 kV to SAT-TAP3 (531442) 115.0 kV Transmission Circuit #1 b.2. HASKELL3 (531374) 115.0 kV to SEWARD-3 (531467) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_359 | Single Phase Fault with Stuck Breaker on PIONTAP3 115.00 (531392) 115 kV Bus a. Apply Fault at the PIONTAP3 115.00 (531392) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PIONTAP3 (531392) 115.0 kV to SAT-TAP3 (531442) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_360 | Single Phase Fault with Stuck Breaker on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.2. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_361 | Single Phase Fault with Stuck Breaker on HUGOTON3 115.00 (531481) 115 kV Bus a. Apply Fault at the HUGOTON3 115.00 (531481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.2. HUGOTON3 (531481) 115.0 kV to WALKMYR3 (531405) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_362 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to EXPEDITION7 (532803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_363 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_364 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 7 (532773) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. SUMMIT 7 (532773) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_365 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_366 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_367 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_368 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_369 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_370 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. VIOLA 7 (532798) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_371 | Single Phase Fault with Stuck Breaker on EXPEDITION7 345.00 (532803) 345 kV Bus a. Apply Fault at the EXPEDITION7 345.00 (532803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EXPEDITION7 (532803) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. EXPEDITION7 (532803) 345.0 kV to EMPEC 7 (532768) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_372 | Single Phase Fault with Stuck Breaker on EVANS N4 138.00 (533040) 138 kV Bus a. Apply Fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.2. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_373 | Single Phase Fault with Stuck Breaker on BERG 3 115.00 (533367) 115 kV Bus a. Apply Fault at the BERG 3 115.00 (533367) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BERG 3 (533367) 115.0 kV to MENTOR 3 (533374) 115.0 kV Transmission Circuit #1 b.2. BERG 3 (533367) 115.0 kV to SMOKYHLLS3 (533378) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_374 | Single Phase Fault with Stuck Breaker on MENTOR 3 115.00 (533374) 115 kV Bus a. Apply Fault at the MENTOR 3 115.00 (533374) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MENTOR 3 (533374) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.2. MENTOR 3 (533374) 115.0 kV to CORONAD3 (533394) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_375 | Single Phase Fault with Stuck Breaker on MOUNDRG3 115.00 (533429) 115 kV Bus a. Apply Fault at the MOUNDRG3 115.00 (533429) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOUNDRG3 (533429) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 b.2. MOUNDRG3 (533429) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_376 | Single Phase Fault with Stuck Breaker on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLATRDG4 (539638) 138.0 kV to THISTLE4 (539804) 138.0 kV Transmission Circuit #1 b.2. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_377 | Single Phase Fault with Stuck Breaker on HAYNE3 115.00 (539640) 115 kV Bus a. Apply Fault at the HAYNE3 115.00 (539640) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYNE3 (539640) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.2. HAYNE3 (539640) 115.0 kV to NLIB 3 (539737) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_378 | Single Phase Fault with Stuck Breaker on CIM-PLT3 115.00 (539654) 115 kV Bus a. Apply Fault at the CIM-PLT3 115.00 (539654) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIM-PLT3 (539654) 115.0 kV to HAYNE3 (539640) 115.0 kV Transmission Circuit #1 b.2. CIM-PLT3 (539654) 115.0 kV to WALKMYR3 (531405) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_379 | Single Phase Fault with Stuck Breaker on E-LIBER3 115.00 (539672) 115 kV Bus a. Apply Fault at the E-LIBER3 115.00 (539672) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. E-LIBER3 (539672) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.2. E-LIBER3 (539672) 115.0 kV to NATBEEF3 (539751) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_380 | Single Phase Fault with Stuck Breaker on NLIB 3 115.00 (539737) 115 kV Bus a. Apply Fault at the NLIB 3 115.00 (539737) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NLIB 3 (539737) 115.0 kV to HAYNE3 (539640) 115.0 kV Transmission Circuit #1 b.2. NLIB 3 (539737) 115.0 kV to NATBEEF3 (539751) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_381 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_382 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. THISTLE7 (539801) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_383 | Single Phase Fault with Stuck Breaker on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply Fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IRONWOOD7 (539803) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.2. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_384 | Single Phase Fault with Stuck Breaker on ELMCREEK7 345.00 (539805) 345 kV Bus a. Apply Fault at the ELMCREEK7 345.00 (539805) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELMCREEK7 (539805) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 b.2. ELMCREEK7 (539805) 345.0 kV to ELMCREK6 (539639) 230.0 kV to ELMCREEK1 (539806) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_385 | Single Phase Fault with Stuck Breaker on POSTOAK2 69.000 (541300) 69 kV Bus a. Apply Fault at the POSTOAK2 69.000 (541300) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTOAK2 (541300) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 b.2. POSTOAK2 (541300) 69.0 kV to WBURGP 2 (541268) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_386 | Single Phase Fault with Stuck Breaker on CLNTPLT2 69.000 (541301) 69 kV Bus a. Apply Fault at the CLNTPLT2 69.000 (541301) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLNTPLT2 (541301) 69.0 kV to CLNTN S2 (541320) 69.0 kV Transmission Circuit #1 b.2. CLNTPLT2 (541301) 69.0 kV to POSTOAK2 (541300) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_387 | Single Phase Fault with Stuck Breaker on URICHTP2 69.000 (541304) 69 kV Bus a. Apply Fault at the URICHTP2 69.000 (541304) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. URICHTP2 (541304) 69.0 kV to APCITY 2 (541306) 69.0 kV Transmission Circuit #1 b.2. URICHTP2 (541304) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_388 | Single Phase Fault with Stuck Breaker on APCITY 2 69.000 (541306) 69 kV Bus a. Apply Fault at the APCITY 2 69.000 (541306) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. APCITY 2 (541306) 69.0 kV to URICHTP2 (541304) 69.0 kV Transmission Circuit #1 b.2. APCITY 2 (541306) 69.0 kV to NEVADA 2 (541308) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_389 | Single Phase Fault with Stuck Breaker on NEVPLT 2 69.000 (541307) 69 kV Bus a. Apply Fault at the NEVPLT 2 69.000 (541307) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEVPLT 2 (541307) 69.0 kV to NEVADA 2 (541308) 69.0 kV Transmission Circuit #2 b.2. NEVPLT 2 (541307) 69.0 kV to NEVADA 2 (541308) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_390 | Single Phase Fault with Stuck Breaker on NEVADA 2 69.000 (541308) 69 kV Bus a. Apply Fault at the NEVADA 2 69.000 (541308) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEVADA 2 (541308) 69.0 kV to NEVPLT 2 (541307) 69.0 kV Transmission Circuit #2 b.2. NEVADA 2 (541308) 69.0 kV to NEVPLT 2 (541307) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_391 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_392 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WGARDNR5 (542966) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 b.2. WGARDNR5 (542966) 161.0 kV to W.GRDNR7 (542965) 345.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_393 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_394 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 5 (542978) 161.0 kV to CRAIG 7 (542977) 345.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 b.2. CRAIG 5 (542978) 161.0 kV to CRAIG 7 (542977) 345.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_395 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_396 | Single Phase Fault with Stuck Breaker on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply Fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHWNMSN5 (543031) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 b.2. SHWNMSN5 (543031) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_397 | Single Phase Fault with Stuck Breaker on MOONLT 5 161.00 (543044) 161 kV Bus a. Apply Fault at the MOONLT 5 161.00 (543044) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOONLT 5 (543044) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 b.2. MOONLT 5 (543044) 161.0 kV to QUARRY 5 (543037) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_398 | Single Phase Fault with Stuck Breaker on SEOTTWA5 161.00 (543055) 161 kV Bus a. Apply Fault at the SEOTTWA5 161.00 (543055) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEOTTWA5 (543055) 161.0 kV to PLSTVAL5 (543077) 161.0 kV Transmission Circuit #1 b.2. SEOTTWA5 (543055) 161.0 kV to S.OTTWA5 (543066) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_399 | Single Phase Fault with Stuck Breaker on MALTABN5 161.00 (543059) 161 kV Bus a. Apply Fault at the MALTABN5 161.00 (543059) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALTABN5 (543059) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.2. MALTABN5 (543059) 161.0 kV to SWAVRLY5 (543063) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_400 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALSBRY5 (543062) 161.0 kV to 5THMHLB4 (301443) 161.0 kV Transmission Circuit #1 b.2. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_401 | Single Phase Fault with Stuck Breaker on CNTRVIL5 161.00 (543065) 161 kV Bus a. Apply Fault at the CNTRVIL5 161.00 (543065) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CNTRVIL5 (543065) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 b.2. CNTRVIL5 (543065) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_402 | Single Phase Fault with Stuck Breaker on S.OTTWA5 161.00 (543066) 161 kV Bus a. Apply Fault at the S.OTTWA5 161.00 (543066) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.OTTWA5 (543066) 161.0 kV to SEOTTWA5 (543055) 161.0 kV Transmission Circuit #1 b.2. S.OTTWA5 (543066) 161.0 kV to S.OTTWA21 (543121) 34.5 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_403 | Single Phase Fault with Stuck Breaker on CENTENL5 161.00 (543067) 161 kV Bus a. Apply Fault at the CENTENL5 161.00 (543067) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTENL5 (543067) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 b.2. CENTENL5 (543067) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_404 | Single Phase Fault with Stuck Breaker on PAOLA 5 161.00 (543069) 161 kV Bus a. Apply Fault at the PAOLA 5 161.00 (543069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAOLA 5 (543069) 161.0 kV to CNTRVIL5 (543065) 161.0 kV Transmission Circuit #1 b.2. PAOLA 5 (543069) 161.0 kV to CENTENL5 (543067) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_405 | Single Phase Fault with Stuck Breaker on S EAST 5 161.00 (543071) 161 kV Bus a. Apply Fault at the S EAST 5 161.00 (543071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S EAST 5 (543071) 161.0 kV to MRSHLJT5 (543072) 161.0 kV Transmission Circuit #1 b.2. S EAST 5 (543071) 161.0 kV to WEST---5 (543070) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_406 | Single Phase Fault with Stuck Breaker on MRSHLJT5 161.00 (543072) 161 kV Bus a. Apply Fault at the MRSHLJT5 161.00 (543072) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MRSHLJT5 (543072) 161.0 kV to MIAMI_ 5 (543073) 161.0 kV Transmission Circuit #1 b.2. MRSHLJT5 (543072) 161.0 kV to S EAST 5 (543071) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_407 | Single Phase Fault with Stuck Breaker on PLSTVAL5 161.00 (543077) 161 kV Bus a. Apply Fault at the PLSTVAL5 161.00 (543077) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLSTVAL5 (543077) 161.0 kV to SEOTTWA5 (543055) 161.0 kV Transmission Circuit #1 b.2. PLSTVAL5 (543077) 161.0 kV to WGARDNR5 (542966) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_408 | Single Phase Fault with Stuck Breaker on COURTNY2 69.000 (543085) 69 kV Bus a. Apply Fault at the COURTNY2 69.000 (543085) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COURTNY2 (543085) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 b.2. COURTNY2 (543085) 69.0 kV to MILCKJT2 (543110) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_409 | Single Phase Fault with Stuck Breaker on LAKCTYJ2 69.000 (543087) 69 kV Bus a. Apply Fault at the LAKCTYJ2 69.000 (543087) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKCTYJ2 (543087) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.2. LAKCTYJ2 (543087) 69.0 kV to LAKCTY 2 (543092) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_410 | Single Phase Fault with Stuck Breaker on BLUSPRG2 69.000 (543088) 69 kV Bus a. Apply Fault at the BLUSPRG2 69.000 (543088) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUSPRG2 (543088) 69.0 kV to LAKCTYK2 (543093) 69.0 kV Transmission Circuit #1 b.2. BLUSPRG2 (543088) 69.0 kV to LAKCTY 2 (543092) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_411 | Single Phase Fault with Stuck Breaker on SUGRCK_TP_W269.000 (543164) 69 kV Bus a. Apply Fault at the SUGRCK_TP_W269.000 (543164) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUGRCK_TP_W2 (543164) 69.0 kV to SUB F (548803) 69.0 kV Transmission Circuit #1 b.2. SUGRCK_TP_W2 (543164) 69.0 kV to SUGRCK_TP_E2 (543165) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_412 | Single Phase Fault with Stuck Breaker on SUGRCK_TP_E269.000 (543165) 69 kV Bus a. Apply Fault at the SUGRCK_TP_E269.000 (543165) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUGRCK_TP_E2 (543165) 69.0 kV to SUGRCK_TP_W2 (543164) 69.0 kV Transmission Circuit #1 b.2. SUGRCK_TP_E2 (543165) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_413 | Single Phase Fault with Stuck Breaker on DAKOTA_5 161.00 (543650) 161 kV Bus a. Apply Fault at the DAKOTA_5 161.00 (543650) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAKOTA_5 (543650) 161.0 kV to MARMTNE5 (532934) 161.0 kV Transmission Circuit #1 b.2. DAKOTA_5 (543650) 161.0 kV to CNTRVIL5 (543065) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_414 | Single Phase Fault with Stuck Breaker on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply Fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP 59 2 (547525) 69.0 kV to GAT258 2 (547551) 69.0 kV Transmission Circuit #1 b.2. JOP 59 2 (547525) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_415 | Single Phase Fault with Stuck Breaker on COL 94 2 69.000 (547530) 69 kV Bus a. Apply Fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL 94 2 (547530) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. COL 94 2 (547530) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_416 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV167 2 (547541) 69.0 kV to RIV4525 (547469) 161.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 b.2. RIV167 2 (547541) 69.0 kV to JOP 59 2 (547525) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_417 | Single Phase Fault with Stuck Breaker on SUB I 69.000 (548800) 69 kV Bus a. Apply Fault at the SUB I 69.000 (548800) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB I (548800) 69.0 kV to SUB C (548825) 69.0 kV Transmission Circuit #1 b.2. SUB I (548800) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_418 | Single Phase Fault with Stuck Breaker on SUB K 69.000 (548801) 69 kV Bus a. Apply Fault at the SUB K 69.000 (548801) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB K (548801) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.2. SUB K (548801) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_419 | Single Phase Fault with Stuck Breaker on SUB H 69.000 (548802) 69 kV Bus a. Apply Fault at the SUB H 69.000 (548802) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB H (548802) 69.0 kV to COURTNY2 (543085) 69.0 kV Transmission Circuit #1 b.2. SUB H (548802) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_420 | Single Phase Fault with Stuck Breaker on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_421 | Single Phase Fault with Stuck Breaker on SHRNKRD 69.000 (548809) 69 kV Bus a. Apply Fault at the SHRNKRD 69.000 (548809) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHRNKRD (548809) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 b.2. SHRNKRD (548809) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_422 | Single Phase Fault with Stuck Breaker on SUB B 69.000 (548810) 69 kV Bus a. Apply Fault at the SUB B 69.000 (548810) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB B (548810) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 b.2. SUB B (548810) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_423 | Single Phase Fault with Stuck Breaker on SUB J 69.000 (548811) 69 kV Bus a. Apply Fault at the SUB J 69.000 (548811) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB J (548811) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.2. SUB J (548811) 69.0 kV to SUB B (548810) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_424 | Single Phase Fault with Stuck Breaker on 7THOMHL 345.00 (300049) 345 kV Bus a. Apply Fault at the 7THOMHL 345.00 (300049) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THOMHLXF3 (301506) 161.0 kV to 7THOMHL (300049) 345.0 kV Two Winding #3 b.2. 5THOMHLXF3 (301506) 161.0 kV to 5THMHLB3 (300133) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_425 | Single Phase Fault with Stuck Breaker on 7THOMHL 345.00 (300049) 345 kV Bus a. Apply Fault at the 7THOMHL 345.00 (300049) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THOMHLXF4 (301510) 161.0 kV to 7THOMHL (300049) 345.0 kV Two Winding #4 b.2. 5THOMHLXF4 (301510) 161.0 kV to 5THMHLB4 (301443) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_426 | Single Phase Fault with Stuck Breaker on 5CLARK 161.00 (300070) 161 kV Bus a. Apply Fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2CLARK (300802) 69.0 kV to 5CLARK (300070) 161.0 kV Two Winding #1 b.2. 2CLARK (300802) 69.0 kV to 2MILO (300654) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_427 | Single Phase Fault with Stuck Breaker on 5NORTON 161.00 (300105) 161 kV Bus a. Apply Fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2NORTON (300540) 69.0 kV to 5NORTON (300105) 161.0 kV Two Winding #2 b.2. 2NORTON (300540) 69.0 kV to 2NAPTON (300538) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_428 | Single Phase Fault with Stuck Breaker on 5NOVELY_SW 161.00 (300106) 161 kV Bus a. Apply Fault at the 5NOVELY_SW 161.00 (300106) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2NOVLTY_SW (300364) 69.0 kV to 5NOVELY_SW (300106) 161.0 kV Two Winding #1 b.2. 2NOVLTY_SW (300364) 69.0 kV to 2BARING (300357) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_429 | Single Phase Fault with Stuck Breaker on 5BUTLER 161.00 (301342) 161 kV Bus a. Apply Fault at the 5BUTLER 161.00 (301342) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2BUTLER (300689) 69.0 kV to 5BUTLER (301342) 161.0 kV Two Winding #1 b.2. 2BUTLER (300689) 69.0 kV to 2BUTLERE (300690) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_430 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 b.2. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_431 | Single Phase Fault with Stuck Breaker on 7JASPER 345.00 (300949) 345 kV Bus a. Apply Fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5JASPER (300950) 161.0 kV to 5LAMAR (300794) 161.0 kV Transmission Circuit #1 b.2. 5JASPER (300950) 161.0 kV to 7JASPER (300949) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_432 | Single Phase Fault with Stuck Breaker on FARML 4 138.00 (512734) 138 kV Bus a. Apply Fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARML 4 (512734) 138.0 kV to DELWARE4 (510379) 138.0 kV Transmission Circuit #1 b.2. FARML 4 (512734) 138.0 kV to SCOFCTY4 (510378) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_433 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARBNGR3 (531510) 115.0 kV to WALKMYR3 (531405) 115.0 kV Transmission Circuit #1 b.2. HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV to HARBNGR-T (531511) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_434 | Single Phase Fault with Stuck Breaker on MOUND 4 138.00 (533013) 138 kV Bus a. Apply Fault at the MOUND 4 138.00 (533013) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOUND 4 (533013) 138.0 kV to MOUND 2 (533742) 69.0 kV to MOUND1X1 (533095) 13.2 kV Three Winding #1 b.2. MOUND 4 (533013) 138.0 kV to HALSTD 4 (533011) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_435 | Single Phase Fault with Stuck Breaker on BARBER 4 138.00 (539674) 138 kV Bus a. Apply Fault at the BARBER 4 138.00 (539674) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARBER 3 (539760) 115.0 kV to SAWYER 3 (539649) 115.0 kV Transmission Circuit #1 b.2. BARBER 3 (539760) 115.0 kV to BARBER 4 (539674) 138.0 kV to BARBER-T (539917) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_436 | Single Phase Fault with Stuck Breaker on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply Fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_437 | Single Phase Fault with Stuck Breaker on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply Fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 b.2. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_438 | Single Phase Fault with Stuck Breaker on NORTHVW3 115.00 (533371) 115 kV Bus a. Apply Fault at the NORTHVW3 115.00 (533371) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTHVW3 (533371) 115.0 kV to G17-120-TAP (760007) 115.0 kV Transmission Circuit #1 b.2. NORTHVW3 (533371) 115.0 kV to NORTHST3 (533370) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_439 | Single Phase Fault with Stuck Breaker on HARPER 4 138.00 (539668) 138 kV Bus a. Apply Fault at the HARPER 4 138.00 (539668) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARPER 4 (539668) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. HARPER 4 (539668) 138.0 kV to ANTHONY4 (539001) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_440 | Single Phase Fault with Stuck Breaker on NORTON 5 161.00 (543064) 161 kV Bus a. Apply Fault at the NORTON 5 161.00 (543064) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTON 5 (543064) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. NORTON 5 (543064) 161.0 kV to 5NORTON (300105) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_441 | Single Phase Fault with Stuck Breaker on SUB M-161 161.00 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 161.00 (548814) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB M (548815) 69.0 kV to SUB M-161 (548814) 161.0 kV Two Winding #1 b.2. SUB M (548815) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_442 | Single Phase Fault with Stuck Breaker on 7JASPER 345.00 (300949) 345 kV Bus a. Apply Fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7JASPER (300949) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit #1 b.2. 7JASPER (300949) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_443 | Single Phase Fault with Stuck Breaker on 5HARRSBRG 161.00 (300953) 161 kV Bus a. Apply Fault at the 5HARRSBRG 161.00 (300953) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HARRSBRG (300953) 161.0 kV to 5HIGBEEB1 (300066) 161.0 kV Transmission Circuit #1 b.2. 5HARRSBRG (300953) 161.0 kV to 5HINTON (300499) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_444 | Single Phase Fault with Stuck Breaker on 5HIGBEEB2 161.00 (301494) 161 kV Bus a. Apply Fault at the 5HIGBEEB2 161.00 (301494) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HIGBEEB2 (301494) 161.0 kV to 5STURGN (300508) 161.0 kV Transmission Circuit #1 b.2. 5HIGBEEB2 (301494) 161.0 kV to 5MOBTAP (300126) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_445 | Single Phase Fault with Stuck Breaker on 5HYDERHL 161.00 (300793) 161 kV Bus a. Apply Fault at the 5HYDERHL 161.00 (300793) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HYDERHL (300793) 161.0 kV to 5CLARK (300070) 161.0 kV Transmission Circuit #1 b.2. 5HYDERHL (300793) 161.0 kV to 2HYDERHL (300798) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_446 | Single Phase Fault with Stuck Breaker on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply Fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LAMAR (300794) 161.0 kV to 5JASPER (300950) 161.0 kV Transmission Circuit #1 b.2. 5LAMAR (300794) 161.0 kV to 2LAMR (300651) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_447 | Single Phase Fault with Stuck Breaker on NEVADA 5 161.00 (541208) 161 kV Bus a. Apply Fault at the NEVADA 5 161.00 (541208) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEVADA 5 (541208) 161.0 kV to 5BUTLER (301342) 161.0 kV Transmission Circuit #1 b.2. NEVADA 5 (541208) 161.0 kV to 5CLARK (300070) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_448 | Single Phase Fault with Stuck Breaker on 5NORTONTP 161.00 (301567) 161 kV Bus a. Apply Fault at the 5NORTONTP 161.00 (301567) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NORTONTP (301567) 161.0 kV to 5GEORGE (300082) 161.0 kV Transmission Circuit #1 b.2. 5NORTONTP (301567) 161.0 kV to 5NORTON (300105) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_449 | Single Phase Fault with Stuck Breaker on 5BEVIER 161.00 (300381) 161 kV Bus a. Apply Fault at the 5BEVIER 161.00 (300381) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BEVIER (300381) 161.0 kV to 5THMHLB2 (300132) 161.0 kV Transmission Circuit #1 b.2. 5BEVIER (300381) 161.0 kV to 2BEVIER (300387) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_450 | Single Phase Fault with Stuck Breaker on 5THOMHLXF1 161.00 (301508) 161 kV Bus a. Apply Fault at the 5THOMHLXF1 161.00 (301508) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THOMHLXF1 (301508) 161.0 kV to 5THMHLB2 (300132) 161.0 kV Transmission Circuit #1 b.2. 5THOMHLXF1 (301508) 161.0 kV to 2THOMHLXF1 (301509) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_451 | Single Phase Fault with Stuck Breaker on 5MEADVLB1 161.00 (300207) 161 kV Bus a. Apply Fault at the 5MEADVLB1 161.00 (300207) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MEADVLB1 (300207) 161.0 kV to 5THMHLB3 (300133) 161.0 kV Transmission Circuit #1 b.2. 5MEADVLB1 (300207) 161.0 kV to 5MEADVLB2 (301562) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_452 | Single Phase Fault with Stuck Breaker on 2MARSHL 69.000 (300537) 69 kV Bus a. Apply Fault at the 2MARSHL 69.000 (300537) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MARSHL (300537) 69.0 kV to 2MALTAJ (300536) 69.0 kV Transmission Circuit #1 b.2. 2MARSHL (300537) 69.0 kV to 2SWSPJC (300543) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_453 | Single Phase Fault with Stuck Breaker on 2PILOTG 69.000 (300560) 69 kV Bus a. Apply Fault at the 2PILOTG 69.000 (300560) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2PILOTG (300560) 69.0 kV to 2NAPTON (300538) 69.0 kV Transmission Circuit #1 b.2. 2PILOTG (300560) 69.0 kV to 2PRARIE (300561) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_454 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_455 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_456 | Single Phase Fault with Stuck Breaker on ADRIAN 5 161.00 (541240) 161 kV Bus a. Apply Fault at the ADRIAN 5 161.00 (541240) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ADRIAN 5 (541240) 161.0 kV to ARCHIE 5 (541207) 161.0 kV Transmission Circuit #1 b.2. ADRIAN 5 (541240) 161.0 kV to 5BUTLER (301342) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_457 | Single Phase Fault with Stuck Breaker on OTTUMWA3 345.00 (631143) 345 kV Bus a. Apply Fault at the OTTUMWA3 345.00 (631143) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTUMWA3 (631143) 345.0 kV to MNTZUMA3 (635730) 345.0 kV Transmission Circuit #1 b.2. OTTUMWA3 (631143) 345.0 kV to OTTUMWA5 (631115) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_458 | Single Phase Fault with Stuck Breaker on CAROLTN5 161.00 (543060) 161 kV Bus a. Apply Fault at the CAROLTN5 161.00 (543060) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit #1 b.2. CAROLTN5 (543060) 161.0 kV to 5MAURER 2 (344558) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_459 | Single Phase Fault with Stuck Breaker on 2LADDONIA 69.000 (346091) 69 kV Bus a. Apply Fault at the 2LADDONIA 69.000 (346091) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2LADDONIA (346091) 69.0 kV to 2VANDAL_AM (346146) 69.0 kV Transmission Circuit #1 b.2. 2LADDONIA (346091) 69.0 kV to 2MEXICO UE (345193) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_460 | Single Phase Fault with Stuck Breaker on 2DUPONT 69.000 (346169) 69 kV Bus a. Apply Fault at the 2DUPONT 69.000 (346169) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2DUPONT (346169) 69.0 kV to 2MOBERLY (345222) 69.0 kV Transmission Circuit #1 b.2. 2DUPONT (346169) 69.0 kV to 2SINNOCK (346142) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_461 | Single Phase Fault with Stuck Breaker on 2ROTH TAP 69.000 (346170) 69 kV Bus a. Apply Fault at the 2ROTH TAP 69.000 (346170) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ROTH TAP (346170) 69.0 kV to 2MOBERLY (345222) 69.0 kV Transmission Circuit #1 b.2. 2ROTH TAP (346170) 69.0 kV to 2MARCELIN (346099) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_462 | Single Phase Fault with Stuck Breaker on 2SPRK TAP 69.000 (346171) 69 kV Bus a. Apply Fault at the 2SPRK TAP 69.000 (346171) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2SPRK TAP (346171) 69.0 kV to 2MOBERLY (345222) 69.0 kV Transmission Circuit #1 b.2. 2SPRK TAP (346171) 69.0 kV to 2HORNER (346067) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_463 | Single Phase Fault with Stuck Breaker on 5ADAIR3 161.00 (344006) 161 kV Bus a. Apply Fault at the 5ADAIR3 161.00 (344006) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ADAIR 2 (346006) 69.0 kV to 5ADAIR3 (344006) 161.0 kV Two Winding #1 b.2. 2ADAIR 2 (346006) 69.0 kV to 2ADAIR 1 (346005) 69.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_464 | Single Phase Fault with Stuck Breaker on 2AUBONPAN 69.000 (346167) 69 kV Bus a. Apply Fault at the 2AUBONPAN 69.000 (346167) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2AUBONPAN (346167) 69.0 kV to 2KINGDCTY (346090) 69.0 kV Transmission Circuit #1 b.2. 2AUBONPAN (346167) 69.0 kV to 2AUDRAIN (346009) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_465 | Single Phase Fault with Stuck Breaker on 2RTE EE 69.000 (346168) 69 kV Bus a. Apply Fault at the 2RTE EE 69.000 (346168) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2RTE EE (346168) 69.0 kV to 2SINNOCK (346142) 69.0 kV Transmission Circuit #1 b.2. 2RTE EE (346168) 69.0 kV to 2CENTRLIA (346032) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_466 | Single Phase Fault with Stuck Breaker on 2JC WESTG 69.000 (346088) 69 kV Bus a. Apply Fault at the 2JC WESTG 69.000 (346088) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2JC WESTG (346088) 69.0 kV to 2GUTHRIE (346063) 69.0 kV Transmission Circuit #1 b.2. 2JC WESTG (346088) 69.0 kV to 2JC FAIR (344805) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_467 | Single Phase Fault with Stuck Breaker on 2NEWBLOOM 69.000 (346111) 69 kV Bus a. Apply Fault at the 2NEWBLOOM 69.000 (346111) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2NEWBLOOM (346111) 69.0 kV to 2GUTHRIE (346063) 69.0 kV Transmission Circuit #1 b.2. 2NEWBLOOM (346111) 69.0 kV to 2HOLTSSUM (346066) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_468 | Single Phase Fault with Stuck Breaker on G07621119-20345.00 (515599) 345 kV Bus a. Apply Fault at the G07621119-20345.00 (515599) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G07621119-20 (515599) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 b.2. G07621119-20 (515599) 345.0 kV to GREAT_WESTRN (585410) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_469 | Single Phase Fault with Stuck Breaker on BECKHAM7 345.00 (516059) 345 kV Bus a. Apply Fault at the BECKHAM7 345.00 (516059) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 b.2. BECKHAM7 (516059) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_470 | Single Phase Fault with Stuck Breaker on G16-003-TAP 345.00 (560071) 345 kV Bus a. Apply Fault at the G16-003-TAP 345.00 (560071) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_471 | Single Phase Fault with Stuck Breaker on SEWARD-3 115.00 (531467) 115 kV Bus a. Apply Fault at the SEWARD-3 115.00 (531467) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWARD-3 (531467) 115.0 kV to HASKELL3 (531374) 115.0 kV Transmission Circuit #1 b.2. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_472 | Single Phase Fault with Stuck Breaker on SCHILNG3 115.00 (533377) 115 kV Bus a. Apply Fault at the SCHILNG3 115.00 (533377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCHILNG3 (533377) 115.0 kV to CRAWFRD3 (533364) 115.0 kV Transmission Circuit #1 b.2. SCHILNG3 (533377) 115.0 kV to MENTOR 3 (533374) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_473 | Single Phase Fault with Stuck Breaker on LABETTS2 69.000 (533696) 69 kV Bus a. Apply Fault at the LABETTS2 69.000 (533696) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.2. LABETTS2 (533696) 69.0 kV to ALTAMNS2 (533672) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_474 | Single Phase Fault with Stuck Breaker on BARBER 4 138.00 (539674) 138 kV Bus a. Apply Fault at the BARBER 4 138.00 (539674) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARBER 4 (539674) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. BARBER 4 (539674) 138.0 kV to BARBER 3 (539760) 115.0 kV to BARBER-T (539917) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_475 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE4 (539804) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. THISTLE4 (539804) 138.0 kV to THISTLE7 (539801) 345.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_476 | Single Phase Fault with Stuck Breaker on NATBEEF3 115.00 (539751) 115 kV Bus a. Apply Fault at the NATBEEF3 115.00 (539751) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NATBEEF3 (539751) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.2. NATBEEF3 (539751) 115.0 kV to NLIB 3 (539737) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_477 | Single Phase Fault with Stuck Breaker on CLNTGRN2 69.000 (541302) 69 kV Bus a. Apply Fault at the CLNTGRN2 69.000 (541302) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLNTGRN2 (541302) 69.0 kV to CLNTN N2 (541303) 69.0 kV Transmission Circuit #1 b.2. CLNTGRN2 (541302) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_478 | Single Phase Fault with Stuck Breaker on CLINTON5 161.00 (541242) 161 kV Bus a. Apply Fault at the CLINTON5 161.00 (541242) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLNTN S2 (541320) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 b.2. CLNTN S2 (541320) 69.0 kV to CLINTON5 (541242) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_479 | Single Phase Fault with Stuck Breaker on CEDRCRK5 161.00 (543049) 161 kV Bus a. Apply Fault at the CEDRCRK5 161.00 (543049) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CEDRCRK5 (543049) 161.0 kV to WGARDNR5 (542966) 161.0 kV Transmission Circuit #1 b.2. CEDRCRK5 (543049) 161.0 kV to SHWNMSN5 (543031) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_480 | Single Phase Fault with Stuck Breaker on BNSF 5 161.00 (543132) 161 kV Bus a. Apply Fault at the BNSF 5 161.00 (543132) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BNSF 5 (543132) 161.0 kV to WGARDNR5 (542966) 161.0 kV Transmission Circuit #1 b.2. BNSF 5 (543132) 161.0 kV to MOONLT 5 (543044) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_481 | Single Phase Fault with Stuck Breaker on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply Fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #z2 b.2. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_482 | Single Phase Fault with Stuck Breaker on SWAVRLY5 161.00 (543063) 161 kV Bus a. Apply Fault at the SWAVRLY5 161.00 (543063) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWAVRLY5 (543063) 161.0 kV to MALTABN5 (543059) 161.0 kV Transmission Circuit #1 b.2. SWAVRLY5 (543063) 161.0 kV to SWAVRLY2 (543094) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_483 | Single Phase Fault with Stuck Breaker on WAGSTAF5 161.00 (543068) 161 kV Bus a. Apply Fault at the WAGSTAF5 161.00 (543068) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGSTAF5 (543068) 161.0 kV to CENTENL5 (543067) 161.0 kV Transmission Circuit #1 b.2. WAGSTAF5 (543068) 161.0 kV to BUCYRUS5 (543057) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_484 | Single Phase Fault with Stuck Breaker on MIAMI_ 5 161.00 (543073) 161 kV Bus a. Apply Fault at the MIAMI_ 5 161.00 (543073) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI_ 5 (543073) 161.0 kV to MRSHLJT5 (543072) 161.0 kV Transmission Circuit #1 b.2. MIAMI_ 5 (543073) 161.0 kV to WEST---5 (543070) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_485 | Single Phase Fault with Stuck Breaker on MILCKJT2 69.000 (543110) 69 kV Bus a. Apply Fault at the MILCKJT2 69.000 (543110) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MILCKJT2 (543110) 69.0 kV to COURTNY2 (543085) 69.0 kV Transmission Circuit #1 b.2. MILCKJT2 (543110) 69.0 kV to LAFJCT 2 (543104) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_486 | Single Phase Fault with Stuck Breaker on LAKCTY 2 69.000 (543092) 69 kV Bus a. Apply Fault at the LAKCTY 2 69.000 (543092) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKCTY 2 (543092) 69.0 kV to LAKCTYJ2 (543087) 69.0 kV Transmission Circuit #1 b.2. LAKCTY 2 (543092) 69.0 kV to BLUSPRG2 (543088) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_487 | Single Phase Fault with Stuck Breaker on LAKCTYK2 69.000 (543093) 69 kV Bus a. Apply Fault at the LAKCTYK2 69.000 (543093) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKCTYK2 (543093) 69.0 kV to DUNCNRD2 (543091) 69.0 kV Transmission Circuit #1 b.2. LAKCTYK2 (543093) 69.0 kV to BLUSPRG2 (543088) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_488 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STL439 5 (547498) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. STL439 5 (547498) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_489 | Single Phase Fault with Stuck Breaker on RIV406 2 69.000 (547602) 69 kV Bus a. Apply Fault at the RIV406 2 69.000 (547602) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV406 2 (547602) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. RIV406 2 (547602) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_490 | Single Phase Fault with Stuck Breaker on GLF339 2 69.000 (547690) 69 kV Bus a. Apply Fault at the GLF339 2 69.000 (547690) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLF339 2 (547690) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. GLF339 2 (547690) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_491 | Single Phase Fault with Stuck Breaker on SUB C 69.000 (548825) 69 kV Bus a. Apply Fault at the SUB C 69.000 (548825) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB C (548825) 69.0 kV to STRLNGRD (548826) 69.0 kV Transmission Circuit #1 b.2. SUB C (548825) 69.0 kV to SUB I (548800) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_492 | Single Phase Fault with Stuck Breaker on SUB P 69.000 (548827) 69 kV Bus a. Apply Fault at the SUB P 69.000 (548827) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB P (548827) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.2. SUB P (548827) 69.0 kV to SUB I (548800) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_493 | Single Phase Fault with Stuck Breaker on SUB R 69.000 (548830) 69 kV Bus a. Apply Fault at the SUB R 69.000 (548830) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB R (548830) 69.0 kV to SHRNKRD (548809) 69.0 kV Transmission Circuit #1 b.2. SUB R (548830) 69.0 kV to SUB K (548801) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_494 | Single Phase Fault with Stuck Breaker on 5NOVELY_SW 161.00 (300106) 161 kV Bus a. Apply Fault at the 5NOVELY_SW 161.00 (300106) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NOVELY_SW (300106) 161.0 kV to 5ADAIR3 (344006) 161.0 kV Transmission Circuit #1 b.2. 5NOVELY_SW (300106) 161.0 kV to 5NEWARK (300363) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_495 | Single Phase Fault with Stuck Breaker on 5GUTHRIE 1 161.00 (344677) 161 kV Bus a. Apply Fault at the 5GUTHRIE 1 161.00 (344677) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5GUTHRIE 1 (344677) 161.0 kV to 2GUTHRIE (346063) 69.0 kV Two Winding #1 b.2. 5GUTHRIE 1 (344677) 161.0 kV to 5LOYMART 1 (344040) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_496 | Single Phase Fault with Stuck Breaker on MOORLND4 138.00 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 138.00 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORLND2 (520995) 69.0 kV to CRTSJCT2 (521197) 69.0 kV Transmission Circuit #1 b.2. MOORLND2 (520995) 69.0 kV to MOORLND4 (520999) 138.0 kV to MLNDTERT (521180) 2.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_497 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 b.2. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_498 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARBNGR7 (531512) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #z1 b.2. HARBNGR7 (531512) 345.0 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR-T (531511) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_499 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to BENTON 7 (532791) 345.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 b.2. BENTON 4 (532986) 138.0 kV to BENTON 7 (532791) 345.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_500 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 b.2. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to SCJ1X1 (999532) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_501 | Single Phase Fault with Stuck Breaker on LAC3_STAR7 345.00 (543667) 345 kV Bus a. Apply Fault at the LAC3_STAR7 345.00 (543667) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAC3_STAR7 (543667) 345.0 kV to LAC3_Y1 (543662) 6.9 kV Two Winding #y b.2. LAC3_STAR7 (543667) 345.0 kV to LAC3_X1 (543661) 6.9 kV Two Winding #x | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_502 | Single Phase Fault with Stuck Breaker on LAC8_STAR7 345.00 (543669) 345 kV Bus a. Apply Fault at the LAC8_STAR7 345.00 (543669) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAC8_STAR7 (543669) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #h b.2. LAC8_STAR7 (543669) 345.0 kV to LAC8_Z1 (543672) 4.0 kV Two Winding #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_503 | Single Phase Fault with Stuck Breaker on NEVADA 5 (541208) 161 kV Bus a. Apply Fault at the NEVADA 5 (541208) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEVADA 5 (541208) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_504 | Single Phase Fault with Stuck Breaker on URICHTP2 (541304) 69 kV Bus a. Apply Fault at the URICHTP2 (541304) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. URICHTP2 (541304) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_505 | Single Phase Fault with Stuck Breaker on NEVPLT 2 (541307) 69 kV Bus a. Apply Fault at the NEVPLT 2 (541307) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEVPLT 2 (541307) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_506 | Single Phase Fault with Stuck Breaker on NEVADA 2 (541308) 69 kV Bus a. Apply Fault at the NEVADA 2 (541308) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEVADA 2 (541308) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_507 | Single Phase Fault with Stuck Breaker on 7THOMHL (300049) 345 kV Bus a. Apply Fault at the 7THOMHL (300049) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7THOMHL (300049) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_508 | Single Phase Fault with Stuck Breaker on 5THMHLB3 (300133) 161 kV Bus a. Apply Fault at the 5THMHLB3 (300133) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB3 (300133) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_509 | Single Phase Fault with Stuck Breaker on 5THMHLB4 (301443) 161 kV Bus a. Apply Fault at the 5THMHLB4 (301443) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB4 (301443) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_510 | Single Phase Fault with Stuck Breaker on 5ADAIR3 (344006) 161 kV Bus a. Apply Fault at the 5ADAIR3 (344006) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5ADAIR3 (344006) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_511 | Single Phase Fault with Stuck Breaker on 5MOBERLY (345221) 161 kV Bus a. Apply Fault at the 5MOBERLY (345221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBERLY (345221) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_512 | Single Phase Fault with Stuck Breaker on 2MOBERLY (345222) 69 kV Bus a. Apply Fault at the 2MOBERLY (345222) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MOBERLY (345222) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_513 | Single Phase Fault with Stuck Breaker on 2ADAIR 1 (346005) 69 kV Bus a. Apply Fault at the 2ADAIR 1 (346005) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ADAIR 1 (346005) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_514 | Single Phase Fault with Stuck Breaker on NORTON 5 (543064) 161 kV Bus a. Apply Fault at the NORTON 5 (543064) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTON 5 (543064) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_515 | Single Phase Fault with Stuck Breaker on W.GRDNR7 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_516 | Single Phase Fault with Stuck Breaker on WGARDNR5 (542966) 161 kV Bus a. Apply Fault at the WGARDNR5 (542966) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WGARDNR5 (542966) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_517 | Single Phase Fault with Stuck Breaker on PAOLA1 (543024) 34.5 kV Bus a. Apply Fault at the PAOLA1 (543024) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAOLA1 (543024) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_518 | Single Phase Fault with Stuck Breaker on SEOTTWA5 (543055) 161 kV Bus a. Apply Fault at the SEOTTWA5 (543055) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEOTTWA5 (543055) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_519 | Single Phase Fault with Stuck Breaker on PAOLA 5 (543069) 161 kV Bus a. Apply Fault at the PAOLA 5 (543069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAOLA 5 (543069) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_520 | Single Phase Fault with Stuck Breaker on WALKMYR3 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 (531405) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_521 | Single Phase Fault with Stuck Breaker on SEWARD-3 (531467) 115 kV Bus a. Apply Fault at the SEWARD-3 (531467) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWARD-3 (531467) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_522 | Single Phase Fault with Stuck Breaker on CMRIVTP3 (539652) 115 kV Bus a. Apply Fault at the CMRIVTP3 (539652) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CMRIVTP3 (539652) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_523 | Single Phase Fault with Stuck Breaker on SUMMIT 7 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 7 (532773) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_524 | Single Phase Fault with Stuck Breaker on SUMMIT 6 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_525 | Single Phase Fault with Stuck Breaker on AEC 3 (533361) 115 kV Bus a. Apply Fault at the AEC 3 (533361) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AEC 3 (533361) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_526 | Single Phase Fault with Stuck Breaker on SUMMIT 3 (533381) 115 kV Bus a. Apply Fault at the SUMMIT 3 (533381) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 3 (533381) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_527 | Single Phase Fault with Stuck Breaker on BLUMILS5 (543004) 161 kV Bus a. Apply Fault at the BLUMILS5 (543004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUMILS5 (543004) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_528 | Single Phase Fault with Stuck Breaker on BLUVLY (548806) 69 kV Bus a. Apply Fault at the BLUVLY (548806) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUVLY (548806) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_529 | Single Phase Fault with Stuck Breaker on SUB M-161 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 (548814) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB M-161 (548814) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_530 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_531 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_532 | Single Phase Fault with Stuck Breaker on 7JASPER (300949) 345 kV Bus a. Apply Fault at the 7JASPER (300949) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7JASPER (300949) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_533 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_534 | Single Phase Fault with Stuck Breaker on G17-009-TAP (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP (532777) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_535 | Single Phase Fault with Stuck Breaker on CANEYRV7 (532780) 345 kV Bus a. Apply Fault at the CANEYRV7 (532780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_536 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_537 | Single Phase Fault with Stuck Breaker on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_538 | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 4 (533021) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_539 | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to remove bus # | P4 | No | Yes | Yes | Yes | Yes | No | Yes | Non-dampening active power oscillations observed at WCGS U1 (532751) following the fault clearance. Issue is also observed in the base case. The following CQ units were determined to be contingent on the upgrade: - GEN-2018-009 : PTDF of 0.0368 - GEN-2018-032 : PTDF of 0.0882 - GEN-2018-049 : PTDF of 0.0640 - GEN-2018-057 : PTDF of 0.0962 | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_540 | Single Phase Fault with Stuck Breaker on RIV4525 (547469) 161 kV Bus a. Apply Fault at the RIV4525 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_541 | Single Phase Fault with Stuck Breaker on G17-209-TAP (760921) 345 kV Bus a. Apply Fault at the G17-209-TAP (760921) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-209-TAP (760921) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_542 | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_543 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_544 | Single Phase Fault with Stuck Breaker on SPERVIL7 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_545 | Single Phase Fault with Stuck Breaker on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_546 | Single Phase Fault with Stuck Breaker on KINGMAN7 (532783) 345 kV Bus a. Apply Fault at the KINGMAN7 (532783) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KINGMAN7 (532783) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_547 | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_548 | Single Phase Fault with Stuck Breaker on FLATRDG4 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 (539638) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLATRDG4 (539638) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_549 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_550 | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_551 | Single Phase Fault with Stuck Breaker on BENTON 7 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_552 | Single Phase Fault with Stuck Breaker on EXPEDITION7 (532803) 345 kV Bus a. Apply Fault at the EXPEDITION7 (532803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EXPEDITION7 (532803) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_553 | Single Phase Fault with Stuck Breaker on EVANS S4 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS S4 (533041) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_554 | Single Phase Fault with Stuck Breaker on RENO 3 (533416) 115 kV Bus a. Apply Fault at the RENO 3 (533416) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 3 (533416) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | No | Yes | Yes | Yes | Yes | No | Yes | Non-dampening active power oscillations observed at WCGS U1 (532751) following the fault clearance. Issue is also observed in the base case. The following CQ units were determined to be contingent on the upgrade: - GEN-2018-009 : PTDF of 0.0368 - GEN-2018-032 : PTDF of 0.0882 - GEN-2018-049 : PTDF of 0.0640 - GEN-2018-057 : PTDF of 0.0962 | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | No | Yes | Yes | Yes | Yes | No | Yes | Non-dampening active power oscillations observed at WCGS U1 (532751) following the fault clearance. Issue is also observed in the base case. The following CQ units were determined to be contingent on the upgrade: - GEN-2018-009 : PTDF of 0.0368 - GEN-2018-032 : PTDF of 0.0882 - GEN-2018-049 : PTDF of 0.0640 - GEN-2018-057 : PTDF of 0.0962 | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply Fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 5HUBEN (300088) 161.0 kV Two Winding #1 b.2. 7HUBEN (300042) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 b.2. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. VIOLA 7 (532798) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. THISTLE7 (539801) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to 7FAIRPT (300039) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 b.2. 5MORGANXF2 (301622) 161.0 kV to 5MORGAN (300101) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on 7JASPER 345.00 (300949) 345 kV Bus a. Apply Fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7JASPER (300949) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit #1 b.2. 7JASPER (300949) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 b.2. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to SCJ1X1 (999532) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE4 (539804) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. THISTLE4 (539804) 138.0 kV to THISTLE7 (539801) 345.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_KACY_FAULT_001 | Single Phase Fault with Stuck Breaker on BARBER 5 (546651) 161 kV Bus a. Apply Fault at the BARBER 5 (546651) 161 kV Bus b. Clear Fault after 9 cycles and trip the following elements: b.1. BARBER 5 (546651) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_KACY_FAULT_002 | Single Phase Fault with Stuck Breaker on SHWNMSN5 (543031) 161 kV Bus a. Apply Fault at the SHWNMSN5 (543031) 161 kV Bus b. Clear Fault after 17.25 cycles and trip the following elements: b.1. SHWNMSN5 (543031) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to remove bus # b.3. SHAWNEE5 (543041) 161.0 kV to Load #3 b.4. SHAWNEE5 (543041) 161.0 kV to Load #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_KACY_FAULT_003 | Single Phase Fault with Stuck Breaker on SHWNMSN5 (543031) 161 kV Bus a. Apply Fault at the SHWNMSN5 (543031) 161 kV Bus b. Clear Fault after 9 cycles and trip the following elements: b.1. SHWNMSN5 (543031) 161.0 kV to SHAWNEE5 (543041) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.3. SHAWNEE5 (543041) 161.0 kV to remove bus # b.4. SHAWNEE5 (543041) 161.0 kV to Load #3 b.5. SHAWNEE5 (543041) 161.0 kV to Load #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_KACY_FAULT_004 | Single Phase Fault with Stuck Breaker on BARBER 5 (546651) 161 kV Bus a. Apply Fault at the BARBER 5 (546651) 161 kV Bus b. Clear Fault after 9 cycles and trip the following elements: b.1. BARBER 5 (546651) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 b.2. BARBER 5 (546651) 161.0 kV to ROSEDALE 5 (546222) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_KACY_FAULT_005 | Single Phase Fault with Stuck Breaker on BARBER 5 (546651) 161 kV Bus a. Apply Fault at the BARBER 5 (546651) 161 kV Bus b. Clear Fault after 9 cycles and trip the following elements: b.1. BARBER 5 (546651) 161.0 kV to SHAWNEE5 (543041) 161.0 kV Transmission Circuit #1 b.2. BARBER 5 (546651) 161.0 kV to ROSEDALE 5 (546222) 161.0 kV Transmission Circuit #1 b.3. SHAWNEE5 (543041) 161.0 kV to SHWNMSN5 (543031) 161.0 kV Transmission Circuit #1 b.4. SHAWNEE5 (543041) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_KACY_FAULT_006 | Single Phase Fault with Stuck Breaker on METRO 5 (546742) 161 kV Bus a. Apply Fault at the METRO 5 (546742) 161 kV Bus b. Clear Fault after 9 cycles and trip the following elements: b.1. METRO 5 (546742) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_KACY_FAULT_007 | Single Phase Fault with Stuck Breaker on SHWNMSN5 (543031) 161 kV Bus a. Apply Fault at the SHWNMSN5 (543031) 161 kV Bus b. Clear Fault after 9 cycles and trip the following elements: b.1. SHWNMSN5 (543031) 161.0 kV to SHAWNEE5 (543041) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.3. SHAWNEE5 (543041) 161.0 kV to remove bus # b.4. SHAWNEE5 (543041) 161.0 kV to Load #3 b.5. SHAWNEE5 (543041) 161.0 kV to Load #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_KACY_FAULT_008 | Single Phase Fault with Stuck Breaker on METRO 5 (546742) 161 kV Bus a. Apply Fault at the METRO 5 (546742) 161 kV Bus b. Clear Fault after 9 cycles and trip the following elements: b.1. METRO 5 (546742) 161.0 kV to MAYSOTH5 (546722) 161.0 kV Transmission Circuit #1 b.2. METRO 5 (546742) 161.0 kV to KAW W 5 (546655) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_KACY_FAULT_009 | Single Phase Fault with Stuck Breaker on METRO 5 (546742) 161 kV Bus a. Apply Fault at the METRO 5 (546742) 161 kV Bus b. Clear Fault after 12 cycles and trip the following elements: b.1. METRO 5 (546742) 161.0 kV to MAYSOTH5 (546722) 161.0 kV Transmission Circuit #1 b.2. METRO 5 (546742) 161.0 kV to EDWRDVL5 (532912) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_KACY_FAULT_010 | Single Phase Fault with Stuck Breaker on METRO 5 (546742) 161 kV Bus a. Apply Fault at the METRO 5 (546742) 161 kV Bus b. Clear Fault after 9 cycles and trip the following elements: b.1. METRO 5 (546742) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_KACY_FAULT_011 | Single Phase Fault with Stuck Breaker on WOLCOTT5 (546669) 161 kV Bus a. Apply Fault at the WOLCOTT5 (546669) 161 kV Bus b. Clear Fault after 9 cycles and trip the following elements: b.1. WOLCOTT5 (546669) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_KACY_FAULT_012 | Single Phase Fault with Stuck Breaker on WOLCOTT5 (546669) 161 kV Bus a. Apply Fault at the WOLCOTT5 (546669) 161 kV Bus b. Clear Fault after 9 cycles and trip the following elements: b.1. WOLCOTT5 (546669) 161.0 kV to PIPER 5 (546668) 161.0 kV Transmission Circuit #1 b.2. WOLCOTT5 (546669) 161.0 kV to MAYWOOD5 (546656) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_KACY_FAULT_013 | Single Phase Fault with Stuck Breaker on WOLCOTT5 (546669) 161 kV Bus a. Apply Fault at the WOLCOTT5 (546669) 161 kV Bus b. Clear Fault after 9 cycles and trip the following elements: b.1. WOLCOTT5 (546669) 161.0 kV to None Transmission Circuit #1 b.2. WOLCOTT5 (546669) 161.0 kV to MAYWOOD5 (546656) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_KACY_FAULT_014 | Single Phase Fault with Stuck Breaker on BARBER 5 (546651) 161 kV Bus a. Apply Fault at the BARBER 5 (546651) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. BARBER 5 (546651) 161.0 kV to ROSEDALE 5 (546222) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_KACY_FAULT_015 | Single Phase Fault with Stuck Breaker on BARBER 5 (546651) 161 kV Bus a. Apply Fault at the BARBER 5 (546651) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. BARBER 5 (546651) 161.0 kV to ROSEDALE 5 (546222) 161.0 kV Transmission Circuit #1 b.2. BARBER 5 (546651) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 b.3. SHAWNEE5 (543041) 161.0 kV to SHWNMSN5 (543031) 161.0 kV Transmission Circuit #1 b.4. SHAWNEE5 (543041) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_KACY_FAULT_016 | Single Phase Fault with Stuck Breaker on METRO 5 (546742) 161 kV Bus a. Apply Fault at the METRO 5 (546742) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. METRO 5 (546742) 161.0 kV to MAYSOTH5 (546722) 161.0 kV Transmission Circuit #1 b.2. METRO 5 (546742) 161.0 kV to EDWRDVL5 (532912) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_KACY_FAULT_017 | Single Phase Fault with Stuck Breaker on METRO 5 (546742) 161 kV Bus a. Apply Fault at the METRO 5 (546742) 161 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. METRO 5 (546742) 161.0 kV to MAYSOTH5 (546722) 161.0 kV Transmission Circuit #1 b.2. METRO 5 (546742) 161.0 kV to KAW W 5 (546655) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_KACY_FAULT_018 | Single Phase Fault with Stuck Breaker on NEARMAN5 (546653) 161 kV Bus a. Apply Fault at the NEARMAN5 (546653) 161 kV Bus b. Clear Fault after 3 cycles and trip the following elements: b.1. NMGEN N1 (546702) 20.0 kV to Generator #1 b.2. NEARMAN5 (546653) 161.0 kV to MAYWOOD5 (546656) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_KACY_FAULT_019 | Single Phase Fault with Stuck Breaker on BARBER 5 (546651) 161 kV Bus a. Apply Fault at the BARBER 5 (546651) 161 kV Bus b. Clear Fault after 25 cycles and trip the following elements: b.1. BARBER 5 (546651) 161.0 kV to ROSEDALE 5 (546222) 161.0 kV Transmission Circuit #1 b.2. BARBER 5 (546651) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 b.3. SHAWNEE5 (543041) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_KACY_FAULT_020 | Single Phase Fault with Stuck Breaker on METRO 5 (546742) 161 kV Bus a. Apply Fault at the METRO 5 (546742) 161 kV Bus b. Clear Fault after 23 cycles and trip the following elements: b.1. METRO 5 (546742) 161.0 kV to MAYSOTH5 (546722) 161.0 kV Transmission Circuit #1 b.2. METRO 5 (546742) 161.0 kV to KAW W 5 (546655) 161.0 kV Transmission Circuit #1 b.3. METRO 5 (546742) 161.0 kV to EDWRDVL5 (532912) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_KACY_FAULT_021 | Single Phase Fault with Stuck Breaker on METRO 5 (546742) 161 kV Bus a. Apply Fault at the METRO 5 (546742) 161 kV Bus b. Clear Fault after 23 cycles and trip the following elements: b.1. METRO 5 (546742) 161.0 kV to MAYSOTH5 (546722) 161.0 kV Transmission Circuit #1 b.2. METRO 5 (546742) 161.0 kV to KAW W 5 (546655) 161.0 kV Transmission Circuit #1 b.3. METRO 5 (546742) 161.0 kV to EDWRDVL5 (532912) 161.0 kV Transmission Circuit #1 b.4. METRO 5 (546742) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_KACY_FAULT_022 | Single Phase Fault with Stuck Breaker on NEARMAN5 (546653) 161 kV Bus a. Apply Fault at the NEARMAN5 (546653) 161 kV Bus b. Clear Fault after 23 cycles and trip the following elements: b.1. NEARMAN5 (546653) 161.0 kV to MAYWOOD5 (546656) 161.0 kV Transmission Circuit #1 b.2. NMGEN N1 (546702) 20.0 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_KACY_FAULT_023 | Single Phase Fault with Stuck Breaker on BARBER 5 (546651) 161 kV Bus a. Apply Fault at the BARBER 5 (546651) 161 kV Bus b. Clear Fault after 23 cycles and trip the following elements: b.1. BARBER 5 (546651) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_KACY_FAULT_024 | Single Phase Fault with Stuck Breaker on METRO 5 (546742) 161 kV Bus a. Apply Fault at the METRO 5 (546742) 161 kV Bus b. Clear Fault after 23 cycles and trip the following elements: b.1. METRO 5 (546742) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_KACY_FAULT_025 | Single Phase Fault with Stuck Breaker on WOLCOTT5 (546669) 161 kV Bus a. Apply Fault at the WOLCOTT5 (546669) 161 kV Bus b. Clear Fault after 23 cycles and trip the following elements: b.1. WOLCOTT5 (546669) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EMDE_FAULT_001 | Single Phase Fault with Stuck Breaker on TIP292 5 161.00 (547472) 161 kV Bus a. Apply Fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.2. RNM393 5 (547500) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.3. MON383 5 (547480) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.5. JOP389 5 (547483) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.7. TIP292 5 (547472) 161.0 kV to Load #1 b.8. TIP292 5 (547472) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EMDE_FAULT_002 | Single Phase Fault with Stuck Breaker on ASB349 5 (547476) 161 kV Bus a. Apply Fault at the ASB349 5 (547476) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. CARTHAG5 (505488) 161.0 kV to CAR395 5 (547485) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.3. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 b.4. CAR395 5 (547485) 161.0 kV to Load #1 b.5. PUR421 5 (547491) 161.0 kV to Load #1 b.6. CAR395 5 (547485) 161.0 kV to remove bus # b.7. PUR421 5 (547491) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EMDE_FAULT_003 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 7 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.2. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EMDE_FAULT_004 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to ORO110 5 (547467) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EMDE_FAULT_005 | Single Phase Fault with Stuck Breaker on TIP292 5 161.00 (547472) 161 kV Bus a. Apply Fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 b.3. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 b.4. RNM393 5 (547500) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.5. MON383 5 (547480) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.6. TIP292 5 (547472) 161.0 kV to Load #1 b.7. TIP292 5 (547472) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EMDE_FAULT_006 | Single Phase Fault with Stuck Breaker on L1G382 1 13.200 (547651) 161 kV Bus a. Apply Fault at the L1G382 1 13.200 (547651) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. LAR382 5 (547479) 161.0 kV to L1G382 1 (547651) 13.2 kV Transmission Circuit #1 b.2. LAR382 5 (547479) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.4. L1G382 1 (547651) 13.2 kV to Generator #1 b.5. L1G382 1 (547651) 13.2 kV to Load #S1 b.6. L1G382 1 (547651) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_SPRM_FAULT_001 | Single Phase Fault with Stuck Breaker on BATTLEFIELD5161 (549959) 161 kV Bus a. Apply Fault at the BATTLEFIELD5161 (549959) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. GOLDEN 2 (549911) 69.0 kV to BATTLEFIELD2 (549979) 69.0 kV Transmission Circuit #1 b.2. DAYTON 2 (549913) 69.0 kV to BATTLEFIELD2 (549979) 69.0 kV Transmission Circuit #1 b.3. MAIN STREET5 (549958) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_SUNC_FAULT_001 | Single Phase Fault with Stuck Breaker on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear Fault after 12 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_INDN_FAULT_001 | Single Phase Fault with Stuck Breaker on SUB M-161 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 (548814) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. SUB M-161 (548814) 161.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.2. SUB M-161 (548814) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.3. SUB M-161 (548814) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #1 b.4. SUB M-161 (548814) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_INDN_FAULT_002 | Single Phase Fault with Stuck Breaker on SUB M-161 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 (548814) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. SUB M-161 (548814) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. SUB M-161 (548814) 161.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.3. SUB M-161 (548814) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #1 b.4. SUB M-161 (548814) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_INDN_FAULT_003 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_INDN_FAULT_004 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_INDN_FAULT_005 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_INDN_FAULT_006 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_INDN_FAULT_007 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.3. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 b.4. BLUMILS5 (543004) 161.0 kV to Load #1 b.5. BLUMILS_TER1 (543117) 12.5 kV to Load #3 b.6. BLUMILS5 (543004) 161.0 kV to remove bus # b.7. BLUEMLS2 (543116) 69.0 kV to remove bus # b.8. BLUMILS_TER1 (543117) 12.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_INDN_FAULT_008 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.3. ECKLES-161 (548808) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 b.4. BLUMILS5 (543004) 161.0 kV to Load #1 b.5. BLUMILS_TER1 (543117) 12.5 kV to Load #3 b.6. BLUMILS5 (543004) 161.0 kV to remove bus # b.7. BLUEMLS2 (543116) 69.0 kV to remove bus # b.8. BLUMILS_TER1 (543117) 12.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_INDN_FAULT_009 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. ECKLES-161 (548808) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 b.3. ECKLES-161 (548808) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_001 | Single Phase Fault with Stuck Breaker on COLBY 3 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 (530555) 115 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.2. COLBY 3 (530555) 115.0 kV to ATWOOD 3 (530554) 115.0 kV Transmission Circuit #1 b.3. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.4. COLBY 3 (530555) 115.0 kV to COLBY 2 (530644) 69.0 kV to CLBYT1 1 (530645) 13.8 kV Three Winding #1 b.5. COLBY 3 (530555) 115.0 kV to remove bus #1 b.6. CLBYT1 1 (530645) 13.8 kV to remove bus #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_002 | Single Phase Fault with Stuck Breaker on BEACH 3 (530557) 115 kV Bus a. Apply Fault at the BEACH 3 (530557) 115 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. REDLIN 3 (530605) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to HOXIE 3 (530556) 115.0 kV Transmission Circuit #1 b.5. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 b.6. BEACH 3 (530557) 115.0 kV to remove bus #1 b.7. HILLCTY3 (531387) 34.5 kV to Generator #1 b.8. HILLCTY3 (531387) 34.5 kV to Generator #2 b.9. HILLCTY3 (531387) 34.5 kV to Generator #3 b.10. HILLCTY3 (531387) 34.5 kV to Generator #4 b.11. HILLCTY3 (531387) 34.5 kV to Generator #5 b.12. HILLCTY3 (531387) 34.5 kV to Generator #6 b.13. HILLCTY3 (531387) 34.5 kV to remove bus # b.14. REDLIN 3 (530605) 115.0 kV to remove bus # b.15. HOXIE 3 (530556) 115.0 kV to remove bus # b.16. REDLIN 3 (530605) 115.0 kV to Load #71 b.17. HOXIE 3 (530556) 115.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_003 | Single Phase Fault with Stuck Breaker on ATWOOD 3 (530554) 115 kV Bus a. Apply Fault at the ATWOOD 3 (530554) 115 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. ATWOOD 3 (530554) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 b.2. ATWOOD 3 (530554) 115.0 kV to ATWODSW3 (531364) 115.0 kV Transmission Circuit #1 b.3. ATWOOD 3 (530554) 115.0 kV to BVERVLLY (531488) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to remove bus #1 b.5. ATWOOD 3 (530554) 115.0 kV to Generator #1 b.6. HILLCTY3 (531387) 34.5 kV to Generator #1 b.7. HILLCTY3 (531387) 34.5 kV to Generator #2 b.8. HILLCTY3 (531387) 34.5 kV to Generator #3 b.9. HILLCTY3 (531387) 34.5 kV to Generator #4 b.10. HILLCTY3 (531387) 34.5 kV to Generator #5 b.11. HILLCTY3 (531387) 34.5 kV to Generator #6 b.12. ATWOOD 3 (530554) 115.0 kV to Load #1 b.13. ATWOOD 3 (530554) 115.0 kV to Load #41 b.14. ATWOOD 3 (530554) 115.0 kV to remove bus # b.15. HILLCTY3 (531387) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_004 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_005 | Single Phase Fault with Stuck Breaker on COLBY 3 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 (530555) 115 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.2. COLBY 3 (530555) 115.0 kV to ATWOOD 3 (530554) 115.0 kV Transmission Circuit #1 b.3. COLBY 3 (530555) 115.0 kV to COLBY 2 (530644) 69.0 kV to CLBYT1 1 (530645) 13.8 kV Three Winding #1 b.4. CLBYT1 1 (530645) 13.8 kV to remove bus #1 b.5. MINGO 3 (531429) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 b.6. COLBY 3 (530555) 115.0 kV to Generator #C3 b.7. COLBY 3 (530555) 115.0 kV to Generator #C4 b.8. COLBY 3 (530555) 115.0 kV to Generator #C5 b.9. COLBY 3 (530555) 115.0 kV to Generator #C6 b.10. COLBY 3 (530555) 115.0 kV to Generator #C7 b.11. COLBY 3 (530555) 115.0 kV to Load #99 b.12. COLBY 3 (530555) 115.0 kV to Generator #C8 b.13. COLBY 3 (530555) 115.0 kV to Load #1 b.14. COLBY 3 (530555) 115.0 kV to Load #CC | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_006 | Single Phase Fault with Stuck Breaker on COLBY 3 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 (530555) 115 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.2. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.3. COLBY 3 (530555) 115.0 kV to ATWOOD 3 (530554) 115.0 kV Transmission Circuit #1 b.4. COLBY 3 (530555) 115.0 kV to COLBY 2 (530644) 69.0 kV to CLBYT1 1 (530645) 13.8 kV Three Winding #1 b.5. CLBYT1 1 (530645) 13.8 kV to remove bus #1 b.6. COLBY 3 (530555) 115.0 kV to Generator #C3 b.7. COLBY 3 (530555) 115.0 kV to Generator #C4 b.8. COLBY 3 (530555) 115.0 kV to Generator #C5 b.9. COLBY 3 (530555) 115.0 kV to Generator #C6 b.10. COLBY 3 (530555) 115.0 kV to Generator #C7 b.11. COLBY 3 (530555) 115.0 kV to Generator #C8 b.12. COLBY 3 (530555) 115.0 kV to Load #99 b.13. COLBY 3 (530555) 115.0 kV to Load #1 b.14. COLBY 3 (530555) 115.0 kV to Load #CC | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_007 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.4. KNOLL 3 (530561) 115.0 kV to SALINE 3 (530551) 115.0 kV Transmission Circuit #1 b.5. REDLIN 3 (530605) 115.0 kV to Load #71 b.6. REDLIN 3 (530605) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_008 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to KNOLL N 6 (530558) 230.0 kV to KNLL1 1 (530629) 11.5 kV Transmission Circuit #1 b.4. REDLIN 3 (530605) 115.0 kV to Load #71 b.5. REDLIN 3 (530605) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_009 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 25 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to SALINE 3 (530551) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.4. REDLIN 3 (530605) 115.0 kV to Load #71 b.5. REDLIN 3 (530605) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_010 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to SALINE 3 (530551) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.3. GMECG1 1 (530674) 13.8 kV to remove bus # b.4. GMECG2 1 (530675) 13.8 kV to remove bus # b.5. GMEC 3 (530676) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_011 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. GMECG1 1 (530674) 13.8 kV to remove bus #1 b.2. GMECG2 1 (530675) 13.8 kV to remove bus #1 b.3. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.4. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.5. CHETOLAH3 (530695) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 b.6. N HAYS3 (530581) 115.0 kV to remove bus #1 b.7. VINETAP3 (530693) 115.0 kV to remove bus #1 b.8. GMEC 3 (530676) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_012 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CHETOLAH3 (530695) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.3. N HAYS3 (530581) 115.0 kV to remove bus #1 b.4. VINETAP3 (530693) 115.0 kV to remove bus #1 b.5. GMECG1 1 (530674) 13.8 kV to remove bus #1 b.6. GMECG2 1 (530675) 13.8 kV to remove bus #1 b.7. GMEC 3 (530676) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_013 | Single Phase Fault with Stuck Breaker on S HAYS 3 (530553) 115 kV Bus a. Apply Fault at the S HAYS 3 (530553) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CHETOLAH3 (530695) 115.0 kV to S HAYS 3 (530553) 115.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. ANGUS 3 (530714) 115.0 kV to GORHAM 3 (530552) 115.0 kV Transmission Circuit #1 b.4. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.5. ANGUS 3 (530714) 115.0 kV to Load #1 b.6. PFEIFER 3 (530725) 115.0 kV to Load #1 b.7. ANGUS 3 (530714) 115.0 kV to remove bus # b.8. PFEIFER 3 (530725) 115.0 kV to remove bus # b.9. GORHAM 3 (530552) 115.0 kV to Load #1 b.10. RUSLPMP3 (530684) 115.0 kV to Load #1 b.11. GORHAM 3 (530552) 115.0 kV to remove bus # b.12. RUSLPMP3 (530684) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_014 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_015 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_016 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_017 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKE_WTG (530705) 0.7 kV to remove bus # b.4. BUCKW_WTG (530708) 0.7 kV to remove bus # b.5. BUCKEYE_230 (530702) 230.0 kV to remove bus # b.6. BUCKEYE_E1 (530703) 34.5 kV to remove bus # b.7. BUCKEYE_E2 (530704) 34.5 kV to remove bus # b.8. BUCKW_TERT (530706) 13.8 kV to remove bus # b.9. BUCKEYE_W2 (530707) 34.5 kV to remove bus # b.10. BUCKE_TERT (530709) 13.8 kV to remove bus # b.11. BUCKEYE_W1 (530710) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_018 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKE_WTG (530705) 0.7 kV to remove bus # b.4. BUCKW_WTG (530708) 0.7 kV to remove bus # b.5. BUCKEYE_230 (530702) 230.0 kV to remove bus # b.6. BUCKEYE_E1 (530703) 34.5 kV to remove bus # b.7. BUCKEYE_E2 (530704) 34.5 kV to remove bus # b.8. BUCKW_TERT (530706) 13.8 kV to remove bus # b.9. BUCKEYE_W2 (530707) 34.5 kV to remove bus # b.10. BUCKE_TERT (530709) 13.8 kV to remove bus # b.11. BUCKEYE_W1 (530710) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_019 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_020 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL N 6 (530558) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_021 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530720) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to remove bus # b.4. KNOLL S 6 (530720) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_022 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 12 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to KNOLL N 6 (530558) 230.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_023 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 b.3. KNOLL S 6 (530720) 230.0 kV to remove bus # b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_024 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to remove bus # b.6. KNOLL S 6 (530720) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_025 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.5. KNOLL N 6 (530558) 230.0 kV to remove bus # b.6. KNOLL S 6 (530720) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_026 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 14 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. SMOKYHL6 (530592) 230.0 kV to SMKYP2 6 (530599) 230.0 kV Transmission Circuit #1 b.4. SHG2 34 1 (530715) 34.5 kV to remove bus # b.5. SMKYP2G1 (530600) 0.6 kV to remove bus #1 b.6. SMKYP2 6 (530599) 230.0 kV to remove bus # b.7. SHP234 1 (530604) 34.5 kV to remove bus # b.8. SMKYT2 1 (530634) 13.9 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_027 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. SMKYP2 6 (530599) 230.0 kV to remove bus #1 b.3. SMKYP1 6 (530593) 230.0 kV to remove bus #1 b.4. SMKYP1G1 (530594) 0.7 kV to remove bus #1 b.5. SMKYP2G1 (530600) 0.6 kV to remove bus #1 b.6. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.7. SHG2 34 1 (530715) 34.5 kV to remove bus # b.8. SMOKYHL6 (530592) 230.0 kV to remove bus # b.9. SHP134 1 (530595) 34.5 kV to remove bus # b.10. SHP234 1 (530604) 34.5 kV to remove bus # b.11. SMKYT1 1 (530633) 13.2 kV to remove bus # b.12. SMKYT2 1 (530634) 13.9 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_028 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 14 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. SMOKYHL6 (530592) 230.0 kV to SMKYP1 6 (530593) 230.0 kV Transmission Circuit #1 b.3. SMKYT2 1 (530634) 13.9 kV to Generator #1 b.4. SMKYT2 1 (530634) 13.9 kV to remove bus # b.5. SMKYP1G1 (530594) 0.7 kV to remove bus #1 b.6. SMKYP1 6 (530593) 230.0 kV to remove bus # b.7. SHP134 1 (530595) 34.5 kV to remove bus # b.8. SMKYT1 1 (530633) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_029 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 5.6 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. SMKYP2 6 (530599) 230.0 kV to remove bus #1 b.3. SMKYP1 6 (530593) 230.0 kV to remove bus #1 b.4. SMKYP1G1 (530594) 0.7 kV to remove bus #1 b.5. SMKYP2G1 (530600) 0.6 kV to remove bus #1 b.6. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.7. SHG2 34 1 (530715) 34.5 kV to remove bus # b.8. SMOKYHL6 (530592) 230.0 kV to remove bus # b.9. SHP134 1 (530595) 34.5 kV to remove bus # b.10. SHP234 1 (530604) 34.5 kV to remove bus # b.11. SMKYT1 1 (530633) 13.2 kV to remove bus # b.12. SMKYT2 1 (530634) 13.9 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_030 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_031 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_032 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_GEN (530614) 0.7 kV to remove bus # b.4. SHAYS_230 (530610) 230.0 kV to remove bus # b.5. SHAYS_13.8 (530611) 13.8 kV to remove bus # b.6. SHAYS_COLLR2 (530612) 34.5 kV to remove bus # b.7. SHAYS_COLLR1 (530613) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_033 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_GEN (530614) 0.7 kV to remove bus # b.4. SHAYS_230 (530610) 230.0 kV to remove bus # b.5. SHAYS_13.8 (530611) 13.8 kV to remove bus # b.6. SHAYS_COLLR2 (530612) 34.5 kV to remove bus # b.7. SHAYS_COLLR1 (530613) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_034 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 17 cycles and trip the following elements: b.1. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.2. LACROS 3 (530603) 115.0 kV to remove bus #1 b.3. NEKOMA 3 (530608) 115.0 kV to remove bus #1 b.4. ALXNDR 3 (530606) 115.0 kV to remove bus #1 b.5. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.6. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 b.7. HZRNGPL3 (530609) 115.0 kV to remove bus # b.8. ALEXNDR1 (539702) 34.5 kV to Load #1 b.9. LAXTAP 3 (530602) 115.0 kV to remove bus # b.10. NKMA2 1 (530630) 12.5 kV to remove bus # b.11. ALEXNDR1 (539702) 34.5 kV to remove bus # b.12. ALEXND-T (539902) 12.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_035 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_036 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 17 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LACROS 3 (530603) 115.0 kV to remove bus #1 b.4. NEKOMA 3 (530608) 115.0 kV to remove bus #1 b.5. ALXNDR 3 (530606) 115.0 kV to remove bus #1 b.7. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.8. ALEXNDR1 (539702) 34.5 kV to Load #1 b.9. LAXTAP 3 (530602) 115.0 kV to remove bus # b.10. NKMA2 1 (530630) 12.5 kV to remove bus # b.11. ALEXNDR1 (539702) 34.5 kV to remove bus # b.12. ALEXND-T (539902) 12.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_037 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to HEIZER 3 (530601) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_038 | Single Phase Fault with Stuck Breaker on RICE 3 (530623) 115 kV Bus a. Apply Fault at the RICE 3 (530623) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. BUSHTON3 (530681) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_039 | Single Phase Fault with Stuck Breaker on RICE 3 (530623) 115 kV Bus a. Apply Fault at the RICE 3 (530623) 115 kV Bus b. Clear Fault after 19 cycles and trip the following elements: b.1. RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.2. RICE 3 (530623) 115.0 kV to Load #1 b.3. RICE 3 (530623) 115.0 kV to Load #K1 b.4. RICE 3 (530623) 115.0 kV to Load #K2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_040 | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply Fault at the RICE 6 (530686) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.2. RICE 6 (530686) 230.0 kV to remove bus #1 b.3. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.4. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.5. PRWINDG1 (530690) 0.7 kV to Generator #1 b.6. BUFLOCRK6 (530688) 230.0 kV to remove bus # b.7. BUFLOCRK1 (530689) 34.5 kV to remove bus # b.8. PRWINDG1 (530690) 0.7 kV to remove bus # b.9. BUFCRKT11 (530691) 12.5 kV to remove bus # b.10. PRWNDCL1 (530701) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_041 | Single Phase Fault with Stuck Breaker on CIRCLE 6 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to RICE 6 (530686) 230.0 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.3. PRWINDG1 (530690) 0.7 kV to Generator #1 b.4. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.5. BUFLOCRK6 (530688) 230.0 kV to remove bus # b.6. BUFLOCRK1 (530689) 34.5 kV to remove bus # b.7. PRWINDG1 (530690) 0.7 kV to remove bus # b.8. BUFCRKT11 (530691) 12.5 kV to remove bus # b.9. PRWNDCL1 (530701) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_042 | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply Fault at the RICE 6 (530686) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to RICE 6 (530686) 230.0 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.3. PRWINDG1 (530690) 0.7 kV to Generator #1 b.4. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.5. BUFLOCRK6 (530688) 230.0 kV to remove bus # b.6. BUFLOCRK1 (530689) 34.5 kV to remove bus # b.7. PRWINDG1 (530690) 0.7 kV to remove bus # b.8. BUFCRKT11 (530691) 12.5 kV to remove bus # b.9. PRWNDCL1 (530701) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_001 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_002 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_003 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_004 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to EMPEC7 1 (532744) 18.0 kV Two Winding #1 b.3. EMPEC7 1 (532744) 18.0 kV to Generator #7 b.4. EMPEC7 1 (532744) 18.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_005 | Single Phase Fault with Stuck Breaker on Jeffrey EC 230 kV (532852) 230 kV Bus a. Apply Fault at the Jeffrey EC 230 kV (532852) 230 kV Bus b. Clear Fault after 5.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 b.2. JEC 6 (532852) 230.0 kV to JEC U1 (532651) 26.0 kV Two Winding #1 b.3. JEC U1 (532651) 26.0 kV to Generator #1 b.4. JEC U1 (532651) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_006 | Single Phase Fault with Stuck Breaker on Jeffrey EC 230 kV (532852) 230 kV Bus a. Apply Fault at the Jeffrey EC 230 kV (532852) 230 kV Bus b. Clear Fault after 5.75 cycles and trip the following elements: b.1. JEC 6 (532852) 230.0 kV to AUBURN 6 (532851) 230.0 kV Transmission Circuit #1 b.2. JEC 6 (532852) 230.0 kV to JEC U1 (532651) 26.0 kV Two Winding #1 b.3. JEC U1 (532651) 26.0 kV to Generator #1 b.4. JEC U1 (532651) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_007 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC U2 (532652) 26.0 kV Two Winding #1 b.3. JEC U2 (532652) 26.0 kV to Generator #1 b.4. JEC U2 (532652) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_008 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC U2 (532652) 26.0 kV Two Winding #1 b.3. JEC U2 (532652) 26.0 kV to Generator #1 b.4. JEC U2 (532652) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_009 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 b.2. JEC N 7 (532766) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_010 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC U3 (532653) 26.0 kV Two Winding #1 b.3. JEC U3 (532653) 26.0 kV to Generator #1 b.4. JEC U3 (532653) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_011 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC U3 (532653) 26.0 kV Two Winding #1 b.3. JEC U3 (532653) 26.0 kV to Generator #1 b.4. JEC U3 (532653) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_012 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 b.2. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_013 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 b.2. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_014 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 b.2. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_015 | Single Phase Fault with Stuck Breaker on Rose Hill 345 kV (532794) 345 kV Bus a. Apply Fault at the Rose Hill 345 kV (532794) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_016 | Single Phase Fault with Stuck Breaker on Rose Hill 345 kV (532794) 345 kV Bus a. Apply Fault at the Rose Hill 345 kV (532794) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_017 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_018 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_019 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_020 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_021 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_022 | Single Phase Fault with Stuck Breaker on Craig 345 kV (542977) 345 kV Bus a. Apply Fault at the Craig 345 kV (542977) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_023 | Single Phase Fault with Stuck Breaker on Craig 345 kV (542977) 345 kV Bus a. Apply Fault at the Craig 345 kV (542977) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_024 | Single Phase Fault with Stuck Breaker on Craig 345 kV (542977) 345 kV Bus a. Apply Fault at the Craig 345 kV (542977) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_025 | Single Phase Fault with Stuck Breaker on Craig 345 kV (542977) 345 kV Bus a. Apply Fault at the Craig 345 kV (542977) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_026 | Single Phase Fault with Stuck Breaker on Craig 345 kV (542977) 345 kV Bus a. Apply Fault at the Craig 345 kV (542977) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_027 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 7.75 cycles and trip the following elements: b.1. HAWTHN5 (543665) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #@1 b.2. HAWTHN5 (543665) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #@2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_028 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_029 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_030 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_031 | Single Phase Fault with Stuck Breaker on Iatan 345 kV (542982) 345 kV Bus a. Apply Fault at the Iatan 345 kV (542982) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. IATAN 7 (542982) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. IATAN 7 (542982) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_032 | Single Phase Fault with Stuck Breaker on Iatan 345 kV (542982) 345 kV Bus a. Apply Fault at the Iatan 345 kV (542982) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. IAT G1 1 (542957) 24.0 kV to remove bus # b.2. IATAN 7 (542982) 345.0 kV to IATAN5 (541350) 161.0 kV to IATAN 11 (541150) 14.4 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_033 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. LAC G2 1 (542956) 24.0 kV to remove bus # b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_034 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 b.3. LACYGNE2 (543659) 69.0 kV to remove bus # b.4. LAC_LAKE_2 (541541) 69.0 kV to remove bus # b.5. LAC_LAKE_2 (541541) 69.0 kV to Load #K1 b.6. LAC_LAKE_2 (541541) 69.0 kV to Load #1 | P4 | No | Yes | Yes | Yes | Yes | No | Yes | Non-dampening active power oscillations observed at WCGS U1 (532751) following the fault clearance. Issue is also observed in the base case. The following CQ units were determined to be contingent on the upgrade: - GEN-2018-009 : PTDF of 0.0368 - GEN-2018-032 : PTDF of 0.0882 - GEN-2018-049 : PTDF of 0.0640 - GEN-2018-057 : PTDF of 0.0962 | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_035 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | No | Yes | Yes | Yes | Yes | No | Yes | Non-dampening active power oscillations observed at WCGS U1 (532751) following the fault clearance. Issue is also observed in the base case. The following CQ units were determined to be contingent on the upgrade: - GEN-2018-009 : PTDF of 0.0368 - GEN-2018-032 : PTDF of 0.0882 - GEN-2018-049 : PTDF of 0.0640 - GEN-2018-057 : PTDF of 0.0962 | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_036 | Single Phase Fault with Stuck Breaker on Nashua 345 kV (542980) 345 kV Bus a. Apply Fault at the Nashua 345 kV (542980) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_037 | Single Phase Fault with Stuck Breaker on Northeast North (543666) 161 kV Bus a. Apply Fault at the Northeast North (543666) 161 kV Bus b. Clear Fault after 7.75 cycles and trip the following elements: b.1. NEASTN5 (543666) 161.0 kV to LEVEE 5 (542976) 161.0 kV Transmission Circuit #1 b.2. NEASTN5 (543666) 161.0 kV to GRAND 5 (542987) 161.0 kV Transmission Circuit #1 b.3. NE CT13 (542970) 13.8 kV to remove bus # b.4. NE CT14 (542971) 13.8 kV to remove bus # b.5. NEASTN5 (543666) 161.0 kV to Load #56 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_038 | Single Phase Fault with Stuck Breaker on Northeast South (542985) 161 kV Bus a. Apply Fault at the Northeast South (542985) 161 kV Bus b. Clear Fault after 7.75 cycles and trip the following elements: b.1. NE CT17 (542983) 13.8 kV to remove bus # b.2. NE CT18 (542984) 13.8 kV to remove bus # b.3. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.4. NEASTS5 (542985) 161.0 kV to CHARLOT5 (543133) 161.0 kV Transmission Circuit #1 b.5. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #@1 b.6. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_039 | Single Phase Fault with Stuck Breaker on Stilwell 345 kV (542968) 345 kV Bus a. Apply Fault at the Stilwell 345 kV (542968) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to PECULR 7 (541198) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_040 | Single Phase Fault with Stuck Breaker on West Gardner 345 kV (542965) 345 kV Bus a. Apply Fault at the West Gardner 345 kV (542965) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_041 | Single Phase Fault with Stuck Breaker on West Gardner 345 kV (542965) 345 kV Bus a. Apply Fault at the West Gardner 345 kV (542965) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_042 | Single Phase Fault with Stuck Breaker on West Gardner 345 kV (542965) 345 kV Bus a. Apply Fault at the West Gardner 345 kV (542965) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_043 | Single Phase Fault with Stuck Breaker on Jeffrey EC 230 kV (532852) 230 kV Bus a. Apply Fault at the Jeffrey EC 230 kV (532852) 230 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. JEC 6 (532852) 230.0 kV to JEC U1 (532651) 26.0 kV Two Winding #1 b.2. JEC U1 (532651) 26.0 kV to remove bus # b.3. JEC U1 (532651) 26.0 kV to Generator #1 b.4. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_044 | Single Phase Fault with Stuck Breaker on Jeffrey EC 230 kV (532852) 230 kV Bus a. Apply Fault at the Jeffrey EC 230 kV (532852) 230 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. JEC 6 (532852) 230.0 kV to AUBURN 6 (532851) 230.0 kV Transmission Circuit #1 b.2. JEC 6 (532852) 230.0 kV to EMANHAT6 (532861) 230.0 kV Transmission Circuit #1 b.3. JEC 6 (532852) 230.0 kV to JEC U1 (532651) 26.0 kV Two Winding #1 b.4. JEC U1 (532651) 26.0 kV to Generator #1 b.5. JEC U1 (532651) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_045 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 13 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC U2 (532652) 26.0 kV Two Winding #1 b.2. JEC U2 (532652) 26.0 kV to remove bus # b.3. JEC U2 (532652) 26.0 kV to Generator #1 b.4. JEC N 7 (532766) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_046 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 13 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC U3 (532653) 26.0 kV Two Winding #1 b.2. JEC U3 (532653) 26.0 kV to remove bus # b.3. JEC U3 (532653) 26.0 kV to Generator #1 b.4. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_047 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 16.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_048 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 16.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_049 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 16.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_050 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to EMPEC121 (532740) 13.8 kV Two Winding #1 b.3. EMPEC121 (532740) 13.8 kV to Generator #1 b.4. EMPEC121 (532740) 13.8 kV to Generator #2 b.5. EMPEC121 (532740) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_051 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to EMPEC121 (532740) 13.8 kV Two Winding #1 b.2. EMPEC121 (532740) 13.8 kV to Generator #1 b.3. EMPEC121 (532740) 13.8 kV to Generator #2 b.4. EMPEC121 (532740) 13.8 kV to remove bus # b.5. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_052 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to EMPEC7 1 (532744) 18.0 kV Two Winding #1 b.3. EMPEC7 1 (532744) 18.0 kV to Generator #7 b.4. EMPEC7 1 (532744) 18.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_053 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to EMPEC7 1 (532744) 18.0 kV Two Winding #1 b.2. EMPEC7 1 (532744) 18.0 kV to Generator #7 b.3. EMPEC7 1 (532744) 18.0 kV to remove bus # b.4. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_054 | Single Phase Fault with Stuck Breaker on Jeffrey EC 230 kV (532852) 230 kV Bus a. Apply Fault at the Jeffrey EC 230 kV (532852) 230 kV Bus b. Clear Fault after 18.25 cycles and trip the following elements: b.1. JEC 6 (532852) 230.0 kV to AUBURN 6 (532851) 230.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_055 | Single Phase Fault with Stuck Breaker on Jeffrey EC 230 kV (532852) 230 kV Bus a. Apply Fault at the Jeffrey EC 230 kV (532852) 230 kV Bus b. Clear Fault after 18.25 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 b.2. JEC 6 (532852) 230.0 kV to AUBURN 6 (532851) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_056 | Single Phase Fault with Stuck Breaker on Jeffrey EC 230 kV (532852) 230 kV Bus a. Apply Fault at the Jeffrey EC 230 kV (532852) 230 kV Bus b. Clear Fault after 18.25 cycles and trip the following elements: b.1. JEC 6 (532852) 230.0 kV to AUBURN 6 (532851) 230.0 kV Transmission Circuit #1 b.2. JEC 6 (532852) 230.0 kV to JEC U1 (532651) 26.0 kV Two Winding #1 b.3. JEC U1 (532651) 26.0 kV to Generator #1 b.4. JEC U1 (532651) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_057 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 13.25 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC U2 (532652) 26.0 kV Two Winding #1 b.3. JEC U2 (532652) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_058 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 13.25 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC U3 (532653) 26.0 kV Two Winding #1 b.3. JEC U3 (532653) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_059 | Single Phase Fault with Stuck Breaker on Rose Hill 345 kV (532794) 345 kV Bus a. Apply Fault at the Rose Hill 345 kV (532794) 345 kV Bus b. Clear Fault after 16.75 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_060 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_061 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_062 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_063 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_064 | Single Phase Fault with Stuck Breaker on Wolf Creek 345 kV (532797) 345 kV Bus a. Apply Fault at the Wolf Creek 345 kV (532797) 345 kV Bus b. Clear Fault after 10.5 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_065 | Single Phase Fault with Stuck Breaker on Wolf Creek 345 kV (532797) 345 kV Bus a. Apply Fault at the Wolf Creek 345 kV (532797) 345 kV Bus b. Clear Fault after 10.5 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_066 | Single Phase Fault with Stuck Breaker on Wolf Creek 345 kV (532797) 345 kV Bus a. Apply Fault at the Wolf Creek 345 kV (532797) 345 kV Bus b. Clear Fault after 10.5 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_067 | Single Phase Fault with Stuck Breaker on Wolf Creek 345 kV (532797) 345 kV Bus a. Apply Fault at the Wolf Creek 345 kV (532797) 345 kV Bus b. Clear Fault after 10.5 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_068 | Single Phase Fault with Stuck Breaker on Craig 345 kV (542977) 345 kV Bus a. Apply Fault at the Craig 345 kV (542977) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. CRAIG 5 (542978) 161.0 kV to CRAIG 7 (542977) 345.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_069 | Single Phase Fault with Stuck Breaker on Craig 345 kV (542977) 345 kV Bus a. Apply Fault at the Craig 345 kV (542977) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. CRAIG 5 (542978) 161.0 kV to CRAIG 7 (542977) 345.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_070 | Single Phase Fault with Stuck Breaker on Craig 345 kV (542977) 345 kV Bus a. Apply Fault at the Craig 345 kV (542977) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 5 (542978) 161.0 kV to CRAIG 7 (542977) 345.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_071 | Single Phase Fault with Stuck Breaker on Craig 345 kV (542977) 345 kV Bus a. Apply Fault at the Craig 345 kV (542977) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 5 (542978) 161.0 kV to CRAIG 7 (542977) 345.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_072 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAW G5 1 (542951) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_073 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAW G5 1 (542951) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_074 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HAWTHN5 (543665) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.3. HAW G5 1 (542951) 22.0 kV to remove bus # b.4. RANDLPH5 (543027) 161.0 kV to Load #1 b.5. RANDLPH5 (543027) 161.0 kV to Load #4 b.6. RANDLPH5 (543027) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_075 | Single Phase Fault with Stuck Breaker on Hawthorn South (542973) 161 kV Bus a. Apply Fault at the Hawthorn South (542973) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 b.2. HAW G5 1 (542951) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_076 | Single Phase Fault with Stuck Breaker on Hawthorn 161 kV (542973) 161 kV Bus a. Apply Fault at the Hawthorn 161 kV (542973) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #@1 b.2. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #@2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_077 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_078 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_079 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_080 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_081 | Single Phase Fault with Stuck Breaker on Iatan 345 kV (542982) 345 kV Bus a. Apply Fault at the Iatan 345 kV (542982) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_082 | Single Phase Fault with Stuck Breaker on Iatan 345 kV (542982) 345 kV Bus a. Apply Fault at the Iatan 345 kV (542982) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. IAT G1 1 (542957) 24.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_083 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 | P4 | No | Yes | Yes | Yes | Yes | No | Yes | Non-dampening active power oscillations observed at WCGS U1 (532751) following the fault clearance. Issue is also observed in the base case. The following CQ units were determined to be contingent on the upgrade: - GEN-2018-009 : PTDF of 0.0368 - GEN-2018-032 : PTDF of 0.0882 - GEN-2018-049 : PTDF of 0.0640 - GEN-2018-057 : PTDF of 0.0962 | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_084 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. LAC G1 1 (542955) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_085 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. LAC G1 1 (542955) 22.0 kV to remove bus # | P4 | No | Yes | Yes | Yes | Yes | No | Yes | Non-dampening active power oscillations observed at WCGS U1 (532751) following the fault clearance. Issue is also observed in the base case. The following CQ units were determined to be contingent on the upgrade: - GEN-2018-009 : PTDF of 0.0368 - GEN-2018-032 : PTDF of 0.0882 - GEN-2018-049 : PTDF of 0.0640 - GEN-2018-057 : PTDF of 0.0962 | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_086 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. LAC G2 1 (542956) 24.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_087 | Single Phase Fault with Stuck Breaker on Nashua 345 kV (542980) 345 kV Bus a. Apply Fault at the Nashua 345 kV (542980) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. IATAN 7 (542982) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_088 | Single Phase Fault with Stuck Breaker on Northeast South (542985) 161 kV Bus a. Apply Fault at the Northeast South (542985) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.3. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #@1 b.4. NEASTN5 (543666) 161.0 kV to Load #78 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_089 | Single Phase Fault with Stuck Breaker on Shawnee Mission 161 kV (543031) 161 kV Bus a. Apply Fault at the Shawnee Mission 161 kV (543031) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. SHWNMSN5 (543031) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 b.2. SHWNMSN5 (543031) 161.0 kV to Load #4 b.3. SHWNMSN5 (543031) 161.0 kV to Load #6 b.4. CEDRCRK5 (543049) 161.0 kV to Load #1 b.5. SHAWNEE5 (543041) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_090 | Single Phase Fault with Stuck Breaker on Shawnee Mission 161 kV (543031) 161 kV Bus a. Apply Fault at the Shawnee Mission 161 kV (543031) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. SHWNMSN5 (543031) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 b.2. SHWNMSN5 (543031) 161.0 kV to Load #2 b.3. SHWNMSN5 (543031) 161.0 kV to Load #4 b.4. SHAWNEE5 (543041) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_091 | Single Phase Fault with Stuck Breaker on Stilwell 345 kV (542968) 345 kV Bus a. Apply Fault at the Stilwell 345 kV (542968) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_092 | Single Phase Fault with Stuck Breaker on West Gardner 345 kV (542965) 345 kV Bus a. Apply Fault at the West Gardner 345 kV (542965) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_093 | Single Phase Fault with Stuck Breaker on West Gardner 345 kV (542965) 345 kV Bus a. Apply Fault at the West Gardner 345 kV (542965) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_094 | Single Phase Fault with Stuck Breaker on Jeffrey EC 230 kV (532852) 230 kV Bus a. Apply Fault at the Jeffrey EC 230 kV (532852) 230 kV Bus b. Clear Fault after 18.25 cycles and trip the following elements: b.1. JEC 6 (532852) 230.0 kV to JEC N 7 (532766) 345.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 b.2. JEC 6 (532852) 230.0 kV to JEC U1 (532651) 26.0 kV Two Winding #1 b.3. JEC U1 (532651) 26.0 kV to Generator #1 b.4. JEC U1 (532651) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_095 | Single Phase Fault with Stuck Breaker on Rose Hill 345 kV (532794) 345 kV Bus a. Apply Fault at the Rose Hill 345 kV (532794) 345 kV Bus b. Clear Fault after 16.75 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_096 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 b.2. STRANGR7 (532772) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_097 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_098 | Single Phase Fault with Stuck Breaker on Craig 345 kV (542977) 345 kV Bus a. Apply Fault at the Craig 345 kV (542977) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CRAIG 5 (542978) 161.0 kV to CRAIG 7 (542977) 345.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 b.2. CRAIG 5 (542978) 161.0 kV to CRAIG 7 (542977) 345.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-001-CF | 25S | Base | GROUP3_P1_LOCAL_FAULT_026 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 4.7 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 4.7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | WCGS U1 (532751) loses synchronism following the fault clearance. | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2018-001-CF | 25S | Base | GROUP3_P1_LOCAL_FAULT_027 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | WCGS U1 (532751) loses synchronism following the fault clearance. | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2018-001-CF | 25S | Base | GROUP3_P1_REGIONAL_FAULT_008 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 4.7 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 4.7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | WCGS U1 (532751) loses synchronism following the fault clearance. | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2018-001-CF | 25S | Base | GROUP3_P1_REGIONAL_FAULT_009 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | WCGS U1 (532751) loses synchronism following the fault clearance. | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2018-001-CF | 25W | Base | GROUP3_P1_LOCAL_FAULT_026 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P4 | No | Yes | Yes | Yes | Yes | No | Yes | WCGS U1 (532751) loses synchronism following the fault clearance. | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2018-001-CF | 25W | Base | GROUP3_P1_LOCAL_FAULT_027 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P4 | No | Yes | Yes | Yes | Yes | No | Yes | WCGS U1 (532751) loses synchronism following the fault clearance. | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2018-001-CF | 25W | Base | GROUP3_P1_REGIONAL_FAULT_008 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P4 | No | Yes | Yes | Yes | Yes | No | Yes | WCGS U1 (532751) loses synchronism following the fault clearance. | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2018-001-CF | 25W | Base | GROUP3_P1_REGIONAL_FAULT_009 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P4 | No | Yes | Yes | Yes | Yes | No | Yes | WCGS U1 (532751) loses synchronism following the fault clearance. | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2018-001-CF | 25W | Base | GROUP3_P4_LOCAL_FAULT_213 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | No | Yes | Yes | Yes | Yes | No | Yes | Non-dampening active power oscillations observed at WCGS U1 (532751) following the fault clearance. | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2018-001-CF | 25W | Base | GROUP3_P4_LOCAL_FAULT_242 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | No | Yes | Yes | Yes | Yes | No | Yes | Non-dampening active power oscillations observed at WCGS U1 (532751) following the fault clearance. | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2018-001-CF | 25W | Base | GROUP3_P4_LOCAL_FAULT_539 | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to remove bus # | P4 | No | Yes | Yes | Yes | Yes | No | Yes | Non-dampening active power oscillations observed at WCGS U1 (532751) following the fault clearance. | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2018-001-CF | 25W | Base | GROUP3_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | No | Yes | Yes | Yes | Yes | No | Yes | Non-dampening active power oscillations observed at WCGS U1 (532751) following the fault clearance. | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2018-001-CF | 25W | Base | GROUP3_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | No | Yes | Yes | Yes | Yes | No | Yes | Non-dampening active power oscillations observed at WCGS U1 (532751) following the fault clearance. | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2018-001-CF | 25W | Base | GROUP3_P4_EVERGY_FAULT_034 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 b.3. LACYGNE2 (543659) 69.0 kV to remove bus # b.4. LAC_LAKE_2 (541541) 69.0 kV to remove bus # b.5. LAC_LAKE_2 (541541) 69.0 kV to Load #K1 b.6. LAC_LAKE_2 (541541) 69.0 kV to Load #1 | P4 | No | Yes | Yes | Yes | Yes | No | Yes | Non-dampening active power oscillations observed at WCGS U1 (532751) following the fault clearance. | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2018-001-CF | 25W | Base | GROUP3_P4_EVERGY_FAULT_035 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | No | Yes | Yes | Yes | Yes | No | Yes | Non-dampening active power oscillations observed at WCGS U1 (532751) following the fault clearance. | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2018-001-CF | 25W | Base | GROUP3_P4_EVERGY_FAULT_083 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 | P4 | No | Yes | Yes | Yes | Yes | No | Yes | Non-dampening active power oscillations observed at WCGS U1 (532751) following the fault clearance. | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2018-001-CF | 25W | Base | GROUP3_P4_EVERGY_FAULT_085 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. LAC G1 1 (542955) 22.0 kV to remove bus # | P4 | No | Yes | Yes | Yes | Yes | No | Yes | Non-dampening active power oscillations observed at WCGS U1 (532751) following the fault clearance. | Line - Wolf Creek - Blackberry 345 kV
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_112GORE4__LAIRGST4 | 3 Phase fault 112GORE4 (511488) 138 kV Bus a. Apply fault at the 112GORE4 (511488) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 138 KV 511488 TO LAIRGST4 138 KV 511510 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_112GORE4__RPPAPER4 | 3 Phase fault 112GORE4 (511488) 138 kV Bus a. Apply fault at the 112GORE4 (511488) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 138 KV 511488 TO RPPAPER4 138 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_2CARNEY__2LUTHER | 3 Phase fault 2CARNEY (300834) 69 kV Bus a. Apply fault at the 2CARNEY (300834) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CARNEY 69 KV 300834 TO 2LUTHER 69 KV 300856 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_2COLINS__COLNSGR2 | 3 Phase fault 2COLINS (300992) 69 kV Bus a. Apply fault at the 2COLINS (300992) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2COLINS 69 KV 300992 TO COLNSGR2 69 KV 512870 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_2MERIDAN__2LUTHER | 3 Phase fault 2MERIDAN (300839) 69 kV Bus a. Apply fault at the 2MERIDAN (300839) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MERIDAN 69 KV 300839 TO 2LUTHER 69 KV 300856 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_2OWASSO__COLNSGR2 | 3 Phase fault 2OWASSO (300998) 69 kV Bus a. Apply fault at the 2OWASSO (300998) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2OWASSO 69 KV 300998 TO COLNSGR2 69 KV 512870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_2OWASSO__DAWSON | 3 Phase fault 2OWASSO (300998) 69 kV Bus a. Apply fault at the 2OWASSO (300998) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2OWASSO 69 KV 300998 TO DAWSON-2 69 KV 509791 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_2VERA__COLNSGR2 | 3 Phase fault 2VERA (301006) 69 kV Bus a. Apply fault at the 2VERA (301006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2VERA 69 KV 301006 TO COLNSGR2 69 KV 512870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_36&MER_4__HOBBYLO4 | 3 Phase fault 36&MER 4 (514888) 138 kV Bus a. Apply fault at the 36&MER 4 (514888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 36&MER 4 138 KV 514888 TO HOBBYLO4 138 KV 515338 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-133 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-133 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_36&MER_4__SW_5TH_4 | 3 Phase fault 36&MER 4 (514888) 138 kV Bus a. Apply fault at the 36&MER 4 (514888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 36&MER 4 138 KV 514888 TO SW 5TH 4 138 KV 514920 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MNCOWNG3 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_38TH_ST2__BETHANY2 | 3 Phase fault 38TH ST2 (514845) 69 kV Bus a. Apply fault at the 38TH ST2 (514845) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 38TH ST2 69 KV 514845 TO BETHANY2 69 KV 514914 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_38TH_ST4__HEFNER_4 | 3 Phase fault 38TH ST4 (514846) 138 kV Bus a. Apply fault at the 38TH ST4 (514846) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TULSA 4 138 KV 514847 TO HEFNER 4 138 KV 514848 CKT 1 b.2. 38TH ST4 138 KV 514846 TO TULSA 4 138 KV 514847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MNCO5G11 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_38TH_ST4__TULSA__4 | 3 Phase fault 38TH ST4 (514846) 138 kV Bus a. Apply fault at the 38TH ST4 (514846) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 38TH ST4 138 KV 514846 TO TULSA 4 138 KV 514847 CKT 1 b.2. LOAD 1 514847 b.3. TULSA 4 138 KV 514847 TO HEFNER 4 138 KV 514848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MNCO5G11 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_3ADA_LA__3MINDEN_LA! | 3 Phase fault 3ADA_LA (337360) 115 kV Bus a. Apply fault at the 3ADA_LA (337360) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3ADA_LA 115 KV 337360 TO 3MINDEN_LA! 115 KV 337361 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_3EL_DORADO!__3ELDORADO.E! | 3 Phase fault 3EL DORADO! (337539) 115 kV Bus a. Apply fault at the 3EL DORADO! (337539) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3EL DORADO! 115 KV 337539 TO 3ELDORADO.E! 115 KV 337553 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_3EL_DORADO!__3ELD_DONAN | 3 Phase fault 3EL DORADO! (337539) 115 kV Bus a. Apply fault at the 3EL DORADO! (337539) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3EL DORADO! 115 KV 337539 TO 3ELD DONAN 115 KV 337540 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_3EL_DORADO!__3ELD_QUINN | 3 Phase fault 3EL DORADO! (337539) 115 kV Bus a. Apply fault at the 3EL DORADO! (337539) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3EL DORADO! 115 KV 337539 TO 3ELD QUINN 115 KV 337560 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_3KERLIN+__3EMERSON! | 3 Phase fault 3KERLIN+ (337524) 115 kV Bus a. Apply fault at the 3KERLIN+ (337524) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3KERLIN+ 115 KV 337524 TO 3EMERSON! 115 KV 337526 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_3MINDEN_LA!__3LA_ORD_PLNT | 3 Phase fault 3MINDEN_LA! (337361) 115 kV Bus a. Apply fault at the 3MINDEN_LA! (337361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MINDEN_LA! 115 KV 337361 TO 3LA_ORD_PLNT 115 KV 337362 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_3MINDEN_LA!__3SAREPTA! | 3 Phase fault 3MINDEN_LA! (337361) 115 kV Bus a. Apply fault at the 3MINDEN_LA! (337361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MINDEN_LA! 115 KV 337361 TO 3SAREPTA! 115 KV 337363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_3MINDEN_LA!__MINDEN | 3 Phase fault 3MINDEN_LA! (337361) 115 kV Bus a. Apply fault at the 3MINDEN_LA! (337361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MINDEN_LA! 115 KV 337361 TO MINDEN-3 115 KV 507788 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_3MINDEN_LG__3MINDEN_LA! | 3 Phase fault 3MINDEN_LG (303302) 115 kV Bus a. Apply fault at the 3MINDEN_LG (303302) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MINDEN_LG 115 KV 303302 TO 3MINDEN_LA! 115 KV 337361 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_3SAREPTA!__3CULLEN | 3 Phase fault 3SAREPTA! (337363) 115 kV Bus a. Apply fault at the 3SAREPTA! (337363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115 KV 337363 TO 3CULLEN 115 KV 337364 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_3SAREPTA!__3EMERSON! | 3 Phase fault 3SAREPTA! (337363) 115 kV Bus a. Apply fault at the 3SAREPTA! (337363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115 KV 337363 TO 3HAYNESVILLE 115 KV 337366 CKT 1 b.2. LOAD 1 337366 b.3. LOAD LG 337366 b.4. 3HAYNESVILLE 115 KV 337366 TO 3EMERSON! 115 KV 337526 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_3SAREPTA!__3SPRINGHILL | 3 Phase fault 3SAREPTA! (337363) 115 kV Bus a. Apply fault at the 3SAREPTA! (337363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115 KV 337363 TO 3SPRINGHILL 115 KV 337365 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_3SMACKOVER+__3EL_DORADO! | 3 Phase fault 3SMACKOVER+ (337537) 115 kV Bus a. Apply fault at the 3SMACKOVER+ (337537) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SMACKOVER+ 115 KV 337537 TO 3EL DORADO! 115 KV 337539 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_3SPRINGHILL__3TAYLOR | 3 Phase fault 3SPRINGHILL (337365) 115 kV Bus a. Apply fault at the 3SPRINGHILL (337365) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SPRINGHILL 115 KV 337365 TO 3TAYLOR 115 KV 337500 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_44&SUNL2__ELMCRK_2 | 3 Phase fault 44&SUNL2 (514979) 69 kV Bus a. Apply fault at the 44&SUNL2 (514979) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 44&SUNL2 69 KV 514979 TO ELMCRK 2 69 KV 514982 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_44&SUNL2__SUNNYLN2 | 3 Phase fault 44&SUNL2 (514979) 69 kV Bus a. Apply fault at the 44&SUNL2 (514979) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 44&SUNL2 69 KV 514979 TO SUNNYLN2 69 KV 514980 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_46ST | 3 Phase fault 46ST--E4 (509837) 138 kV Bus a. Apply fault at the 46ST--E4 (509837) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 46ST--E4 138 KV 509837 TO 46ST-TP-4 138 KV 509900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_4BRISTOW__4SILVCTY | 3 Phase fault 4BRISTOW (300137) 138 kV Bus a. Apply fault at the 4BRISTOW (300137) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4BRISTOW 138 KV 300137 TO 4SILVCTY 138 KV 300140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_4CLEVLND__4SFORKKTP | 3 Phase fault 4CLEVLND (300138) 138 kV Bus a. Apply fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138 KV 300138 TO 4JAVINE 138 KV 300996 CKT 1 b.2. LOAD 1 300996 b.3. LOAD 2 300996 b.4. 4JAVINE 138 KV 300996 TO 4SFORKKTP 138 KV 301339 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_4CLEVLND__4SILVCTY | 3 Phase fault 4CLEVLND (300138) 138 kV Bus a. Apply fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138 KV 300138 TO 4SILVCTY 138 KV 300140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_4CLEVLND__CLEVLND_4 | 3 Phase fault 4CLEVLND (300138) 138 kV Bus a. Apply fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138 KV 300138 TO CLEVLND 4 138 KV 512729 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2015-066 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_4CLEVLND__PAWNSW4 | 3 Phase fault 4CLEVLND (300138) 138 kV Bus a. Apply fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138 KV 300138 TO PAWNSW4 138 KV 512749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_4FAIRFAX__PAWNSW4 | 3 Phase fault 4FAIRFAX (300139) 138 kV Bus a. Apply fault at the 4FAIRFAX (300139) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FAIRFAX 138 KV 300139 TO PAWNSW4 138 KV 512749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_4FISHERTP__4SILVCTY | 3 Phase fault 4FISHERTP (300131) 138 kV Bus a. Apply fault at the 4FISHERTP (300131) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FISHERTP 138 KV 300131 TO 4SILVCTY 138 KV 300140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_4LUTHER__4MEMORALT | 3 Phase fault 4LUTHER (300135) 138 kV Bus a. Apply fault at the 4LUTHER (300135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4LUTHER 138 KV 300135 TO 4MEMORALT 138 KV 300136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_4LUTHER__4STROUD138 | 3 Phase fault 4LUTHER (300135) 138 kV Bus a. Apply fault at the 4LUTHER (300135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4LUTHER 138 KV 300135 TO 4LUTHERD 138 KV 301372 CKT 1 b.2. LOAD 1 301372 b.3. 4WARWICK 138 KV 300915 TO 4LUTHERD 138 KV 301372 CKT 1 b.4. LOAD 1 301372 b.5. 4STROUD138 138 KV 300914 TO 4WARWICK 138 KV 300915 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_4MEMORALT__4MEMORAL | 3 Phase fault 4MEMORALT (300136) 138 kV Bus a. Apply fault at the 4MEMORALT (300136) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MEMORALT 138 KV 300136 TO 4MEMORAL 138 KV 301541 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-029 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-029 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_4MEMORALT__JNSKAMO4 | 3 Phase fault 4MEMORALT (300136) 138 kV Bus a. Apply fault at the 4MEMORALT (300136) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MEMORALT 138 KV 300136 TO JNSKAMO4 138 KV 514906 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_4MURFBORO__SNASHVL4 | 3 Phase fault 4MURFBORO (337672) 138 kV Bus a. Apply fault at the 4MURFBORO (337672) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MURFBORO 138 KV 337672 TO SNASHVL4 138 KV 507434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_4SFORKK__4SFORKKTP | 3 Phase fault 4SFORKK (300165) 138 kV Bus a. Apply fault at the 4SFORKK (300165) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SFORKK 138 KV 300165 TO 4SFORKKTP 138 KV 301339 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_4SILVCTY__4STILWTR | 3 Phase fault 4SILVCTY (300140) 138 kV Bus a. Apply fault at the 4SILVCTY (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY 138 KV 300140 TO 4STILWTR 138 KV 300141 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_4SILVCTY__SILVCTYGR4 | 3 Phase fault 4SILVCTY (300140) 138 kV Bus a. Apply fault at the 4SILVCTY (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY 138 KV 300140 TO SILVCTYGR4 138 KV 512726 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_4SKIAETP__4SFORKKTP | 3 Phase fault 4SKIAETP (300146) 138 kV Bus a. Apply fault at the 4SKIAETP (300146) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SKIAETP 138 KV 300146 TO 4SFORKKTP 138 KV 301339 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_4SKIAETP__COLLINS4 | 3 Phase fault 4SKIAETP (300146) 138 kV Bus a. Apply fault at the 4SKIAETP (300146) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SKIAETP 138 KV 300146 TO COLLINS4 138 KV 512705 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_4STROUDDIST__4STROUD138 | 3 Phase fault 4STROUDDIST (300838) 138 kV Bus a. Apply fault at the 4STROUDDIST (300838) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STROUDDIST 138 KV 300838 TO 4STROUD138 138 KV 300914 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_52DEL | 3 Phase fault 52DEL-W4 (509856) 138 kV Bus a. Apply fault at the 52DEL-W4 (509856) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 52DEL-W4 138 KV 509856 TO S HILLW4 138 KV 509859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_52DELTP4__T.P.S. | 3 Phase fault 52DELTP4 (509776) 138 kV Bus a. Apply fault at the 52DELTP4 (509776) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 52DELTP4 138 KV 509776 TO 36LEWIS4 138 KV 509800 CKT 1 b.2. LOAD 1 509800 b.3. T.P.S.-4 138 KV 509788 TO 36LEWIS4 138 KV 509800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_52DELTP4__T.S.E. | 3 Phase fault 52DELTP4 (509776) 138 kV Bus a. Apply fault at the 52DELTP4 (509776) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 52DELTP4 138 KV 509776 TO T.S.E.-4 138 KV 509811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_52DELTP4__ZUNIS | 3 Phase fault 52DELTP4 (509776) 138 kV Bus a. Apply fault at the 52DELTP4 (509776) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 52DELTP4 138 KV 509776 TO ZUNIS-S4 138 KV 509826 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_52DELWT4__S_HILLW4 | 3 Phase fault 52DELWT4 (509814) 138 kV Bus a. Apply fault at the 52DELWT4 (509814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 52DELWT4 138 KV 509814 TO S HILLW4 138 KV 509859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_53CACHE4__ARTVLTP4 | 3 Phase fault 53CACHE4 (511509) 138 kV Bus a. Apply fault at the 53CACHE4 (511509) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53CACHE4 138 KV 511509 TO ARTVLTP4 138 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_53GARNT4__77MEMTP4 | 3 Phase fault 53GARNT4 (509762) 138 kV Bus a. Apply fault at the 53GARNT4 (509762) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARNT4 138 KV 509762 TO 77MEMTP4 138 KV 509765 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_53GARNT4__T.S.E. | 3 Phase fault 53GARNT4 (509762) 138 kV Bus a. Apply fault at the 53GARNT4 (509762) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARNT4 138 KV 509762 TO T.S.E.-4 138 KV 509811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_53GARN_4__53GARNT4 | 3 Phase fault 53GARN 4 (509734) 138 kV Bus a. Apply fault at the 53GARN 4 (509734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARN 4 138 KV 509734 TO 53GARNT4 138 KV 509762 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_53GARST4__53GARNS4 | 3 Phase fault 53GARST4 (509763) 138 kV Bus a. Apply fault at the 53GARST4 (509763) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARST4 138 KV 509763 TO 53GARNS4 138 KV 509774 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_53GARST4__FORD | 3 Phase fault 53GARST4 (509763) 138 kV Bus a. Apply fault at the 53GARST4 (509763) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARST4 138 KV 509763 TO FORD---4 138 KV 509772 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_53GARST4__T.S.E. | 3 Phase fault 53GARST4 (509763) 138 kV Bus a. Apply fault at the 53GARST4 (509763) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARST4 138 KV 509763 TO T.S.E.-4 138 KV 509811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_5CDRCRST__TAHLQH_5 | 3 Phase fault 5CDRCRST (301344) 161 kV Bus a. Apply fault at the 5CDRCRST (301344) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CDRCRST 161 KV 301344 TO TAHLQH 5 161 KV 512655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_5CHOTEAU1__5CHOTEAU2 | 3 Phase fault 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 161 KV 300069 TO 5CHOTEAU2 161 KV 301348 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_5CHOTEAU1__MAID___5 | 3 Phase fault 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 161 KV 300069 TO MAID 5 161 KV 512648 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_5ELMCRK__CATSAGR5 | 3 Phase fault 5ELMCRK (300993) 161 kV Bus a. Apply fault at the 5ELMCRK (300993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ELMCRK 161 KV 300993 TO CATSAGR5 161 KV 512638 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_5PARK__TAHLQH_5 | 3 Phase fault 5PARK (301307) 161 kV Bus a. Apply fault at the 5PARK (301307) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PARK 161 KV 301307 TO TAHLQH 5 161 KV 512655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_5TRIBES2__AGENCY_2 | 3 Phase fault 5TRIBES2 (515227) 69 kV Bus a. Apply fault at the 5TRIBES2 (515227) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TENYSON2 69 KV 515217 TO 5TRIBES2 69 KV 515227 CKT 1 b.2. HONORHT2 69 KV 515216 TO TENYSON2 69 KV 515217 CKT 1 b.3. LOAD 1 515217 b.4. HONORHT2 69 KV 515216 TO AGENCY 2 69 KV 515229 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_5TRIBES2__WELLSPA2 | 3 Phase fault 5TRIBES2 (515227) 69 kV Bus a. Apply fault at the 5TRIBES2 (515227) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHECOTA2 69 KV 515201 TO WELLS 2 69 KV 515202 CKT 1 b.2. LOAD 1 515202 b.3. CHECOTA2 69 KV 515201 TO 5TRIBES2 69 KV 515227 CKT 1 b.4. WELLS 2 69 KV 515202 TO WELLSPA2 69 KV 515215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_5TRIBES5__MUSKOGE5 | 3 Phase fault 5TRIBES5 (515228) 161 kV Bus a. Apply fault at the 5TRIBES5 (515228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TRIBES5 161 KV 515228 TO HANCOK-5 161 KV 515250 CKT 1 b.2. LOAD 1 515250 b.3. HANCOK-5 161 KV 515250 TO THRERVR5 161 KV 515640 CKT 1 b.4. LOAD 1 515640 b.5. MUSKOGE5 161 KV 515222 TO THRERVR5 161 KV 515640 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_5TRIBES5__PECANCK5 | 3 Phase fault 5TRIBES5 (515228) 161 kV Bus a. Apply fault at the 5TRIBES5 (515228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TRIBES5 161 KV 515228 TO PECANCK5 161 KV 515234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_77MEM | 3 Phase fault 77MEM-E4 (509735) 138 kV Bus a. Apply fault at the 77MEM-E4 (509735) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 77MEM-E4 138 KV 509735 TO 77MEMTP4 138 KV 509765 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_77MEM | 3 Phase fault 77MEM-W4 (509766) 138 kV Bus a. Apply fault at the 77MEM-W4 (509766) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 77MEM-W4 138 KV 509766 TO E.61ST-4 138 KV 509831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_77MEMTP4__81GARN | 3 Phase fault 77MEMTP4 (509765) 138 kV Bus a. Apply fault at the 77MEMTP4 (509765) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 77MEMTP4 138 KV 509765 TO 81GARN-4 138 KV 509855 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_7BLACKBERRY__NEOSHO_7 | 3 Phase fault 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY 345 KV 300739 TO NEOSHO 7 345 KV 532793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | P1WF trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_7SAREPTA%__7EL_DORADO | 3 Phase fault 7SAREPTA% (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345 KV 337376 TO 7EL DORADO 345 KV 337562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_7SAREPTA%__LONGWD_7 | 3 Phase fault 7SAREPTA% (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345 KV 337376 TO LONGWD 7 345 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_7SPORTSMAN__GRDA1__7 | 3 Phase fault 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN 345 KV 300740 TO GRDA1 7 345 KV 512650 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_81GARN | 3 Phase fault 81GARN-4 (509855) 138 kV Bus a. Apply fault at the 81GARN-4 (509855) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81GARN-4 138 KV 509855 TO E_121ST4 138 KV 509889 CKT 1 b.2. LOAD 1 509889 b.3. 121LYNN4 138 KV 509869 TO E_121ST4 138 KV 509889 CKT 1 b.4. LOAD 1 509889 b.5. ONETA--4 138 KV 509806 TO 121LYNN4 138 KV 509869 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_81YALEN4__81YALTP4 | 3 Phase fault 81YALEN4 (509730) 138 kV Bus a. Apply fault at the 81YALEN4 (509730) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81YALEN4 138 KV 509730 TO 81YALTP4 138 KV 509809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_81YALES4__WARNTAP4 | 3 Phase fault 81YALES4 (509810) 138 kV Bus a. Apply fault at the 81YALES4 (509810) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81YALES4 138 KV 509810 TO WARNTAP4 138 KV 509858 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_81YALTP4__SHILETP4 | 3 Phase fault 81YALTP4 (509809) 138 kV Bus a. Apply fault at the 81YALTP4 (509809) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81YALTP4 138 KV 509809 TO SHILETP4 138 KV 509813 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_8ANO%__8P.HILL% | 3 Phase fault 8ANO% (337909) 500 kV Bus a. Apply fault at the 8ANO% (337909) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500 KV 337909 TO 8P.HILL% 500 KV 337922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_8ANO%__FTSMITH8 | 3 Phase fault 8ANO% (337909) 500 kV Bus a. Apply fault at the 8ANO% (337909) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500 KV 337909 TO FTSMITH8 500 KV 515305 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_8EL_DORADO%__8PANDA% | 3 Phase fault 8EL DORADO% (337561) 500 kV Bus a. Apply fault at the 8EL DORADO% (337561) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 500 KV 337561 TO 8PANDA% 500 KV 338440 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_8EL_DORADO%__8SHERIDAN% | 3 Phase fault 8EL DORADO% (337561) 500 kV Bus a. Apply fault at the 8EL DORADO% (337561) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 500 KV 337561 TO 8SHERIDAN% 500 KV 337643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_8HAPPYVALY%__8ANO% | 3 Phase fault 8HAPPYVALY% (337811) 500 kV Bus a. Apply fault at the 8HAPPYVALY% (337811) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8HAPPYVALY% 500 KV 337811 TO 8ANO% 500 KV 337909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_8MCNEIL%__8EL_DORADO% | 3 Phase fault 8MCNEIL% (337515) 500 kV Bus a. Apply fault at the 8MCNEIL% (337515) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MCNEIL% 500 KV 337515 TO 8EL DORADO% 500 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_8MCNEIL%__8ETTA% | 3 Phase fault 8MCNEIL% (337515) 500 kV Bus a. Apply fault at the 8MCNEIL% (337515) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MCNEIL% 500 KV 337515 TO 8ETTA% 500 KV 337754 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_8MT_OLIVE%__8EL_DORADO% | 3 Phase fault 8MT_OLIVE% (337368) 500 kV Bus a. Apply fault at the 8MT_OLIVE% (337368) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MT_OLIVE% 500 KV 337368 TO 8EL DORADO% 500 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_8MT_OLIVE%__LAYFLD8 | 3 Phase fault 8MT_OLIVE% (337368) 500 kV Bus a. Apply fault at the 8MT_OLIVE% (337368) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MT_OLIVE% 500 KV 337368 TO LAYFLD8 500 KV 509366 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_8SHERIDAN%__8MABELVALE% | 3 Phase fault 8SHERIDAN% (337643) 500 kV Bus a. Apply fault at the 8SHERIDAN% (337643) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHERIDAN% 500 KV 337643 TO 8MABELVALE% 500 KV 337808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_8SHERIDAN%__8MAGNETCOVE% | 3 Phase fault 8SHERIDAN% (337643) 500 kV Bus a. Apply fault at the 8SHERIDAN% (337643) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHERIDAN% 500 KV 337643 TO 8MAGNETCOVE% 500 KV 337763 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_8SHERIDAN%__8WHT_BLUFF% | 3 Phase fault 8SHERIDAN% (337643) 500 kV Bus a. Apply fault at the 8SHERIDAN% (337643) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHERIDAN% 500 KV 337643 TO 8WHT BLUFF% 500 KV 337651 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_8STERLING%__8EL_DORADO% | 3 Phase fault 8STERLING% (337420) 500 kV Bus a. Apply fault at the 8STERLING% (337420) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8STERLING% 500 KV 337420 TO 8EL DORADO% 500 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_8STERLING%__8PERRYVILLE% | 3 Phase fault 8STERLING% (337420) 500 kV Bus a. Apply fault at the 8STERLING% (337420) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8STERLING% 500 KV 337420 TO 8PERRYVILLE% 500 KV 337427 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_8STERLING2%__8STERLING% | 3 Phase fault 8STERLING2% (337413) 500 kV Bus a. Apply fault at the 8STERLING2% (337413) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8STERLING2% 500 KV 337413 TO 8STERLING% 500 KV 337420 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_A.A__CDC | 3 Phase fault A.A.---4 (509784) 138 kV Bus a. Apply fault at the A.A.---4 (509784) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. A.A.---4 138 KV 509784 TO CDC-WT 4 138 KV 509842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-028 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-028 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_A.A.__MINGORD4 | 3 Phase fault A.A.---4 (509784) 138 kV Bus a. Apply fault at the A.A.---4 (509784) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. A.A.---4 138 KV 509784 TO MINGORD4 138 KV 509802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-028 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-028 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_A.A.__PPTAP4 | 3 Phase fault A.A.---4 (509784) 138 kV Bus a. Apply fault at the A.A.---4 (509784) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOHAWK 4 138 KV 509801 TO PPTAP 4 138 KV 509863 CKT 1 b.2. A.A.---4 138 KV 509784 TO MOHAWK 4 138 KV 509801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-028 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-028 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AGENCY_2__JAMESVL2 | 3 Phase fault AGENCY 2 (515229) 69 kV Bus a. Apply fault at the AGENCY 2 (515229) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AGENCY 2 69 KV 515229 TO JAMESVL2 69 KV 515240 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AGENCY_5__EUCLID_5 | 3 Phase fault AGENCY 5 (515230) 161 kV Bus a. Apply fault at the AGENCY 5 (515230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AGENCY 5 161 KV 515230 TO EUCLID 5 161 KV 515251 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AGENCY_5__PECANCK5 | 3 Phase fault AGENCY 5 (515230) 161 kV Bus a. Apply fault at the AGENCY 5 (515230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AGENCY 5 161 KV 515230 TO PECANCK5 161 KV 515234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ALWUETP4__ALLUWE_4 | 3 Phase fault ALWUETP4 (510429) 138 kV Bus a. Apply fault at the ALWUETP4 (510429) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALWUETP4 138 KV 510429 TO ALLUWE 4 138 KV 510430 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ANADARK2__CADDO__2 | 3 Phase fault ANADARK2 (520810) 69 kV Bus a. Apply fault at the ANADARK2 (520810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK2 69 KV 520810 TO CADDO 2 69 KV 520838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ANADARK4__CHERRYRD_4 | 3 Phase fault ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138 KV 520814 TO CHERRYRD 4 138 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | RKYRDGW-2WG trips on voltage protection settings | Disabling voltage protection settings for RKYRDGW-2WG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ANADARK4__FLETCH | 3 Phase fault ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138 KV 520814 TO GEORGIA4 138 KV 520923 CKT 1 b.2. LOAD 1 520923 b.3. FLETCH-4 138 KV 520912 TO GEORGIA4 138 KV 520923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ANADARK4__TUTLETP4 | 3 Phase fault ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138 KV 520814 TO POCASET4 138 KV 521031 CKT 1 b.2. LOAD 1 521031 b.3. POCASET4 138 KV 521031 TO TUTLETP4 138 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ANDRCKT2__MAUDT__2 | 3 Phase fault ANDRCKT2 (509658) 69 kV Bus a. Apply fault at the ANDRCKT2 (509658) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUDT 2 69 KV 509653 TO MAUD 2 69 KV 509657 CKT 1 b.2. LOAD 1 509657 b.3. MAUD 2 69 KV 509657 TO ANDRCKT2 69 KV 509658 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ANDRCKT2__SPRNGHL2 | 3 Phase fault ANDRCKT2 (509658) 69 kV Bus a. Apply fault at the ANDRCKT2 (509658) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDRCKT2 69 KV 509658 TO SIMMS 2 69 KV 509659 CKT 1 b.2. LOAD 1 509659 b.3. SIMMS 2 69 KV 509659 TO SDEKALB2 69 KV 509660 CKT 1 b.4. LOAD 1 509660 b.5. SDEKALB2 69 KV 509660 TO WDEKALB2 69 KV 509661 CKT 1 b.6. LOAD 1 509661 b.7. WDEKALB2 69 KV 509661 TO SPRNGHL2 69 KV 509662 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ANDRSNC4__MUNZCTY4 | 3 Phase fault ANDRSNC4 (508050) 138 kV Bus a. Apply fault at the ANDRSNC4 (508050) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDRSNC4 138 KV 508050 TO BRYANML4 138 KV 508056 CKT 1 b.2. LOAD 1 508056 b.3. BRYANML4 138 KV 508056 TO MUNZCTY4 138 KV 508064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ARAPAHO2__HM | 3 Phase fault ARAPAHO2 (520815) 69 kV Bus a. Apply fault at the ARAPAHO2 (520815) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARAPAHO2 69 KV 520815 TO HM-BTTP2 69 KV 520942 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ARBUCKL4__VANOSTP4 | 3 Phase fault ARBUCKL4 (515117) 138 kV Bus a. Apply fault at the ARBUCKL4 (515117) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARBUCKL4 138 KV 515117 TO VANOSTP4 138 KV 515531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ARCADIA4__DANFRTH4 | 3 Phase fault ARCADIA4 (514907) 138 kV Bus a. Apply fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 138 KV 514907 TO RNDBARN4 138 KV 515461 CKT 1 b.2. LOAD 1 515461 b.3. BURGETT4 138 KV 514510 TO RNDBARN4 138 KV 515461 CKT 1 b.4. LOAD 1 515461 b.5. BURGETT4 138 KV 514510 TO DANFRTH4 138 KV 514833 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ARCADIA4__LGARBER4 | 3 Phase fault ARCADIA4 (514907) 138 kV Bus a. Apply fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 138 KV 514907 TO LGARBER4 138 KV 515465 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ARCADIA7__GEN | 3 Phase fault ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345 KV 514908 TO GEN-2017-133 345 KV 760032 CKT 4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ARCADIA7__REDBUD_7 | 3 Phase fault ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345 KV 514908 TO REDBUD 7 345 KV 514909 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MINCO5 trips on voltage protection settings | Disabling voltage protection settings for MINCO5 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ARCADIA7__SEMINOL7 | 3 Phase fault ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345 KV 514908 TO SEMINOL7 345 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ARSHILL4__FTHUMBG4 | 3 Phase fault ARSHILL4 (507711) 138 kV Bus a. Apply fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138 KV 507711 TO FTHUMBG4 138 KV 507731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ARSHILL4__LIEBERM4 | 3 Phase fault ARSHILL4 (507711) 138 kV Bus a. Apply fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138 KV 507711 TO LIEBERM4 138 KV 508806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ARSHILL4__MCWILLI4 | 3 Phase fault ARSHILL4 (507711) 138 kV Bus a. Apply fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138 KV 507711 TO MCWILLI4 138 KV 507742 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ARSHILL4__RAINES_4 | 3 Phase fault ARSHILL4 (507711) 138 kV Bus a. Apply fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138 KV 507711 TO RAINES 4 138 KV 507749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ARSHILL4__STLGENS4 | 3 Phase fault ARSHILL4 (507711) 138 kV Bus a. Apply fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138 KV 507711 TO STLGENS4 138 KV 507789 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ARTVLTP4__ARTVILL4 | 3 Phase fault ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTVLTP4 138 KV 511537 TO ARTVILL4 138 KV 511538 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ASPEN__4__MOORLND4 | 3 Phase fault ASPEN 4 (520462) 138 kV Bus a. Apply fault at the ASPEN 4 (520462) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASPEN 4 138 KV 520462 TO MOORLND4 138 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_B.BOWTP4__CRAIGJT4 | 3 Phase fault B.BOWTP4 (510888) 138 kV Bus a. Apply fault at the B.BOWTP4 (510888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B.BOWTP4 138 KV 510888 TO CRAIGJT4 138 KV 510890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_B.BOW__4__B.BOWTP4 | 3 Phase fault B.BOW 4 (510864) 138 kV Bus a. Apply fault at the B.BOW 4 (510864) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B.BOW 4 138 KV 510864 TO B.BOWTP4 138 KV 510888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_B111 | 3 Phase fault B111---4 (509767) 138 kV Bus a. Apply fault at the B111---4 (509767) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B111---4 138 KV 509767 TO BA101ST4 138 KV 509768 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BA.N | 3 Phase fault BA.N-ST4 (509786) 138 kV Bus a. Apply fault at the BA.N-ST4 (509786) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.N-ST4 138 KV 509786 TO LLANETP4 138 KV 509804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BA.N | 3 Phase fault BA.N-ST4 (509786) 138 kV Bus a. Apply fault at the BA.N-ST4 (509786) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.N-ST4 138 KV 509786 TO ONETA--4 138 KV 509806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BA.NO | 3 Phase fault BA.NO-S4 (509721) 138 kV Bus a. Apply fault at the BA.NO-S4 (509721) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.NO-S4 138 KV 509721 TO BA.N-ST4 138 KV 509786 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BA101ST4__ONETA | 3 Phase fault BA101ST4 (509768) 138 kV Bus a. Apply fault at the BA101ST4 (509768) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101ST4 138 KV 509768 TO ONETA--4 138 KV 509806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BA101_S4__BA101ST4 | 3 Phase fault BA101 S4 (509737) 138 kV Bus a. Apply fault at the BA101 S4 (509737) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101 S4 138 KV 509737 TO BA101ST4 138 KV 509768 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BA81 | 3 Phase fault BA81---4 (509747) 138 kV Bus a. Apply fault at the BA81---4 (509747) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA81---4 138 KV 509747 TO BA101-N4 138 KV 509769 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BA81 | 3 Phase fault BA81---4 (509747) 138 kV Bus a. Apply fault at the BA81---4 (509747) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA81---4 138 KV 509747 TO FORD---4 138 KV 509772 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BADGER_7__BLUWND_7 | 3 Phase fault BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345 KV 515677 TO BLUWND 7 345 KV 515686 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BADGER_7__G16 | 3 Phase fault BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345 KV 515677 TO G16-003-TAP 345 KV 560071 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BADGER_7__GEN | 3 Phase fault BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345 KV 515677 TO GEN-2015-082 345 KV 585190 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BANNTAP4__E41ST_E4 | 3 Phase fault BANNTAP4 (509785) 138 kV Bus a. Apply fault at the BANNTAP4 (509785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANNTAP4 138 KV 509785 TO E41ST_E4 138 KV 509861 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BANN___2__LSORDTP2 | 3 Phase fault BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69 KV 508053 TO LSORDTP2 69 KV 508063 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BANN___2__SUGHLWT2 | 3 Phase fault BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69 KV 508053 TO REDLICK2 69 KV 508073 CKT 1 b.2. LOAD 1 508073 b.3. REDLICK2 69 KV 508073 TO RICHMND2 69 KV 508076 CKT 1 b.4. LOAD 1 508076 b.5. NW_TEXAR 2 69 KV 504109 TO RICHMND2 69 KV 508076 CKT 1 b.6. LOAD 1 508076 b.7. NW_TEXAR 2 69 KV 504109 TO SUGHLWT2 69 KV 508082 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BANN___2__TAYLOR_2 | 3 Phase fault BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69 KV 508053 TO KINGHWY2 69 KV 508061 CKT 1 b.2. LOAD 1 508061 b.3. KINGHWY2 69 KV 508061 TO TEXOPER2 69 KV 508087 CKT 1 b.4. LOAD 1 508087 b.5. TAYLOR 2 69 KV 508083 TO TEXOPER2 69 KV 508087 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BANN___4__NWT | 3 Phase fault BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138 KV 508054 TO NWT-BNT4 138 KV 508070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BANN___4__REDSPRG4 | 3 Phase fault BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138 KV 508054 TO REDSPRG4 138 KV 508075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BANN___4__SETEXAR4 | 3 Phase fault BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138 KV 508054 TO SETEXAR4 138 KV 508078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BARITE | 3 Phase fault BARITE-RD 4 (504379) 138 kV Bus a. Apply fault at the BARITE-RD 4 (504379) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARITE-RD 4 138 KV 504379 TO BARITERDTP 4 138 KV 507463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BARNSAL4__MOUNDRD4 | 3 Phase fault BARNSAL4 (510388) 138 kV Bus a. Apply fault at the BARNSAL4 (510388) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARNSAL4 138 KV 510388 TO BARNPMP4 138 KV 510433 CKT 1 b.2. LOAD 1 510433 b.3. MOUNDRD4 138 KV 510395 TO BARNPMP4 138 KV 510433 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BAWATAP2__COWETAP2 | 3 Phase fault BAWATAP2 (509718) 69 kV Bus a. Apply fault at the BAWATAP2 (509718) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAWATAP2 69 KV 509718 TO COWETAP2 69 KV 509781 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BAWATAP2__T.S.E. | 3 Phase fault BAWATAP2 (509718) 69 kV Bus a. Apply fault at the BAWATAP2 (509718) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAWATAP2 69 KV 509718 TO T.S.E.-2 69 KV 509820 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BAWATER2__BAWATAP2 | 3 Phase fault BAWATER2 (509717) 69 kV Bus a. Apply fault at the BAWATER2 (509717) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAWATER2 69 KV 509717 TO BAWATAP2 69 KV 509718 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BCVI_HVB__SLKHILLS_4 | 3 Phase fault BCVI_HVB (520514) 138 kV Bus a. Apply fault at the BCVI_HVB (520514) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BCVI_HVB 138 KV 520514 TO SLKHILLS 4 138 KV 521103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BCV_SW_4__CHERRYRD_4 | 3 Phase fault BCV SW 4 (520513) 138 kV Bus a. Apply fault at the BCV SW 4 (520513) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BCV SW 4 138 KV 520513 TO CHERRYRD 4 138 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BC_SW__4__SLKHILLS_4 | 3 Phase fault BC SW 4 (520512) 138 kV Bus a. Apply fault at the BC SW 4 (520512) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BC SW 4 138 KV 520512 TO SLKHILLS 4 138 KV 521103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BEELINE4__BLUEBEL4 | 3 Phase fault BEELINE4 (515247) 138 kV Bus a. Apply fault at the BEELINE4 (515247) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONESTR4 138 KV 515245 TO BEELINE4 138 KV 515247 CKT 1 b.2. LOAD 1 515247 b.3. KELLYVL4 138 KV 515200 TO LONESTR4 138 KV 515245 CKT 1 b.4. LOAD 1 515245 b.5. KELLYVL4 138 KV 515200 TO BLUEBEL4 138 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BEELINE4__EXPGLNT4 | 3 Phase fault BEELINE4 (515247) 138 kV Bus a. Apply fault at the BEELINE4 (515247) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEELINE4 138 KV 515247 TO EXPGLNT4 138 KV 515473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BEELINE4__POLECTP4 | 3 Phase fault BEELINE4 (515247) 138 kV Bus a. Apply fault at the BEELINE4 (515247) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIBBENS4 138 KV 515237 TO BEELINE4 138 KV 515247 CKT 1 b.2. LOAD 1 515247 b.3. POLECTP4 138 KV 515218 TO TIBBENS4 138 KV 515237 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BELISLE4__38TH_ST4 | 3 Phase fault BELISLE4 (514844) 138 kV Bus a. Apply fault at the BELISLE4 (514844) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELISLE4 138 KV 514844 TO 38TH ST4 138 KV 514846 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MINCO5G11 trips on voltage protection settings | Disabling voltage protection settings for MINCO5G11 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BELISLE4__WESTERN4 | 3 Phase fault BELISLE4 (514844) 138 kV Bus a. Apply fault at the BELISLE4 (514844) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELISLE4 138 KV 514844 TO WESTERN4 138 KV 514869 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MINCO5G11 trips on voltage protection settings | Disabling voltage protection settings for MINCO5G11 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BEVYTAP5__FTSMTHE5 | 3 Phase fault BEVYTAP5 (515299) 161 kV Bus a. Apply fault at the BEVYTAP5 (515299) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVYTAP5 161 KV 515299 TO FTSMTHE5 161 KV 515300 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BING | 3 Phase fault BING-TP2 (511443) 69 kV Bus a. Apply fault at the BING-TP2 (511443) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BING-TP2 69 KV 511443 TO S.W.S.-2 69 KV 511476 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BINGERJ4__NIJECT_4 | 3 Phase fault BINGERJ4 (520827) 138 kV Bus a. Apply fault at the BINGERJ4 (520827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BINGERJ4 138 KV 520827 TO NIJECT 4 138 KV 521010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BINGERJ4__SICKLES4 | 3 Phase fault BINGERJ4 (520827) 138 kV Bus a. Apply fault at the BINGERJ4 (520827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BINGERJ4 138 KV 520827 TO SICKLES4 138 KV 521050 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BLANCH | 3 Phase fault BLANCH-2 (508801) 69 kV Bus a. Apply fault at the BLANCH-2 (508801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCH-2 69 KV 508801 TO LIEBERM2 69 KV 508805 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BLANCHD4__OU_SW_4 | 3 Phase fault BLANCHD4 (520828) 138 kV Bus a. Apply fault at the BLANCHD4 (520828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCHD4 138 KV 520828 TO OU SW 4 138 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BLOOMBG2__IPC_TAP2 | 3 Phase fault BLOOMBG2 (508055) 69 kV Bus a. Apply fault at the BLOOMBG2 (508055) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLOOMBG2 69 KV 508055 TO IPC TAP2 69 KV 508058 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BLUEBEL4__BOWDEN_4 | 3 Phase fault BLUEBEL4 (515242) 138 kV Bus a. Apply fault at the BLUEBEL4 (515242) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBEL4 138 KV 515242 TO BOWDEN 4 138 KV 515243 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BLUERIV4__PARKLN_4 | 3 Phase fault BLUERIV4 (515133) 138 kV Bus a. Apply fault at the BLUERIV4 (515133) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUERIV4 138 KV 515133 TO PARKLN 4 138 KV 515178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BORDER_____7__BECKHAM7 | 3 Phase fault BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345 KV 515458 TO BECKHAM7 345 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BORDER_____7__TUCO_INT___7 | 3 Phase fault BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345 KV 515458 TO TUCO_INT 7 345 KV 525832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BOWMAN_2__KNGINDT2 | 3 Phase fault BOWMAN 2 (514813) 69 kV Bus a. Apply fault at the BOWMAN 2 (514813) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOWMAN 2 69 KV 514813 TO KNGINDT2 69 KV 515625 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BOWMAN_2__OMKINGF2 | 3 Phase fault BOWMAN 2 (514813) 69 kV Bus a. Apply fault at the BOWMAN 2 (514813) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOWMAN 2 69 KV 514813 TO OMKINGF2 69 KV 529280 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BOWMAN_2__TURCRKT2 | 3 Phase fault BOWMAN 2 (514813) 69 kV Bus a. Apply fault at the BOWMAN 2 (514813) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOWMAN 2 69 KV 514813 TO TURCRKT2 69 KV 515517 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BRANDYBR__PIRKEY_4 | 3 Phase fault BRANDYBR (508596) 138 kV Bus a. Apply fault at the BRANDYBR (508596) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRANDYBR 138 KV 508596 TO EASTON 4 138 KV 509092 CKT 1 b.2. LOAD 1 509092 b.3. PIRKEY 4 138 KV 508562 TO EASTON 4 138 KV 509092 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BRCKWND4__BRECKNR4 | 3 Phase fault BRCKWND4 (514642) 138 kV Bus a. Apply fault at the BRCKWND4 (514642) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRCKWND4 138 KV 514642 TO BRECKNR4 138 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BRECKNR4__ENIDINT4 | 3 Phase fault BRECKNR4 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 138 KV 514815 TO ENIDINT4 138 KV 515383 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BRECKNR4__PLNSMEN4 | 3 Phase fault BRECKNR4 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 138 KV 514815 TO PLNSMEN4 138 KV 515641 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BRIDGCR4__SUNSHIN4 | 3 Phase fault BRIDGCR4 (520501) 138 kV Bus a. Apply fault at the BRIDGCR4 (520501) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRIDGCR4 138 KV 520501 TO SUNSHIN4 138 KV 521059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BRIDGCR4__TUTLETP4 | 3 Phase fault BRIDGCR4 (520501) 138 kV Bus a. Apply fault at the BRIDGCR4 (520501) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRIDGCR4 138 KV 520501 TO TUTLETP4 138 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BRISTOW4__BLUEBEL4 | 3 Phase fault BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 138 KV 515035 TO BLUEBEL4 138 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BRISTOW4__GRNWOOD4 | 3 Phase fault BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 138 KV 515035 TO GRNWOOD4 138 KV 515417 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BRISTOW4__KEYWEST4 | 3 Phase fault BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 138 KV 515035 TO KEYWEST4 138 KV 515048 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BRKN_BW4__BETHEL_4 | 3 Phase fault BRKN BW4 (505614) 138 kV Bus a. Apply fault at the BRKN BW4 (505614) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRKN BW4 138 KV 505614 TO BETHEL 4 138 KV 510928 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BRKN_BW4__CRAIGJT4 | 3 Phase fault BRKN BW4 (505614) 138 kV Bus a. Apply fault at the BRKN BW4 (505614) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRKN BW4 138 KV 505614 TO CRAIGJT4 138 KV 510890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BRKN_BW4__HOCHTWN4 | 3 Phase fault BRKN BW4 (505614) 138 kV Bus a. Apply fault at the BRKN BW4 (505614) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRKN BW4 138 KV 505614 TO HOCHTWN4 138 KV 520943 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BRYANML4__MUNZCTY4 | 3 Phase fault BRYANML4 (508056) 138 kV Bus a. Apply fault at the BRYANML4 (508056) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRYANML4 138 KV 508056 TO MUNZCTY4 138 KV 508064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BTLRJCT2__HM | 3 Phase fault BTLRJCT2 (520457) 69 kV Bus a. Apply fault at the BTLRJCT2 (520457) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BTLRJCT2 69 KV 520457 TO HM-BTTP2 69 KV 520942 CKT NO c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BUFFALO7__THISTLE7 | 3 Phase fault BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345 KV 532782 TO THISTLE7 345 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-221, GEN-2017-121, GEN-2018-057, and AGSI-2015-001 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-221, GEN-2017-121, GEN-2018-057, and AGSI-2015-001 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BUFORDR2__COOKVTP2 | 3 Phase fault BUFORDR2 (508287) 69 kV Bus a. Apply fault at the BUFORDR2 (508287) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFORDR2 69 KV 508287 TO COOKVTP2 69 KV 508338 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BUFORDR2__DEKALB_2 | 3 Phase fault BUFORDR2 (508287) 69 kV Bus a. Apply fault at the BUFORDR2 (508287) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFORDR2 69 KV 508287 TO DEKALB 2 69 KV 508289 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BUFORDR2__NAPLES_2 | 3 Phase fault BUFORDR2 (508287) 69 kV Bus a. Apply fault at the BUFORDR2 (508287) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFORDR2 69 KV 508287 TO NAPLES 2 69 KV 508307 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BULFOOT4__BULFTTP4 | 3 Phase fault BULFOOT4 (515960) 138 kV Bus a. Apply fault at the BULFOOT4 (515960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFOOT4 138 KV 515960 TO BULFTTP4 138 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BULFTTP4__DOVERSW4 | 3 Phase fault BULFTTP4 (520535) 138 kV Bus a. Apply fault at the BULFTTP4 (520535) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFTTP4 138 KV 520535 TO DOVERSW4 138 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BUNCHCK4__BRECKNR4 | 3 Phase fault BUNCHCK4 (514701) 138 kV Bus a. Apply fault at the BUNCHCK4 (514701) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 138 KV 514701 TO BRECKNR4 138 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BV | 3 Phase fault BV-COM-4 (510390) 138 kV Bus a. Apply fault at the BV-COM-4 (510390) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BV-COM-4 138 KV 510390 TO BV-SE--4 138 KV 510391 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | CGENSUB2 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BV | 3 Phase fault BV-COM-4 (510390) 138 kV Bus a. Apply fault at the BV-COM-4 (510390) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BV-COM-4 138 KV 510390 TO MOUNDRD4 138 KV 510395 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | CGENSUB2 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BV | 3 Phase fault BV-SE--4 (510391) 138 kV Bus a. Apply fault at the BV-SE--4 (510391) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BV-SE--4 138 KV 510391 TO BLUESTM4 138 KV 510394 CKT 1 b.2. LOAD 1 510394 b.3. BV-COM-4 138 KV 510390 TO BLUESTM4 138 KV 510394 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | CGENSUB2 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BV | 3 Phase fault BV-SE--4 (510391) 138 kV Bus a. Apply fault at the BV-SE--4 (510391) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NBVILLE4 138 KV 510386 TO BV-SE--4 138 KV 510391 CKT 1 b.2. LOAD 1 510391 b.3. NBVILLE4 138 KV 510386 TO COFFEYT4 138 KV 510422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | CGENSUB2 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BVRCNTY7__BADGER_7 | 3 Phase fault BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345 KV 515554 TO BADGER 7 345 KV 515677 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_C | 3 Phase fault C-RIVER4 (510946) 138 kV Bus a. Apply fault at the C-RIVER4 (510946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C-RIVER4 138 KV 510946 TO TALAWANDA 4 138 KV 510951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_C | 3 Phase fault C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 345 KV 515422 TO FIREWHL-TAP 345 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CADDO__2__WASHITA2 | 3 Phase fault CADDO 2 (520838) 69 kV Bus a. Apply fault at the CADDO 2 (520838) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CADDO 2 69 KV 520838 TO WASHITA2 69 KV 521088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CALRYTP2__MUSKOGE2 | 3 Phase fault CALRYTP2 (515211) 69 kV Bus a. Apply fault at the CALRYTP2 (515211) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALRYTP2 69 KV 515211 TO MUSKOGE2 69 KV 515221 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CANADN___CANADASN4 | 3 Phase fault CANADN-4 (514947) 138 kV Bus a. Apply fault at the CANADN-4 (514947) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADN-4 138 KV 514947 TO CANADNS4 138 KV 520842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | RKYRDGW-2WG trips on voltage protection settings | Disabling voltage protection settings for RKYRDGW-2WG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CANADN7__FSHRTAP7 | 3 Phase fault CANADN7 (515605) 345 kV Bus a. Apply fault at the CANADN7 (515605) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANADN7 345 KV 515605 TO FSHRTAP7 345 KV 515610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CANADNS4__GOLDSBY4 | 3 Phase fault CANADNS4 (520842) 138 kV Bus a. Apply fault at the CANADNS4 (520842) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 138 KV 520842 TO GOLDSBY4 138 KV 520924 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | RKYRDGW-2WG trips on voltage protection settings | Disabling voltage protection settings for RKYRDGW-2WG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CANA___4__CALUMET4 | 3 Phase fault CANA 4 (520502) 138 kV Bus a. Apply fault at the CANA 4 (520502) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANA 4 138 KV 520502 TO CALUMET4 138 KV 520839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CAN_GAS4__JENSEN_4 | 3 Phase fault CAN_GAS4 (511540) 138 kV Bus a. Apply fault at the CAN_GAS4 (511540) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 138 KV 511540 TO JENSEN 4 138 KV 514821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CARROLL6__DOLHILL6 | 3 Phase fault CARROLL6 (500140) 230 kV Bus a. Apply fault at the CARROLL6 (500140) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARROLL6 230 KV 500140 TO DOLHILL6 230 KV 500260 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CARSN | 3 Phase fault CARSN-N4 (509741) 138 kV Bus a. Apply fault at the CARSN-N4 (509741) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-N4 138 KV 509741 TO CARSONT4 138 KV 509865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on frequency protection settings GEN-2017-141 trips on voltage protection settings | Disabling frequency protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. Disabling voltage protection settings for GEN-2017-141 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CARSN | 3 Phase fault CARSN-S4 (509756) 138 kV Bus a. Apply fault at the CARSN-S4 (509756) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-S4 138 KV 509756 TO KENSH-W4 138 KV 509777 CKT 1 b.2. LOAD 1 509777 b.3. DENVR-C4 138 KV 509742 TO KENSH-W4 138 KV 509777 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on frequency protection settings GEN-2017-141 trips on voltage protection settings | Disabling frequency protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. Disabling voltage protection settings for GEN-2017-141 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CARSN | 3 Phase fault CARSN-S4 (509756) 138 kV Bus a. Apply fault at the CARSN-S4 (509756) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-S4 138 KV 509756 TO T.P.S.-4 138 KV 509788 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on frequency protection settings GEN-2017-141 trips on voltage protection settings | Disabling frequency protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. Disabling voltage protection settings for GEN-2017-141 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CARSN | 3 Phase fault CARSN-T4 (509739) 138 kV Bus a. Apply fault at the CARSN-T4 (509739) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-T4 138 KV 509739 TO UNIONAV4 138 KV 509740 CKT 1 b.2. LOAD 1 509740 b.3. UNIONAV4 138 KV 509740 TO CARSN-C4 138 KV 509749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on frequency protection settings GEN-2017-141 trips on voltage protection settings | Disabling frequency protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. Disabling voltage protection settings for GEN-2017-141 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CARSN | 3 Phase fault CARSN-T4 (509739) 138 kV Bus a. Apply fault at the CARSN-T4 (509739) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-T4 138 KV 509739 TO S.S.---4 138 KV 509815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on frequency protection settings GEN-2017-141 trips on voltage protection settings | Disabling frequency protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. Disabling voltage protection settings for GEN-2017-141 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CARTER_4__CHIKSAW4 | 3 Phase fault CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138 KV 515138 TO CHIKSAW4 138 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CARTER_4__HONEYCK4 | 3 Phase fault CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138 KV 515138 TO HONEYCK4 138 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CARTHGT4__LOGANSP4 | 3 Phase fault CARTHGT4 (509060) 138 kV Bus a. Apply fault at the CARTHGT4 (509060) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHGT4 138 KV 509060 TO LOGANSP4 138 KV 509071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CARTRCO4__GEN | 3 Phase fault CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138 KV 515561 TO GEN-2017-027 138 KV 588710 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CARTRCO4__ORIGINW4 | 3 Phase fault CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138 KV 515561 TO ORIGINW4 138 KV 515563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on frequency protection settings | Disabling frequency protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CASHION4__TWNLKJT4 | 3 Phase fault CASHION4 (520479) 138 kV Bus a. Apply fault at the CASHION4 (520479) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASHION4 138 KV 520479 TO TWNLKJT4 138 KV 520847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CATOOSA2__DAWSON | 3 Phase fault CATOOSA2 (509799) 69 kV Bus a. Apply fault at the CATOOSA2 (509799) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BCIRCLE2 69 KV 509794 TO CATOOSA2 69 KV 509799 CKT 1 b.2. DAWSON-2 69 KV 509791 TO BCIRCLE2 69 KV 509794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CATOOSA4__CDC | 3 Phase fault CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138 KV 509790 TO OWAS88_4 138 KV 509887 CKT 1 b.2. LOAD 1 509887 b.3. CDC-ET 4 138 KV 509839 TO OWAS88_4 138 KV 509887 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-141 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-141 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CATOOSA4__LLANETP4 | 3 Phase fault CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138 KV 509790 TO LLANETP4 138 KV 509804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CATOOSA4__PCATSAT4 | 3 Phase fault CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138 KV 509790 TO PCATSAT4 138 KV 509841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CATOOSA4__TERNITP4 | 3 Phase fault CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138 KV 509790 TO TERNITP4 138 KV 509835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CATSAGR5__COLINS_5 | 3 Phase fault CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ELMCRK 161 KV 300993 TO CATSAGR5 161 KV 512638 CKT 1 b.2. 5ELMCRK 161 KV 300993 TO COLINS 5 161 KV 512627 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-028 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-028 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CATSAGR5__MAID___5 | 3 Phase fault CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 161 KV 512638 TO MAID 5 161 KV 512648 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CDC | 3 Phase fault CDC-ET 4 (509839) 138 kV Bus a. Apply fault at the CDC-ET 4 (509839) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CDC-ET 4 138 KV 509839 TO OWAS88_4 138 KV 509887 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CDRDLTP4__OKEENE_4 | 3 Phase fault CDRDLTP4 (520848) 138 kV Bus a. Apply fault at the CDRDLTP4 (520848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CDRDLTP4 138 KV 520848 TO OKEENE 4 138 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CEDARLN4__SOONRTP4 | 3 Phase fault CEDARLN4 (514948) 138 kV Bus a. Apply fault at the CEDARLN4 (514948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARLN4 138 KV 514948 TO SOONRTP4 138 KV 514949 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MINCO-WTG34 trips on voltage protection setings | Disabling instantaneous voltage protection settings for MINCO-WTG34 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CEDRDAL4__CDRDLTP4 | 3 Phase fault CEDRDAL4 (520507) 138 kV Bus a. Apply fault at the CEDRDAL4 (520507) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDRDAL4 138 KV 520507 TO CDRDLTP4 138 KV 520848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CEMRD_TP4__CMTRYRD4 | 3 Phase fault CEMRD_TP4 (511576) 138 kV Bus a. Apply fault at the CEMRD_TP4 (511576) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEMRD_TP4 138 KV 511576 TO CMTRYRD4 138 KV 515864 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CHAMSPR7__CLARKSV7 | 3 Phase fault CHAMSPR7 (506945) 345 kV Bus a. Apply fault at the CHAMSPR7 (506945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAMSPR7 345 KV 506945 TO CLARKSV7 345 KV 509745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CHAMSPR7__TONTITN7 | 3 Phase fault CHAMSPR7 (506945) 345 kV Bus a. Apply fault at the CHAMSPR7 (506945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAMSPR7 345 KV 506945 TO TONTITN7 345 KV 506959 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CHAPELH4__CHAPLHL4 | 3 Phase fault CHAPELH4 (508337) 138 kV Bus a. Apply fault at the CHAPELH4 (508337) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPELH4 138 KV 508337 TO CHAPLHL4 138 KV 509664 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CHCKSHA4__CKSHATP4 | 3 Phase fault CHCKSHA4 (520472) 138 kV Bus a. Apply fault at the CHCKSHA4 (520472) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHCKSHA4 138 KV 520472 TO CKSHATP4 138 KV 520473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CHEEKTP4__CHEEK_4 | 3 Phase fault CHEEKTP4 (515415) 138 kV Bus a. Apply fault at the CHEEKTP4 (515415) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHEEKTP4 138 KV 515415 TO CHEEK_4 138 KV 521125 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CHERYCK4__NORMHLL4 | 3 Phase fault CHERYCK4 (514957) 138 kV Bus a. Apply fault at the CHERYCK4 (514957) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERYCK4 138 KV 514957 TO NORMHLL4 138 KV 516097 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CHISHOLM7__BECKHAM7 | 3 Phase fault CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345 KV 511553 TO BECKHAM7 345 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CHISHOLM7__G16 | 3 Phase fault CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345 KV 511553 TO G16-037-TAP 345 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CHISHOM4__FAIRFLD4 | 3 Phase fault CHISHOM4 (515374) 138 kV Bus a. Apply fault at the CHISHOM4 (515374) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOM4 138 KV 515374 TO FAIRFLD4 138 KV 515468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CHOUTEAUCRK5__GEN | 3 Phase fault CHOUTEAUCRK5 (513570) 161 kV Bus a. Apply fault at the CHOUTEAUCRK5 (513570) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHOUTEAUCRK5 161 KV 513570 TO GEN-2017-061 161 KV 588990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CIMARON4__DVISION4 | 3 Phase fault CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYMAKR4 138 KV 514863 TO CIMARON4 138 KV 514898 CKT 1 b.2. DVISION4 138 KV 514853 TO HAYMAKR4 138 KV 514863 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MINCO-WTG34 trips on voltage protection setings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CIMARON4__MCCLAIN4 | 3 Phase fault CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA 4 138 KV 514895 TO CIMARON4 138 KV 514898 CKT 1 b.2. SARA 4 138 KV 514895 TO MCCLAIN4 138 KV 514902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MINCO-WTG33 trips on voltage protection setings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CIMARON4__MUSTANG4 | 3 Phase fault CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CZECHAL4 138 KV 514894 TO CIMARON4 138 KV 514898 CKT 1 b.2. XEROX 4 138 KV 514893 TO CZECHAL4 138 KV 514894 CKT 1 b.3. LOAD 1 514894 b.4. XEROX 4 138 KV 514893 TO MORGAN 4 138 KV 514896 CKT 1 b.5. LOAD 1 514896 b.6. MUSTANG4 138 KV 514861 TO MORGAN 4 138 KV 514896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MINCO-WTG34 trips on voltage protection setings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CIMARON7__FSHRTAP7 | 3 Phase fault CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345 KV 514901 TO FSHRTAP7 345 KV 515610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | KNGFSHR trips on voltage protection settings | Disabling voltage protection settings for KNGFSHR prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CIMARON7__MATHWSN7 | 3 Phase fault CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345 KV 514901 TO MATHWSN7 345 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CIMARON7__NORMHLL7 | 3 Phase fault CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345 KV 514901 TO NORMHLL7 345 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CIP____4__CDC | 3 Phase fault CIP 4 (509714) 138 kV Bus a. Apply fault at the CIP 4 (509714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIP 4 138 KV 509714 TO CDC-ET 4 138 KV 509839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CIP____4__CDC____4 | 3 Phase fault CIP 4 (509714) 138 kV Bus a. Apply fault at the CIP 4 (509714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIP 4 138 KV 509714 TO CDC 4 138 KV 509715 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CKSHATP4__CORN_TP4 | 3 Phase fault CKSHATP4 (520473) 138 kV Bus a. Apply fault at the CKSHATP4 (520473) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CKSHATP4 138 KV 520473 TO CORN TP4 138 KV 520867 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CL | 3 Phase fault CL-AFTP4 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 138 KV 511446 TO ELKCTY-4 138 KV 511458 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CL | 3 Phase fault CL-AFTP4 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 138 KV 511446 TO HOB-JCT4 138 KV 511463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CLARKCOUNTY7__THISTLE7 | 3 Phase fault CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345 KV 539800 TO THISTLE7 345 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2011-008 trips on frequency protection settings | Disabling frequency protection settings for GEN-2011-008 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CLARKSV7__GEN | 3 Phase fault CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345 KV 509745 TO GEN-2017-140 345 KV 760389 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-141, GEN-2017-140 trips on frequency protection settings | Disabling frequency protection settings for GEN-2017-141, GEN-2017-140 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CLARKSV7__MUSKOGE7 | 3 Phase fault CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345 KV 509745 TO MUSKOGE7 345 KV 515224 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-141 trips on frequency protection settings | Disabling frequency protection settings for GEN-2017-141 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CLARKSV7__ONETA | 3 Phase fault CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345 KV 509745 TO ONETA--7 345 KV 509807 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-140 trips on frequency protection settings | Disabling frequency protection settings for GEN-2017-140 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CLARMR_5__CHOUTEAUCRK5 | 3 Phase fault CLARMR 5 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 161 KV 512651 TO CHOUTEAUCRK5 161 KV 513570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CLASSEN4__TROSPER4 | 3 Phase fault CLASSEN4 (514922) 138 kV Bus a. Apply fault at the CLASSEN4 (514922) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLASSEN4 138 KV 514922 TO CROSTWN4 138 KV 515851 CKT 1 b.2. LOAD 1 515851 b.3. LIGHTCK4 138 KV 514923 TO CROSTWN4 138 KV 515851 CKT 1 b.4. LOAD 1 515851 b.5. LIGHTCK4 138 KV 514923 TO TROSPER4 138 KV 514963 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-029 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-029 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CLEOSW_2__RNGWODJ2 | 3 Phase fault CLEOSW 2 (520855) 69 kV Bus a. Apply fault at the CLEOSW 2 (520855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOSW 2 69 KV 520855 TO RNGWODJ2 69 KV 521039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CLEVETP2__SO4TH__2 | 3 Phase fault CLEVETP2 (514722) 69 kV Bus a. Apply fault at the CLEVETP2 (514722) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVETP2 69 KV 514722 TO SO4TH 2 69 KV 514730 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CLEVLND7__G15 | 3 Phase fault CLEVLND7 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 345 KV 512694 TO G15-066T 345 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CLVLDSW4__AMBERTP4 | 3 Phase fault CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138 KV 520508 TO AMBERTP4 138 KV 520530 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CLVLDSW4__ANADARK4 | 3 Phase fault CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138 KV 520508 TO ANADARK4 138 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CLVLDSW4__COGAR__4 | 3 Phase fault CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138 KV 520508 TO COGAR 4 138 KV 520859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CMBLCRK4__CMBLTP_4 | 3 Phase fault CMBLCRK4 (515930) 138 kV Bus a. Apply fault at the CMBLCRK4 (515930) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMBLCRK4 138 KV 515930 TO CMBLTP 4 138 KV 520474 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CMBLTP_4__FOURCTP4 | 3 Phase fault CMBLTP 4 (520474) 138 kV Bus a. Apply fault at the CMBLTP 4 (520474) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMBLTP 4 138 KV 520474 TO FOURCTP4 138 KV 520545 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_COBRN_CREEK3__WHEELER____3 | 3 Phase fault COBRN_CREEK3 (523772) 115 kV Bus a. Apply fault at the COBRN_CREEK3 (523772) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COBRN_CREEK3 115 KV 523772 TO WHEELER 3 115 KV 523776 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_COFFEYT4__DEARING4 | 3 Phase fault COFFEYT4 (510422) 138 kV Bus a. Apply fault at the COFFEYT4 (510422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COFFEYT4 138 KV 510422 TO DEARING4 138 KV 533002 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | CGENSUB2 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_COLE___4__OU_SW_4 | 3 Phase fault COLE 4 (520861) 138 kV Bus a. Apply fault at the COLE 4 (520861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLE 4 138 KV 520861 TO OU SW 4 138 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_COLINS_5__CLARMR_5 | 3 Phase fault COLINS 5 (512627) 161 kV Bus a. Apply fault at the COLINS 5 (512627) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5KETONVL 161 KV 300997 TO COLINS 5 161 KV 512627 CKT 1 b.2. 5KETONVL 161 KV 300997 TO CLARMR 5 161 KV 512651 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_COMANC | 3 Phase fault COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69 KV 511436 TO L.E.S.-2 69 KV 511466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_COMANC | 3 Phase fault COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138 KV 511437 TO 112GORE4 138 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_COMANC | 3 Phase fault COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138 KV 511437 TO COMMTAP4 138 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_COMANC | 3 Phase fault COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138 KV 511437 TO L.E.S.-4 138 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_COMMTAP4__OMDUNCN4 | 3 Phase fault COMMTAP4 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMMTAP4 138 KV 511494 TO OMDUNCN4 138 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CORNVIL4__ALEX_BR4 | 3 Phase fault CORNVIL4 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138 KV 511449 TO ALEX BR4 138 KV 511516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CORNVIL4__CORN_TP4 | 3 Phase fault CORNVIL4 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138 KV 511449 TO CORN TP4 138 KV 520867 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CORNVIL4__LEONARD4 | 3 Phase fault CORNVIL4 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138 KV 511449 TO LEONARD4 138 KV 511575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CORNVIL4__MAUD___4 | 3 Phase fault CORNVIL4 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCHD4 138 KV 511508 TO MAUD 4 138 KV 515055 CKT 1 b.2. CORNVIL4 138 KV 511449 TO BLANCHD4 138 KV 511508 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CORNVIL4__N29CHIK4 | 3 Phase fault CORNVIL4 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138 KV 511449 TO N29CHIK4 138 KV 511502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CORNVIL4__NORGE | 3 Phase fault CORNVIL4 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138 KV 511449 TO NORGE--4 138 KV 511483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CORNVIL4__SANTAFE4 | 3 Phase fault CORNVIL4 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138 KV 511449 TO SANTAFE4 138 KV 511492 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CRAIGJT4__HOCHJCT4 | 3 Phase fault CRAIGJT4 (510890) 138 kV Bus a. Apply fault at the CRAIGJT4 (510890) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIGJT4 138 KV 510890 TO MTRIVER4 138 KV 521004 CKT 1 b.2. LOAD 1 521004 b.3. HOCHJCT4 138 KV 520823 TO MTRIVER4 138 KV 521004 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CRAIGJT4__MENA___4 | 3 Phase fault CRAIGJT4 (510890) 138 kV Bus a. Apply fault at the CRAIGJT4 (510890) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENA 4 138 KV 507436 TO GORDON TAP 4 138 KV 507461 CKT 1 b.2. LOAD A1 507461 b.3. GORDON TAP 4 138 KV 507461 TO CRAIGJT4 138 KV 510890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CRESENT4__GEN | 3 Phase fault CRESENT4 (515377) 138 kV Bus a. Apply fault at the CRESENT4 (515377) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESENT4 138 KV 515377 TO GEN-2016-032 138 KV 587210 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CRESENT4__TWNLKSW4 | 3 Phase fault CRESENT4 (515377) 138 kV Bus a. Apply fault at the CRESENT4 (515377) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESENT4 138 KV 515377 TO TWNLKSW4 138 KV 521073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CTNWOOD4__ARCADIA4 | 3 Phase fault CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138 KV 514827 TO ARCADIA4 138 KV 514907 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CTNWOOD4__CRESENT4 | 3 Phase fault CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138 KV 514827 TO CRESENT4 138 KV 515377 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CTNWOOD4__KETCHTP4 | 3 Phase fault CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138 KV 514827 TO LBRTYLK4 138 KV 515373 CKT 1 b.2. LOAD 1 515373 b.3. WATRLOO4 138 KV 514831 TO LBRTYLK4 138 KV 515373 CKT 1 b.4. LOAD 1 515373 b.5. WATRLOO4 138 KV 514831 TO WHITESB4 138 KV 515467 CKT 1 b.6. LOAD 1 515467 b.7. MITCHSB4 138 KV 515466 TO WHITESB4 138 KV 515467 CKT 1 b.8. LOAD 1 515467 b.9. KETCHTP4 138 KV 514828 TO MITCHSB4 138 KV 515466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-118 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CTNWOOD4__KINZE__4 | 3 Phase fault CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138 KV 514827 TO PINE ST4 138 KV 514829 CKT 1 b.2. LOAD 1 514829 b.3. LOAD 2 514829 b.4. PINE ST4 138 KV 514829 TO FITZGRD4 138 KV 514830 CKT 1 b.5. LOAD 1 514830 b.6. FITZGRD4 138 KV 514830 TO KINZE 4 138 KV 515008 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CTNWOOD4__LBRTYLK4 | 3 Phase fault CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138 KV 514827 TO LBRTYLK4 138 KV 515373 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CUSTDAY1_5__HERRON_5 | 3 Phase fault CUSTDAY1 5 (513590) 161 kV Bus a. Apply fault at the CUSTDAY1 5 (513590) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTDAY1 5 161 KV 513590 TO HERRON 5 161 KV 513591 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DANFRTH4__KETCH__4 | 3 Phase fault DANFRTH4 (514833) 138 kV Bus a. Apply fault at the DANFRTH4 (514833) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DANFRTH4 138 KV 514833 TO KETCH 4 138 KV 514834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DARENCT2__ALAMANC2 | 3 Phase fault DARENCT2 (509647) 69 kV Bus a. Apply fault at the DARENCT2 (509647) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DARENCT2 69 KV 509647 TO ALAMANC2 69 KV 509649 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DARENCT2__DARENCO2 | 3 Phase fault DARENCT2 (509647) 69 kV Bus a. Apply fault at the DARENCT2 (509647) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DARENCT2 69 KV 509647 TO DARENCO2 69 KV 509648 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DAWSON | 3 Phase fault DAWSON-4 (509792) 138 kV Bus a. Apply fault at the DAWSON-4 (509792) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSON-4 138 KV 509792 TO DAWSONT4 138 KV 509803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DAWSONT4__N21ST | 3 Phase fault DAWSONT4 (509803) 138 kV Bus a. Apply fault at the DAWSONT4 (509803) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONT4 138 KV 509803 TO N21ST--4 138 KV 509866 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DAYTON_4__HOBBYLO4 | 3 Phase fault DAYTON 4 (514892) 138 kV Bus a. Apply fault at the DAYTON 4 (514892) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAYTON 4 138 KV 514892 TO HOBBYLO4 138 KV 515338 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MINCO-WTG34 trips on voltage protection setings | Disabling instantaneous voltage protection settings for MINCO-WTG34 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DEEPFKT2__DEEPFRK2 | 3 Phase fault DEEPFKT2 (514970) 69 kV Bus a. Apply fault at the DEEPFKT2 (514970) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEEPFKT2 69 KV 514970 TO DEEPFRK2 69 KV 514974 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DELWARE4__FARML__4 | 3 Phase fault DELWARE4 (510379) 138 kV Bus a. Apply fault at the DELWARE4 (510379) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELWARE4 138 KV 510379 TO FARML 4 138 KV 512734 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | CGENSUB2 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DELWARE7__N.E.S. | 3 Phase fault DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 345 KV 510380 TO N.E.S.-7 345 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DELWARE7__NEOSHO_7 | 3 Phase fault DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 345 KV 510380 TO NEOSHO 7 345 KV 532793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | ELKRVR-WTG2 trips on voltage protection settings | Disabling instantaneous voltage protection settings for ELKRVR-WTG2 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DENVR | 3 Phase fault DENVR-E4 (509743) 138 kV Bus a. Apply fault at the DENVR-E4 (509743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVR-E4 138 KV 509743 TO DENVTAP4 138 KV 509746 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DENVR | 3 Phase fault DENVR-W4 (509748) 138 kV Bus a. Apply fault at the DENVR-W4 (509748) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVR-W4 138 KV 509748 TO DENV_WTAP4 138 KV 509896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DENVTAP4__T.NO. | 3 Phase fault DENVTAP4 (509746) 138 kV Bus a. Apply fault at the DENVTAP4 (509746) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVTAP4 138 KV 509746 TO T.NO.--4 138 KV 509817 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DENVTAP4__W.ED. | 3 Phase fault DENVTAP4 (509746) 138 kV Bus a. Apply fault at the DENVTAP4 (509746) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVTAP4 138 KV 509746 TO W.ED.-E4 138 KV 509822 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DEQUEEN2__LOCKESB2 | 3 Phase fault DEQUEEN2 (507418) 69 kV Bus a. Apply fault at the DEQUEEN2 (507418) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEQUEEN2 69 KV 507418 TO LOCKESB2 69 KV 507422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DEQUEEN4__CRAIGJT4 | 3 Phase fault DEQUEEN4 (507419) 138 kV Bus a. Apply fault at the DEQUEEN4 (507419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEQUEEN4 138 KV 507419 TO CRAIGJT4 138 KV 510890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DEWEY__4__CANTNLK4 | 3 Phase fault DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138 KV 514787 TO CANTNLK4 138 KV 515964 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DEWEY__4__REDCLFT4 | 3 Phase fault DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138 KV 514787 TO REDCLFT4 138 KV 515533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DEWEY__4__TALOGA_4 | 3 Phase fault DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138 KV 514787 TO TALOGA 4 138 KV 521065 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DEWEY__4__TLGAWND4 | 3 Phase fault DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138 KV 514787 TO TLGAWND4 138 KV 515390 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DGRASSE4__MOORLND4 | 3 Phase fault DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138 KV 515853 TO MOORLND4 138 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DGRASSE4__ROSEVLY4 | 3 Phase fault DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138 KV 515853 TO ROSEVLY4 138 KV 520436 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DGRASSE7__THISTLE7 | 3 Phase fault DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 345 KV 515852 TO THISTLE7 345 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2011-008 trips on voltage protection settings | Disabling voltage protection settings for GEN-2011-008 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DIANA__4__DIANASW4 | 3 Phase fault DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 138 KV 508831 TO DIANASW4 138 KV 509639 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DIANA__4__NGPLTAP4 | 3 Phase fault DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 138 KV 508831 TO NGPLTAP4 138 KV 508837 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DILLARD4__WOLFCRK4 | 3 Phase fault DILLARD4 (515142) 138 kV Bus a. Apply fault at the DILLARD4 (515142) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DILLARD4 138 KV 515142 TO WOLFCRK4 138 KV 515143 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DOLHILL7__SW_SHV_7 | 3 Phase fault DOLHILL7 (500250) 345 kV Bus a. Apply fault at the DOLHILL7 (500250) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DOLHILL7 345 KV 500250 TO SW SHV 7 345 KV 507760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DOUGLTP4__CLASSEN4 | 3 Phase fault DOUGLTP4 (514868) 138 kV Bus a. Apply fault at the DOUGLTP4 (514868) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOUGLTP4 138 KV 514868 TO CLASSEN4 138 KV 514922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-029 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-029 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DOUGLTP4__WESTERN4 | 3 Phase fault DOUGLTP4 (514868) 138 kV Bus a. Apply fault at the DOUGLTP4 (514868) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOUGLTP4 138 KV 514868 TO WESTERN4 138 KV 514869 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-029 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-029 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DOVERSW2__HENESEY2 | 3 Phase fault DOVERSW2 (520881) 69 kV Bus a. Apply fault at the DOVERSW2 (520881) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW2 69 KV 520881 TO HENESEY2 69 KV 520940 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DOVERSW2__LACEY__2 | 3 Phase fault DOVERSW2 (520881) 69 kV Bus a. Apply fault at the DOVERSW2 (520881) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW2 69 KV 520881 TO LACEY 2 69 KV 520967 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DOVERSW4__GEN | 3 Phase fault DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138 KV 520882 TO GEN-2016-118 138 KV 587940 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DOVERSW4__GEN | 3 Phase fault DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138 KV 520882 TO GEN-2018-011 138 KV 762493 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DOVERSW4__KGFSJCT4 | 3 Phase fault DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKNGFSH4 138 KV 520603 TO DOVERSW4 138 KV 520882 CKT 1 b.2. KGFSJCT4 138 KV 520405 TO NKNGFSH4 138 KV 520603 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DOVERSW4__OKEENE_4 | 3 Phase fault DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138 KV 520882 TO OKEENE 4 138 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DOVERSW4__TWNLKSW4 | 3 Phase fault DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVER 4 138 KV 520879 TO DOVERSW4 138 KV 520882 CKT 1 b.2. TWNLAKE4 138 KV 520540 TO DOVER 4 138 KV 520879 CKT 1 b.3. LOAD 1 520879 b.4. TWNLAKE4 138 KV 520540 TO TWNLKSW4 138 KV 521073 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DOVERTP2__DOVERSW2 | 3 Phase fault DOVERTP2 (514772) 69 kV Bus a. Apply fault at the DOVERTP2 (514772) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERTP2 69 KV 514772 TO DOVERSW2 69 KV 520881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DOVERTP2__REDWING2 | 3 Phase fault DOVERTP2 (514772) 69 kV Bus a. Apply fault at the DOVERTP2 (514772) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERTP2 69 KV 514772 TO REDWING2 69 KV 515976 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DOVERTP2__TURCRKT2 | 3 Phase fault DOVERTP2 (514772) 69 kV Bus a. Apply fault at the DOVERTP2 (514772) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERTP2 69 KV 514772 TO TURCRKT2 69 KV 515517 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DRAPER_4__BARNES_4 | 3 Phase fault DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138 KV 514933 TO BARNES 4 138 KV 515003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DRAPER_4__GM_____4 | 3 Phase fault DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138 KV 514933 TO GM 4 138 KV 514961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DRAPER_4__MIDWEST4 | 3 Phase fault DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138 KV 514933 TO MIDWEST4 138 KV 514946 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DRAPER_4__SOONRTP4 | 3 Phase fault DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138 KV 514933 TO SOONRTP4 138 KV 514949 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DRAPER_7__NORMHLL7 | 3 Phase fault DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345 KV 514934 TO NORMHLL7 345 KV 516096 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DRAPER_7__SEMINOL7 | 3 Phase fault DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345 KV 514934 TO SEMINOL7 345 KV 515045 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | RKYRDGW-2WG trips on voltage protection settings | Disabling voltage protection settings for RKYRDGW-2WG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DRYGULCH5__GEN | 3 Phase fault DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 161 KV 512629 TO GEN-2017-073 161 KV 589110 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DUGLASV2__DARENCT2 | 3 Phase fault DUGLASV2 (509645) 69 kV Bus a. Apply fault at the DUGLASV2 (509645) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUGLASV2 69 KV 509645 TO BLALOCK2 69 KV 509646 CKT 1 b.2. LOAD 1 509646 b.3. BLALOCK2 69 KV 509646 TO DARENCT2 69 KV 509647 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DUGLASV2__MAUDT__2 | 3 Phase fault DUGLASV2 (509645) 69 kV Bus a. Apply fault at the DUGLASV2 (509645) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUGLASV2 69 KV 509645 TO MAUDT 2 69 KV 509653 CKT NO c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DUGLASV2__ROACH__2 | 3 Phase fault DUGLASV2 (509645) 69 kV Bus a. Apply fault at the DUGLASV2 (509645) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUGLASV2 69 KV 509645 TO NLINDEN2 69 KV 509652 CKT 1 b.2. LOAD 1 509652 b.3. NLINDEN2 69 KV 509652 TO ROACH 2 69 KV 509668 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DUNCAN | 3 Phase fault DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138 KV 511453 TO OMDUNCN4 138 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DVISION4__HAYMAKR4 | 3 Phase fault DVISION4 (514853) 138 kV Bus a. Apply fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 138 KV 514853 TO HAYMAKR4 138 KV 514863 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-029 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-029 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DVISION4__HEFNER_4 | 3 Phase fault DVISION4 (514853) 138 kV Bus a. Apply fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKESID4 138 KV 514849 TO DVISION4 138 KV 514853 CKT 1 b.2. LOAD 1 514853 b.3. HEFNER 4 138 KV 514848 TO LAKESID4 138 KV 514849 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-029 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-029 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DVISION4__MUSTANG4 | 3 Phase fault DVISION4 (514853) 138 kV Bus a. Apply fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 138 KV 514853 TO MUSTANG4 138 KV 514861 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-029 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-029 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DVISION4__NORTWST4 | 3 Phase fault DVISION4 (514853) 138 kV Bus a. Apply fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 138 KV 514853 TO RICHRDS4 138 KV 514862 CKT 1 b.2. LOAD 1 514862 b.3. RICHRDS4 138 KV 514862 TO PIEDMNT4 138 KV 514864 CKT 1 b.4. LOAD 1 514864 b.5. PIEDMNT4 138 KV 514864 TO NORTWST4 138 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DVISION4__RICHRDS4 | 3 Phase fault DVISION4 (514853) 138 kV Bus a. Apply fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 138 KV 514853 TO RICHRDS4 138 KV 514862 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-029 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-029 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DX | 3 Phase fault DX----W2 (509796) 69 kV Bus a. Apply fault at the DX----W2 (509796) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DX----W2 69 KV 509796 TO S.S.---2 69 KV 509816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_EAGLCHF2__RNGWODJ2 | 3 Phase fault EAGLCHF2 (520890) 69 kV Bus a. Apply fault at the EAGLCHF2 (520890) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLCHF2 69 KV 520890 TO RNGWODJ2 69 KV 521039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_EKNGFSH4__EKFSHTP4 | 3 Phase fault EKNGFSH4 (520484) 138 kV Bus a. Apply fault at the EKNGFSH4 (520484) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EKNGFSH4 138 KV 520484 TO EKFSHTP4 138 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ELRENO_CIMARON | 3 Phase fault EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138 KV 514819 TO CIMARON4 138 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ELRENO_JENSENT | 3 Phase fault EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138 KV 514819 TO JENSENT4 138 KV 514820 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ELRENO_ROMNOSE | 3 Phase fault EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138 KV 514819 TO OMEGA 4 138 KV 515962 CKT 1 b.2. LOAD 1 515962 b.3. ROMNOSE4 138 KV 514823 TO OMEGA 4 138 KV 515962 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ELKCITY6__CHISHOLM6 | 3 Phase fault ELKCITY6 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 230 KV 511490 TO CHISHOLM6 230 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ELKCTY_CLINTJC4 | 3 Phase fault ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 138 KV 511458 TO CLINTJC4 138 KV 511485 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ELKCTY_FALCNRD | 3 Phase fault ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 138 KV 511458 TO FALCNRD4 138 KV 511511 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ELKCTY_REDHLSW | 3 Phase fault ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 138 KV 511458 TO REDHLSW4 138 KV 521116 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_EMPIRE_4__FLETCH | 3 Phase fault EMPIRE 4 (520900) 138 kV Bus a. Apply fault at the EMPIRE 4 (520900) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMPIRE 4 138 KV 520900 TO FLETCH-4 138 KV 520912 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ENID___2__SO4TH__2 | 3 Phase fault ENID 2 (514727) 69 kV Bus a. Apply fault at the ENID 2 (514727) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENID 2 69 KV 514727 TO SO4TH 2 69 KV 514730 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ERLSBOR2__FRSTHIL2 | 3 Phase fault ERLSBOR2 (515073) 69 kV Bus a. Apply fault at the ERLSBOR2 (515073) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ERLSBOR2 69 KV 515073 TO FRSTHIL2 69 KV 515074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_EUFREST2__WELLSPA2 | 3 Phase fault EUFREST2 (515214) 69 kV Bus a. Apply fault at the EUFREST2 (515214) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUFREST2 69 KV 515214 TO WELLSPA2 69 KV 515215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_EXCLART4__EXPCLAR4 | 3 Phase fault EXCLART4 (510401) 138 kV Bus a. Apply fault at the EXCLART4 (510401) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXCLART4 138 KV 510401 TO EXPCLAR4 138 KV 510405 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_EXCLART4__G17 | 3 Phase fault EXCLART4 (510401) 138 kV Bus a. Apply fault at the EXCLART4 (510401) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXCLART4 138 KV 510401 TO G17-077-TAP 138 KV 589154 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_EXPLGLN4__EXPGLNT4 | 3 Phase fault EXPLGLN4 (515248) 138 kV Bus a. Apply fault at the EXPLGLN4 (515248) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXPLGLN4 138 KV 515248 TO EXPGLNT4 138 KV 515473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_EYLAU__4__BUCHANN4 | 3 Phase fault EYLAU 4 (509655) 138 kV Bus a. Apply fault at the EYLAU 4 (509655) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EYLAU 4 138 KV 509655 TO BUCHANN4 138 KV 509656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FAIRVEW2__OKEENE_2 | 3 Phase fault FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69 KV 520909 TO OKEENE 2 69 KV 521015 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FAIRVEW2__OMFAIRV2 | 3 Phase fault FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69 KV 520909 TO OMFAIRV2 69 KV 529343 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FAIRVEW2__RNGWODJ2 | 3 Phase fault FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69 KV 520909 TO RNGWODJ2 69 KV 521039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FIXCT4__FIXICO_4 | 3 Phase fault FIXCT4 (510877) 138 kV Bus a. Apply fault at the FIXCT4 (510877) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIXCT4 138 KV 510877 TO FIXICO 4 138 KV 515078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FIXCT4__WELETK4 | 3 Phase fault FIXCT4 (510877) 138 kV Bus a. Apply fault at the FIXCT4 (510877) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIXCT4 138 KV 510877 TO WELETK4 138 KV 510902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FLETCHR4__FLE_TAP4 | 3 Phase fault FLETCHR4 (511422) 138 kV Bus a. Apply fault at the FLETCHR4 (511422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR4 138 KV 511422 TO FLE TAP4 138 KV 511423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FLE_TAP4__G16 | 3 Phase fault FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138 KV 511423 TO G16-097-TAP 138 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FLE_TAP4__L.E.S. | 3 Phase fault FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138 KV 511423 TO L.E.S.-4 138 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FLOURNY2__PINESRD2 | 3 Phase fault FLOURNY2 (507726) 69 kV Bus a. Apply fault at the FLOURNY2 (507726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 69 KV 507726 TO PINESRD2 69 KV 507747 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FLOURNY2__WASKOM_2 | 3 Phase fault FLOURNY2 (507726) 69 kV Bus a. Apply fault at the FLOURNY2 (507726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 69 KV 507726 TO WASKOM 2 69 KV 508839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FLOURNY2__WOOLWTP2 | 3 Phase fault FLOURNY2 (507726) 69 kV Bus a. Apply fault at the FLOURNY2 (507726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 69 KV 507726 TO WOOLWTP2 69 KV 507770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FOREMAN2__DEQUEEN2 | 3 Phase fault FOREMAN2 (507421) 69 kV Bus a. Apply fault at the FOREMAN2 (507421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORMANR2 69 KV 507407 TO FOREMAN2 69 KV 507421 CKT 1 b.2. LOAD 1 507421 b.3. DEQUEEN 2 69 KV 504120 TO FORMANR2 69 KV 507407 CKT 1 b.4. LOAD A1 507407 b.5. DEQUEEN 2 69 KV 504120 TO DEQUEEN2 69 KV 507418 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FOREMAN2__FOREMAG2 | 3 Phase fault FOREMAN2 (507421) 69 kV Bus a. Apply fault at the FOREMAN2 (507421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOREMAN2 69 KV 507421 TO FOREMAG2 69 KV 507440 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FOREMAN2__PATTERS2 | 3 Phase fault FOREMAN2 (507421) 69 kV Bus a. Apply fault at the FOREMAN2 (507421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOREMAN2 69 KV 507421 TO PATTERS2 69 KV 507429 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FOURCTP4__FOURCNT4 | 3 Phase fault FOURCTP4 (520545) 138 kV Bus a. Apply fault at the FOURCTP4 (520545) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOURCTP4 138 KV 520545 TO FOURCNT4 138 KV 520546 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FOURCTP4__TWNLKJT4 | 3 Phase fault FOURCTP4 (520545) 138 kV Bus a. Apply fault at the FOURCTP4 (520545) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOURCTP4 138 KV 520545 TO TWNLKJT4 138 KV 520847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FRMNTAP4__FAIRMON4 | 3 Phase fault FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138 KV 514709 TO FAIRMON4 138 KV 514712 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FRMNTAP4__SO4TH__4 | 3 Phase fault FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138 KV 514709 TO SO4TH 4 138 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FRMNTAP4__WOODRNG4 | 3 Phase fault FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138 KV 514709 TO WOODRNG4 138 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FRNKLNS4__CANADNS4 | 3 Phase fault FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRNKLNS4 138 KV 520917 TO LIDDELL4 138 KV 520975 CKT 1 b.2. LOAD 1 520975 b.3. NOBLE4 138 KV 520400 TO LIDDELL4 138 KV 520975 CKT 1 b.4. LOAD 1 520975 b.5. NOBLE4 138 KV 520400 TO CANADNS4 138 KV 520842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-045 trips on voltage protection settings | Disabling voltage protection settings for GEN-2016-045 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FRNKLNS4__OU_SW_4 | 3 Phase fault FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ACME 4 138 KV 520802 TO FRNKLNS4 138 KV 520917 CKT 1 b.2. ACME 4 138 KV 520802 TO WNORMAN4 138 KV 521095 CKT 1 b.3. LOAD 1 521095 b.4. LAMAR4 138 KV 520403 TO WNORMAN4 138 KV 521095 CKT 1 b.5. LOAD 1 521095 b.6. LAMAR4 138 KV 520403 TO OU SW 4 138 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-045 trips on voltage protection settings | Disabling voltage protection settings for GEN-2016-045 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FRNKLNS4__PINK_SW4 | 3 Phase fault FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLN4 138 KV 520913 TO FRNKLNS4 138 KV 520917 CKT 1 b.2. FRANKLN4 138 KV 520913 TO PINK SW4 138 KV 521028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-045 trips on voltage protection settings | Disabling voltage protection settings for GEN-2016-045 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FRNKLNS4__SUNSHIN4 | 3 Phase fault FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRNKLNS4 138 KV 520917 TO WMOORE 4 138 KV 521123 CKT 1 b.2. LOAD 1 521123 b.3. BAILEY4 138 KV 520401 TO WMOORE 4 138 KV 521123 CKT 1 b.4. LOAD 1 521123 b.5. BAILEY4 138 KV 520401 TO SUNSHIN4 138 KV 521059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FROGVIL4__HUGO_PP4 | 3 Phase fault FROGVIL4 (520918) 138 kV Bus a. Apply fault at the FROGVIL4 (520918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FROGVIL4 138 KV 520918 TO HUGO PP4 138 KV 520948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FRSTHIL4__STRLGTP4 | 3 Phase fault FRSTHIL4 (515075) 138 kV Bus a. Apply fault at the FRSTHIL4 (515075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRSTHIL4 138 KV 515075 TO STRLGTP4 138 KV 515286 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FTSMTHE5__COLONY_5 | 3 Phase fault FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5 (515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161 KV 515300 TO COLONY 5 161 KV 515345 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FTSMTHE5__FTSMTHW5 | 3 Phase fault FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5 (515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161 KV 515300 TO FTSMTHW5 161 KV 515301 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FTSMTHE5__QUANXTP5 | 3 Phase fault FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5 (515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161 KV 515300 TO QUANXTP5 161 KV 515310 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FTSMTHW5__ARKOMA_5 | 3 Phase fault FTSMTHW5 (515301) 161 kV Bus a. Apply fault at the FTSMTHW5 (515301) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 161 KV 515301 TO ARKOMA 5 161 KV 515306 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FT_GIB_5__OKAYGR_5 | 3 Phase fault FT GIB 5 (505560) 161 kV Bus a. Apply fault at the FT GIB 5 (505560) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FT GIB 5 161 KV 505560 TO OKAYGR 5 161 KV 512640 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FULTONE4__21STTAP4 | 3 Phase fault FULTONE4 (509797) 138 kV Bus a. Apply fault at the FULTONE4 (509797) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FULTONE4 138 KV 509797 TO S21ST--4 138 KV 509808 CKT 1 b.2. LOAD 1 509808 b.3. S21ST--4 138 KV 509808 TO 21STTAP4 138 KV 509828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FULTONW4__KENSH | 3 Phase fault FULTONW4 (509829) 138 kV Bus a. Apply fault at the FULTONW4 (509829) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FULTONW4 138 KV 509829 TO KENSH-E-TP4 138 KV 509830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FULTON____3__HOPE___3 | 3 Phase fault FULTON 3 (503912) 115 kV Bus a. Apply fault at the FULTON 3 (503912) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FULTON 3 115 KV 503912 TO HOPE 3 115 KV 507453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_G07621119 | 3 Phase fault G07621119-20 (515599) 345 kV Bus a. Apply fault at the G07621119-20 (515599) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G07621119-20 345 KV 515599 TO GREAT_WESTRN 345 KV 585410 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MINCO-WTG34 trips on voltage protection setings | Disabling instantaneous voltage protection settings for MINCO-WTG34 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_G07621119 | 3 Phase fault G07621119-20 (515599) 345 kV Bus a. Apply fault at the G07621119-20 (515599) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G07621119-20 345 KV 515599 TO PRSIMN_CRK1 345 KV 585430 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MINCO-WTG34 trips on voltage protection setings | Disabling instantaneous voltage protection settings for MINCO-WTG34 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_G15 | 3 Phase fault G15-066T (560056) 345 kV Bus a. Apply fault at the G15-066T (560056) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G15-066T 345 KV 560056 TO GEN-2015-066 345 KV 585040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_G16 | 3 Phase fault G16-003-TAP (560071) 345 kV Bus a. Apply fault at the G16-003-TAP (560071) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP 345 KV 560071 TO GEN-2017-011 345 KV 588560 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_G16 | 3 Phase fault G16-037-TAP (560078) 345 kV Bus a. Apply fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345 KV 560078 TO GEN-2016-037 345 KV 587230 CKT 1 | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_G16 | 3 Phase fault G16-091-TAP (587744) 345 kV Bus a. Apply fault at the G16-091-TAP (587744) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-091-TAP 345 KV 587744 TO GEN-2016-095 345 KV 587770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_G16133G16146__G16133_345GS | 3 Phase fault G16133G16146 (588039) 345 kV Bus a. Apply fault at the G16133G16146 (588039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16133G16146 345 KV 588039 TO G16133_345GS 345 KV 588040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_G17-009_NESHO | 3 Phase fault G17-009-TAP (532777) 345 kV Bus a. Apply fault at the G17-009-TAP (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP 345 KV 532777 TO NEOSHO 7 345 KV 532793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-009 trips on frequency protection settings | Disabling frequency protection settings for GEN-2017-009 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_G17-092_FIREWHLTAP | 3 Phase fault G17-092-SWYD (588838) 345 kV Bus a. Apply fault at the G17-092-SWYD (588838) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-092-SWYD 345 KV 588838 TO FIREWHL-TAP 345 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-024 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-024 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_G17_151_G18-015 | 3 Phase fault G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345 KV 762216 TO G18-015-TAP 345 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GLASMTN4__MOORLND4 | 3 Phase fault GLASMTN4 (514788) 138 kV Bus a. Apply fault at the GLASMTN4 (514788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLASMTN4 138 KV 514788 TO MOORLND4 138 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GLENWD_4__IMO____4 | 3 Phase fault GLENWD 4 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 138 KV 514734 TO IMO 4 138 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HUGOITC4__HUGO_PP4 | 3 Phase fault HUGOITC4 (520560) 138 kV Bus a. Apply fault at the HUGOITC4 (520560) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOITC4 138 KV 520560 TO HUGO PP4 138 KV 520948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GORE___5__EUFAULA5 | 3 Phase fault GORE 5 (505552) 161 kV Bus a. Apply fault at the GORE 5 (505552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161 KV 505552 TO EUFAULA5 161 KV 505570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GORE___5__MUSKTAP5 | 3 Phase fault GORE 5 (505552) 161 kV Bus a. Apply fault at the GORE 5 (505552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161 KV 505552 TO MUSKTAP5 161 KV 505558 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GORE___5__TENKIL_5 | 3 Phase fault GORE 5 (505552) 161 kV Bus a. Apply fault at the GORE 5 (505552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161 KV 505552 TO TENKIL 5 161 KV 505566 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GORE___5__WEBFALL5 | 3 Phase fault GORE 5 (505552) 161 kV Bus a. Apply fault at the GORE 5 (505552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161 KV 505552 TO WEBFALL5 161 KV 505554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GORE___5__WELEETK5 | 3 Phase fault GORE 5 (505552) 161 kV Bus a. Apply fault at the GORE 5 (505552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161 KV 505552 TO WELEETK5 161 KV 505590 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRACMNT4__ANADARK4 | 3 Phase fault GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138 KV 515802 TO ANADARK4 138 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | RKYRDGW-2WG trips on voltage protection settings | Disabling voltage protection settings for RKYRDGW-2WG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRACMNT4__WASHITA4 | 3 Phase fault GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138 KV 515802 TO WASHITA4 138 KV 521089 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | RKYRDGW-2WG trips on voltage protection settings | Disabling voltage protection settings for RKYRDGW-2WG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRACMNT7__G16 | 3 Phase fault GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345 KV 515800 TO G16-037-TAP 345 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MINCO5 trips on voltage protection settings | Disabling voltage protection settings for MINCO5 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRACMNT7__G16 | 3 Phase fault GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345 KV 515800 TO G16-091-TAP 345 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MINCO5 trips on voltage protection settings | Disabling voltage protection settings for MINCO5 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRACMNT7__GEN | 3 Phase fault GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345 KV 515800 TO GEN-2015-093 345 KV 563269 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRANNIS___2__DEQUEEN2 | 3 Phase fault GRANNIS 2 (504129) 69 kV Bus a. Apply fault at the GRANNIS 2 (504129) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANNIS 2 69 KV 504129 TO DEQUEEN2 69 KV 507418 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRAPEVINE__6__NICHOLS____6 | 3 Phase fault GRAPEVINE 6 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 230 KV 523771 TO NICHOLS 6 230 KV 524044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRAPEVINE__6__WHEELER____6 | 3 Phase fault GRAPEVINE 6 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 230 KV 523771 TO WHEELER 6 230 KV 523777 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA1__5__CHOUTEAUCRK5 | 3 Phase fault GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 161 KV 512656 TO CHOUTEAUCRK5 161 KV 513570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA1__5__MAID___5 | 3 Phase fault GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 161 KV 512656 TO WMAIN ST5 161 KV 512742 CKT 1 b.2. LOAD 1 512742 b.3. WMAIN ST5 161 KV 512742 TO NWMAID5 161 KV 512757 CKT 1 b.4. LOAD 1 512757 b.5. NWMAID5 161 KV 512757 TO GERALDGAY5 161 KV 512760 CKT 1 b.6. LOAD 1 512760 b.7. MAID 5 161 KV 512648 TO GERALDGAY5 161 KV 512760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA1__5__WAGNOR_5 | 3 Phase fault GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 161 KV 512656 TO WAGNOR 5 161 KV 512700 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA1__7__GREC_TAP5 | 3 Phase fault GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 345 KV 512650 TO GREC TAP5 345 KV 512865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA1__7__TONECE7 | 3 Phase fault GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 345 KV 512650 TO TONECE7 345 KV 512750 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDGVTP4__MEEKRSW4 | 3 Phase fault GRDGVTP4 (520526) 138 kV Bus a. Apply fault at the GRDGVTP4 (520526) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDGVTP4 138 KV 520526 TO MEEKRSW4 138 KV 520994 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GREAT_WESTRN__COWBOY_RIDGE | 3 Phase fault GREAT_WESTRN (585410) 345 kV Bus a. Apply fault at the GREAT_WESTRN (585410) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GREAT_WESTRN 345 KV 585410 TO COWBOY_RIDGE 345 KV 585420 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GREC_TAP5__IGLOOV_7 | 3 Phase fault GREC TAP5 (512865) 345 kV Bus a. Apply fault at the GREC TAP5 (512865) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GREC TAP5 345 KV 512865 TO IGLOOV 7 345 KV 513596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRTWSRN7__GUTHRIE7 | 3 Phase fault GRTWSRN7 (515825) 345 kV Bus a. Apply fault at the GRTWSRN7 (515825) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRTWSRN7 345 KV 515825 TO GUTHRIE7 345 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HAMMTAP4__HAMMETT4 | 3 Phase fault HAMMTAP4 (515046) 138 kV Bus a. Apply fault at the HAMMTAP4 (515046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMMTAP4 138 KV 515046 TO HAMMETT4 138 KV 520951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-029 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-029 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HAMMTAP4__LINCOLN4 | 3 Phase fault HAMMTAP4 (515046) 138 kV Bus a. Apply fault at the HAMMTAP4 (515046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMMTAP4 138 KV 515046 TO LINCOLN4 138 KV 515442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-029 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-029 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HARPER2__ANADARK2 | 3 Phase fault HARPER2 (520440) 69 kV Bus a. Apply fault at the HARPER2 (520440) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER2 69 KV 520440 TO ANADARK2 69 KV 520810 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HARRISN4__KNOXLEE4 | 3 Phase fault HARRISN4 (508544) 138 kV Bus a. Apply fault at the HARRISN4 (508544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRISN4 138 KV 508544 TO KNOXLEE4 138 KV 508548 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HARTSIS4__S_SHV__4 | 3 Phase fault HARTSIS4 (507735) 138 kV Bus a. Apply fault at the HARTSIS4 (507735) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARTSIS4 138 KV 507735 TO S SHV 4 138 KV 507755 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HEFNER_4__TENESTP4 | 3 Phase fault HEFNER 4 (514848) 138 kV Bus a. Apply fault at the HEFNER 4 (514848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILSHIR4 138 KV 514836 TO HEFNER 4 138 KV 514848 CKT 1 b.2. WILSHIR4 138 KV 514836 TO TENNESE4 138 KV 514838 CKT 1 b.3. LOAD 1 514838 b.4. TENESTP4 138 KV 514837 TO TENNESE4 138 KV 514838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MNCOWNG3 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HENESEY4__BULFTTP4 | 3 Phase fault HENESEY4 (514774) 138 kV Bus a. Apply fault at the HENESEY4 (514774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 138 KV 514774 TO BULFTTP4 138 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HENESEY4__DOVERSW4 | 3 Phase fault HENESEY4 (514774) 138 kV Bus a. Apply fault at the HENESEY4 (514774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 138 KV 514774 TO DOVERSW4 138 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HERRON_5__IGLOOV1_5 | 3 Phase fault HERRON 5 (513591) 161 kV Bus a. Apply fault at the HERRON 5 (513591) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HERRON 5 161 KV 513591 TO IGLOOV1 5 161 KV 513593 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HERRON_5__IGLOOV2_5 | 3 Phase fault HERRON 5 (513591) 161 kV Bus a. Apply fault at the HERRON 5 (513591) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HERRON 5 161 KV 513591 TO IGLOOV2 5 161 KV 513595 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HIGHLND4__PINK_SW4 | 3 Phase fault HIGHLND4 (520941) 138 kV Bus a. Apply fault at the HIGHLND4 (520941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGHLND4 138 KV 520941 TO PINK SW4 138 KV 521028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HLTOPTP__BEELINE2 | 3 Phase fault HLTOPTP (514200) 69 kV Bus a. Apply fault at the HLTOPTP (514200) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLTOPTP 69 KV 514200 TO BEELINE2 69 KV 515246 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HOB | 3 Phase fault HOB-JCT4 (511463) 138 kV Bus a. Apply fault at the HOB-JCT4 (511463) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT4 138 KV 511463 TO MARTHA 4 138 KV 511564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HOB | 3 Phase fault HOB-JCT4 (511463) 138 kV Bus a. Apply fault at the HOB-JCT4 (511463) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT4 138 KV 511463 TO RKY_RDG4 138 KV 511554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HOBBYLO4__CHEMTRN4 | 3 Phase fault HOBBYLO4 (515338) 138 kV Bus a. Apply fault at the HOBBYLO4 (515338) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBYLO4 138 KV 515338 TO CHEMTRN4 138 KV 515367 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MINCO-WTG34 trips on voltage protection setings | Disabling instantaneous voltage protection settings for MINCO-WTG34 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HOCHJCT4__DOMINJCT4 | 3 Phase fault HOCHJCT4 (520823) 138 kV Bus a. Apply fault at the HOCHJCT4 (520823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOCHJCT4 138 KV 520823 TO DOMINJCT4 138 KV 521195 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HOCHJCT4__HOCHTWN4 | 3 Phase fault HOCHJCT4 (520823) 138 kV Bus a. Apply fault at the HOCHJCT4 (520823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOCHJCT4 138 KV 520823 TO HOCHTWN4 138 KV 520943 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HOLLYWD4__INDNHIL4 | 3 Phase fault HOLLYWD4 (514953) 138 kV Bus a. Apply fault at the HOLLYWD4 (514953) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLLYWD4 138 KV 514953 TO INDNHIL4 138 KV 514954 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MNCOWNG3 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HOOKS__2__LSORDTP2 | 3 Phase fault HOOKS 2 (508057) 69 kV Bus a. Apply fault at the HOOKS 2 (508057) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOKS 2 69 KV 508057 TO LSORDTP2 69 KV 508063 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HOOKS__2__REDRVR | 3 Phase fault HOOKS 2 (508057) 69 kV Bus a. Apply fault at the HOOKS 2 (508057) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOKS 2 69 KV 508057 TO REDRVR-2 69 KV 508074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HOPESWI3__HOPE___3 | 3 Phase fault HOPESWI3 (507452) 115 kV Bus a. Apply fault at the HOPESWI3 (507452) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOPESWI3 115 KV 507452 TO HOPE 3 115 KV 507453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HSLEAST2__DEEPFKT2 | 3 Phase fault HSLEAST2 (514927) 69 kV Bus a. Apply fault at the HSLEAST2 (514927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69 KV 514927 TO GRNPAST2 69 KV 514971 CKT 1 b.2. LOAD 1 514971 b.3. DEEPFKT2 69 KV 514970 TO GRNPAST2 69 KV 514971 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HSLEAST2__HSLWEST2 | 3 Phase fault HSLEAST2 (514927) 69 kV Bus a. Apply fault at the HSLEAST2 (514927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69 KV 514927 TO HSLWEST2 69 KV 514937 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HSLEAST2__MCLOUDT2 | 3 Phase fault HSLEAST2 (514927) 69 kV Bus a. Apply fault at the HSLEAST2 (514927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69 KV 514927 TO MCLOUDT2 69 KV 515504 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HSLEAST2__TXSTELA2 | 3 Phase fault HSLEAST2 (514927) 69 kV Bus a. Apply fault at the HSLEAST2 (514927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69 KV 514927 TO TXSTELA2 69 KV 514985 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HSL____4__GEN | 3 Phase fault HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138 KV 514941 TO GEN-2018-029 138 KV 762647 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG, MINCO5G11 trips on voltage protection settings | Disabling voltage protection settings for BCV WTG, MINCO5G11 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HSL____4__HAMMTAP4 | 3 Phase fault HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138 KV 514941 TO HAMMTAP4 138 KV 515046 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-029 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-029 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HSL____4__JONESSB4 | 3 Phase fault HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138 KV 514941 TO JONESSB4 138 KV 515480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MINCO5G11 trips on voltage protection settings GEN-2018-029 trips on frequency protection settings | Disabling voltage protection settings for MINCO5G11 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800. Disabling frequency protection settings for GEN-2018-029 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HSL____4__RENO___4 | 3 Phase fault HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138 KV 514941 TO MIDWAY 4 138 KV 514966 CKT 1 b.2. LOAD 1 514966 b.3. NE10TH 4 138 KV 514964 TO MIDWAY 4 138 KV 514966 CKT 1 b.4. LOAD 1 514966 b.5. NE10TH 4 138 KV 514964 TO RENO 4 138 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-029 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-029 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HSL____4__SE15TH_4 | 3 Phase fault HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138 KV 514941 TO SE15TH 4 138 KV 514993 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-029 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-029 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HSL____4__SQUIRCK4 | 3 Phase fault HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138 KV 514941 TO DALE 4 138 KV 514987 CKT 1 b.2. LOAD 1 514987 b.3. DALE 4 138 KV 514987 TO SQUIRCK4 138 KV 515059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-029 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-029 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HUGO | 3 Phase fault HUGO---4 (510901) 138 kV Bus a. Apply fault at the HUGO---4 (510901) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGO---4 138 KV 510901 TO VALIANT4 138 KV 510918 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GOLDSBY4__OU_SW_4 | 3 Phase fault GOLDSBY4 (520924) 138 kV Bus a. Apply fault at the GOLDSBY4 (520924) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOLDSBY4 138 KV 520924 TO OU SW 4 138 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HUGO_PP4__GEN | 3 Phase fault HUGO PP4 (520948) 138 kV Bus a. Apply fault at the HUGO PP4 (520948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGO PP4 138 KV 520948 TO GEN-2017-023 138 KV 588670 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HUGO_PP4__VALLANT4 | 3 Phase fault HUGO PP4 (520948) 138 kV Bus a. Apply fault at the HUGO PP4 (520948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGO PP4 138 KV 520948 TO VALLANT4 138 KV 521079 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HUGO___7__G17 | 3 Phase fault HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 345 KV 521157 TO G17-075-TAP 345 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HUNTERS7__CHSHLMV7 | 3 Phase fault HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 345 KV 515476 TO CHSHLMV7 345 KV 515477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HUNTERS7__RENFROW7 | 3 Phase fault HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 345 KV 515476 TO RENFROW7 345 KV 515543 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HWY20 | 3 Phase fault HWY20-T4 (509821) 138 kV Bus a. Apply fault at the HWY20-T4 (509821) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HWY20-T4 138 KV 509821 TO WLDCT_HIL4 138 KV 509897 CKT 1 b.2. LOAD 1 509897 b.3. HWY20--4 138 KV 509798 TO WLDCT_HIL4 138 KV 509897 CKT 1 b.4. LOAD 1 509897 b.5. HWY20--4 138 KV 509798 TO OMHOMNY4 138 KV 529306 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_INOLATP4__CATOOSA4 | 3 Phase fault INOLATP4 (509752) 138 kV Bus a. Apply fault at the INOLATP4 (509752) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INOLATP4 138 KV 509752 TO CATOOSA4 138 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_INOLATP4__EXCLART4 | 3 Phase fault INOLATP4 (509752) 138 kV Bus a. Apply fault at the INOLATP4 (509752) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INOLATP4 138 KV 509752 TO ROCKPT-4 138 KV 510437 CKT 1 b.2. LOAD 1 510437 b.3. CHOUTEA4 138 KV 510373 TO ROCKPT-4 138 KV 510437 CKT 1 b.4. LOAD 1 510437 b.5. CHOUTEA4 138 KV 510373 TO EXCLART4 138 KV 510401 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_INOLA__4__INOLATP4 | 3 Phase fault INOLA 4 (509736) 138 kV Bus a. Apply fault at the INOLA 4 (509736) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INOLA 4 138 KV 509736 TO INOLATP4 138 KV 509752 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_IODINE_4__MOORLND4 | 3 Phase fault IODINE 4 (520957) 138 kV Bus a. Apply fault at the IODINE 4 (520957) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IODINE 4 138 KV 520957 TO MOORLND4 138 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_IPC_TAP2__IPC____2 | 3 Phase fault IPC TAP2 (508058) 69 kV Bus a. Apply fault at the IPC TAP2 (508058) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC TAP2 69 KV 508058 TO IPC 2 69 KV 508092 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_IPC_T__4__CASSTP4 | 3 Phase fault IPC T 4 (508059) 138 kV Bus a. Apply fault at the IPC T 4 (508059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138 KV 508059 TO CASSTP4 138 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_IPC_T__4__IPC____4 | 3 Phase fault IPC T 4 (508059) 138 kV Bus a. Apply fault at the IPC T 4 (508059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138 KV 508059 TO IPC 4 138 KV 508095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_JEFFRSN4__LAKEPIN4 | 3 Phase fault JEFFRSN4 (508835) 138 kV Bus a. Apply fault at the JEFFRSN4 (508835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138 KV 508835 TO LAKEPIN4 138 KV 509624 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_JEFFRSN4__WILKES_4 | 3 Phase fault JEFFRSN4 (508835) 138 kV Bus a. Apply fault at the JEFFRSN4 (508835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138 KV 508835 TO WILKES 4 138 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_JENSENT4__CIMARON4 | 3 Phase fault JENSENT4 (514820) 138 kV Bus a. Apply fault at the JENSENT4 (514820) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSENT4 138 KV 514820 TO CIMARON4 138 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_JENSENT4__JENSEN_4 | 3 Phase fault JENSENT4 (514820) 138 kV Bus a. Apply fault at the JENSENT4 (514820) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSENT4 138 KV 514820 TO JENSEN 4 138 KV 514821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_JENSEN_4__EL_RENO4 | 3 Phase fault JENSEN 4 (514821) 138 kV Bus a. Apply fault at the JENSEN 4 (514821) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSEN 4 138 KV 514821 TO EL RENO4 138 KV 520893 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_JNSKAMO4__ARCADIA4 | 3 Phase fault JNSKAMO4 (514906) 138 kV Bus a. Apply fault at the JNSKAMO4 (514906) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 138 KV 514906 TO ARCADIA4 138 KV 514907 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-029 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-029 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_JNSKAMO4__HSL____4 | 3 Phase fault JNSKAMO4 (514906) 138 kV Bus a. Apply fault at the JNSKAMO4 (514906) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 138 KV 514906 TO HSL 4 138 KV 514941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-029 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-029 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_JOHNCO_4__CANEYCK4 | 3 Phase fault JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138 KV 514808 TO CANEYCK4 138 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_JOHNCO_4__RUSSET | 3 Phase fault JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138 KV 514808 TO RUSSET-4 138 KV 515120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_JOHNCO_4__SXMLCKT4 | 3 Phase fault JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138 KV 514808 TO SXMLCKT4 138 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_JOHNCO_7__DMNDSPG7 | 3 Phase fault JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345 KV 514809 TO DMNDSPG7 345 KV 516006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_JOHNCO_7__GEN | 3 Phase fault JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345 KV 514809 TO GEN-2017-149 345 KV 760830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_JOHNCO_7__SUNNYSD7 | 3 Phase fault JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345 KV 514809 TO SUNNYSD7 345 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_JONESSB4__LGARBER4 | 3 Phase fault JONESSB4 (515480) 138 kV Bus a. Apply fault at the JONESSB4 (515480) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHTWOOD4 138 KV 514842 TO JONESSB4 138 KV 515480 CKT 1 b.2. CHTWOOD4 138 KV 514842 TO LGARBER4 138 KV 515465 CKT 1 b.3. LOAD 1 515465 b.4. ARCADIA4 138 KV 514907 TO LGARBER4 138 KV 515465 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | RKYRDGW-2WG trips on voltage protection settings | Disabling voltage protection settings for RKYRDGW-2WG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_KANSATP5__KANSAS_5 | 3 Phase fault KANSATP5 (512714) 161 kV Bus a. Apply fault at the KANSATP5 (512714) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KANSATP5 161 KV 512714 TO KANSAS 5 161 KV 512716 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-141 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-141 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_KELLYAV4__MEMRIAL4 | 3 Phase fault KELLYAV4 (514501) 138 kV Bus a. Apply fault at the KELLYAV4 (514501) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLYAV4 138 KV 514501 TO MEMRIAL4 138 KV 514835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_KENSH | 3 Phase fault KENSH-E4 (509744) 138 kV Bus a. Apply fault at the KENSH-E4 (509744) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENSH-E4 138 KV 509744 TO ZUNIS-N4 138 KV 509827 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_KENTUKT2__44&SUNL2 | 3 Phase fault KENTUKT2 (514977) 69 kV Bus a. Apply fault at the KENTUKT2 (514977) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENTUKT2 69 KV 514977 TO SAGE 2 69 KV 514978 CKT 1 b.2. LOAD 1 514978 b.3. SAGE 2 69 KV 514978 TO 44&SUNL2 69 KV 514979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-026 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_KERR_GR5__KANSATP5 | 3 Phase fault KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161 KV 512635 TO 412SUB 5 161 KV 512637 CKT 1 b.2. LOAD 1 512637 b.3. 412SUB 5 161 KV 512637 TO KANSATP5 161 KV 512714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_KERR_GR5__KERR_BRK1_5 | 3 Phase fault KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161 KV 512635 TO KERR BRK1 5 161 KV 512770 CKT Z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_KERR_GR5__MAID___5 | 3 Phase fault KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161 KV 512635 TO MAID 5 161 KV 512648 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_KERR_GR5__PENSA__5 | 3 Phase fault KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161 KV 512635 TO PENSA 5 161 KV 512654 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_KERR_GR5__SALNCRK5 | 3 Phase fault KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161 KV 512635 TO SALNCRK5 161 KV 512805 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_KETCHTP4__KETCH__4 | 3 Phase fault KETCHTP4 (514828) 138 kV Bus a. Apply fault at the KETCHTP4 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 138 KV 514828 TO KETCH 4 138 KV 514834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MINCO5G11 trips on voltage protection settings | Disabling voltage protection settings for MINCO5G11 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_KETCHTP4__NORTWST4 | 3 Phase fault KETCHTP4 (514828) 138 kV Bus a. Apply fault at the KETCHTP4 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 138 KV 514828 TO NORTWST4 138 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MINCO5G11 trips on voltage protection settings | Disabling voltage protection settings for MINCO5G11 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_KETCH__4__FAIRFLD4 | 3 Phase fault KETCH 4 (514834) 138 kV Bus a. Apply fault at the KETCH 4 (514834) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCH 4 138 KV 514834 TO FAIRFLD4 138 KV 515468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_KEYSTON4__WEKIWA | 3 Phase fault KEYSTON4 (505610) 138 kV Bus a. Apply fault at the KEYSTON4 (505610) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON4 138 KV 505610 TO WEKIWA-4 138 KV 509757 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_KGFSHSW4__CALUMET4 | 3 Phase fault KGFSHSW4 (520533) 138 kV Bus a. Apply fault at the KGFSHSW4 (520533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSHSW4 138 KV 520533 TO CONCHO 4 138 KV 520865 CKT 1 b.2. LOAD 1 520865 b.3. CALUMET4 138 KV 520839 TO CONCHO 4 138 KV 520865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_KGFSHSW4__CMBLTP_4 | 3 Phase fault KGFSHSW4 (520533) 138 kV Bus a. Apply fault at the KGFSHSW4 (520533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSHSW4 138 KV 520533 TO REEDING4 138 KV 521037 CKT 1 b.2. LOAD 1 521037 b.3. CMBLTP 4 138 KV 520474 TO REEDING4 138 KV 521037 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_KGFSHSW4__EKFSHTP4 | 3 Phase fault KGFSHSW4 (520533) 138 kV Bus a. Apply fault at the KGFSHSW4 (520533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSHSW4 138 KV 520533 TO EKFSHTP4 138 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_KGFSJCT4__EKFSHTP4 | 3 Phase fault KGFSJCT4 (520405) 138 kV Bus a. Apply fault at the KGFSJCT4 (520405) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSJCT4 138 KV 520405 TO EKFSHTP4 138 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_KINZEGR4__KINZE__4 | 3 Phase fault KINZEGR4 (512710) 138 kV Bus a. Apply fault at the KINZEGR4 (512710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZEGR4 138 KV 512710 TO KINZE 4 138 KV 515008 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_KINZE__4__UNVRSTY4 | 3 Phase fault KINZE 4 (515008) 138 kV Bus a. Apply fault at the KINZE 4 (515008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZE 4 138 KV 515008 TO UNVRSTY4 138 KV 515181 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_KIPUMPT2__FTOWSON2 | 3 Phase fault KIPUMPT2 (510876) 69 kV Bus a. Apply fault at the KIPUMPT2 (510876) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KIPUMPT2 69 KV 510876 TO FTOWSON2 69 KV 510917 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_KIPUMPT2__VALIANT2 | 3 Phase fault KIPUMPT2 (510876) 69 kV Bus a. Apply fault at the KIPUMPT2 (510876) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KIPUMPT2 69 KV 510876 TO VALIANT2 69 KV 510910 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_KI_PMPN2__KIPUMPT2 | 3 Phase fault KI PMPN2 (510875) 69 kV Bus a. Apply fault at the KI PMPN2 (510875) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KI PMPN2 69 KV 510875 TO KIPUMPT2 69 KV 510876 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_KNGFSHR7__FSHRTAP7 | 3 Phase fault KNGFSHR7 (515600) 345 kV Bus a. Apply fault at the KNGFSHR7 (515600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KNGFSHR7 345 KV 515600 TO FSHRTAP7 345 KV 515610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_KNOBHIL4__DGRASSE4 | 3 Phase fault KNOBHIL4 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 138 KV 514795 TO DGRASSE4 138 KV 515853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_KNOXLEE4__BRANDYBR | 3 Phase fault KNOXLEE4 (508548) 138 kV Bus a. Apply fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138 KV 508548 TO BRANDYBR 138 KV 508596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_KNOXLEE4__CHEROKE4 | 3 Phase fault KNOXLEE4 (508548) 138 kV Bus a. Apply fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138 KV 508548 TO CHEROKE4 138 KV 509059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_KNOXLEE4__MONROER4 | 3 Phase fault KNOXLEE4 (508548) 138 kV Bus a. Apply fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138 KV 508548 TO MONROER4 138 KV 509073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_KNOXLEE4__OAK2HIL4 | 3 Phase fault KNOXLEE4 (508548) 138 kV Bus a. Apply fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138 KV 508548 TO OAK2HIL4 138 KV 509078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_KNOXLEE4__SOTXEST4 | 3 Phase fault KNOXLEE4 (508548) 138 kV Bus a. Apply fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138 KV 508548 TO SOTXEST4 138 KV 508570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_L.E.S._LGOREN2 | 3 Phase fault L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69 KV 511466 TO LGORE-N2 69 KV 511469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_L.E.S._LGORES2 | 3 Phase fault L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69 KV 511466 TO LGORE-S2 69 KV 511470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_L.E.S._ARTVLTP4 | 3 Phase fault L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138 KV 511467 TO SHERID4 138 KV 511474 CKT 1 b.2. LOAD 1 511474 b.3. SHERID4 138 KV 511474 TO ARTVLTP4 138 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_L.E.S._COMMTAP4 | 3 Phase fault L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138 KV 511467 TO COMMTAP4 138 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_L.E.S._ELGINJT4 | 3 Phase fault L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138 KV 511467 TO ELGINJT4 138 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_L.E.S._SHERID4 | 3 Phase fault L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138 KV 511467 TO SHERID4 138 KV 511474 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_L.E.S._G16-091-TAP | 3 Phase fault L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345 KV 511468 TO G16-091-TAP 345 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_L.E.S._G17-171-TAP | 3 Phase fault L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345 KV 511468 TO G17-171-TAP 345 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LEASIDE_4__LOGANSP4 | 3 Phase fault LEASIDE 4 (507793) 138 kV Bus a. Apply fault at the LEASIDE 4 (507793) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEASIDE 4 138 KV 507793 TO STONWAL4 138 KV 509052 CKT 1 b.2. LOAD 1 509052 b.3. KEATCHI4 138 KV 509050 TO STONWAL4 138 KV 509052 CKT 1 b.4. LOAD 1 509052 b.5. KEATCHI4 138 KV 509050 TO GEORPAC4 138 KV 509064 CKT 1 b.6. GEORPAC4 138 KV 509064 TO LOGANSP4 138 KV 509071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LEONARD4__MLCLMRD4 | 3 Phase fault LEONARD4 (511575) 138 kV Bus a. Apply fault at the LEONARD4 (511575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEONARD4 138 KV 511575 TO MLCLMRD4 138 KV 515933 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LGYEAR_112GORE | 3 Phase fault LG-YEAR4 (511428) 138 kV Bus a. Apply fault at the LG-YEAR4 (511428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-YEAR4 138 KV 511428 TO 112GORE4 138 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LIEBERM2__OILCITY2 | 3 Phase fault LIEBERM2 (508805) 69 kV Bus a. Apply fault at the LIEBERM2 (508805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM2 69 KV 508805 TO OILCITY2 69 KV 508812 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LIEBERM4__G16 | 3 Phase fault LIEBERM4 (508806) 138 kV Bus a. Apply fault at the LIEBERM4 (508806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138 KV 508806 TO G16-167-TAP 138 KV 588404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LIEBERM4__JEFFRSN4 | 3 Phase fault LIEBERM4 (508806) 138 kV Bus a. Apply fault at the LIEBERM4 (508806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138 KV 508806 TO IPCJEFF4 138 KV 508833 CKT 1 b.2. LOAD 1 508833 b.3. IPCJEFF4 138 KV 508833 TO JEFFRSN4 138 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LIEBERM4__LONGWD_4 | 3 Phase fault LIEBERM4 (508806) 138 kV Bus a. Apply fault at the LIEBERM4 (508806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138 KV 508806 TO LONGWD 4 138 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LINCOLN4__MEEKRSW4 | 3 Phase fault LINCOLN4 (515442) 138 kV Bus a. Apply fault at the LINCOLN4 (515442) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINCOLN4 138 KV 515442 TO MEEKER 4 138 KV 520464 CKT 1 b.2. LOAD 1 520464 b.3. MEEKER 4 138 KV 520464 TO MEEKRSW4 138 KV 520994 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LINCOLN4__WOLVRNT4 | 3 Phase fault LINCOLN4 (515442) 138 kV Bus a. Apply fault at the LINCOLN4 (515442) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JACKTWN4 138 KV 515051 TO LINCOLN4 138 KV 515442 CKT 1 b.2. JACKTWN4 138 KV 515051 TO WOLVRNT4 138 KV 515532 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LINTNRD4__NBENTON4 | 3 Phase fault LINTNRD4 (508807) 138 kV Bus a. Apply fault at the LINTNRD4 (508807) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINTNRD4 138 KV 508807 TO NBENTON4 138 KV 508811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LINWOOD4__POWELL_4 | 3 Phase fault LINWOOD4 (507738) 138 kV Bus a. Apply fault at the LINWOOD4 (507738) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINWOOD4 138 KV 507738 TO POWELL 4 138 KV 507748 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LITTLAX2__LITLAXT2 | 3 Phase fault LITTLAX2 (514951) 69 kV Bus a. Apply fault at the LITTLAX2 (514951) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTLAX2 69 KV 514951 TO LITLAXT2 69 KV 515502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LLANE_LLANET | 3 Phase fault LLANE-E4 (509728) 138 kV Bus a. Apply fault at the LLANE-E4 (509728) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LLANE-E4 138 KV 509728 TO LLAN ET4 138 KV 509771 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LLANE_LLANWT | 3 Phase fault LLANE-W4 (509720) 138 kV Bus a. Apply fault at the LLANE-W4 (509720) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LLANE-W4 138 KV 509720 TO LLAN WT4 138 KV 509770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LLAN_ET4__CATOOSA4 | 3 Phase fault LLAN ET4 (509771) 138 kV Bus a. Apply fault at the LLAN ET4 (509771) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LLAN ET4 138 KV 509771 TO CATOOSA4 138 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LLAN_WT4__DAWSONT4 | 3 Phase fault LLAN WT4 (509770) 138 kV Bus a. Apply fault at the LLAN WT4 (509770) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LLAN WT4 138 KV 509770 TO DAWSONT4 138 KV 509803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LLAN_WT4__LLANETP4 | 3 Phase fault LLAN WT4 (509770) 138 kV Bus a. Apply fault at the LLAN WT4 (509770) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LLAN WT4 138 KV 509770 TO LLANETP4 138 KV 509804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LNEOAK_4__NORTWST4 | 3 Phase fault LNEOAK 4 (514873) 138 kV Bus a. Apply fault at the LNEOAK 4 (514873) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNEOAK 4 138 KV 514873 TO NORTWST4 138 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LOCKESB2__NASHVIL2 | 3 Phase fault LOCKESB2 (507422) 69 kV Bus a. Apply fault at the LOCKESB2 (507422) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOCKESB2 69 KV 507422 TO NASHVIL2 69 KV 507426 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LONEGRV4__CHEEKTP4 | 3 Phase fault LONEGRV4 (515144) 138 kV Bus a. Apply fault at the LONEGRV4 (515144) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONEGRV4 138 KV 515144 TO CHEEKTP4 138 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LONGVHT4__WHITNEY4 | 3 Phase fault LONGVHT4 (508554) 138 kV Bus a. Apply fault at the LONGVHT4 (508554) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGVHT4 138 KV 508554 TO WHITNEY4 138 KV 508575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LONGWD_4__FLOURNY4 | 3 Phase fault LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 138 KV 508808 TO OAKPH 4 138 KV 508816 CKT 1 b.2. LOAD 1 508816 b.3. FLOURNY4 138 KV 507727 TO OAKPH 4 138 KV 508816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LONGWD_4__RAINES_4 | 3 Phase fault LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORAM 4 138 KV 507774 TO LONGWD 4 138 KV 508808 CKT 1 b.2. RAINES 4 138 KV 507749 TO NORAM 4 138 KV 507774 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LONGWD_4__SABMINT4 | 3 Phase fault LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SABMINT4 138 KV 508566 TO SEMRSHL4 138 KV 508569 CKT 1 b.2. LOAD 1 508569 b.3. SCOTTSV4 138 KV 508567 TO SEMRSHL4 138 KV 508569 CKT 1 b.4. LOAD 1 508569 b.5. SCOTTSV4 138 KV 508567 TO LONGWD 4 138 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LONGWD_7__GEN | 3 Phase fault LONGWD 7 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345 KV 508809 TO GEN-2018-050 345 KV 762845 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LONGWD_7__WILKES_7 | 3 Phase fault LONGWD 7 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345 KV 508809 TO WILKES 7 345 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LSORDTP2__LSORD__2 | 3 Phase fault LSORDTP2 (508063) 69 kV Bus a. Apply fault at the LSORDTP2 (508063) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSORDTP2 69 KV 508063 TO LSORD 2 69 KV 508093 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LSSOUTH4__DIANA__4 | 3 Phase fault LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138 KV 508297 TO DIANA 4 138 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LSSOUTH4__PITTSB_4 | 3 Phase fault LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138 KV 508297 TO PITTSB_4 138 KV 508313 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LSSOUTH4__WILKES_4 | 3 Phase fault LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138 KV 508297 TO WILKES 4 138 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LTLRLKT2__TXPLSTP2 | 3 Phase fault LTLRLKT2 (514983) 69 kV Bus a. Apply fault at the LTLRLKT2 (514983) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LTLRLKT2 69 KV 514983 TO TXPLSTP2 69 KV 515516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LWS_112GORE | 3 Phase fault LWS-NTP4 (511471) 138 kV Bus a. Apply fault at the LWS-NTP4 (511471) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS-NTP4 138 KV 511471 TO 112GORE4 138 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LWSTAP_4__L.E.S. | 3 Phase fault LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138 KV 511439 TO L.E.S.-4 138 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LWSTAP_4__RPPAPER4 | 3 Phase fault LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138 KV 511439 TO RPPAPER4 138 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LWS___S4__LWSTAP_4 | 3 Phase fault LWS S4 (511431) 138 kV Bus a. Apply fault at the LWS S4 (511431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS S4 138 KV 511431 TO LWSTAP 4 138 KV 511439 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LYDIA__7__VALIANT7 | 3 Phase fault LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345 KV 508298 TO VALIANT7 345 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LYDIA__7__WELSH__7 | 3 Phase fault LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345 KV 508298 TO WELSH 7 345 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MACOCTP2__LITLAXT2 | 3 Phase fault MACOCTP2 (514956) 69 kV Bus a. Apply fault at the MACOCTP2 (514956) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MACOCTP2 69 KV 514956 TO LITLAXT2 69 KV 515502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MAIDTP2__GRDA1_2 | 3 Phase fault MAIDTP2 (512625) 69 kV Bus a. Apply fault at the MAIDTP2 (512625) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIDTP2 69 KV 512625 TO GRDA1 2 69 KV 512727 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MAID___2__AMERCAST_S2 | 3 Phase fault MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 69 KV 512626 TO AMERCAST S2 69 KV 512681 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MAID___2__REDDEN_2 | 3 Phase fault MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 69 KV 512626 TO REDDEN 2 69 KV 512698 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MAID___5__5CDRCRST | 3 Phase fault MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 161 KV 512648 TO LOCSTGVKM 5 161 KV 513050 CKT 1 b.2. LOAD 1 513050 b.3. 5CDRCRST 161 KV 301344 TO LOCSTGVKM 5 161 KV 513050 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MAID___5__GERALDGAY5 | 3 Phase fault MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 161 KV 512648 TO GERALDGAY5 161 KV 512760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MAID___5__GRDA1__5 | 3 Phase fault MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 161 KV 512648 TO GRDA1 5 161 KV 512656 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MAID___5__PENSA__5 | 3 Phase fault MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 161 KV 512629 TO MAID 5 161 KV 512648 CKT 1 b.2. DRYGULCH5 161 KV 512629 TO PENSA 5 161 KV 512654 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MARSHL_JEFFRSN | 3 Phase fault MARSHL-4 (508557) 138 kV Bus a. Apply fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138 KV 508557 TO JEFFRSN4 138 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MARSHL_PIRKEY | 3 Phase fault MARSHL-4 (508557) 138 kV Bus a. Apply fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138 KV 508557 TO PIRKEY 4 138 KV 508562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MARSHL_4__CTNWOOD4 | 3 Phase fault MARSHL 4 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138 KV 514733 TO CTNWOOD4 138 KV 514827 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MARSHL_4__MARSHAL4 | 3 Phase fault MARSHL 4 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138 KV 514733 TO MARSHAL4 138 KV 521006 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MATHWSN7__REDNGTN7 | 3 Phase fault MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345 KV 515497 TO REDNGTN7 345 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MATHWSN7__TRAVERSE3 | 3 Phase fault MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345 KV 515497 TO TRAVERSE3 345 KV 900001 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MAUDT__2__REDWATR2 | 3 Phase fault MAUDT 2 (509653) 69 kV Bus a. Apply fault at the MAUDT 2 (509653) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUDT 2 69 KV 509653 TO REDWATR2 69 KV 509667 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MAUD___2__ERLSBOR2 | 3 Phase fault MAUD 2 (515054) 69 kV Bus a. Apply fault at the MAUD 2 (515054) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 2 69 KV 515054 TO ERLSBOR2 69 KV 515073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MAUD___2__KNAWATP2 | 3 Phase fault MAUD 2 (515054) 69 kV Bus a. Apply fault at the MAUD 2 (515054) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 2 69 KV 515054 TO KNAWATP2 69 KV 515496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MAUD___2__LTRIVRT2 | 3 Phase fault MAUD 2 (515054) 69 kV Bus a. Apply fault at the MAUD 2 (515054) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 2 69 KV 515054 TO LTRIVRT2 69 KV 515503 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MAUD___4__FIXCT4 | 3 Phase fault MAUD 4 (515055) 138 kV Bus a. Apply fault at the MAUD 4 (515055) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EARLSBORO 4 138 KV 510948 TO MAUD 4 138 KV 515055 CKT 1 b.2. FIXCT4 138 KV 510877 TO EARLSBORO 4 138 KV 510948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MAUD___4__FRSTHIL4 | 3 Phase fault MAUD 4 (515055) 138 kV Bus a. Apply fault at the MAUD 4 (515055) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 4 138 KV 515055 TO FRSTHIL4 138 KV 515075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MAYO_LLANET | 3 Phase fault MAYO--N4 (509779) 138 kV Bus a. Apply fault at the MAYO--N4 (509779) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYO--N4 138 KV 509779 TO E41ST_W4 138 KV 509886 CKT 1 b.2. LOAD 1 509886 b.3. LLAN ET4 138 KV 509771 TO E41ST_W4 138 KV 509886 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MAYO_BANNTP4 | 3 Phase fault MAYO--S4 (509780) 138 kV Bus a. Apply fault at the MAYO--S4 (509780) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYO--S4 138 KV 509780 TO BANNTAP4 138 KV 509785 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MCALEST4__TALAWANDA__4 | 3 Phase fault MCALEST4 (510908) 138 kV Bus a. Apply fault at the MCALEST4 (510908) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCALEST4 138 KV 510908 TO TALAWANDA 4 138 KV 510951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MCALESTIND_4__TALAWANDA__4 | 3 Phase fault MCALESTIND 4 (510909) 138 kV Bus a. Apply fault at the MCALESTIND 4 (510909) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCALESTIND 4 138 KV 510909 TO TALAWANDA 4 138 KV 510951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MCCLAIN4__NORMHLL4 | 3 Phase fault MCCLAIN4 (514902) 138 kV Bus a. Apply fault at the MCCLAIN4 (514902) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCLAIN4 138 KV 514902 TO NORMHLL4 138 KV 516097 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MNCOWNG3 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MCLOUDT2__SINCPNT2 | 3 Phase fault MCLOUDT2 (515504) 69 kV Bus a. Apply fault at the MCLOUDT2 (515504) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCLOUDT2 69 KV 515504 TO SINCPNT2 69 KV 515642 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MCLOUD_2__MCLOUDT2 | 3 Phase fault MCLOUD 2 (515065) 69 kV Bus a. Apply fault at the MCLOUD 2 (515065) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCLOUD 2 69 KV 515065 TO MCLOUDT2 69 KV 515504 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MEEKRSW4__WREDHIL4 | 3 Phase fault MEEKRSW4 (520994) 138 kV Bus a. Apply fault at the MEEKRSW4 (520994) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEEKRSW4 138 KV 520994 TO WREDHIL4 138 KV 521097 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MEMRIAL4__DANFRTH4 | 3 Phase fault MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTERN4 138 KV 514832 TO MEMRIAL4 138 KV 514835 CKT 1 b.2. LOAD 1 514835 b.3. EASTERN4 138 KV 514832 TO HAFERSB4 138 KV 515469 CKT 1 b.4. LOAD 1 515469 b.5. DANFRTH4 138 KV 514833 TO HAFERSB4 138 KV 515469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MEMRIAL4__JONESSB4 | 3 Phase fault MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138 KV 514835 TO BRYANT 4 138 KV 514839 CKT 1 b.2. LOAD 1 514839 b.3. BRYANT 4 138 KV 514839 TO ACORN 4 138 KV 515459 CKT 1 b.4. LOAD 1 515459 b.5. ACORN 4 138 KV 515459 TO JONESSB4 138 KV 515480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MEMRIAL4__REMPKTP4 | 3 Phase fault MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLYAV4 138 KV 514501 TO MEMRIAL4 138 KV 514835 CKT 1 b.2. LOAD 1 514835 b.3. KELLYAV4 138 KV 514501 TO REMPKTP4 138 KV 514872 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MEMRIAL4__SKYLINE4 | 3 Phase fault MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138 KV 514835 TO SKYLINE4 138 KV 514850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MEMRIAL4__TENESTP4 | 3 Phase fault MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138 KV 514835 TO TENESTP4 138 KV 514837 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MENOTAP4__IMO____4 | 3 Phase fault MENOTAP4 (514789) 138 kV Bus a. Apply fault at the MENOTAP4 (514789) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENOTAP4 138 KV 514789 TO IMO 4 138 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MIDWEST4__FRNKLNS4 | 3 Phase fault MIDWEST4 (514946) 138 kV Bus a. Apply fault at the MIDWEST4 (514946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWEST4 138 KV 514946 TO FRNKLNS4 138 KV 520917 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MIDWEST4__HOLLYWD4 | 3 Phase fault MIDWEST4 (514946) 138 kV Bus a. Apply fault at the MIDWEST4 (514946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWEST4 138 KV 514946 TO HOLLYWD4 138 KV 514953 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MINCO__7__CIMARON7 | 3 Phase fault MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345 KV 514801 TO CIMARON7 345 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MINCO__7__GEN-2017-233 | 3 Phase fault MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345 KV 514801 TO GEN-2017-233 345 KV 761250 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MINCO__7__GRACMNT7 | 3 Phase fault MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345 KV 514801 TO GRACMNT7 345 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MINCO__7__MCNOWND7 | 3 Phase fault MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345 KV 514801 TO MCNOWND7 345 KV 515444 CKT 1 | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MINCO__7__MNCWND37 | 3 Phase fault MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345 KV 514801 TO MNCWND37 345 KV 515549 CKT 1 | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MINCO__7__NORMHLL7 | 3 Phase fault MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345 KV 514801 TO NORMHLL7 345 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MINGO_21STTAP | 3 Phase fault MINGO-N4 (509760) 138 kV Bus a. Apply fault at the MINGO-N4 (509760) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGO-N4 138 KV 509760 TO 21STTAP4 138 KV 509828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MINGO_MAYON4 | 3 Phase fault MINGO-N4 (509760) 138 kV Bus a. Apply fault at the MINGO-N4 (509760) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGO-N4 138 KV 509760 TO MAYO--N4 138 KV 509779 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MINGO_MAYOS4 | 3 Phase fault MINGO-S4 (509761) 138 kV Bus a. Apply fault at the MINGO-S4 (509761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGO-S4 138 KV 509761 TO MAYO--S4 138 KV 509780 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MINGO_TSE4 | 3 Phase fault MINGO-S4 (509761) 138 kV Bus a. Apply fault at the MINGO-S4 (509761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGO-S4 138 KV 509761 TO T.S.E.-4 138 KV 509811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MINGORD4__CATOOSA4 | 3 Phase fault MINGORD4 (509802) 138 kV Bus a. Apply fault at the MINGORD4 (509802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSN-N4 138 KV 509787 TO MINGORD4 138 KV 509802 CKT 1 b.2. LOAD 1 509802 b.3. DAWSN-N4 138 KV 509787 TO 141PINE4 138 KV 509892 CKT 1 b.4. LOAD 1 509892 b.5. SPNKY CK4 138 KV 509722 TO 141PINE4 138 KV 509892 CKT 1 b.6. LOAD 1 509892 b.7. SPNKY CK4 138 KV 509722 TO CATOOSA4 138 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-028 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-028 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MOORE__2__FRNKLNS2 | 3 Phase fault MOORE 2 (520489) 69 kV Bus a. Apply fault at the MOORE 2 (520489) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE 2 69 KV 520489 TO FRNKLNS2 69 KV 520916 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MOORLND4__GEN-2016-020 | 3 Phase fault MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND4 138 KV 520999 TO GEN-2016-020 138 KV 587140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MOUNDRD4__ELIZACK4 | 3 Phase fault MOUNDRD4 (510395) 138 kV Bus a. Apply fault at the MOUNDRD4 (510395) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUNDRD4 138 KV 510395 TO ELIZACK4 138 KV 510435 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MRIETA_2__ROCKYPT4 | 3 Phase fault MRIETA 2 (515160) 138 kV Bus a. Apply fault at the MRIETA 2 (515160) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 2 138 KV 515160 TO ROCKYPT4 138 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MSKPORT5__MSKPTAP5 | 3 Phase fault MSKPORT5 (515184) 161 kV Bus a. Apply fault at the MSKPORT5 (515184) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSKPORT5 161 KV 515184 TO MSKPTAP5 161 KV 515232 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-141 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-141 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MSKPTAP5__EUCLID_5 | 3 Phase fault MSKPTAP5 (515232) 161 kV Bus a. Apply fault at the MSKPTAP5 (515232) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSKPTAP5 161 KV 515232 TO EUCLID 5 161 KV 515251 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MUNZCTY4__DUGLASV4 | 3 Phase fault MUNZCTY4 (508064) 138 kV Bus a. Apply fault at the MUNZCTY4 (508064) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138 KV 508064 TO DUGLASV4 138 KV 509666 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MUNZCTY4__WILKES_4 | 3 Phase fault MUNZCTY4 (508064) 138 kV Bus a. Apply fault at the MUNZCTY4 (508064) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138 KV 508064 TO WILKES 4 138 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MUSKOGE5__MSKPTAP5 | 3 Phase fault MUSKOGE5 (515222) 161 kV Bus a. Apply fault at the MUSKOGE5 (515222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKOGE5 161 KV 515222 TO MSKPTAP5 161 KV 515232 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MUSKOGE5__TAHLQH_5 | 3 Phase fault MUSKOGE5 (515222) 161 kV Bus a. Apply fault at the MUSKOGE5 (515222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKOGE5 161 KV 515222 TO KETOWAH5 161 KV 516027 CKT 1 b.2. LOAD 1 516027 b.3. 7CLANS 5 161 KV 515956 TO KETOWAH5 161 KV 516027 CKT 1 b.4. LOAD 1 516027 b.5. TAHLQH 5 161 KV 512655 TO 7CLANS 5 161 KV 515956 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MUSKOGE7__FIREWHL | 3 Phase fault MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345 KV 515224 TO FIREWHL-TAP 345 KV 588839 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MUSKOGE7__FTSMITH7 | 3 Phase fault MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345 KV 515224 TO FTSMITH7 345 KV 515302 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MUSKOGE7__PECANCK7 | 3 Phase fault MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345 KV 515224 TO PECANCK7 345 KV 515235 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MUSKTAP5__FT_GIB_5 | 3 Phase fault MUSKTAP5 (505558) 161 kV Bus a. Apply fault at the MUSKTAP5 (505558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKTAP5 161 KV 505558 TO FT GIB 5 161 KV 505560 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MUSKTAP5__MUSKOGE5 | 3 Phase fault MUSKTAP5 (505558) 161 kV Bus a. Apply fault at the MUSKTAP5 (505558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKTAP5 161 KV 505558 TO MUSKOGE5 161 KV 515222 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MUSTANG4__DAYTON_4 | 3 Phase fault MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138 KV 514861 TO DAYTON 4 138 KV 514892 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MUSTANG4__DOUGLTP4 | 3 Phase fault MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138 KV 514861 TO COUNCIL4 138 KV 514865 CKT 1 b.2. LOAD 1 514865 b.3. COUNCIL4 138 KV 514865 TO WESTOAK4 138 KV 514866 CKT 1 b.4. LOAD 1 514866 b.5. WESTOAK4 138 KV 514866 TO MERIDAN4 138 KV 514867 CKT 1 b.6. LOAD 1 514867 b.7. MERIDAN4 138 KV 514867 TO DOUGLTP4 138 KV 514868 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings GEN-2018-029 trips on frequency protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800. Disabling frequency protection settings for GEN-2018-029 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MUSTANG4__GEN-2018-026 | 3 Phase fault MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138 KV 514861 TO GEN-2018-026 138 KV 762614 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MUSTANG4__MORGAN_4 | 3 Phase fault MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138 KV 514861 TO MORGAN 4 138 KV 514896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MUSTANG4__SW_5TH_4 | 3 Phase fault MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138 KV 514861 TO SW 5TH 4 138 KV 514920 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_N.E.S._ALWUETP4 | 3 Phase fault N.E.S.-4 (510396) 138 kV Bus a. Apply fault at the N.E.S.-4 (510396) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.E.S.-4 138 KV 510396 TO HAWTHRN4 138 KV 510413 CKT 1 b.2. LOAD 1 510413 b.3. CHELSA4 138 KV 510410 TO HAWTHRN4 138 KV 510413 CKT 1 b.4. LOAD 1 510413 b.5. CHELSA4 138 KV 510410 TO ALWUETP4 138 KV 510429 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-028 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-028 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_N.E.S._BVSE4 | 3 Phase fault N.E.S.-4 (510396) 138 kV Bus a. Apply fault at the N.E.S.-4 (510396) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATOVA 4 138 KV 510384 TO N.E.S.-4 138 KV 510396 CKT 1 b.2. LOAD 1 510396 b.3. WATOVA 4 138 KV 510384 TO NOWATA-4 138 KV 510397 CKT 1 b.4. LOAD 1 510397 b.5. BV-SE--4 138 KV 510391 TO NOWATA-4 138 KV 510397 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-028 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-028 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_N.E.S._CLARMR | 3 Phase fault N.E.S.-4 (510396) 138 kV Bus a. Apply fault at the N.E.S.-4 (510396) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.E.S.-4 138 KV 510396 TO OOLOGAHKM 4 138 KV 513124 CKT 1 b.2. LOAD 1 513124 b.3. CLARMR 4 138 KV 512707 TO OOLOGAHKM 4 138 KV 513124 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-028 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-028 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_N.E.S._PCATSAT | 3 Phase fault N.E.S.-4 (510396) 138 kV Bus a. Apply fault at the N.E.S.-4 (510396) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCATSAT4 138 KV 509841 TO OWASO2_4 138 KV 509843 CKT 1 b.2. LOAD 1 509843 b.3. OWASO2_4 138 KV 509843 TO N.E.S.-4 138 KV 510396 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-028 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-028 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_N.E.S._TERNITP4 | 3 Phase fault N.E.S.-4 (510396) 138 kV Bus a. Apply fault at the N.E.S.-4 (510396) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARTOK4 138 KV 509864 TO N.E.S.-4 138 KV 510396 CKT 1 b.2. LOAD 1 510396 b.3. VERDIGS4 138 KV 509854 TO CLARTOK4 138 KV 509864 CKT 1 b.4. LOAD 1 509864 b.5. TERNITP4 138 KV 509835 TO VERDIGS4 138 KV 509854 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-028 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-028 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NASH___4__ALUMAX_4 | 3 Phase fault NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138 KV 508049 TO ALUMAX 4 138 KV 508091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NASH___4__BANN___4 | 3 Phase fault NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138 KV 508049 TO BANN 4 138 KV 508054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NASH___4__NWTXARK4 | 3 Phase fault NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138 KV 508049 TO NWTXARK4 138 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NBENTON4__G16 | 3 Phase fault NBENTON4 (508811) 138 kV Bus a. Apply fault at the NBENTON4 (508811) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NBENTON4 138 KV 508811 TO G16-167-TAP 138 KV 588404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NE10TH_4__RENO___4 | 3 Phase fault NE10TH 4 (514964) 138 kV Bus a. Apply fault at the NE10TH 4 (514964) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE10TH 4 138 KV 514964 TO RENO 4 138 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-029 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-029 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NE30TH_2__DEEPFKT2 | 3 Phase fault NE30TH 2 (514969) 69 kV Bus a. Apply fault at the NE30TH 2 (514969) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE30TH 2 69 KV 514969 TO DEEPFKT2 69 KV 514970 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NE30TH_2__RENO___2 | 3 Phase fault NE30TH 2 (514969) 69 kV Bus a. Apply fault at the NE30TH 2 (514969) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE30TH 2 69 KV 514969 TO RENO 2 69 KV 514972 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NE45TAP4__RUSHING4 | 3 Phase fault NE45TAP4 (515062) 138 kV Bus a. Apply fault at the NE45TAP4 (515062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE45TAP4 138 KV 515062 TO RUSHING4 138 KV 515064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NE45TAP4__WOLVRNT4 | 3 Phase fault NE45TAP4 (515062) 138 kV Bus a. Apply fault at the NE45TAP4 (515062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCK CK4 138 KV 515058 TO NE45TAP4 138 KV 515062 CKT 1 b.2. MOBIL 4 138 KV 515057 TO ROCK CK4 138 KV 515058 CKT 1 b.3. LOAD 1 515058 b.4. MOBIL 4 138 KV 515057 TO WOLVRNT4 138 KV 515532 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NEKOOSA2__HOLOX__2 | 3 Phase fault NEKOOSA2 (508065) 69 kV Bus a. Apply fault at the NEKOOSA2 (508065) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEKOOSA2 69 KV 508065 TO HOLOX 2 69 KV 508094 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NEKOSAT2__HOLOX__2 | 3 Phase fault NEKOSAT2 (508066) 69 kV Bus a. Apply fault at the NEKOSAT2 (508066) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEKOSAT2 69 KV 508066 TO HOLOX 2 69 KV 508094 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NEKOSAT2__SUGHLET2 | 3 Phase fault NEKOSAT2 (508066) 69 kV Bus a. Apply fault at the NEKOSAT2 (508066) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEKOSAT2 69 KV 508066 TO SUGHLET2 69 KV 508081 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NEOSHO_7__G17 | 3 Phase fault NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 345 KV 532793 TO G17-209-TAP 345 KV 760921 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NEOSHO_7__GEN | 3 Phase fault NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 345 KV 532793 TO GEN-2018-032 345 KV 762680 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NEWBOST2__DEKALB_2 | 3 Phase fault NEWBOST2 (508067) 69 kV Bus a. Apply fault at the NEWBOST2 (508067) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWBOST2 69 KV 508067 TO DEKALB 2 69 KV 508289 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NEWBOST2__NNBOSTN2 | 3 Phase fault NEWBOST2 (508067) 69 kV Bus a. Apply fault at the NEWBOST2 (508067) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWBOST2 69 KV 508067 TO NNBOSTN2 69 KV 508068 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NEWBOST2__REDRVR | 3 Phase fault NEWBOST2 (508067) 69 kV Bus a. Apply fault at the NEWBOST2 (508067) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWBOST2 69 KV 508067 TO REDRVR-2 69 KV 508074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NNBOSTN4__ANDRSNC4 | 3 Phase fault NNBOSTN4 (508069) 138 kV Bus a. Apply fault at the NNBOSTN4 (508069) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN4 138 KV 508069 TO RIFFIN REC4 138 KV 508104 CKT 1 b.2. LOAD 1 508104 b.3. ANDRSNC4 138 KV 508050 TO RIFFIN REC4 138 KV 508104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NNBOSTN4__G18 | 3 Phase fault NNBOSTN4 (508069) 138 kV Bus a. Apply fault at the NNBOSTN4 (508069) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN4 138 KV 508069 TO G18-003-TAP 138 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NORTWST7__ARCADIA7 | 3 Phase fault NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345 KV 514880 TO ARCADIA7 345 KV 514908 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NORTWST7__CIMARON7 | 3 Phase fault NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345 KV 514880 TO CIMARON7 345 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NORTWST7__MATHWSN7 | 3 Phase fault NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345 KV 514880 TO MATHWSN7 345 KV 515497 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NORTWST7__SPRNGCK7 | 3 Phase fault NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345 KV 514880 TO SPRNGCK7 345 KV 514881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NSHVILR2__NASHVIL2 | 3 Phase fault NSHVILR2 (507413) 69 kV Bus a. Apply fault at the NSHVILR2 (507413) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NSHVILR2 69 KV 507413 TO NASHVIL2 69 KV 507426 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NWT-BNT4_G18-003-TAP | 3 Phase fault NWT-BNT4 (508070) 138 kV Bus a. Apply fault at the NWT-BNT4 (508070) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138 KV 508070 TO G18-003-TAP 138 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NWT-BNT4_NWTXARX4 | 3 Phase fault NWT-BNT4 (508070) 138 kV Bus a. Apply fault at the NWT-BNT4 (508070) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138 KV 508070 TO NWTXARK4 138 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NWTXARK4__SUGARHL4 | 3 Phase fault NWTXARK4 (508071) 138 kV Bus a. Apply fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 138 KV 508071 TO SUGARHL4 138 KV 508080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NWTXARK7__LYDIA__7 | 3 Phase fault NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345 KV 508072 TO LYDIA 7 345 KV 508298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NWTXARK7__VALIANT7 | 3 Phase fault NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345 KV 508072 TO VALIANT7 345 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NWTXARK7__WELSH__7 | 3 Phase fault NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345 KV 508072 TO WELSH 7 345 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_O.K.U._G17-151-TAP | 3 Phase fault O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345 KV 511456 TO G17-151TAP 345 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_O.K.U._G18-015-Tap | 3 Phase fault O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345 KV 511456 TO G18-015-TAP 345 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_O.K.U._GEN-2017-033 | 3 Phase fault O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345 KV 511456 TO GEN-2017-033 345 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_O.K.U._L.E.S. | 3 Phase fault O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345 KV 511456 TO L.E.S.-7 345 KV 511468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_O.K.U._OKLAUN HVDC | 3 Phase fault O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345 KV 511456 TO OKLAUN HVDC7 345 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OAKCRK_4__DRAPER_4 | 3 Phase fault OAKCRK 4 (514960) 138 kV Bus a. Apply fault at the OAKCRK 4 (514960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKCRK 4 138 KV 514960 TO WILDMRY4 138 KV 514984 CKT 1 b.2. LOAD 1 514984 b.3. WILDMRY4 138 KV 514984 TO AIRDEPT4 138 KV 515457 CKT 1 b.4. LOAD 1 515457 b.5. GM 4 138 KV 514961 TO AIRDEPT4 138 KV 515457 CKT 1 b.6. LOAD 1 515457 b.7. DRAPER 4 138 KV 514933 TO GM 4 138 KV 514961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OAKCRK_4__INDNHIL4 | 3 Phase fault OAKCRK 4 (514960) 138 kV Bus a. Apply fault at the OAKCRK 4 (514960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE 4 138 KV 514955 TO OAKCRK 4 138 KV 514960 CKT 1 b.2. MOORE 4 138 KV 514955 TO INDIANH4 138 KV 515380 CKT 1 b.3. LOAD 1 515380 b.4. INDNHIL4 138 KV 514954 TO INDIANH4 138 KV 515380 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OAKCRK_4__SELNDTP4 | 3 Phase fault OAKCRK 4 (514960) 138 kV Bus a. Apply fault at the OAKCRK 4 (514960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKCRK 4 138 KV 514960 TO SELNDTP4 138 KV 515965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OAKS_OASETP | 3 Phase fault OAKS--E4 (509846) 138 kV Bus a. Apply fault at the OAKS--E4 (509846) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKS--E4 138 KV 509846 TO OAKSETP4 138 KV 509850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OAKSWTP4__SAPLPRD4 | 3 Phase fault OAKSWTP4 (509848) 138 kV Bus a. Apply fault at the OAKSWTP4 (509848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKSWTP4 138 KV 509848 TO SAPLPRD4 138 KV 509871 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OAKS__W4__OAKSWTP4 | 3 Phase fault OAKS W4 (509727) 138 kV Bus a. Apply fault at the OAKS W4 (509727) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKS W4 138 KV 509727 TO OAKSWTP4 138 KV 509848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OAKTRET4__SOONRTP4 | 3 Phase fault OAKTRET4 (514930) 138 kV Bus a. Apply fault at the OAKTRET4 (514930) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKTRET4 138 KV 514930 TO SOONRTP4 138 KV 514949 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | RKYRDGW-2WG trips on voltage protection settings | Disabling voltage protection settings for RKYRDGW-2WG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OGMARTN2__DX | 3 Phase fault OGMARTN2 (509751) 69 kV Bus a. Apply fault at the OGMARTN2 (509751) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGMARTN2 69 KV 509751 TO DX----E2 69 KV 509795 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OGMARTN2__T.P.S. | 3 Phase fault OGMARTN2 (509751) 69 kV Bus a. Apply fault at the OGMARTN2 (509751) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLPIP2 69 KV 509750 TO OGMARTN2 69 KV 509751 CKT 1 b.2. LOAD 1 509751 b.3. WILLPIP2 69 KV 509750 TO T.P.S.-2 69 KV 509789 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKAYGR_5__WAGNOR_5 | 3 Phase fault OKAYGR 5 (512640) 161 kV Bus a. Apply fault at the OKAYGR 5 (512640) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAYGR 5 161 KV 512640 TO WAGNOR 5 161 KV 512700 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKAY___2__NASHVIL2 | 3 Phase fault OKAY 2 (507427) 69 kV Bus a. Apply fault at the OKAY 2 (507427) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWAYR2 69 KV 507410 TO TOLETTE2 69 KV 507415 CKT 1 b.2. LOAD A1 507415 b.3. TOLETTE2 69 KV 507415 TO OKAY 2 69 KV 507427 CKT 1 b.4. LOAD 1 507427 b.5. MIDWAYR2 69 KV 507410 TO NASHVIL2 69 KV 507426 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKAY___4__TURK___4 | 3 Phase fault OKAY 4 (507428) 138 kV Bus a. Apply fault at the OKAY 4 (507428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAY 4 138 KV 507428 TO TURK 4 138 KV 507454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKEENE_2__TALOGA_2 | 3 Phase fault OKEENE 2 (521015) 69 kV Bus a. Apply fault at the OKEENE 2 (521015) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANTON-2 69 KV 520843 TO OKEENE 2 69 KV 521015 CKT 1 b.2. LOAD 1 521015 b.3. CANTON-2 69 KV 520843 TO TALOGA 2 69 KV 521064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKMULGE4__EC.HEN | 3 Phase fault OKMULGE4 (510898) 138 kV Bus a. Apply fault at the OKMULGE4 (510898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKMULGE4 138 KV 510898 TO EC.HEN-4 138 KV 510923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKMULGE4__KELCO_4 | 3 Phase fault OKMULGE4 (510898) 138 kV Bus a. Apply fault at the OKMULGE4 (510898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKMULGE4 138 KV 510898 TO KELCO 4 138 KV 510931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OMAHA__2__DUGLASV2 | 3 Phase fault OMAHA 2 (509644) 69 kV Bus a. Apply fault at the OMAHA 2 (509644) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMAHA 2 69 KV 509644 TO DUGLASV2 69 KV 509645 CKT NO c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ONETA_121LYNN | 3 Phase fault ONETA--4 (509806) 138 kV Bus a. Apply fault at the ONETA--4 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 138 KV 509806 TO 121LYNN4 138 KV 509869 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ONETA_BA81 | 3 Phase fault ONETA--4 (509806) 138 kV Bus a. Apply fault at the ONETA--4 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101-N4 138 KV 509769 TO ONETA--4 138 KV 509806 CKT 1 b.2. LOAD 1 509806 b.3. BA81---4 138 KV 509747 TO BA101-N4 138 KV 509769 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ONETA_BANNTAP4 | 3 Phase fault ONETA--4 (509806) 138 kV Bus a. Apply fault at the ONETA--4 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 138 KV 509806 TO BA_71ST4 138 KV 509891 CKT 1 b.2. LOAD 1 509891 b.3. BANNTAP4 138 KV 509785 TO BA_71ST4 138 KV 509891 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ONETA_NES | 3 Phase fault ONETA--7 (509807) 345 kV Bus a. Apply fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 345 KV 509807 TO N.E.S.-7 345 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-141 trips on frequency protection settings | Disabling frequency protection settings for GEN-2017-141 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ONETA_OEC | 3 Phase fault ONETA--7 (509807) 345 kV Bus a. Apply fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 345 KV 509807 TO OEC 7 345 KV 509836 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ORU_ETP4__WARNTAP4 | 3 Phase fault ORU ETP4 (509849) 138 kV Bus a. Apply fault at the ORU ETP4 (509849) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU ETP4 138 KV 509849 TO WARNTAP4 138 KV 509858 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ORU___E4__ORU_ETP4 | 3 Phase fault ORU E4 (509738) 138 kV Bus a. Apply fault at the ORU E4 (509738) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU E4 138 KV 509738 TO ORU ETP4 138 KV 509849 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ORU___W4__ORU | 3 Phase fault ORU W4 (509732) 138 kV Bus a. Apply fault at the ORU W4 (509732) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU W4 138 KV 509732 TO ORU-WTP4 138 KV 509853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OTTER__4__ARMFTWD4 | 3 Phase fault OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138 KV 514708 TO ARMFTWD4 138 KV 515694 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OTTER__4__WOODRNG4 | 3 Phase fault OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138 KV 514708 TO WOODRNG4 138 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OTTER__4__WRVALLY4 | 3 Phase fault OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138 KV 514708 TO WRVALLY4 138 KV 514713 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OWASO1_4__OWASOTP4 | 3 Phase fault OWASO1_4 (509726) 138 kV Bus a. Apply fault at the OWASO1_4 (509726) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OWASO1_4 138 KV 509726 TO OWASOTP4 138 KV 509844 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OWASOTP4__N.E.S. | 3 Phase fault OWASOTP4 (509844) 138 kV Bus a. Apply fault at the OWASOTP4 (509844) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OWAS1094 138 KV 509860 TO N.E.S.-4 138 KV 510396 CKT 1 b.2. LOAD 1 510396 b.3. OWASOTP4 138 KV 509844 TO OWAS1094 138 KV 509860 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PAOLI | 3 Phase fault PAOLI- 4 (515100) 138 kV Bus a. Apply fault at the PAOLI- 4 (515100) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAOLI- 4 138 KV 515100 TO CHIGLEY4 138 KV 515114 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PAOLI | 3 Phase fault PAOLI- 4 (515100) 138 kV Bus a. Apply fault at the PAOLI- 4 (515100) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAOLI- 4 138 KV 515100 TO MAYSVIL4 138 KV 515124 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PARADSE4__CHERRYRD_4 | 3 Phase fault PARADSE4 (521024) 138 kV Bus a. Apply fault at the PARADSE4 (521024) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARADSE4 138 KV 521024 TO CHERRYRD 4 138 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PARKLN_4__LKKONWA4 | 3 Phase fault PARKLN 4 (515178) 138 kV Bus a. Apply fault at the PARKLN 4 (515178) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKLN 4 138 KV 515178 TO LKKONWA4 138 KV 515977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PARKLN_4__SOTHADA4 | 3 Phase fault PARKLN 4 (515178) 138 kV Bus a. Apply fault at the PARKLN 4 (515178) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKLN 4 138 KV 515178 TO SOTHADA4 138 KV 515318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PARKMEDTP__COLNSGR2 | 3 Phase fault PARKMEDTP (512703) 69 kV Bus a. Apply fault at the PARKMEDTP (512703) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKMEDTP 69 KV 512703 TO COLNSGR2 69 KV 512870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PATTERS2__NEKOOSA2 | 3 Phase fault PATTERS2 (507429) 69 kV Bus a. Apply fault at the PATTERS2 (507429) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS2 69 KV 507429 TO NEKOOSA2 69 KV 508065 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PATTERS2__NEKOSAT2 | 3 Phase fault PATTERS2 (507429) 69 kV Bus a. Apply fault at the PATTERS2 (507429) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS2 69 KV 507429 TO ASHDOWN2 69 KV 508051 CKT 1 b.2. LOAD 1 508051 b.3. ASHDOWN2 69 KV 508051 TO NEKOSAT2 69 KV 508066 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PATTERS4__BARITERDTP_4 | 3 Phase fault PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOCKSBRG 4 138 KV 504123 TO PATTERS4 138 KV 507431 CKT 1 b.2. LOCKSBRG 4 138 KV 504123 TO BARITERDTP 4 138 KV 507463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | WLDHRSE trips on voltage protection settings | Disabling voltage protection settings for WLDHRSE prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PATTERS4__CRAIGJT4 | 3 Phase fault PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHDWN_W 4 138 KV 504124 TO PATTERS4 138 KV 507431 CKT 1 b.2. ASHDWN_W 4 138 KV 504124 TO CRAIGJT4 138 KV 510890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | WLDHRSE trips on voltage protection settings | Disabling voltage protection settings for WLDHRSE prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PATTERS4__NWTXARK4 | 3 Phase fault PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS4 138 KV 507431 TO NWTXARK4 138 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | WLDHRSE trips on voltage protection settings | Disabling voltage protection settings for WLDHRSE prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PATTERS4__OKAY___4 | 3 Phase fault PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHDWNR4 138 KV 507402 TO OKAY 4 138 KV 507428 CKT 1 b.2. ASHDWNR4 138 KV 507402 TO PATTERS4 138 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | WLDHRSE trips on voltage protection settings | Disabling voltage protection settings for WLDHRSE prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PATTERS4__SNASHVL4 | 3 Phase fault PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS4 138 KV 507431 TO SNASHVL4 138 KV 507434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | WLDHRSE trips on voltage protection settings | Disabling voltage protection settings for WLDHRSE prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PAWNSW4__GLENCOKM_4 | 3 Phase fault PAWNSW4 (512749) 138 kV Bus a. Apply fault at the PAWNSW4 (512749) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAWNSW4 138 KV 512749 TO GLENCOKM 4 138 KV 513095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PCATSAT4__PCATOSA4 | 3 Phase fault PCATSAT4 (509841) 138 kV Bus a. Apply fault at the PCATSAT4 (509841) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCATSAT4 138 KV 509841 TO BIRDCREE-4 138 KV 509899 CKT 1 b.2. LOAD 1 509899 b.3. PCATOSA4 138 KV 509725 TO BIRDCREE-4 138 KV 509899 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PEARLHL2__ROACH__2 | 3 Phase fault PEARLHL2 (509651) 69 kV Bus a. Apply fault at the PEARLHL2 (509651) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEARLHL2 69 KV 509651 TO ROACH 2 69 KV 509668 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PEARSNT2__MAUD___2 | 3 Phase fault PEARSNT2 (515053) 69 kV Bus a. Apply fault at the PEARSNT2 (515053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEARSNT2 69 KV 515053 TO MAUD 2 69 KV 515054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PECANCK4__BRISTOW4 | 3 Phase fault PECANCK4 (515233) 138 kV Bus a. Apply fault at the PECANCK4 (515233) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK4 138 KV 515233 TO BEGGS 4 138 KV 515249 CKT 1 b.2. LOAD 1 515249 b.3. BRISTOW4 138 KV 515035 TO BEGGS 4 138 KV 515249 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PECANCK7__GEN | 3 Phase fault PECANCK7 (515235) 345 kV Bus a. Apply fault at the PECANCK7 (515235) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECANCK7 345 KV 515235 TO GEN-2018-048 345 KV 762823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PENN___2__KENTUKT2 | 3 Phase fault PENN 2 (514924) 69 kV Bus a. Apply fault at the PENN 2 (514924) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENN 2 69 KV 514924 TO KENTUKT2 69 KV 514977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-026 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PENN___4__36&MER_4 | 3 Phase fault PENN 4 (514925) 138 kV Bus a. Apply fault at the PENN 4 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRAIRPT4 138 KV 514889 TO PENN 4 138 KV 514925 CKT 1 b.2. LOAD 1 514925 b.3. 36&MER 4 138 KV 514888 TO WRAIRPT4 138 KV 514889 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PENN___4__OAKCRK_4 | 3 Phase fault PENN 4 (514925) 138 kV Bus a. Apply fault at the PENN 4 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENN 4 138 KV 514925 TO SANTAFE4 138 KV 514926 CKT 1 b.2. LOAD 1 514926 b.3. SANTAFE4 138 KV 514926 TO OAKCRK 4 138 KV 514960 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PENSA__5__KETCHUM5 | 3 Phase fault PENSA 5 (512654) 161 kV Bus a. Apply fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 5 161 KV 512654 TO KETCHUM5 161 KV 512669 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PERDUE_4__DIANA__4 | 3 Phase fault PERDUE 4 (508351) 138 kV Bus a. Apply fault at the PERDUE 4 (508351) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERDUE 4 138 KV 508351 TO DIANA 4 138 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PERSIMN7__GUTHRIE7 | 3 Phase fault PERSIMN7 (515951) 345 kV Bus a. Apply fault at the PERSIMN7 (515951) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PERSIMN7 345 KV 515951 TO GUTHRIE7 345 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PETTY__4__CHAPELH4 | 3 Phase fault PETTY 4 (508310) 138 kV Bus a. Apply fault at the PETTY 4 (508310) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PETTY 4 138 KV 508310 TO CHAPELH4 138 KV 508337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PIC4__CDRDLTP4 | 3 Phase fault PIC4 (520425) 138 kV Bus a. Apply fault at the PIC4 (520425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIC4 138 KV 520425 TO CDRDLTP4 138 KV 520848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PIC4__MOORLND4 | 3 Phase fault PIC4 (520425) 138 kV Bus a. Apply fault at the PIC4 (520425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIC4 138 KV 520425 TO MOORLND4 138 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PIEDMNT4__NORTWST4 | 3 Phase fault PIEDMNT4 (514864) 138 kV Bus a. Apply fault at the PIEDMNT4 (514864) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIEDMNT4 138 KV 514864 TO NORTWST4 138 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MINCO-WTG34 trips on voltage protection setings | Disabling instantaneous voltage protection settings for MINCO-WTG34 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PINERTP2__WASHITA2 | 3 Phase fault PINERTP2 (521027) 69 kV Bus a. Apply fault at the PINERTP2 (521027) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PINERTP2 69 KV 521027 TO WASHITA2 69 KV 521088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PINK_SW4__SHAWNEE4 | 3 Phase fault PINK SW4 (521028) 138 kV Bus a. Apply fault at the PINK SW4 (521028) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PINK SW4 138 KV 521028 TO SHAWNEE4 138 KV 521048 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PINK___4__PINK_SW4 | 3 Phase fault PINK 4 (520494) 138 kV Bus a. Apply fault at the PINK 4 (520494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PINK 4 138 KV 520494 TO PINK SW4 138 KV 521028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PINTAIL7__KINGWD_7 | 3 Phase fault PINTAIL7 (516010) 345 kV Bus a. Apply fault at the PINTAIL7 (516010) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PINTAIL7 345 KV 516010 TO KINGWD 7 345 KV 516019 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PIRKEY_4__SABMINT4 | 3 Phase fault PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138 KV 508562 TO SABMINT4 138 KV 508566 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PIRKEY_4__WHITNEY4 | 3 Phase fault PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138 KV 508562 TO HALLSVLS4 138 KV 508595 CKT 1 b.2. LOAD 1 508595 b.3. WHITNEY4 138 KV 508575 TO HALLSVLS4 138 KV 508595 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PIRKEY_7__DIANA__7 | 3 Phase fault PIRKEY 7 (508563) 345 kV Bus a. Apply fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345 KV 508563 TO DIANA 7 345 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PIRKEY_7__LEBROCK7 | 3 Phase fault PIRKEY 7 (508563) 345 kV Bus a. Apply fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345 KV 508563 TO LEBROCK7 345 KV 508572 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PITTSB_CRIVER | 3 Phase fault PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345 KV 510907 TO C-RIVER7 345 KV 515422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PITTSB_JOHNCO | 3 Phase fault PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345 KV 510907 TO JOHNCO 7 345 KV 514809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PITTSB_KIOWA | 3 Phase fault PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345 KV 510907 TO KIOWA 7 345 KV 510925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PITTSB_SEMINOL | 3 Phase fault PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345 KV 510907 TO SEMINOL7 345 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PITTSB_VALIANT | 3 Phase fault PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345 KV 510907 TO VALIANT7 345 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_POLECTP4__HICKORY4 | 3 Phase fault POLECTP4 (515218) 138 kV Bus a. Apply fault at the POLECTP4 (515218) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POLECTP4 138 KV 515218 TO HICKORY4 138 KV 515244 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_POLECTP4__POLECAT4 | 3 Phase fault POLECTP4 (515218) 138 kV Bus a. Apply fault at the POLECTP4 (515218) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POLECTP4 138 KV 515218 TO POLECAT4 138 KV 515219 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_POOLVIL_CARTCO4 | 3 Phase fault POOLVIL4 (515130) 138 kV Bus a. Apply fault at the POOLVIL4 (515130) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POOLVIL4 138 KV 515130 TO CARTRCO4 138 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_POWELL_4__SW_SHV_4 | 3 Phase fault POWELL 4 (507748) 138 kV Bus a. Apply fault at the POWELL 4 (507748) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POWELL 4 138 KV 507748 TO SW SHV 4 138 KV 507759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PP_YARCHT | 3 Phase fault PP----E4 (509818) 138 kV Bus a. Apply fault at the PP----E4 (509818) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PP----E4 138 KV 509818 TO YARCHT 4 138 KV 509862 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PP_P&PWTP4 | 3 Phase fault PP----W4 (509805) 138 kV Bus a. Apply fault at the PP----W4 (509805) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PP----W4 138 KV 509805 TO P&P WTP4 138 KV 509851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PPTAP__4__46ST | 3 Phase fault PPTAP 4 (509863) 138 kV Bus a. Apply fault at the PPTAP 4 (509863) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PPTAP 4 138 KV 509863 TO 46ST-TP-4 138 KV 509900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_QUAILCK4__LNEOAK_4 | 3 Phase fault QUAILCK4 (514851) 138 kV Bus a. Apply fault at the QUAILCK4 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 138 KV 514851 TO LNEOAK 4 138 KV 514873 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_QUAILCK4__NORTWST4 | 3 Phase fault QUAILCK4 (514851) 138 kV Bus a. Apply fault at the QUAILCK4 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNEOAK 4 138 KV 514873 TO NORTWST4 138 KV 514879 CKT 1 b.2. QUAILCK4 138 KV 514851 TO LNEOAK 4 138 KV 514873 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_QUAILCK4__SLVRLAK4 | 3 Phase fault QUAILCK4 (514851) 138 kV Bus a. Apply fault at the QUAILCK4 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 138 KV 514851 TO SLVRLAK4 138 KV 514852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_R.S.S_5DELT | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138 KV 509783 TO 52DELWT4 138 KV 509814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_R.S.S._KIMCLRK4 | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 136YALE4 138 KV 509775 TO R.S.S.-4 138 KV 509783 CKT 1 b.2. 136YALE4 138 KV 509775 TO KIMCLRK4 138 KV 509845 CKT 1 b.3. LOAD 1 509845 b.4. B111---4 138 KV 509767 TO KIMCLRK4 138 KV 509845 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_R.S.S._EXPGLNT4 | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138 KV 509783 TO EXPGLNT4 138 KV 515473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_R.S.S._OAKSETP4 | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138 KV 509783 TO OAKSETP4 138 KV 509850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_R.S.S._EXP_OKM4 | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138 KV 509783 TO EXP_OKM4 138 KV 510904 CKT 1 b.2. LOAD 1 510904 b.3. OKMULGE4 138 KV 510898 TO EXP_OKM4 138 KV 510904 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_R.S.S._ORU-WTP4 | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138 KV 509783 TO ORU-WTP4 138 KV 509853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_R.S.S._ORU ETP4 | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138 KV 509783 TO ORU ETP4 138 KV 509849 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_R.S.S._RSST2 | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138 KV 509783 TO RSS T2 4 138 KV 509875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_R.S.S._COGENT | 3 Phase fault R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345 KV 509782 TO COGENT 7 345 KV 509834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027, GEN-2017-140 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-027, GEN-2017-140 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_R.S.S._G16133G16146 | 3 Phase fault R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345 KV 509782 TO G16133G16146 345 KV 588039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_R.S.S._ONETA | 3 Phase fault R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345 KV 509782 TO ONETA--7 345 KV 509807 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027, GEN-2017-140 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-027, GEN-2017-140 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_R.S.S._PECANCK7 | 3 Phase fault R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345 KV 509782 TO PECANCK7 345 KV 515235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027, GEN-2017-140 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-027, GEN-2017-140 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_R.S.S._REDBUD | 3 Phase fault R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345 KV 509782 TO REDBUD 7 345 KV 514909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027, GEN-2017-140 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-027, GEN-2017-140 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_R.S.S._SAPLPRD | 3 Phase fault R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345 KV 509782 TO SAPLPRD7 345 KV 509870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027, GEN-2017-140 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-027, GEN-2017-140 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_RATLIFF4__CARTRCO4 | 3 Phase fault RATLIFF4 (515129) 138 kV Bus a. Apply fault at the RATLIFF4 (515129) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RATLIFF4 138 KV 515129 TO CARTRCO4 138 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_REDBAYOU_6__DOLHILL6 | 3 Phase fault REDBAYOU_6 (500255) 230 kV Bus a. Apply fault at the REDBAYOU_6 (500255) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBAYOU_6 230 KV 500255 TO DOLHILL6 230 KV 500260 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_REDBDPLN4__LEONARD4 | 3 Phase fault REDBDPLN4 (511573) 138 kV Bus a. Apply fault at the REDBDPLN4 (511573) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBDPLN4 138 KV 511573 TO LEONARD4 138 KV 511575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_REDCLFT4__REDCLF_4 | 3 Phase fault REDCLFT4 (515533) 138 kV Bus a. Apply fault at the REDCLFT4 (515533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDCLFT4 138 KV 515533 TO REDCLF 4 138 KV 515863 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_REDNGTN7__REDDIRT7 | 3 Phase fault REDNGTN7 (515875) 345 kV Bus a. Apply fault at the REDNGTN7 (515875) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDNGTN7 345 KV 515875 TO REDDIRT7 345 KV 515877 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_REDSPRG4__EYLAU__4 | 3 Phase fault REDSPRG4 (508075) 138 kV Bus a. Apply fault at the REDSPRG4 (508075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDSPRG4 138 KV 508075 TO EYLAU 4 138 KV 509655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_REDSPRG4__IPC_T__4 | 3 Phase fault REDSPRG4 (508075) 138 kV Bus a. Apply fault at the REDSPRG4 (508075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC-DOM4 138 KV 508060 TO REDSPRG4 138 KV 508075 CKT 1 b.2. LOAD 1 508075 b.3. IPC T 4 138 KV 508059 TO IPC-DOM4 138 KV 508060 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_REDWATR4__EYLAU__4 | 3 Phase fault REDWATR4 (509654) 138 kV Bus a. Apply fault at the REDWATR4 (509654) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDWATR4 138 KV 509654 TO EYLAU 4 138 KV 509655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_REMPKTP4__REMNGPK4 | 3 Phase fault REMPKTP4 (514872) 138 kV Bus a. Apply fault at the REMPKTP4 (514872) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REMPKTP4 138 KV 514872 TO REMNGPK4 138 KV 514874 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-133 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-133 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_RENO___2__SUNNYLN2 | 3 Phase fault RENO 2 (514972) 69 kV Bus a. Apply fault at the RENO 2 (514972) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 2 69 KV 514972 TO SUNNYLN2 69 KV 514980 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_RENO___4__WASHPRK4 | 3 Phase fault RENO 4 (514973) 138 kV Bus a. Apply fault at the RENO 4 (514973) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 4 138 KV 514973 TO WASHPRK4 138 KV 515156 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MNCOWNG3 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_RICHRDS4__PIEDMNT4 | 3 Phase fault RICHRDS4 (514862) 138 kV Bus a. Apply fault at the RICHRDS4 (514862) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHRDS4 138 KV 514862 TO PIEDMNT4 138 KV 514864 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ROCKYPT4__SPRNDAL4 | 3 Phase fault ROCKYPT4 (515164) 138 kV Bus a. Apply fault at the ROCKYPT4 (515164) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT4 138 KV 515164 TO SPRNDAL4 138 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ROKHILL4__NEWPROS4 | 3 Phase fault ROKHILL4 (509083) 138 kV Bus a. Apply fault at the ROKHILL4 (509083) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL4 138 KV 509083 TO NEWPROS4 138 KV 509102 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ROKHILL4__TATUM__4 | 3 Phase fault ROKHILL4 (509083) 138 kV Bus a. Apply fault at the ROKHILL4 (509083) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL4 138 KV 509083 TO TATUM 4 138 KV 509087 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ROMNOSE4__GEARYTP4 | 3 Phase fault ROMNOSE4 (514823) 138 kV Bus a. Apply fault at the ROMNOSE4 (514823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROMNOSE4 138 KV 514823 TO GEARYTP4 138 KV 515931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_RSS_T1_4__R.S.S. | 3 Phase fault RSS T1 4 (509773) 138 kV Bus a. Apply fault at the RSS T1 4 (509773) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T1 4 138 KV 509773 TO R.S.S.-4 138 KV 509783 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_RUSHSPR7__GEN | 3 Phase fault RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345 KV 511571 TO GEN-2018-055 345 KV 762900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_RVRFANT2__MUSKOGE2 | 3 Phase fault RVRFANT2 (515210) 69 kV Bus a. Apply fault at the RVRFANT2 (515210) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RVRFANT2 69 KV 515210 TO MUSKOGE2 69 KV 515221 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_RVRSID_2__MUSKOGE2 | 3 Phase fault RVRSID 2 (515205) 69 kV Bus a. Apply fault at the RVRSID 2 (515205) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RVRSID 2 69 KV 515205 TO MUSKOGE2 69 KV 515221 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_S.HIL_E4__SHILETP4 | 3 Phase fault S.HIL E4 (509731) 138 kV Bus a. Apply fault at the S.HIL E4 (509731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HIL E4 138 KV 509731 TO SHILETP4 138 KV 509813 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_S.S._BLUEBEL4 | 3 Phase fault S.S.---4 (509815) 138 kV Bus a. Apply fault at the S.S.---4 (509815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRATTV-4 138 KV 509758 TO S.S.---4 138 KV 509815 CKT 1 b.2. LOAD 1 509815 b.3. PRATTV-4 138 KV 509758 TO BLUEBEL4 138 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_S.S._DENV_WTAP | 3 Phase fault S.S.---4 (509815) 138 kV Bus a. Apply fault at the S.S.---4 (509815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---4 138 KV 509815 TO DENV_WTAP4 138 KV 509896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_S.S._HWY20-T | 3 Phase fault S.S.---4 (509815) 138 kV Bus a. Apply fault at the S.S.---4 (509815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---4 138 KV 509815 TO HWY20-T4 138 KV 509821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_S.S._WED-TAP4 | 3 Phase fault S.S.---4 (509815) 138 kV Bus a. Apply fault at the S.S.---4 (509815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---4 138 KV 509815 TO WED-TAP4 138 KV 509823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_S.W.S._ANADARK | 3 Phase fault S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138 KV 511477 TO ANADARK4 138 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_S.W.S._CORNVIL4 | 3 Phase fault S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VERDEN 4 138 KV 511421 TO S.W.S.-4 138 KV 511477 CKT 1 b.2. VERDEN 4 138 KV 511421 TO N29CHIK4 138 KV 511502 CKT 1 b.3. LOAD 1 511502 b.4. CORNVIL4 138 KV 511449 TO N29CHIK4 138 KV 511502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_S.W.S._ELGINJT4 | 3 Phase fault S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138 KV 511477 TO ELSWORTH 4 138 KV 511563 CKT 1 b.2. LOAD 1 511563 b.3. LOAD 2 511563 b.4. ELGINJT4 138 KV 511486 TO ELSWORTH 4 138 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_S.W.S._G16-097-TAP | 3 Phase fault S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138 KV 511477 TO G16-097-TAP 138 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_S.W.S._HOBJCT | 3 Phase fault S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNEG-4 138 KV 511445 TO S.W.S.-4 138 KV 511477 CKT 1 b.2. CARNEG-4 138 KV 511445 TO HOB-JCT4 138 KV 511463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_S.W.S._WASHITA | 3 Phase fault S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138 KV 511477 TO WASHITA4 138 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_S52DEL_4__52DELTP4 | 3 Phase fault S52DEL 4 (509716) 138 kV Bus a. Apply fault at the S52DEL 4 (509716) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S52DEL 4 138 KV 509716 TO 52DELTP4 138 KV 509776 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SABMINT4__SABINEM4 | 3 Phase fault SABMINT4 (508566) 138 kV Bus a. Apply fault at the SABMINT4 (508566) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SABMINT4 138 KV 508566 TO SABINEM4 138 KV 508577 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SALINA_5__SALNCRK5 | 3 Phase fault SALINA 5 (512686) 161 kV Bus a. Apply fault at the SALINA 5 (512686) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINA 5 161 KV 512686 TO SALNCRK5 161 KV 512805 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SALISAW5__GORE___5 | 3 Phase fault SALISAW5 (505550) 161 kV Bus a. Apply fault at the SALISAW5 (505550) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALISAW5 161 KV 505550 TO GORE 5 161 KV 505552 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SAPLPRD4__DENV_WTAP4 | 3 Phase fault SAPLPRD4 (509871) 138 kV Bus a. Apply fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 138 KV 509871 TO DENV_WTAP4 138 KV 509896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SAPLPRD4__R.S.S. | 3 Phase fault SAPLPRD4 (509871) 138 kV Bus a. Apply fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENKS--4 138 KV 509759 TO SAPLPRD4 138 KV 509871 CKT 1 b.2. 116JENK4 138 KV 509753 TO JENKS--4 138 KV 509759 CKT 1 b.3. LOAD 1 509759 b.4. 116JENK4 138 KV 509753 TO R.S.S.-4 138 KV 509783 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on frequency protection settings GEN-2017-141 trips on voltage protection settings | Disabling frequency protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. Disabling voltage protection settings for GEN-2017-141 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SAPULPA2__BEELINE2 | 3 Phase fault SAPULPA2 (515236) 69 kV Bus a. Apply fault at the SAPULPA2 (515236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPULPA2 69 KV 515236 TO BEELINE2 69 KV 515246 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SARA_RD4__SUNSHIN4 | 3 Phase fault SARA RD4 (521005) 138 kV Bus a. Apply fault at the SARA RD4 (521005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA RD4 138 KV 521005 TO SUNSHIN4 138 KV 521059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SARA___4__MCCLAIN4 | 3 Phase fault SARA 4 (514895) 138 kV Bus a. Apply fault at the SARA 4 (514895) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA 4 138 KV 514895 TO MCCLAIN4 138 KV 514902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SAWYER4__HUGO_PP4 | 3 Phase fault SAWYER4 (520411) 138 kV Bus a. Apply fault at the SAWYER4 (520411) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAWYER4 138 KV 520411 TO HUGO PP4 138 KV 520948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SCOFCTY4__COFFEYT4 | 3 Phase fault SCOFCTY4 (510378) 138 kV Bus a. Apply fault at the SCOFCTY4 (510378) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOFCTY4 138 KV 510378 TO COFFEYT4 138 KV 510422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | CGENSUB2 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SDIERKS2__DIERKSR2 | 3 Phase fault SDIERKS2 (507432) 69 kV Bus a. Apply fault at the SDIERKS2 (507432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SDIERKS2 69 KV 507432 TO DIERKSR2 69 KV 507437 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SDIERKS4__BARITERDTP_4 | 3 Phase fault SDIERKS4 (507433) 138 kV Bus a. Apply fault at the SDIERKS4 (507433) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SDIERKS4 138 KV 507433 TO BARITERDTP 4 138 KV 507463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SE15TH_4__BARNES_4 | 3 Phase fault SE15TH 4 (514993) 138 kV Bus a. Apply fault at the SE15TH 4 (514993) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SE15TH 4 138 KV 514993 TO BARNES 4 138 KV 515003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SE15TH_4__TINKER54 | 3 Phase fault SE15TH 4 (514993) 138 kV Bus a. Apply fault at the SE15TH 4 (514993) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDAL4 138 KV 514986 TO SE15TH 4 138 KV 514993 CKT 1 b.2. LOAD 1 514993 b.3. GLENDAL4 138 KV 514986 TO TINKER74 138 KV 515959 CKT 1 b.4. LOAD 1 515959 b.5. TINKER64 138 KV 515806 TO TINKER74 138 KV 515959 CKT 1 b.6. LOAD 1 515959 b.7. TINKER54 138 KV 514994 TO TINKER64 138 KV 515806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SELNDTP4__SELNDFL4 | 3 Phase fault SELNDTP4 (515965) 138 kV Bus a. Apply fault at the SELNDTP4 (515965) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SELNDTP4 138 KV 515965 TO SELNDFL4 138 KV 515966 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MINCO5G11 trips on voltage protection settings | Disabling voltage protection settings for MINCO5G11 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SELNDTP4__TROSPER4 | 3 Phase fault SELNDTP4 (515965) 138 kV Bus a. Apply fault at the SELNDTP4 (515965) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DISCVRY4 138 KV 514962 TO SELNDTP4 138 KV 515965 CKT 1 b.2. FOSTER 4 138 KV 514959 TO DISCVRY4 138 KV 514962 CKT 1 b.3. LOAD 1 514962 b.4. FOSTER 4 138 KV 514959 TO NEWDOMI4 138 KV 515387 CKT 1 b.5. LOAD 1 515387 b.6. TROSPER4 138 KV 514963 TO NEWDOMI4 138 KV 515387 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SEMINOL4__LKKONWA4 | 3 Phase fault SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138 KV 515044 TO LKKONWA4 138 KV 515977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SEMINOL4__MAUD___4 | 3 Phase fault SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138 KV 515044 TO MAUD 4 138 KV 515055 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SEMINOL4__PAOLI | 3 Phase fault SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138 KV 515044 TO PAOLI- 4 138 KV 515100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SEMINOL4__VANOSTP4 | 3 Phase fault SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138 KV 515044 TO VANOSTP4 138 KV 515531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SEMINOL7__FIREWHL | 3 Phase fault SEMINOL7 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 345 KV 515045 TO FIREWHL-TAP 345 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SEQUOYAHJ4__ANADARK4 | 3 Phase fault SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138 KV 520422 TO ANADARK4 138 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SEQUOYAHJ4__CKSHATP4 | 3 Phase fault SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138 KV 520422 TO CKSHATP4 138 KV 520473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SEQUOYAHJ4__SEQOYAH4 | 3 Phase fault SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138 KV 520422 TO SEQOYAH4 138 KV 520547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SETEXAR2__TEXARK_2 | 3 Phase fault SETEXAR2 (508077) 69 kV Bus a. Apply fault at the SETEXAR2 (508077) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETEXAR2 69 KV 508077 TO TEXARK 2 69 KV 508086 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SETEXAR4__MANDEVILTP4 | 3 Phase fault SETEXAR4 (508078) 138 kV Bus a. Apply fault at the SETEXAR4 (508078) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETEXAR4 138 KV 508078 TO MANDEVILTP4 138 KV 508105 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SFOREMAN__4__NNBOSTN4 | 3 Phase fault SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4 (504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 138 KV 504029 TO NNBOSTN4 138 KV 508069 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SFOREMAN__4__PATTERS4 | 3 Phase fault SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4 (504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 138 KV 504029 TO PATTERS4 138 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SHAWNEE2__SINCPNT2 | 3 Phase fault SHAWNEE2 (515068) 69 kV Bus a. Apply fault at the SHAWNEE2 (515068) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHAWNEE2 69 KV 515068 TO SINCPNT2 69 KV 515642 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SHILETP4__ORU | 3 Phase fault SHILETP4 (509813) 138 kV Bus a. Apply fault at the SHILETP4 (509813) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHILETP4 138 KV 509813 TO ORU-WTP4 138 KV 509853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-141 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-141 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SILSPWW5__KANSATP5 | 3 Phase fault SILSPWW5 (512642) 161 kV Bus a. Apply fault at the SILSPWW5 (512642) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILSPWW5 161 KV 512642 TO KANSATP5 161 KV 512714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SINCPAN2__SINCPNT2 | 3 Phase fault SINCPAN2 (515072) 69 kV Bus a. Apply fault at the SINCPAN2 (515072) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SINCPAN2 69 KV 515072 TO SINCPNT2 69 KV 515642 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SKELTON7__GEN | 3 Phase fault SKELTON7 (515990) 345 kV Bus a. Apply fault at the SKELTON7 (515990) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SKELTON7 345 KV 515990 TO GEN-2016-128 345 KV 588190 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SKYLINE4__FAIRFLD4 | 3 Phase fault SKYLINE4 (514850) 138 kV Bus a. Apply fault at the SKYLINE4 (514850) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SKYLINE4 138 KV 514850 TO CHISHOM4 138 KV 515374 CKT 1 b.2. LOAD 1 515374 b.3. CHISHOM4 138 KV 515374 TO FAIRFLD4 138 KV 515468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SKYLINE4__QUAILCK4 | 3 Phase fault SKYLINE4 (514850) 138 kV Bus a. Apply fault at the SKYLINE4 (514850) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SKYLINE4 138 KV 514850 TO QUAILCK4 138 KV 514851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SLVRLAK4__DVISION4 | 3 Phase fault SLVRLAK4 (514852) 138 kV Bus a. Apply fault at the SLVRLAK4 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 138 KV 514852 TO DVISION4 138 KV 514853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-029 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-029 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SLVRLAK4__NORTWST4 | 3 Phase fault SLVRLAK4 (514852) 138 kV Bus a. Apply fault at the SLVRLAK4 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 138 KV 514852 TO BRADEN 4 138 KV 514854 CKT 1 b.2. LOAD 1 514854 b.3. BRADEN 4 138 KV 514854 TO NORTWST4 138 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-029 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-029 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SMITHCO4__DAYTON_4 | 3 Phase fault SMITHCO4 (514891) 138 kV Bus a. Apply fault at the SMITHCO4 (514891) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMITHCO4 138 KV 514891 TO DAYTON 4 138 KV 514892 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SO4TH__2__CHSTNTT2 | 3 Phase fault SO4TH 2 (514730) 69 kV Bus a. Apply fault at the SO4TH 2 (514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 69 KV 514730 TO CHSTNTT2 69 KV 515456 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SO4TH__4__BRECKNR4 | 3 Phase fault SO4TH 4 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138 KV 514731 TO BRECKNR4 138 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SO4TH__4__IMO____4 | 3 Phase fault SO4TH 4 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138 KV 514731 TO IMO 4 138 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SOONER_7__G15 | 3 Phase fault SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345 KV 514803 TO G15-066T 345 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SOONER_7__G16 | 3 Phase fault SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345 KV 514803 TO G16-119-TAP 345 KV 587804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SOONER_7__PINTAIL7 | 3 Phase fault SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345 KV 514803 TO PINTAIL7 345 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SOONER_7__RANCHRD7 | 3 Phase fault SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345 KV 514803 TO RANCHRD7 345 KV 515576 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SOONER_7__THUNDER7 | 3 Phase fault SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345 KV 514803 TO THUNDER7 345 KV 515894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SOUTHRD4__ROMNOSE4 | 3 Phase fault SOUTHRD4 (514822) 138 kV Bus a. Apply fault at the SOUTHRD4 (514822) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOUTHRD4 138 KV 514822 TO ROMNOSE4 138 KV 514823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SPNKY_CK4__CATOOSA4 | 3 Phase fault SPNKY CK4 (509722) 138 kV Bus a. Apply fault at the SPNKY CK4 (509722) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPNKY CK4 138 KV 509722 TO CATOOSA4 138 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SPPMAINBUS__WELSH__7 | 3 Phase fault SPPMAINBUS (5917) 345 kV Bus a. Apply fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPPMAIN345 KV 5917 TO WELSH 7 345 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SPRHILL4__DIANA__4 | 3 Phase fault SPRHILL4 (508571) 138 kV Bus a. Apply fault at the SPRHILL4 (508571) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRHILL4 138 KV 508571 TO DIANA 4 138 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SQUIRCK4__NE45TAP4 | 3 Phase fault SQUIRCK4 (515059) 138 kV Bus a. Apply fault at the SQUIRCK4 (515059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQUIRCK4 138 KV 515059 TO INGLEWD4 138 KV 515060 CKT 1 b.2. LOAD 1 515060 b.3. INGLEWD4 138 KV 515060 TO STGREG 4 138 KV 515061 CKT 1 b.4. LOAD 1 515061 b.5. STGREG 4 138 KV 515061 TO NE45TAP4 138 KV 515062 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SQUIRCK4__STRLGTP4 | 3 Phase fault SQUIRCK4 (515059) 138 kV Bus a. Apply fault at the SQUIRCK4 (515059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQUIRCK4 138 KV 515059 TO STRLGTP4 138 KV 515286 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_STALOGA2__PUTNAM_2 | 3 Phase fault STALOGA2 (520454) 69 kV Bus a. Apply fault at the STALOGA2 (520454) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STALOGA2 69 KV 520454 TO PUTNAM 2 69 KV 521033 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_STNWAL_4__REMPKTP4 | 3 Phase fault STNWAL 4 (514870) 138 kV Bus a. Apply fault at the STNWAL 4 (514870) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNWAL 4 138 KV 514870 TO REMPKTP4 138 KV 514872 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_STNWAL_4__RENO___4 | 3 Phase fault STNWAL 4 (514870) 138 kV Bus a. Apply fault at the STNWAL 4 (514870) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNWAL 4 138 KV 514870 TO OUMED 4 138 KV 514875 CKT 1 b.2. LOAD 1 514875 b.3. OUMED 4 138 KV 514875 TO GATEWAY4 138 KV 515963 CKT 1 b.4. LOAD 1 515963 b.5. WASHPRK4 138 KV 515156 TO GATEWAY4 138 KV 515963 CKT 1 b.6. LOAD 1 515963 b.7. RENO 4 138 KV 514973 TO WASHPRK4 138 KV 515156 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_STRLGTP4__STERLNG4 | 3 Phase fault STRLGTP4 (515286) 138 kV Bus a. Apply fault at the STRLGTP4 (515286) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STRLGTP4 138 KV 515286 TO STERLNG4 138 KV 520449 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_STUBMAN4__HOLLYWD4 | 3 Phase fault STUBMAN4 (514952) 138 kV Bus a. Apply fault at the STUBMAN4 (514952) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STUBMAN4 138 KV 514952 TO HOLLYWD4 138 KV 514953 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | RKYRDGW-2WG trips on voltage protection settings | Disabling voltage protection settings for RKYRDGW-2WG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SUGARHL2__SUGHLET2 | 3 Phase fault SUGARHL2 (508079) 69 kV Bus a. Apply fault at the SUGARHL2 (508079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGARHL2 69 KV 508079 TO SUGHLET2 69 KV 508081 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SUGARHL2__SUGHLWT2 | 3 Phase fault SUGARHL2 (508079) 69 kV Bus a. Apply fault at the SUGARHL2 (508079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGARHL2 69 KV 508079 TO SUGHLWT2 69 KV 508082 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SUGHLET2__TEXARK_2 | 3 Phase fault SUGHLET2 (508081) 69 kV Bus a. Apply fault at the SUGHLET2 (508081) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGHLET2 69 KV 508081 TO TEX12ST2 69 KV 508084 CKT 1 b.2. LOAD 1 508084 b.3. TEX12ST2 69 KV 508084 TO WASHST 2 69 KV 508088 CKT 1 b.4. LOAD 1 508088 b.5. TEXARK 2 69 KV 508086 TO WASHST 2 69 KV 508088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SUGHLWT2__TEX39ST2 | 3 Phase fault SUGHLWT2 (508082) 69 kV Bus a. Apply fault at the SUGHLWT2 (508082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGHLWT2 69 KV 508082 TO TEX39ST2 69 KV 508085 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SUMMERG2__LEASIDE_2 | 3 Phase fault SUMMERG2 (507758) 69 kV Bus a. Apply fault at the SUMMERG2 (507758) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMERG2 69 KV 507758 TO LEASIDE 2 69 KV 507794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SUNNYLN2__TINKER32 | 3 Phase fault SUNNYLN2 (514980) 69 kV Bus a. Apply fault at the SUNNYLN2 (514980) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYLN2 69 KV 514980 TO TINKER32 69 KV 514981 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SUNNYSD4__ARDWEST4 | 3 Phase fault SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNIROY 4 138 KV 515137 TO ARDWEST4 138 KV 515372 CKT 1 b.2. LOAD 1 515372 b.3. SUNNYSD4 138 KV 515135 TO UNIROY 4 138 KV 515137 CKT 1 b.4. LOAD 1 515137 b.5. CARTER 4 138 KV 515138 TO ARDWEST4 138 KV 515372 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SUNNYSD4__CARTRCO4 | 3 Phase fault SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138 KV 515135 TO CARTRCO4 138 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SUNNYSD4__LONEGRV4 | 3 Phase fault SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138 KV 515135 TO LONEGRV4 138 KV 515144 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SUNNYSD4__ROCKYPT4 | 3 Phase fault SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138 KV 515135 TO ROCKYPT4 138 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SUNNYSD7__G17 | 3 Phase fault SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345 KV 515136 TO G17-075-TAP 345 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SUNNYSD7__GEN | 3 Phase fault SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345 KV 515136 TO GEN-2017-167 345 KV 761859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SW134TP4__MCCLAIN4 | 3 Phase fault SW134TP4 (514876) 138 kV Bus a. Apply fault at the SW134TP4 (514876) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW134TP4 138 KV 514876 TO MCCLAIN4 138 KV 514902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SW134TP4__NORMHLL4 | 3 Phase fault SW134TP4 (514876) 138 kV Bus a. Apply fault at the SW134TP4 (514876) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW134TP4 138 KV 514876 TO SOGATE 4 138 KV 514928 CKT 1 b.2. LOAD 1 514928 b.3. SOGATE 4 138 KV 514928 TO TURNER 4 138 KV 514992 CKT 1 b.4. LOAD 1 514992 b.5. TURNER 4 138 KV 514992 TO NORMHLL4 138 KV 516097 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SW134TP4__PENN___4 | 3 Phase fault SW134TP4 (514876) 138 kV Bus a. Apply fault at the SW134TP4 (514876) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW134TP4 138 KV 514876 TO WESTMOR4 138 KV 514887 CKT 1 b.2. LOAD 1 514887 b.3. WESTMOR4 138 KV 514887 TO PENN 4 138 KV 514925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SWEETWT6__BUFFCK6 | 3 Phase fault SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230 KV 511541 TO BUFFCK6 230 KV 511542 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SWEETWT6__CHISHOLM6 | 3 Phase fault SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230 KV 511541 TO CHISHOLM6 230 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SWEETWT6__DEMPSEY6 | 3 Phase fault SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230 KV 511541 TO DEMPSEY6 230 KV 511544 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SWEETWT6__ROARK6 | 3 Phase fault SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230 KV 511541 TO ROARK6 230 KV 511547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SWEETWT6__STLN | 3 Phase fault SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230 KV 511541 TO STLN-DEMARC6 230 KV 523779 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SWISHER____6__TUCO_INT___6 | 3 Phase fault SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230 KV 525213 TO TUCO_INT 6 230 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SW_5TH_2__38TH_ST2 | 3 Phase fault SW 5TH 2 (514919) 69 kV Bus a. Apply fault at the SW 5TH 2 (514919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAY AVE2 69 KV 514913 TO SW 5TH 2 69 KV 514919 CKT 1 b.2. 38TH ST2 69 KV 514845 TO MAY AVE2 69 KV 514913 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-026 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SW_5TH_2__KENTUKT2 | 3 Phase fault SW 5TH 2 (514919) 69 kV Bus a. Apply fault at the SW 5TH 2 (514919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW 5TH 2 69 KV 514919 TO SW22ND 2 69 KV 514975 CKT 1 b.2. LOAD 1 514975 b.3. SW22ND 2 69 KV 514975 TO KENTUKY2 69 KV 514976 CKT 1 b.4. LOAD 1 514976 b.5. KENTUKY2 69 KV 514976 TO KENTUKT2 69 KV 514977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-026 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SW_5TH_4__CLASSEN4 | 3 Phase fault SW 5TH 4 (514920) 138 kV Bus a. Apply fault at the SW 5TH 4 (514920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW 5TH 4 138 KV 514920 TO CLASSEN4 138 KV 514922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SW_64TH2__PENN___2 | 3 Phase fault SW 64TH2 (514918) 69 kV Bus a. Apply fault at the SW 64TH2 (514918) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW 64TH2 69 KV 514918 TO PENN 2 69 KV 514924 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SW_SHV_4__FLOURNY4 | 3 Phase fault SW SHV 4 (507759) 138 kV Bus a. Apply fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENMOTR4 138 KV 507732 TO SW SHV 4 138 KV 507759 CKT 1 b.2. FLOURNY4 138 KV 507727 TO GENMOTR4 138 KV 507732 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SW_SHV_4__LEASIDE_4 | 3 Phase fault SW SHV 4 (507759) 138 kV Bus a. Apply fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW SHV 4 138 KV 507759 TO LEASIDE 4 138 KV 507793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SW_SHV_4__ROKHILL4 | 3 Phase fault SW SHV 4 (507759) 138 kV Bus a. Apply fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRIDGE4 138 KV 507757 TO SW SHV 4 138 KV 507759 CKT 1 b.2. SPRIDGE4 138 KV 507757 TO WLNTSPRINGS4 138 KV 509103 CKT 1 b.3. LOAD 1 509103 b.4. ROKHILL4 138 KV 509083 TO WLNTSPRINGS4 138 KV 509103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SW_SHV_7__DIANA__7 | 3 Phase fault SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345 KV 507760 TO DIANA 7 345 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SW_SHV_7__LONGWD_7 | 3 Phase fault SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345 KV 507760 TO LONGWD 7 345 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_S_SHV__4__CEDARGR4 | 3 Phase fault S SHV 4 (507755) 138 kV Bus a. Apply fault at the S SHV 4 (507755) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138 KV 507755 TO CEDARGR4 138 KV 507771 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_S_SHV__4__SW_SHV_4 | 3 Phase fault S SHV 4 (507755) 138 kV Bus a. Apply fault at the S SHV 4 (507755) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138 KV 507755 TO SW SHV 4 138 KV 507759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_S_SHV__4__WALLAKE4 | 3 Phase fault S SHV 4 (507755) 138 kV Bus a. Apply fault at the S SHV 4 (507755) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138 KV 507755 TO WALLAKE4 138 KV 507765 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_S_SHV__4__WESTELC4 | 3 Phase fault S SHV 4 (507755) 138 kV Bus a. Apply fault at the S SHV 4 (507755) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138 KV 507755 TO WESTELC4 138 KV 507767 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TCONCO_CEMRD_TP4 | 3 Phase fault T-CONCO4 (511424) 138 kV Bus a. Apply fault at the T-CONCO4 (511424) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T-CONCO4 138 KV 511424 TO CEMRD_TP4 138 KV 511576 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_T.NO._46STTP4 | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO 46ST-TP-4 138 KV 509900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_T.NO._BARNSAL4 | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO SKIATOK4 138 KV 509884 CKT 1 b.2. LOAD 1 509884 b.3. SKIATOK4 138 KV 509884 TO BARNSAL4 138 KV 510388 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_T.NO._CDC-ET4 | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO CDC-ET 4 138 KV 509839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_T.NO._CDC-WT4 | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO CDC-WT 4 138 KV 509842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_T.NO._NES | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO N.E.S.-4 138 KV 510396 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_T.NO._OWASOTP | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO OWASOTP4 138 KV 509844 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_T.NO._P&PWTP4 | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO P&P WTP4 138 KV 509851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_T.NO._TNO24 | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO T.NO.2-4 138 KV 509895 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_T.NO._CLEVLND7 | 3 Phase fault T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345 KV 509852 TO CLEVLND7 345 KV 512694 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-028 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-028 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_T.NO._IGLOOV7 | 3 Phase fault T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345 KV 509852 TO IGLOOV 7 345 KV 513596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-028 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-028 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_T.NO._NES7 | 3 Phase fault T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345 KV 509852 TO N.E.S.-7 345 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_T.NO.2_GEN-2018-028 | 3 Phase fault T.NO.2-4 (509895) 138 kV Bus a. Apply fault at the T.NO.2-4 (509895) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.2-4 138 KV 509895 TO GEN-2018-028 138 KV 762636 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_T.P.S._52DELWT | 3 Phase fault T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138 KV 509788 TO 52DELWT4 138 KV 509814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_T.P.S._CARSN-T4 | 3 Phase fault T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 36&OLY-4 138 KV 509724 TO T.P.S.-4 138 KV 509788 CKT 1 b.2. LOAD 1 509788 b.3. 36&OLY-4 138 KV 509724 TO CARSN-T4 138 KV 509739 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_T.P.S._GEN-2018-027 | 3 Phase fault T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138 KV 509788 TO GEN-2018-027 138 KV 762625 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_T.P.S._OAKSETP4 | 3 Phase fault T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138 KV 509788 TO OAKSETP4 138 KV 509850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_T.P.S._OAKSWTP4 | 3 Phase fault T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138 KV 509788 TO OAKSWTP4 138 KV 509848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_T.P.S._SAPLPRD | 3 Phase fault T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138 KV 509788 TO 72ELWOD4 138 KV 509888 CKT 1 b.2. LOAD 1 509888 b.3. SAPLPRD4 138 KV 509871 TO 72ELWOD4 138 KV 509888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_T.S.E._21STTAP4 | 3 Phase fault T.S.E.-4 (509811) 138 kV Bus a. Apply fault at the T.S.E.-4 (509811) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.S.E.-4 138 KV 509811 TO 21STTAP4 138 KV 509828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_T.S.E._E61ST | 3 Phase fault T.S.E.-4 (509811) 138 kV Bus a. Apply fault at the T.S.E.-4 (509811) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.S.E.-4 138 KV 509811 TO E.61ST-4 138 KV 509831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_T.S.E._KENSHETP4 | 3 Phase fault T.S.E.-4 (509811) 138 kV Bus a. Apply fault at the T.S.E.-4 (509811) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.S.E.-4 138 KV 509811 TO KENSH-E-TP4 138 KV 509830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_T.S.E._SHUD4 | 3 Phase fault T.S.E.-4 (509811) 138 kV Bus a. Apply fault at the T.S.E.-4 (509811) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.S.E.-4 138 KV 509811 TO S.HUD.-4 138 KV 509833 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TAHLQH_5__BRIGSKM_5 | 3 Phase fault TAHLQH 5 (512655) 161 kV Bus a. Apply fault at the TAHLQH 5 (512655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 161 KV 512655 TO BRIGSKM 5 161 KV 513044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TAHLQH_5__HWY59TP5 | 3 Phase fault TAHLQH 5 (512655) 161 kV Bus a. Apply fault at the TAHLQH 5 (512655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 161 KV 512655 TO HWY59TP5 161 KV 515527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TALOGA_2__HMBTTP | 3 Phase fault TALOGA 2 (521064) 69 kV Bus a. Apply fault at the TALOGA 2 (521064) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STALOGA2 69 KV 520454 TO TALOGA 2 69 KV 521064 CKT 1 b.2. STALOGA2 69 KV 520454 TO PUTNAM 2 69 KV 521033 CKT 1 b.3. LOAD 1 521033 b.4. HM-BTTP2 69 KV 520942 TO PUTNAM 2 69 KV 521033 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TALOGA_2__WOODWRD2 | 3 Phase fault TALOGA 2 (521064) 69 kV Bus a. Apply fault at the TALOGA 2 (521064) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALOGA 2 69 KV 521064 TO VICI 2 69 KV 521082 CKT 1 b.2. LOAD 1 521082 b.3. VICI 2 69 KV 521082 TO WOODWRD2 69 KV 521096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TALOGA_4__MOORLND4 | 3 Phase fault TALOGA 4 (521065) 138 kV Bus a. Apply fault at the TALOGA 4 (521065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEILING4 138 KV 520553 TO TALOGA 4 138 KV 521065 CKT 1 b.2. SEILING4 138 KV 520553 TO MOORLND4 138 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TATONGA7__CRSRDSW7 | 3 Phase fault TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345 KV 515407 TO CRSRDSW7 345 KV 515448 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TATONGA7__MAMTHPW7 | 3 Phase fault TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345 KV 515407 TO MAMTHPW7 345 KV 515585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TATONGA7__MATHWSN7 | 3 Phase fault TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345 KV 515407 TO MATHWSN7 345 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TATONGA7__SLNGWND7 | 3 Phase fault TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345 KV 515407 TO SLNGWND7 345 KV 515582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TAYLOR_2__TEX39ST2 | 3 Phase fault TAYLOR 2 (508083) 69 kV Bus a. Apply fault at the TAYLOR 2 (508083) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 2 69 KV 508083 TO TEX39ST2 69 KV 508085 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TAYLOR_2__TEXARK_2 | 3 Phase fault TAYLOR 2 (508083) 69 kV Bus a. Apply fault at the TAYLOR 2 (508083) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 2 69 KV 508083 TO TEXARK 2 69 KV 508086 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TECUMSH2__FRSTHIL2 | 3 Phase fault TECUMSH2 (515071) 69 kV Bus a. Apply fault at the TECUMSH2 (515071) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECUMSH2 69 KV 515071 TO FRSTHIL2 69 KV 515074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TENESTP4__84TH_ST4 | 3 Phase fault TENESTP4 (514837) 138 kV Bus a. Apply fault at the TENESTP4 (514837) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TENESTP4 138 KV 514837 TO 84TH ST4 138 KV 514843 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TERNIT_TERNITP4 | 3 Phase fault TER-NIT4 (509723) 138 kV Bus a. Apply fault at the TER-NIT4 (509723) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TER-NIT4 138 KV 509723 TO PCATOSA4 138 KV 509725 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TERNIT_TERNITP4 | 3 Phase fault TER-NIT4 (509723) 138 kV Bus a. Apply fault at the TER-NIT4 (509723) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TER-NIT4 138 KV 509723 TO TERNITP4 138 KV 509835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TERNITP4__VERDIGS4 | 3 Phase fault TERNITP4 (509835) 138 kV Bus a. Apply fault at the TERNITP4 (509835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERNITP4 138 KV 509835 TO VERDIGS4 138 KV 509854 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TERRYRD7__G17_171_TAP | 3 Phase fault TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345 KV 511568 TO G17-171-TAP 345 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TERRYRD7__RSHSPR1_MPT1 | 3 Phase fault TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345 KV 511568 TO RSHSPR1_MPT1 345 KV 511979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TERRYRD7__RUSHSPR7 | 3 Phase fault TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345 KV 511568 TO RUSHSPR7 345 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TERRYRD7__SUNNYSD7 | 3 Phase fault TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345 KV 511568 TO SUNNYSD7 345 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TEXARK_2__IPC_TAP2 | 3 Phase fault TEXARK 2 (508086) 69 kV Bus a. Apply fault at the TEXARK 2 (508086) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S_TEXARK 2 69 KV 504117 TO PLEASHL2 69 KV 508048 CKT 1 b.2. LOAD 1 508048 b.3. S_TEXARK 2 69 KV 504117 TO TEXARK 2 69 KV 508086 CKT 1 b.4. LOAD 1 508086 b.5. PLEASHL2 69 KV 508048 TO IPC TAP2 69 KV 508058 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_THISTLE7__GEN_2017-018 | 3 Phase fault THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345 KV 539801 TO GEN-2017-018 345 KV 588630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_THISTLE7__GEN-2018-049 | 3 Phase fault THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345 KV 539801 TO GEN-2018-049 345 KV 762834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TINKER54__BARNES_4 | 3 Phase fault TINKER54 (514994) 138 kV Bus a. Apply fault at the TINKER54 (514994) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TINKER54 138 KV 514994 TO BARNES 4 138 KV 515003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TOLK_______6__TUCO_INT___6 | 3 Phase fault TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230 KV 525531 TO TUCO_INT 6 230 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TROSPER4__RENO___4 | 3 Phase fault TROSPER4 (514963) 138 kV Bus a. Apply fault at the TROSPER4 (514963) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROSPER4 138 KV 514963 TO RENO 4 138 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MINCO5G11 trips on voltage protection settings | Disabling voltage protection settings for MINCO5G11 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TUCO_INT___6__ANTELOPE_1_6 | 3 Phase fault TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230 KV 525830 TO ANTELOPE_1 6 230 KV 525840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TUCO_INT___6__CARLISLE___6 | 3 Phase fault TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230 KV 525830 TO CARLISLE 6 230 KV 526161 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TUCO_INT___6__HALE_WNDCL16 | 3 Phase fault TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230 KV 525830 TO HALE_WNDCL16 230 KV 525957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TUCO_INT___6__JONES______6 | 3 Phase fault TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230 KV 525830 TO JONES 6 230 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TUCO_INT___7__ELK_CT1 | 3 Phase fault TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345 KV 525832 TO ELK_CT1 345 KV 525850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TUCO_INT___7__G17 | 3 Phase fault TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345 KV 525832 TO G17-151TAP 345 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TUCO_INT___7__YOAKUM_345 | 3 Phase fault TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345 KV 525832 TO YOAKUM_345 345 KV 526936 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TURCRK_2__TURCRKT2 | 3 Phase fault TURCRK 2 (514735) 69 kV Bus a. Apply fault at the TURCRK 2 (514735) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURCRK 2 69 KV 514735 TO TURCRKT2 69 KV 515517 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TURK___3__HOPE___3 | 3 Phase fault TURK 3 (507456) 115 kV Bus a. Apply fault at the TURK 3 (507456) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCNAB 3 115 KV 504122 TO TURK 3 115 KV 507456 CKT 1 b.2. MCNAB 3 115 KV 504122 TO HOPE 3 115 KV 507453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TURK___4__MANDEVILTP4 | 3 Phase fault TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 4 138 KV 507454 TO MANDEVILTP4 138 KV 508105 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TURK___4__SUGARHL4 | 3 Phase fault TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 4 138 KV 507454 TO SUGARHL4 138 KV 508080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TURK___7__NWTXARK7 | 3 Phase fault TURK 7 (507455) 345 kV Bus a. Apply fault at the TURK 7 (507455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURK 7 345 KV 507455 TO NWTXARK7 345 KV 508072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TUTCONT4__CEMRD_TP4 | 3 Phase fault TUTCONT4 (511425) 138 kV Bus a. Apply fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTCONT4 138 KV 511425 TO CEMRD_TP4 138 KV 511576 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TUTCONT4__CIMARON4 | 3 Phase fault TUTCONT4 (511425) 138 kV Bus a. Apply fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTCONT4 138 KV 511425 TO CIMARON4 138 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TUTCONT4__LEONARD4 | 3 Phase fault TUTCONT4 (511425) 138 kV Bus a. Apply fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTCONT4 138 KV 511425 TO TUTTLE4 138 KV 511501 CKT 1 b.2. LOAD 1 511501 b.3. TUTTLE4 138 KV 511501 TO LEONARD4 138 KV 511575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TUTTLE_4__TUTLETP4 | 3 Phase fault TUTTLE 4 (520496) 138 kV Bus a. Apply fault at the TUTTLE 4 (520496) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTTLE 4 138 KV 520496 TO TUTLETP4 138 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TWNLKJT4__TWNLKSW4 | 3 Phase fault TWNLKJT4 (520847) 138 kV Bus a. Apply fault at the TWNLKJT4 (520847) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWNLKJT4 138 KV 520847 TO TWNLKSW4 138 KV 521073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TXPLSTE2__TXPLSTP2 | 3 Phase fault TXPLSTE2 (514989) 69 kV Bus a. Apply fault at the TXPLSTE2 (514989) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXPLSTE2 69 KV 514989 TO TXPLSTP2 69 KV 515516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TXSTELA2__LITLAXT2 | 3 Phase fault TXSTELA2 (514985) 69 kV Bus a. Apply fault at the TXSTELA2 (514985) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXSTELA2 69 KV 514985 TO LITLAXT2 69 KV 515502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TXSTELA2__TXPLSTP2 | 3 Phase fault TXSTELA2 (514985) 69 kV Bus a. Apply fault at the TXSTELA2 (514985) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXSTELA2 69 KV 514985 TO TXPLSTP2 69 KV 515516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_VWEYCO4_VALIANT4 | 3 Phase fault V-WEYCO4 (510866) 138 kV Bus a. Apply fault at the V-WEYCO4 (510866) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. V-WEYCO4 138 KV 510866 TO VALIANT4 138 KV 510918 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_VALIANT4__B.BOWTP4 | 3 Phase fault VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IDABEL-4 138 KV 510886 TO VALIANT4 138 KV 510918 CKT 1 b.2. IDABEL-4 138 KV 510886 TO B.BOWTP4 138 KV 510888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_VALIANT4__HUGO_PP4 | 3 Phase fault VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 138 KV 510918 TO HUGO PP4 138 KV 520948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_VALIANT7__HUGO___7 | 3 Phase fault VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345 KV 510911 TO HUGO 7 345 KV 521157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_VANCE__2__SO4TH__2 | 3 Phase fault VANCE 2 (514718) 69 kV Bus a. Apply fault at the VANCE 2 (514718) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANCE 2 69 KV 514718 TO SO4TH 2 69 KV 514730 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_VANOSS_4__PARKLN_4 | 3 Phase fault VANOSS 4 (515174) 138 kV Bus a. Apply fault at the VANOSS 4 (515174) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANOSS 4 138 KV 515174 TO PARKLN 4 138 KV 515178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_VANOSS_4__VANOSTP4 | 3 Phase fault VANOSS 4 (515174) 138 kV Bus a. Apply fault at the VANOSS 4 (515174) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANOSS 4 138 KV 515174 TO VANOSTP4 138 KV 515531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_VINITA_VINITAJC2 | 3 Phase fault VINITA-2 (510404) 69 kV Bus a. Apply fault at the VINITA-2 (510404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINITA-2 69 KV 510404 TO VINTAJC2 69 KV 510418 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_VINTAJC4__ALWUETP4 | 3 Phase fault VINTAJC4 (510417) 138 kV Bus a. Apply fault at the VINTAJC4 (510417) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC4 138 KV 510417 TO ALWUETP4 138 KV 510429 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_VINTAJC4__HOC404_4 | 3 Phase fault VINTAJC4 (510417) 138 kV Bus a. Apply fault at the VINTAJC4 (510417) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC4 138 KV 510417 TO HOC404 4 138 KV 547486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_W.ED._CARSONT4 | 3 Phase fault W.ED.-W4 (509832) 138 kV Bus a. Apply fault at the W.ED.-W4 (509832) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W.ED.-W4 138 KV 509832 TO CARSONT4 138 KV 509865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WARNTAP4__77MEMW4 | 3 Phase fault WARNTAP4 (509858) 138 kV Bus a. Apply fault at the WARNTAP4 (509858) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 96YALE-4 138 KV 509847 TO WARNTAP4 138 KV 509858 CKT 1 b.2. 77MEM-W4 138 KV 509766 TO 96YALE-4 138 KV 509847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-141 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-141 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WARWICK4__BELLCOW4 | 3 Phase fault WARWICK4 (515047) 138 kV Bus a. Apply fault at the WARWICK4 (515047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARWICK4 138 KV 515047 TO BELLCOW4 138 KV 515369 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WARWICK4__TRYON_4 | 3 Phase fault WARWICK4 (515047) 138 kV Bus a. Apply fault at the WARWICK4 (515047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARWICK4 138 KV 515047 TO TRYON 4 138 KV 515675 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WARWICK4__WFROSST4 | 3 Phase fault WARWICK4 (515047) 138 kV Bus a. Apply fault at the WARWICK4 (515047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARWICK4 138 KV 515047 TO WFROSST4 138 KV 515366 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WASHITA4__BINGERJ4 | 3 Phase fault WASHITA4 (521089) 138 kV Bus a. Apply fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEY 4 138 KV 521017 TO WASHITA4 138 KV 521089 CKT 1 b.2. BINGERJ4 138 KV 520827 TO ONEY 4 138 KV 521017 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WASHITA4__SLKHILLS_4 | 3 Phase fault WASHITA4 (521089) 138 kV Bus a. Apply fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 138 KV 521089 TO SLKHILLS 4 138 KV 521103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WATLANT4__CASSTP4 | 3 Phase fault WATLANT4 (508090) 138 kV Bus a. Apply fault at the WATLANT4 (508090) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138 KV 508090 TO CASSTP4 138 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WATLANT4__WILKES_4 | 3 Phase fault WATLANT4 (508090) 138 kV Bus a. Apply fault at the WATLANT4 (508090) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138 KV 508090 TO WILKES 4 138 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WATNGSW4__CALUMET4 | 3 Phase fault WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138 KV 520536 TO CALUMET4 138 KV 520839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WATNGSW4__FAY____4 | 3 Phase fault WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138 KV 520536 TO WATONGA4 138 KV 521091 CKT 1 b.2. LOAD 1 521091 b.3. FAY 4 138 KV 520538 TO WATONGA4 138 KV 521091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WATNGSW4__KGFSHSW4 | 3 Phase fault WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138 KV 520536 TO OMEGA 4 138 KV 520964 CKT 1 b.2. LOAD 1 520964 b.3. PARKCOM4 138 KV 520475 TO OMEGA 4 138 KV 520964 CKT 1 b.4. LOAD 1 520964 b.5. PARKCOM4 138 KV 520475 TO KGFSHSW4 138 KV 520533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WATNGSW4__OKEENE_4 | 3 Phase fault WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138 KV 520536 TO OKEENE 4 138 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WAUKOTP4__HENESEY4 | 3 Phase fault WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 138 KV 514710 TO HENESEY4 138 KV 514774 CKT 1 b.2. LOAD 1 514774 b.3. WAUKOMI4 138 KV 514710 TO WAUKOTP4 138 KV 514711 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WAUKOTP4__SO4TH__4 | 3 Phase fault WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138 KV 514711 TO SO4TH 4 138 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WAUKOTP4__WOODRNG4 | 3 Phase fault WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138 KV 514711 TO WOODRNG4 138 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WCITYTP2__VALIANT2 | 3 Phase fault WCITYTP2 (510870) 69 kV Bus a. Apply fault at the WCITYTP2 (510870) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WCITYTP2 69 KV 510870 TO VALIANT2 69 KV 510910 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WED_CARSON4 | 3 Phase fault WED-TAP4 (509823) 138 kV Bus a. Apply fault at the WED-TAP4 (509823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WED-TAP4 138 KV 509823 TO CARSONT4 138 KV 509865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WEKIWA_GEN_2010_055 | 3 Phase fault WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138 KV 509757 TO GEN-2010-055 138 KV 560389 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WEKIWA_P&PWTP4 | 3 Phase fault WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138 KV 509757 TO P&P WTP4 138 KV 509851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WEKIWA_SS4 | 3 Phase fault WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEFFD-4 138 KV 509812 TO S.S.---4 138 KV 509815 CKT 1 b.2. LOAD 1 509815 b.3. WEKIWA-4 138 KV 509757 TO SHEFFD-4 138 KV 509812 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2015-066 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WEKIWA_SHEFFD | 3 Phase fault WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138 KV 509757 TO SHEFFD-4 138 KV 509812 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2015-066 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WEKIWA_SILCTYGR4 | 3 Phase fault WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138 KV 509757 TO SILVCTYGR4 138 KV 512726 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WEKIWA_WEDTAP4 | 3 Phase fault WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138 KV 509757 TO WED-TAP4 138 KV 509823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WEKIWA_SAPLPRD | 3 Phase fault WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345 KV 509755 TO SAPLPRD7 345 KV 509870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WEKIWA_SOONER | 3 Phase fault WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345 KV 509755 TO SOONER 7 345 KV 514803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WEKIWA_TNO7 | 3 Phase fault WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345 KV 509755 TO T.NO.--7 345 KV 509852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MINCO5 trips on voltage protection settings | Disabling voltage protection settings for MINCO5 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WELLSPA2__ONAPA__2 | 3 Phase fault WELLSPA2 (515215) 69 kV Bus a. Apply fault at the WELLSPA2 (515215) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELLSPA2 69 KV 515215 TO ONAPA 2 69 KV 521020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WELSHRE4__WILKES_4 | 3 Phase fault WELSHRE4 (508355) 138 kV Bus a. Apply fault at the WELSHRE4 (508355) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELSHRE4 138 KV 508355 TO WILKES 4 138 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WELSH__7__DIANA__7 | 3 Phase fault WELSH 7 (508359) 345 kV Bus a. Apply fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345 KV 508359 TO DIANA 7 345 KV 508832 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WELSH__7__WILKES_7 | 3 Phase fault WELSH 7 (508359) 345 kV Bus a. Apply fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345 KV 508359 TO WILKES 7 345 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WESTELC4__LEASIDE_4 | 3 Phase fault WESTELC4 (507767) 138 kV Bus a. Apply fault at the WESTELC4 (507767) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTELC4 138 KV 507767 TO LEASIDE 4 138 KV 507793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WESTERN4__STNWAL_4 | 3 Phase fault WESTERN4 (514869) 138 kV Bus a. Apply fault at the WESTERN4 (514869) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTERN4 138 KV 514869 TO STNWAL 4 138 KV 514870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WESTHSE4__INDNHIL4 | 3 Phase fault WESTHSE4 (514904) 138 kV Bus a. Apply fault at the WESTHSE4 (514904) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTHSE4 138 KV 514904 TO INDNHIL4 138 KV 514954 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFROSST4__LINCOLN4 | 3 Phase fault WFROSST4 (515366) 138 kV Bus a. Apply fault at the WFROSST4 (515366) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WFROSST4 138 KV 515366 TO LINCOLN4 138 KV 515442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFROSST4__RSSVILE4 | 3 Phase fault WFROSST4 (515366) 138 kV Bus a. Apply fault at the WFROSST4 (515366) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WFROSST4 138 KV 515366 TO RSSVILE4 138 KV 521107 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WHEELER____3__HOWARD_____3 | 3 Phase fault WHEELER 3 (523776) 115 kV Bus a. Apply fault at the WHEELER 3 (523776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 3 115 KV 523776 TO HOWARD 3 115 KV 523797 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WHEELER____6__STLN | 3 Phase fault WHEELER 6 (523777) 230 kV Bus a. Apply fault at the WHEELER 6 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 230 KV 523777 TO STLN-DEMARC6 230 KV 523779 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WHIRLPO4__CDC | 3 Phase fault WHIRLPO4 (509840) 138 kV Bus a. Apply fault at the WHIRLPO4 (509840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHIRLPO4 138 KV 509840 TO CDC-WT 4 138 KV 509842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WHITNEY4__EASTEX_4 | 3 Phase fault WHITNEY4 (508575) 138 kV Bus a. Apply fault at the WHITNEY4 (508575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY4 138 KV 508575 TO EASTEX 4 138 KV 508582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WHORSE_HWY20 | 3 Phase fault WHORSE-4 (509754) 138 kV Bus a. Apply fault at the WHORSE-4 (509754) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHORSE-4 138 KV 509754 TO HWY20-T4 138 KV 509821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WILKES_4__CHAPELH4 | 3 Phase fault WILKES 4 (508840) 138 kV Bus a. Apply fault at the WILKES 4 (508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPELH4 138 KV 508337 TO WELSHRE4 138 KV 508355 CKT 1 b.2. LOAD 1 508355 b.3. WELSHRE4 138 KV 508355 TO WILKES 4 138 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WINDFRM4__MOORLND4 | 3 Phase fault WINDFRM4 (515785) 138 kV Bus a. Apply fault at the WINDFRM4 (515785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 138 KV 515785 TO MOORLND4 138 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WLNUTCK4__PAOLI | 3 Phase fault WLNUTCK4 (515097) 138 kV Bus a. Apply fault at the WLNUTCK4 (515097) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WLNUTCK4 138 KV 515097 TO PAOLI- 4 138 KV 515100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WODWRD_2__WOODWRD2 | 3 Phase fault WODWRD 2 (514782) 69 kV Bus a. Apply fault at the WODWRD 2 (514782) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WODWRD 2 69 KV 514782 TO WOODWRD2 69 KV 521096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WOLFCRK4__CHEEKTP4 | 3 Phase fault WOLFCRK4 (515143) 138 kV Bus a. Apply fault at the WOLFCRK4 (515143) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK4 138 KV 515143 TO CHEEKTP4 138 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WOLVERN4__WOLVRNT4 | 3 Phase fault WOLVERN4 (515056) 138 kV Bus a. Apply fault at the WOLVERN4 (515056) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLVERN4 138 KV 515056 TO WOLVRNT4 138 KV 515532 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WOODRNG4__MARSHL_4 | 3 Phase fault WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 138 KV 514714 TO MARSHL 4 138 KV 514733 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WOODRNG7__GEN-2017-164 | 3 Phase fault WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345 KV 514715 TO GEN-2017-164 345 KV 762321 CKT 1 | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WOODRNG7__HUNTERS7 | 3 Phase fault WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345 KV 514715 TO HUNTERS7 345 KV 515476 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WOODRNG7__PINTAIL7 | 3 Phase fault WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345 KV 514715 TO PINTAIL7 345 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WOODRNG7__REDNGTN7 | 3 Phase fault WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345 KV 514715 TO REDNGTN7 345 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WOODRNG7__SKELTON7 | 3 Phase fault WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345 KV 514715 TO SKELTON7 345 KV 515990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WOODWRD2__CRTSJCT2 | 3 Phase fault WOODWRD2 (521096) 69 kV Bus a. Apply fault at the WOODWRD2 (521096) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD2 69 KV 521096 TO CRTSJCT2 69 KV 521197 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WOODWRD2__FARGOJCT2 | 3 Phase fault WOODWRD2 (521096) 69 kV Bus a. Apply fault at the WOODWRD2 (521096) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD2 69 KV 521096 TO FARGOJCT2 69 KV 521196 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WOODWRD4__CENT___4 | 3 Phase fault WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138 KV 514785 TO CENT 4 138 KV 515363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WOODWRD4__WINDFRM4 | 3 Phase fault WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138 KV 514785 TO WINDFRM4 138 KV 515785 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WOODWRD4__WWRDEHV4 | 3 Phase fault WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138 KV 514785 TO WWRDEHV4 138 KV 515376 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WRNMED_WRNMEDT4 | 3 Phase fault WRN-MED4 (509729) 138 kV Bus a. Apply fault at the WRN-MED4 (509729) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRN-MED4 138 KV 509729 TO WRNMEDT4 138 KV 509764 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WRNMEDT4__81YALTP4 | 3 Phase fault WRNMEDT4 (509764) 138 kV Bus a. Apply fault at the WRNMEDT4 (509764) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRNMEDT4 138 KV 509764 TO 81YALTP4 138 KV 509809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WRNMEDT4__S.HUD. | 3 Phase fault WRNMEDT4 (509764) 138 kV Bus a. Apply fault at the WRNMEDT4 (509764) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRNMEDT4 138 KV 509764 TO S.HUD.-4 138 KV 509833 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WWRDEHV4__KEENAN_4 | 3 Phase fault WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138 KV 515376 TO KEENAN 4 138 KV 515394 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WWRDEHV4__OUSPRT_4 | 3 Phase fault WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138 KV 515376 TO OUSPRT 4 138 KV 515398 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WWRDEHV4__REDCLFT4 | 3 Phase fault WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IODINE-4 138 KV 514796 TO WWRDEHV4 138 KV 515376 CKT 1 b.2. IODINE-4 138 KV 514796 TO REDCLFT4 138 KV 515533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WWRDEHV4__WWDPST_4 | 3 Phase fault WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138 KV 515376 TO WWDPST 4 138 KV 515425 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WWRDEHV7__BECKHAM7 | 3 Phase fault WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345 KV 515375 TO BECKHAM7 345 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WWRDEHV7__DGRASSE7 | 3 Phase fault WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345 KV 515375 TO DGRASSE7 345 KV 515852 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WWRDEHV7__G07621119 | 3 Phase fault WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345 KV 515375 TO G07621119-20 345 KV 515599 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WWRDEHV7__G16 | 3 Phase fault WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345 KV 515375 TO G16-003-TAP 345 KV 560071 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WWRDEHV7__GUTHRIE7 | 3 Phase fault WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345 KV 515375 TO GUTHRIE7 345 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WWRDEHV7__TATONGA7 | 3 Phase fault WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345 KV 515375 TO TATONGA7 345 KV 515407 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_YARCH_YARCHT4 | 3 Phase fault YARCH-N4 (509825) 138 kV Bus a. Apply fault at the YARCH-N4 (509825) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YARCH-N4 138 KV 509825 TO YARCHT 4 138 KV 509862 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_YARCH_PPTAP | 3 Phase fault YARCH-S4 (509824) 138 kV Bus a. Apply fault at the YARCH-S4 (509824) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YARCH-S4 138 KV 509824 TO KENSH-E-TP4 138 KV 509830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_YARCHT_4__PPTAP__4 | 3 Phase fault YARCHT 4 (509862) 138 kV Bus a. Apply fault at the YARCHT 4 (509862) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YARCHT 4 138 KV 509862 TO PPTAP 4 138 KV 509863 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_YOAKUM_345__HOBBS_INT__7 | 3 Phase fault YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345 KV 526936 TO HOBBS_INT 7 345 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ZUNIS_FULTONW4 | 3 Phase fault ZUNIS-N4 (509827) 138 kV Bus a. Apply fault at the ZUNIS-N4 (509827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ZUNIS-N4 138 KV 509827 TO FULTONW4 138 KV 509829 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_38TH_ST2__514846 | 3 Phase fault 38TH ST2 (514845) 69 kV Bus a. Apply fault at the 38TH ST2 (514845) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 38TH ST2 514845 TO 38TH ST4 514846 TO 38TH ST1 515768 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-026 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_4MURFBORO__337673 | 3 Phase fault 4MURFBORO (337672) 138 kV Bus a. Apply fault at the 4MURFBORO (337672) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MURFBORO 337672 TO 3MURFBORO.S! 337673 TO 1MURFBORO 337671 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_5TRIBES2__515228 | 3 Phase fault 5TRIBES2 (515227) 69 kV Bus a. Apply fault at the 5TRIBES2 (515227) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TRIBES2 515227 TO 5TRIBES5 515228 TO 5TRIBES1 515723 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_8ANO%__337912 | 3 Phase fault 8ANO% (337909) 500 kV Bus a. Apply fault at the 8ANO% (337909) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 337909 TO 5ANO% 337912 TO 1ANO AUX 337913 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_8EL_DORADO%__337539 | 3 Phase fault 8EL DORADO% (337561) 500 kV Bus a. Apply fault at the 8EL DORADO% (337561) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 337561 TO 3EL DORADO! 337539 TO 1EL DORADO3 337566 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_8EL_DORADO%__337562 | 3 Phase fault 8EL DORADO% (337561) 500 kV Bus a. Apply fault at the 8EL DORADO% (337561) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 337561 TO 7EL DORADO 337562 TO 1EL DORADO2 337565 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_8STERLING%__337415 | 3 Phase fault 8STERLING% (337420) 500 kV Bus a. Apply fault at the 8STERLING% (337420) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8STERLING% 337420 TO 3STERLING% 337415 TO 1STERLING3 337412 CKT 3 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AGENCY_2__515230 | 3 Phase fault AGENCY 2 (515229) 69 kV Bus a. Apply fault at the AGENCY 2 (515229) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AGENCY 2 515229 TO AGENCY 5 515230 TO AGENCY 1 515701 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ANADARK4__520810 | 3 Phase fault ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 520814 TO ANADARK2 520810 TO ADRKTERT 521181 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ARCADIA4__514908 | 3 Phase fault ARCADIA4 (514907) 138 kV Bus a. Apply fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 514907 TO ARCADIA7 514908 TO ARCADI31 515704 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ARSHILL2__507711 | 3 Phase fault ARSHILL2 (507710) 69 kV Bus a. Apply fault at the ARSHILL2 (507710) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL2 507710 TO ARSHILL4 507711 TO ARSH2-1 507714 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BANN___2__508054 | 3 Phase fault BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 508053 TO BANN 4 508054 TO BANN1-1 508097 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BEELINE2__515247 | 3 Phase fault BEELINE2 (515246) 69 kV Bus a. Apply fault at the BEELINE2 (515246) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEELINE2 515246 TO BEELINE4 515247 TO BEELINE1 515705 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BLUEBEL2__515242 | 3 Phase fault BLUEBEL2 (515241) 69 kV Bus a. Apply fault at the BLUEBEL2 (515241) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBEL2 515241 TO BLUEBEL4 515242 TO BLUEBEL1 515706 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BRISTOW2__515035 | 3 Phase fault BRISTOW2 (515034) 69 kV Bus a. Apply fault at the BRISTOW2 (515034) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW2 515034 TO BRISTOW4 515035 TO BRISTOW1 515709 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_BV_XFMR | 3 Phase fault BV-COM-2 (510389) 69 kV Bus a. Apply fault at the BV-COM-2 (510389) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BV-COM-2 510389 TO BV-COM-4 510390 TO BVCOM3-1 510372 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CRIVER_XFMR | 3 Phase fault C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 515422 TO C-RIVER4 510946 TO C-RIVER1 510947 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-140 trips on frequency protection settings | Disabling frequency protection settings for GEN-2017-140 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CANADNS4__520841 | 3 Phase fault CANADNS4 (520842) 138 kV Bus a. Apply fault at the CANADNS4 (520842) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 520842 TO CANADNS2 520841 TO CANTERT 521164 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CATOOSA2__509790 | 3 Phase fault CATOOSA2 (509799) 69 kV Bus a. Apply fault at the CATOOSA2 (509799) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA2 509799 TO CATOOSA4 509790 TO CATOO1-1 509867 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CATSAGR5__509790 | 3 Phase fault CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 512638 TO CATOOSA4 509790 TO 512835 CKT 3 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CHAMSPR5__506945 | 3 Phase fault CHAMSPR5 (506944) 161 kV Bus a. Apply fault at the CHAMSPR5 (506944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAMSPR5 506944 TO CHAMSPR7 506945 TO CHAMSPR1 506919 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CHISHOLM6__511553 | 3 Phase fault CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6 (511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CIMARON4__514901 | 3 Phase fault CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 514898 TO CIMARON7 514901 TO CIMARO21 515715 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MINCO5 trips on voltage protection settings | Disabling voltage protection settings for MINCO5 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CLARMR_5__512679 | 3 Phase fault CLARMR 5 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 512651 TO CLARMR 2 512679 TO CLARMR2 512815 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CLARMR_5__512707 | 3 Phase fault CLARMR 5 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 512651 TO CLARMR 4 512707 TO CLARMR4 512813 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CLEVLND7__512729 | 3 Phase fault CLEVLND7 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 512694 TO CLEVLND 4 512729 TO CLEVLND1 512817 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_COLINS_5__512705 | 3 Phase fault COLINS 5 (512627) 161 kV Bus a. Apply fault at the COLINS 5 (512627) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINS 5 512627 TO COLLINS4 512705 TO COLLIN1 1 512838 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_COLNSGR2__512627 | 3 Phase fault COLNSGR2 (512870) 69 kV Bus a. Apply fault at the COLNSGR2 (512870) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLNSGR2 512870 TO COLINS 5 512627 TO COLLIN3 1 512840 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_CORNVIL2__511449 | 3 Phase fault CORNVIL2 (511450) 69 kV Bus a. Apply fault at the CORNVIL2 (511450) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL2 511450 TO CORNVIL4 511449 TO CORNV2-1 511418 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DAWSON_XFMR | 3 Phase fault DAWSON-2 (509791) 69 kV Bus a. Apply fault at the DAWSON-2 (509791) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSON-2 509791 TO DAWSON-4 509792 TO DAWSN3-1 509877 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DELWARE4__510380 | 3 Phase fault DELWARE4 (510379) 138 kV Bus a. Apply fault at the DELWARE4 (510379) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELWARE4 510379 TO DELWARE7 510380 TO DELAWAR1 510370 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | CGENSUB2 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DEQUEEN2__507419 | 3 Phase fault DEQUEEN2 (507418) 69 kV Bus a. Apply fault at the DEQUEEN2 (507418) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEQUEEN2 507418 TO DEQUEEN4 507419 TO DQUEN1-1 507441 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DGRASSE4__515852 | 3 Phase fault DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 515853 TO DGRASSE7 515852 TO DGRASSE1 515854 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DIANA__4__508832 | 3 Phase fault DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 508831 TO DIANA 7 508832 TO DIANA-N1 508845 CKT 3 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DOVERSW4__520881 | 3 Phase fault DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 520882 TO DOVERSW2 520881 TO DVRTERT 521166 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_DRAPER_4__514934 | 3 Phase fault DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 514933 TO DRAPER 7 514934 TO DRAPER21 515792 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ELGINJT2__511486 | 3 Phase fault ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2 (511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ELKCTY_XFMR | 3 Phase fault ELKCTY-2 (511459) 69 kV Bus a. Apply fault at the ELKCTY-2 (511459) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-2 511459 TO ELKCTY-4 511458 TO ELKC4-1 511493 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ELKCTY_XFMR | 3 Phase fault ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 511458 TO ELKCITY6 511490 TO ELKC2-1 511482 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ELRENO_2__514819 | 3 Phase fault ELRENO 2 (514818) 69 kV Bus a. Apply fault at the ELRENO 2 (514818) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELRENO 2 514818 TO EL-RENO4 514819 TO EL RENO1 515722 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FLETCH_XFMR | 3 Phase fault FLETCH-4 (520912) 138 kV Bus a. Apply fault at the FLETCH-4 (520912) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCH-4 520912 TO FLETCHR2 520911 TO FLCHTERT 521168 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FLOURNY2__507727 | 3 Phase fault FLOURNY2 (507726) 69 kV Bus a. Apply fault at the FLOURNY2 (507726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 507726 TO FLOURNY4 507727 TO FLOURNY1 507740 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FRNKLNS4__520916 | 3 Phase fault FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRNKLNS4 520917 TO FRNKLNS2 520916 TO FRNKTERT 521169 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FRSTHIL2__515075 | 3 Phase fault FRSTHIL2 (515074) 69 kV Bus a. Apply fault at the FRSTHIL2 (515074) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRSTHIL2 515074 TO FRSTHIL4 515075 TO FRSTHIL1 515725 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FTSMITH7__515305 | 3 Phase fault FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 515302 TO FTSMITH8 515305 TO FTSMTH11 515726 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FTSMTHE5__515305 | 3 Phase fault FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5 (515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 515300 TO FTSMITH8 515305 TO FTSMTH31 515727 CKT 3 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FTSMTHW5__515302 | 3 Phase fault FTSMTHW5 (515301) 161 kV Bus a. Apply fault at the FTSMTHW5 (515301) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 515301 TO FTSMITH7 515302 TO FTSMTH51 515728 CKT 5 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_FTSMTHW5__515305 | 3 Phase fault FTSMTHW5 (515301) 161 kV Bus a. Apply fault at the FTSMTHW5 (515301) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 515301 TO FTSMITH8 515305 TO FTSMTH41 515791 CKT 4 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GORE___5__512644 | 3 Phase fault GORE 5 (505552) 161 kV Bus a. Apply fault at the GORE 5 (505552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 505552 TO GORE GR2 512644 TO GORTER1 512832 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRACMNT4__515800 | 3 Phase fault GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRAPEVINE__6__523770 | 3 Phase fault GRAPEVINE 6 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 523771 TO GRAPEVINE 3 523770 TO GRAPEVN_TR11 523769 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA1__5__512727 | 3 Phase fault GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 512656 TO GRDA1 2 512727 TO GRDA1 1 512816 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA1__7__512656 | 3 Phase fault GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 512650 TO GRDA1 5 512656 TO GRDA2 1 512826 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRTWSRN7__515820 | 3 Phase fault GRTWSRN7 (515825) 345 kV Bus a. Apply fault at the GRTWSRN7 (515825) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRTWSRN7 515825 TO GRTWSL11 515820 TO GRTWST11 515860 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRTWSRN7__515823 | 3 Phase fault GRTWSRN7 (515825) 345 kV Bus a. Apply fault at the GRTWSRN7 (515825) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRTWSRN7 515825 TO GRTWSL21 515823 TO GRTWST21 515824 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HOB_XFMR | 3 Phase fault HOB-JCT2 (511464) 69 kV Bus a. Apply fault at the HOB-JCT2 (511464) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT2 511464 TO HOB-JCT4 511463 TO HOBJT1-1 511417 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HOC404_5__547486 | 3 Phase fault HOC404 5 (547487) 161 kV Bus a. Apply fault at the HOC404 5 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 547487 TO HOC404 4 547486 TO HOC404A1 547715 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HSLWEST2__514941 | 3 Phase fault HSLWEST2 (514937) 69 kV Bus a. Apply fault at the HSLWEST2 (514937) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLWEST2 514937 TO HSL 4 514941 TO HSL 1 515731 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HUGO_XFMR | 3 Phase fault HUGO---2 (510893) 69 kV Bus a. Apply fault at the HUGO---2 (510893) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGO---2 510893 TO HUGO---4 510901 TO HUGO4-1 510859 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_HUGO___7__520560 | 3 Phase fault HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 521157 TO HUGOITC4 520560 TO HUGO TERTA 521189 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_IGLOOV_7__513593 | 3 Phase fault IGLOOV 7 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 513596 TO IGLOOV1 5 513593 TO IGLOTER1 1 513592 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_IGLOOV_7__513595 | 3 Phase fault IGLOOV 7 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 513596 TO IGLOOV2 5 513595 TO IGLOTER2 1 513594 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_IMO____2__514790 | 3 Phase fault IMO 2 (514721) 69 kV Bus a. Apply fault at the IMO 2 (514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 514721 TO IMO 4 514790 TO IMO 1 515788 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_JOHNCO_4__514809 | 3 Phase fault JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 514808 TO JOHNCO 7 514809 TO JOHNCO11 514810 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_KEENAN_1__515394 | 3 Phase fault KEENAN 1 (515393) 34.5 kV Bus a. Apply fault at the KEENAN 1 (515393) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEENAN 1 515393 TO KEENAN 4 515394 TO KEENAN T 515392 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_KNOXLEE2__508548 | 3 Phase fault KNOXLEE2 (508547) 69 kV Bus a. Apply fault at the KNOXLEE2 (508547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE2 508547 TO KNOXLEE4 508548 TO KXLEE-1 508584 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_L.E.S._XFMR | 3 Phase fault L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_L.E.S._XFMR | 3 Phase fault L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LEASIDE_2__507793 | 3 Phase fault LEASIDE 2 (507794) 69 kV Bus a. Apply fault at the LEASIDE 2 (507794) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEASIDE 2 507794 TO LEASIDE 4 507793 TO LEASIDE 1-1 507795 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LIEBERM2__508806 | 3 Phase fault LIEBERM2 (508805) 69 kV Bus a. Apply fault at the LIEBERM2 (508805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM2 508805 TO LIEBERM4 508806 TO LBMN3-1 508822 CKT 3 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LOGANSP2__509071 | 3 Phase fault LOGANSP2 (509070) 69 kV Bus a. Apply fault at the LOGANSP2 (509070) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGANSP2 509070 TO LOGANSP4 509071 TO 509094 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LONGWD_4__508809 | 3 Phase fault LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 508808 TO LONGWD 7 508809 TO LONGW1-1 508819 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_LSSOUTH2__508297 | 3 Phase fault LSSOUTH2 (508296) 69 kV Bus a. Apply fault at the LSSOUTH2 (508296) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH2 508296 TO LSSOUTH4 508297 TO LSS-1 508325 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MAID___5__512626 | 3 Phase fault MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 512648 TO MAID 2 512626 TO MAITER2 1 512837 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MANDEVILTP4__504363 | 3 Phase fault MANDEVILTP4 (508105) 138 kV Bus a. Apply fault at the MANDEVILTP4 (508105) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANDEVILTP4 508105 TO NE-TEXARK2 504363 TO NE-TEXARK1 504364 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MARAUTO2__508557 | 3 Phase fault MARAUTO2 (508576) 69 kV Bus a. Apply fault at the MARAUTO2 (508576) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARAUTO2 508576 TO MARSHL-4 508557 TO MRSH4#21 508592 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MAUD___4__515054 | 3 Phase fault MAUD 4 (515055) 138 kV Bus a. Apply fault at the MAUD 4 (515055) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 4 515055 TO MAUD 2 515054 TO MAUD 1 515736 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MENA___2__507436 | 3 Phase fault MENA 2 (508301) 69 kV Bus a. Apply fault at the MENA 2 (508301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENA 2 508301 TO MENA 4 507436 TO MENA3-1 507438 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MOORLND4__520995 | 3 Phase fault MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND4 520999 TO MOORLND2 520995 TO MLNDTERT 521180 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MSTANG_2__514861 | 3 Phase fault MSTANG 2 (514860) 69 kV Bus a. Apply fault at the MSTANG 2 (514860) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTANG 2 514860 TO MUSTANG4 514861 TO MUSTANG1 515740 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MSTNG10G__514861 | 3 Phase fault MSTNG10G (515672) 13.8 kV Bus a. Apply fault at the MSTNG10G (515672) 13.8 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTNG10G 515672 TO MUSTANG4 514861 TO MSTNG11G 515673 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MSTNG_8G__514861 | 3 Phase fault MSTNG 8G (515670) 13.8 kV Bus a. Apply fault at the MSTNG 8G (515670) 13.8 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTNG 8G 515670 TO MUSTANG4 514861 TO MSTNG 9G 515671 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_MUSKOGE2__515222 | 3 Phase fault MUSKOGE2 (515221) 69 kV Bus a. Apply fault at the MUSKOGE2 (515221) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKOGE2 515221 TO MUSKOGE5 515222 TO MUSKOG41 515797 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NBENTON2__508811 | 3 Phase fault NBENTON2 (508810) 69 kV Bus a. Apply fault at the NBENTON2 (508810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NBENTON2 508810 TO NBENTON4 508811 TO NBENTON1 508823 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NEOSHO_7__532937 | 3 Phase fault NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 532793 TO NEOSHO 5 532937 TO N345 2 1 532825 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NEOSHO_7__533021 | 3 Phase fault NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 532793 TO NEOSHO 4 533021 TO N345 1 1 532824 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NNBOSTN2__508069 | 3 Phase fault NNBOSTN2 (508068) 69 kV Bus a. Apply fault at the NNBOSTN2 (508068) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN2 508068 TO NNBOSTN4 508069 TO NNBT2-1 508099 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NORMHLL7__516097 | 3 Phase fault NORMHLL7 (516096) 345 kV Bus a. Apply fault at the NORMHLL7 (516096) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORMHLL7 516096 TO NORMHLL4 516097 TO NORMHL21 516099 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NORTWST4__514880 | 3 Phase fault NORTWST4 (514879) 138 kV Bus a. Apply fault at the NORTWST4 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTWST4 514879 TO NORTWST7 514880 TO NORTWS31 515743 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MINCO5 trips on voltage protection settings | Disabling voltage protection settings for MINCO5 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_NWTXARK4__508072 | 3 Phase fault NWTXARK4 (508071) 138 kV Bus a. Apply fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 508071 TO NWTXARK7 508072 TO NWTEX2-1 508101 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKAY___2__507428 | 3 Phase fault OKAY 2 (507427) 69 kV Bus a. Apply fault at the OKAY 2 (507427) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAY 2 507427 TO OKAY 4 507428 TO OKAY1-1 507442 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKEENE_4__521015 | 3 Phase fault OKEENE 4 (521016) 138 kV Bus a. Apply fault at the OKEENE 4 (521016) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKEENE 4 521016 TO OKEENE 2 521015 TO OKENTERT 521173 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ONETA_XFMR | 3 Phase fault ONETA--4 (509806) 138 kV Bus a. Apply fault at the ONETA--4 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 509806 TO ONETA--7 509807 TO ONETA1-1 509881 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OUSPRT_1__515398 | 3 Phase fault OUSPRT 1 (515397) 34.5 kV Bus a. Apply fault at the OUSPRT 1 (515397) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OUSPRT 1 515397 TO OUSPRT 4 515398 TO OUSPRT T 515396 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PALIOGE2__515100 | 3 Phase fault PALIOGE2 (515099) 69 kV Bus a. Apply fault at the PALIOGE2 (515099) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PALIOGE2 515099 TO PAOLI- 4 515100 TO PAOLI 1 515746 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PARKLN_2__515178 | 3 Phase fault PARKLN 2 (515177) 69 kV Bus a. Apply fault at the PARKLN 2 (515177) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKLN 2 515177 TO PARKLN 4 515178 TO PARKLN21 515748 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PATTERS2__507431 | 3 Phase fault PATTERS2 (507429) 69 kV Bus a. Apply fault at the PATTERS2 (507429) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS2 507429 TO PATTERS4 507431 TO PATTN2-1 507444 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003, WLDHRSE trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003, WLDHRSE prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PECANCK4__515234 | 3 Phase fault PECANCK4 (515233) 138 kV Bus a. Apply fault at the PECANCK4 (515233) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK4 515233 TO PECANCK5 515234 TO PECANC31 515750 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PECANCK5__515235 | 3 Phase fault PECANCK5 (515234) 161 kV Bus a. Apply fault at the PECANCK5 (515234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK5 515234 TO PECANCK7 515235 TO PECANC21 515759 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PENN___2__514925 | 3 Phase fault PENN 2 (514924) 69 kV Bus a. Apply fault at the PENN 2 (514924) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENN 2 514924 TO PENN 4 514925 TO PENN 1 515751 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PENSA__5__512628 | 3 Phase fault PENSA 5 (512654) 161 kV Bus a. Apply fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 5 512654 TO PENSA 2 512628 TO PENSA 1 512841 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_PIRKEY_4__508563 | 3 Phase fault PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY2-1 508588 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_R.S.S.XFMR | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 509783 TO RSS NG3 511844 TO RSS NG4 511845 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_REDBUD1S__514909 | 3 Phase fault REDBUD1S (514899) 18 kV Bus a. Apply fault at the REDBUD1S (514899) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD1S 514899 TO REDBUD 7 514909 TO REDBUD1G 514910 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_REDBUD2S__514909 | 3 Phase fault REDBUD2S (514900) 18 kV Bus a. Apply fault at the REDBUD2S (514900) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD2S 514900 TO REDBUD 7 514909 TO REDBUD2G 514911 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_REDBUD3S__514909 | 3 Phase fault REDBUD3S (514905) 18 kV Bus a. Apply fault at the REDBUD3S (514905) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD3S 514905 TO REDBUD 7 514909 TO REDBUD3G 514912 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_REDBUD4S__514909 | 3 Phase fault REDBUD4S (514940) 18 kV Bus a. Apply fault at the REDBUD4S (514940) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD4S 514940 TO REDBUD 7 514909 TO REDBUD4G 514942 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_RENO___2__514973 | 3 Phase fault RENO 2 (514972) 69 kV Bus a. Apply fault at the RENO 2 (514972) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 2 514972 TO RENO 4 514973 TO RENO 1 515753 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ROCKYPT2__515164 | 3 Phase fault ROCKYPT2 (515163) 69 kV Bus a. Apply fault at the ROCKYPT2 (515163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 515163 TO ROCKYPT4 515164 TO ROCKYPT1 515754 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_ROKHILL2__509083 | 3 Phase fault ROKHILL2 (509082) 69 kV Bus a. Apply fault at the ROKHILL2 (509082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL2 509082 TO ROKHILL4 509083 TO RKHIL2-1 509091 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_RSS_T1_4__509782 | 3 Phase fault RSS T1 4 (509773) 138 kV Bus a. Apply fault at the RSS T1 4 (509773) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T1 4 509773 TO R.S.S.-7 509782 TO RSST1 T1 509882 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_RSS_T2_4__509782 | 3 Phase fault RSS T2 4 (509875) 138 kV Bus a. Apply fault at the RSS T2 4 (509875) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T2 4 509875 TO R.S.S.-7 509782 TO RSST2 T1 509876 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_RUSHING2__515064 | 3 Phase fault RUSHING2 (515063) 69 kV Bus a. Apply fault at the RUSHING2 (515063) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSHING2 515063 TO RUSHING4 515064 TO RUSHING1 515755 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_RUSHSPR7__511965 | 3 Phase fault RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 511571 TO RUSHSPRW1-1 511965 TO RUSHSPR1-1 511572 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_S.S._XFMR | 3 Phase fault S.S.---2 (509816) 69 kV Bus a. Apply fault at the S.S.---2 (509816) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---2 509816 TO S.S.---4 509815 TO SS6-1 509878 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_S.W.S.2_XFMR | 3 Phase fault S.W.S.-2 (511476) 69 kV Bus a. Apply fault at the S.W.S.-2 (511476) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-2 511476 TO S.W.S.-4 511477 TO SWS#1--1 511413 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_S.W.S.4_XFMR | 3 Phase fault S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 511477 TO SWS NG4 511849 TO SWS NG5 511850 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SAPLPRD4__509870 | 3 Phase fault SAPLPRD4 (509871) 138 kV Bus a. Apply fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 509871 TO SAPLPRD7 509870 TO SAPLPRD1 509872 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SDIERKS2__507433 | 3 Phase fault SDIERKS2 (507432) 69 kV Bus a. Apply fault at the SDIERKS2 (507432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SDIERKS2 507432 TO SDIERKS4 507433 TO SDRKS1-1 507446 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SEMINOL4__515045 | 3 Phase fault SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 515044 TO SEMINOL7 515045 TO SEMINO21 515757 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SETEXAR2__508078 | 3 Phase fault SETEXAR2 (508077) 69 kV Bus a. Apply fault at the SETEXAR2 (508077) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETEXAR2 508077 TO SETEXAR4 508078 TO SETEX1-1 508102 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SFOREMAN__4__504030 | 3 Phase fault SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4 (504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 504029 TO SFORE_1 2 504030 TO SFORE_T1 1 504031 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SKELTON7__515991 | 3 Phase fault SKELTON7 (515990) 345 kV Bus a. Apply fault at the SKELTON7 (515990) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SKELTON7 515990 TO SKELTL11 515991 TO SKELTT11 515992 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SO4TH__2__514731 | 3 Phase fault SO4TH 2 (514730) 69 kV Bus a. Apply fault at the SO4TH 2 (514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 514730 TO SO4TH 4 514731 TO SO4TH 1 515758 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SOONER_4__514803 | 3 Phase fault SOONER 4 (514802) 138 kV Bus a. Apply fault at the SOONER 4 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 4 514802 TO SOONER 7 514803 TO SOONER 1 515760 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SUGARHL2__508080 | 3 Phase fault SUGARHL2 (508079) 69 kV Bus a. Apply fault at the SUGARHL2 (508079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGARHL2 508079 TO SUGARHL4 508080 TO SHILL1-1 508103 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SUNNYSD4__515136 | 3 Phase fault SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SUNNYSD7__515135 | 3 Phase fault SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SW_5TH_2__514920 | 3 Phase fault SW 5TH 2 (514919) 69 kV Bus a. Apply fault at the SW 5TH 2 (514919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW 5TH 2 514919 TO SW 5TH 4 514920 TO SW 5TH 1 515763 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-026 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SW_SHV_7__507759 | 3 Phase fault SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV1-1 507778 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_S_SHV__2__507755 | 3 Phase fault S SHV 2 (507754) 69 kV Bus a. Apply fault at the S SHV 2 (507754) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 2 507754 TO S SHV 4 507755 TO SSHV2-1 507776 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_T.NO.2_XFMR | 3 Phase fault T.NO.2-4 (509895) 138 kV Bus a. Apply fault at the T.NO.2-4 (509895) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.2-4 509895 TO T.NO.--7 509852 TO TNO2-1 509894 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_T.P.S._XFMR | 3 Phase fault T.P.S.-2 (509789) 69 kV Bus a. Apply fault at the T.P.S.-2 (509789) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-2 509789 TO T.P.S.-4 509788 TO TPS5-1 509880 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_T.S.E._XFMR | 3 Phase fault T.S.E.-2 (509820) 69 kV Bus a. Apply fault at the T.S.E.-2 (509820) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.S.E.-2 509820 TO T.S.E.-4 509811 TO TSE3-1 509873 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TAHLQH_5__512647 | 3 Phase fault TAHLQH 5 (512655) 161 kV Bus a. Apply fault at the TAHLQH 5 (512655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 512655 TO TAHLQH 2 512647 TO TAHLQH1 512851 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TALOGA_4__521064 | 3 Phase fault TALOGA 4 (521065) 138 kV Bus a. Apply fault at the TALOGA 4 (521065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALOGA 4 521065 TO TALOGA 2 521064 TO TLGTERT 521178 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_THISTLE7__539804 | 3 Phase fault THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 539801 TO THISTLE4 539804 TO THISTLE T1 539802 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TUCO_INT___6__525828 | 3 Phase fault TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 525830 TO TUCO_INT 3 525828 TO TUCO_TR4 1 525821 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TUCO_INT___7__525830 | 3 Phase fault TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 525832 TO TUCO_INT 6 525830 TO TUCO_TR2 1 525825 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TURK___3__507454 | 3 Phase fault TURK 3 (507456) 115 kV Bus a. Apply fault at the TURK 3 (507456) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 3 507456 TO TURK 4 507454 TO TURK1 1 507458 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_TURK___4__507455 | 3 Phase fault TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 4 507454 TO TURK 7 507455 TO TURK 1 507457 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_VALIANT2__510918 | 3 Phase fault VALIANT2 (510910) 69 kV Bus a. Apply fault at the VALIANT2 (510910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT2 510910 TO VALIANT4 510918 TO VALN1-1 510937 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_VALIANT4__510911 | 3 Phase fault VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 510918 TO VALIANT7 510911 TO VALN3-1 510939 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_VINTAJC2__510417 | 3 Phase fault VINTAJC2 (510418) 69 kV Bus a. Apply fault at the VINTAJC2 (510418) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC2 510418 TO VINTAJC4 510417 TO VINJT1-1 510367 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WAGNOR_5__512697 | 3 Phase fault WAGNOR 5 (512700) 161 kV Bus a. Apply fault at the WAGNOR 5 (512700) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAGNOR 5 512700 TO WAGNOR 2 512697 TO WAGNOR1 512818 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WASHITA4__521088 | 3 Phase fault WASHITA4 (521089) 138 kV Bus a. Apply fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 521089 TO WASHITA2 521088 TO WASHTERT 521179 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WATLANT2__508090 | 3 Phase fault WATLANT2 (508089) 69 kV Bus a. Apply fault at the WATLANT2 (508089) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT2 508089 TO WATLANT4 508090 TO WATL2-1 508046 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WEKIWA_XFMR | 3 Phase fault WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 509757 TO WEKIWA-7 509755 TO WEKIW1-1 509879 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2015-066 trips on voltage protection settings GEN-2018-027 trips on frequency protection settings | Operational steady state fixes (existing caps/taps/gen set points) avoids tripping of GEN-2015-066. Disabling frequency protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WHEELER____6__523776 | 3 Phase fault WHEELER 6 (523777) 230 kV Bus a. Apply fault at the WHEELER 6 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 523777 TO WHEELER 3 523776 TO WHEELER_TR11 523774 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WHITNEY2__508575 | 3 Phase fault WHITNEY2 (508574) 69 kV Bus a. Apply fault at the WHITNEY2 (508574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY2 508574 TO WHITNEY4 508575 TO WHIT2-1 508590 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WILKES_4__508841 | 3 Phase fault WILKES 4 (508840) 138 kV Bus a. Apply fault at the WILKES 4 (508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 508840 TO WILKES 7 508841 TO WILKES-1 508826 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WOODRNG4__514715 | 3 Phase fault WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 514714 TO WOODRNG7 514715 TO WOODRNG1 515770 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WOODWRD4__514782 | 3 Phase fault WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 514785 TO WODWRD 2 514782 TO WOODWR21 515771 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WWRDEHV4__515375 | 3 Phase fault WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_YOAKUM_345__526935 | 3 Phase fault YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 526936 TO YOAKUM 6 526935 TO YOAKUM_TR1 526937 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_112GORE4__LAIRGST4 | 3 Phase fault 112GORE4 (511488) 138 kV Bus a. Apply fault at the 112GORE4 (511488) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 138 KV 511488 TO LAIRGST4 138 KV 511510 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_112GORE4__RPPAPER4 | 3 Phase fault 112GORE4 (511488) 138 kV Bus a. Apply fault at the 112GORE4 (511488) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 138 KV 511488 TO RPPAPER4 138 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_2CARNEY__2LUTHER | 3 Phase fault 2CARNEY (300834) 69 kV Bus a. Apply fault at the 2CARNEY (300834) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CARNEY 69 KV 300834 TO 2LUTHER 69 KV 300856 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_2COLINS__COLNSGR2 | 3 Phase fault 2COLINS (300992) 69 kV Bus a. Apply fault at the 2COLINS (300992) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2COLINS 69 KV 300992 TO COLNSGR2 69 KV 512870 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_2MERIDAN__2LUTHER | 3 Phase fault 2MERIDAN (300839) 69 kV Bus a. Apply fault at the 2MERIDAN (300839) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MERIDAN 69 KV 300839 TO 2LUTHER 69 KV 300856 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_2OWASSO__COLNSGR2 | 3 Phase fault 2OWASSO (300998) 69 kV Bus a. Apply fault at the 2OWASSO (300998) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2OWASSO 69 KV 300998 TO COLNSGR2 69 KV 512870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_2OWASSO__DAWSON | 3 Phase fault 2OWASSO (300998) 69 kV Bus a. Apply fault at the 2OWASSO (300998) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2OWASSO 69 KV 300998 TO DAWSON-2 69 KV 509791 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_2VERA__COLNSGR2 | 3 Phase fault 2VERA (301006) 69 kV Bus a. Apply fault at the 2VERA (301006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2VERA 69 KV 301006 TO COLNSGR2 69 KV 512870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_36&MER_4__HOBBYLO4 | 3 Phase fault 36&MER 4 (514888) 138 kV Bus a. Apply fault at the 36&MER 4 (514888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 36&MER 4 138 KV 514888 TO HOBBYLO4 138 KV 515338 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_36&MER_4__SW_5TH_4 | 3 Phase fault 36&MER 4 (514888) 138 kV Bus a. Apply fault at the 36&MER 4 (514888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 36&MER 4 138 KV 514888 TO SW 5TH 4 138 KV 514920 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_38TH_ST2__BETHANY2 | 3 Phase fault 38TH ST2 (514845) 69 kV Bus a. Apply fault at the 38TH ST2 (514845) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 38TH ST2 69 KV 514845 TO BETHANY2 69 KV 514914 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_38TH_ST4__HEFNER_4 | 3 Phase fault 38TH ST4 (514846) 138 kV Bus a. Apply fault at the 38TH ST4 (514846) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TULSA 4 138 KV 514847 TO HEFNER 4 138 KV 514848 CKT 1 b.2. 38TH ST4 138 KV 514846 TO TULSA 4 138 KV 514847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_38TH_ST4__TULSA__4 | 3 Phase fault 38TH ST4 (514846) 138 kV Bus a. Apply fault at the 38TH ST4 (514846) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 38TH ST4 138 KV 514846 TO TULSA 4 138 KV 514847 CKT 1 b.2. LOAD 1 514847 b.3. TULSA 4 138 KV 514847 TO HEFNER 4 138 KV 514848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_3ADA_LA__3MINDEN_LA! | 3 Phase fault 3ADA_LA (337360) 115 kV Bus a. Apply fault at the 3ADA_LA (337360) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3ADA_LA 115 KV 337360 TO 3MINDEN_LA! 115 KV 337361 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_3EL_DORADO!__3ELDORADO.E! | 3 Phase fault 3EL DORADO! (337539) 115 kV Bus a. Apply fault at the 3EL DORADO! (337539) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3EL DORADO! 115 KV 337539 TO 3ELDORADO.E! 115 KV 337553 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_3EL_DORADO!__3ELD_DONAN | 3 Phase fault 3EL DORADO! (337539) 115 kV Bus a. Apply fault at the 3EL DORADO! (337539) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3EL DORADO! 115 KV 337539 TO 3ELD DONAN 115 KV 337540 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_3EL_DORADO!__3ELD_QUINN | 3 Phase fault 3EL DORADO! (337539) 115 kV Bus a. Apply fault at the 3EL DORADO! (337539) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3EL DORADO! 115 KV 337539 TO 3ELD QUINN 115 KV 337560 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_3KERLIN+__3EMERSON! | 3 Phase fault 3KERLIN+ (337524) 115 kV Bus a. Apply fault at the 3KERLIN+ (337524) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3KERLIN+ 115 KV 337524 TO 3EMERSON! 115 KV 337526 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_3MINDEN_LA!__3LA_ORD_PLNT | 3 Phase fault 3MINDEN_LA! (337361) 115 kV Bus a. Apply fault at the 3MINDEN_LA! (337361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MINDEN_LA! 115 KV 337361 TO 3LA_ORD_PLNT 115 KV 337362 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_3MINDEN_LA!__3SAREPTA! | 3 Phase fault 3MINDEN_LA! (337361) 115 kV Bus a. Apply fault at the 3MINDEN_LA! (337361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MINDEN_LA! 115 KV 337361 TO 3SAREPTA! 115 KV 337363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_3MINDEN_LA!__MINDEN | 3 Phase fault 3MINDEN_LA! (337361) 115 kV Bus a. Apply fault at the 3MINDEN_LA! (337361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MINDEN_LA! 115 KV 337361 TO MINDEN-3 115 KV 507788 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_3MINDEN_LG__3MINDEN_LA! | 3 Phase fault 3MINDEN_LG (303302) 115 kV Bus a. Apply fault at the 3MINDEN_LG (303302) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MINDEN_LG 115 KV 303302 TO 3MINDEN_LA! 115 KV 337361 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_3SAREPTA!__3CULLEN | 3 Phase fault 3SAREPTA! (337363) 115 kV Bus a. Apply fault at the 3SAREPTA! (337363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115 KV 337363 TO 3CULLEN 115 KV 337364 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_3SAREPTA!__3EMERSON! | 3 Phase fault 3SAREPTA! (337363) 115 kV Bus a. Apply fault at the 3SAREPTA! (337363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115 KV 337363 TO 3HAYNESVILLE 115 KV 337366 CKT 1 b.2. LOAD 1 337366 b.3. LOAD LG 337366 b.4. 3HAYNESVILLE 115 KV 337366 TO 3EMERSON! 115 KV 337526 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_3SAREPTA!__3SPRINGHILL | 3 Phase fault 3SAREPTA! (337363) 115 kV Bus a. Apply fault at the 3SAREPTA! (337363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115 KV 337363 TO 3SPRINGHILL 115 KV 337365 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_3SMACKOVER+__3EL_DORADO! | 3 Phase fault 3SMACKOVER+ (337537) 115 kV Bus a. Apply fault at the 3SMACKOVER+ (337537) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SMACKOVER+ 115 KV 337537 TO 3EL DORADO! 115 KV 337539 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_3SPRINGHILL__3TAYLOR | 3 Phase fault 3SPRINGHILL (337365) 115 kV Bus a. Apply fault at the 3SPRINGHILL (337365) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SPRINGHILL 115 KV 337365 TO 3TAYLOR 115 KV 337500 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_44&SUNL2__ELMCRK_2 | 3 Phase fault 44&SUNL2 (514979) 69 kV Bus a. Apply fault at the 44&SUNL2 (514979) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 44&SUNL2 69 KV 514979 TO ELMCRK 2 69 KV 514982 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_44&SUNL2__SUNNYLN2 | 3 Phase fault 44&SUNL2 (514979) 69 kV Bus a. Apply fault at the 44&SUNL2 (514979) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 44&SUNL2 69 KV 514979 TO SUNNYLN2 69 KV 514980 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_46ST | 3 Phase fault 46ST--E4 (509837) 138 kV Bus a. Apply fault at the 46ST--E4 (509837) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 46ST--E4 138 KV 509837 TO 46ST-TP-4 138 KV 509900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_4BRISTOW__4SILVCTY | 3 Phase fault 4BRISTOW (300137) 138 kV Bus a. Apply fault at the 4BRISTOW (300137) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4BRISTOW 138 KV 300137 TO 4SILVCTY 138 KV 300140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_4CLEVLND__4SFORKKTP | 3 Phase fault 4CLEVLND (300138) 138 kV Bus a. Apply fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138 KV 300138 TO 4JAVINE 138 KV 300996 CKT 1 b.2. LOAD 1 300996 b.3. LOAD 2 300996 b.4. 4JAVINE 138 KV 300996 TO 4SFORKKTP 138 KV 301339 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_4CLEVLND__4SILVCTY | 3 Phase fault 4CLEVLND (300138) 138 kV Bus a. Apply fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138 KV 300138 TO 4SILVCTY 138 KV 300140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_4CLEVLND__CLEVLND_4 | 3 Phase fault 4CLEVLND (300138) 138 kV Bus a. Apply fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138 KV 300138 TO CLEVLND 4 138 KV 512729 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_4CLEVLND__PAWNSW4 | 3 Phase fault 4CLEVLND (300138) 138 kV Bus a. Apply fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138 KV 300138 TO PAWNSW4 138 KV 512749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_4FAIRFAX__PAWNSW4 | 3 Phase fault 4FAIRFAX (300139) 138 kV Bus a. Apply fault at the 4FAIRFAX (300139) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FAIRFAX 138 KV 300139 TO PAWNSW4 138 KV 512749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_4FISHERTP__4SILVCTY | 3 Phase fault 4FISHERTP (300131) 138 kV Bus a. Apply fault at the 4FISHERTP (300131) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FISHERTP 138 KV 300131 TO 4SILVCTY 138 KV 300140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_4LUTHER__4MEMORALT | 3 Phase fault 4LUTHER (300135) 138 kV Bus a. Apply fault at the 4LUTHER (300135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4LUTHER 138 KV 300135 TO 4MEMORALT 138 KV 300136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_4LUTHER__4STROUD138 | 3 Phase fault 4LUTHER (300135) 138 kV Bus a. Apply fault at the 4LUTHER (300135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4LUTHER 138 KV 300135 TO 4LUTHERD 138 KV 301372 CKT 1 b.2. LOAD 1 301372 b.3. 4WARWICK 138 KV 300915 TO 4LUTHERD 138 KV 301372 CKT 1 b.4. LOAD 1 301372 b.5. 4STROUD138 138 KV 300914 TO 4WARWICK 138 KV 300915 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_4MEMORALT__4MEMORAL | 3 Phase fault 4MEMORALT (300136) 138 kV Bus a. Apply fault at the 4MEMORALT (300136) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MEMORALT 138 KV 300136 TO 4MEMORAL 138 KV 301541 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_4MEMORALT__JNSKAMO4 | 3 Phase fault 4MEMORALT (300136) 138 kV Bus a. Apply fault at the 4MEMORALT (300136) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MEMORALT 138 KV 300136 TO JNSKAMO4 138 KV 514906 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_4MURFBORO__SNASHVL4 | 3 Phase fault 4MURFBORO (337672) 138 kV Bus a. Apply fault at the 4MURFBORO (337672) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MURFBORO 138 KV 337672 TO SNASHVL4 138 KV 507434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_4SFORKK__4SFORKKTP | 3 Phase fault 4SFORKK (300165) 138 kV Bus a. Apply fault at the 4SFORKK (300165) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SFORKK 138 KV 300165 TO 4SFORKKTP 138 KV 301339 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_4SILVCTY__4STILWTR | 3 Phase fault 4SILVCTY (300140) 138 kV Bus a. Apply fault at the 4SILVCTY (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY 138 KV 300140 TO 4STILWTR 138 KV 300141 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_4SILVCTY__SILVCTYGR4 | 3 Phase fault 4SILVCTY (300140) 138 kV Bus a. Apply fault at the 4SILVCTY (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY 138 KV 300140 TO SILVCTYGR4 138 KV 512726 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_4SKIAETP__4SFORKKTP | 3 Phase fault 4SKIAETP (300146) 138 kV Bus a. Apply fault at the 4SKIAETP (300146) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SKIAETP 138 KV 300146 TO 4SFORKKTP 138 KV 301339 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_4SKIAETP__COLLINS4 | 3 Phase fault 4SKIAETP (300146) 138 kV Bus a. Apply fault at the 4SKIAETP (300146) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SKIAETP 138 KV 300146 TO COLLINS4 138 KV 512705 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_4STROUDDIST__4STROUD138 | 3 Phase fault 4STROUDDIST (300838) 138 kV Bus a. Apply fault at the 4STROUDDIST (300838) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STROUDDIST 138 KV 300838 TO 4STROUD138 138 KV 300914 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_52DEL | 3 Phase fault 52DEL-W4 (509856) 138 kV Bus a. Apply fault at the 52DEL-W4 (509856) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 52DEL-W4 138 KV 509856 TO S HILLW4 138 KV 509859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_52DELTP4__T.P.S. | 3 Phase fault 52DELTP4 (509776) 138 kV Bus a. Apply fault at the 52DELTP4 (509776) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 52DELTP4 138 KV 509776 TO 36LEWIS4 138 KV 509800 CKT 1 b.2. LOAD 1 509800 b.3. T.P.S.-4 138 KV 509788 TO 36LEWIS4 138 KV 509800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_52DELTP4__T.S.E. | 3 Phase fault 52DELTP4 (509776) 138 kV Bus a. Apply fault at the 52DELTP4 (509776) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 52DELTP4 138 KV 509776 TO T.S.E.-4 138 KV 509811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_52DELTP4__ZUNIS | 3 Phase fault 52DELTP4 (509776) 138 kV Bus a. Apply fault at the 52DELTP4 (509776) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 52DELTP4 138 KV 509776 TO ZUNIS-S4 138 KV 509826 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_52DELWT4__S_HILLW4 | 3 Phase fault 52DELWT4 (509814) 138 kV Bus a. Apply fault at the 52DELWT4 (509814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 52DELWT4 138 KV 509814 TO S HILLW4 138 KV 509859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_53CACHE4__ARTVLTP4 | 3 Phase fault 53CACHE4 (511509) 138 kV Bus a. Apply fault at the 53CACHE4 (511509) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53CACHE4 138 KV 511509 TO ARTVLTP4 138 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_53GARNT4__77MEMTP4 | 3 Phase fault 53GARNT4 (509762) 138 kV Bus a. Apply fault at the 53GARNT4 (509762) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARNT4 138 KV 509762 TO 77MEMTP4 138 KV 509765 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_53GARNT4__T.S.E. | 3 Phase fault 53GARNT4 (509762) 138 kV Bus a. Apply fault at the 53GARNT4 (509762) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARNT4 138 KV 509762 TO T.S.E.-4 138 KV 509811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_53GARN_4__53GARNT4 | 3 Phase fault 53GARN 4 (509734) 138 kV Bus a. Apply fault at the 53GARN 4 (509734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARN 4 138 KV 509734 TO 53GARNT4 138 KV 509762 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_53GARST4__53GARNS4 | 3 Phase fault 53GARST4 (509763) 138 kV Bus a. Apply fault at the 53GARST4 (509763) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARST4 138 KV 509763 TO 53GARNS4 138 KV 509774 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_53GARST4__FORD | 3 Phase fault 53GARST4 (509763) 138 kV Bus a. Apply fault at the 53GARST4 (509763) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARST4 138 KV 509763 TO FORD---4 138 KV 509772 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_53GARST4__T.S.E. | 3 Phase fault 53GARST4 (509763) 138 kV Bus a. Apply fault at the 53GARST4 (509763) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARST4 138 KV 509763 TO T.S.E.-4 138 KV 509811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_5CDRCRST__TAHLQH_5 | 3 Phase fault 5CDRCRST (301344) 161 kV Bus a. Apply fault at the 5CDRCRST (301344) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CDRCRST 161 KV 301344 TO TAHLQH 5 161 KV 512655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_5CHOTEAU1__5CHOTEAU2 | 3 Phase fault 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 161 KV 300069 TO 5CHOTEAU2 161 KV 301348 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_5CHOTEAU1__MAID___5 | 3 Phase fault 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 161 KV 300069 TO MAID 5 161 KV 512648 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_5ELMCRK__CATSAGR5 | 3 Phase fault 5ELMCRK (300993) 161 kV Bus a. Apply fault at the 5ELMCRK (300993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ELMCRK 161 KV 300993 TO CATSAGR5 161 KV 512638 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_5PARK__TAHLQH_5 | 3 Phase fault 5PARK (301307) 161 kV Bus a. Apply fault at the 5PARK (301307) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PARK 161 KV 301307 TO TAHLQH 5 161 KV 512655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_5TRIBES2__AGENCY_2 | 3 Phase fault 5TRIBES2 (515227) 69 kV Bus a. Apply fault at the 5TRIBES2 (515227) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TENYSON2 69 KV 515217 TO 5TRIBES2 69 KV 515227 CKT 1 b.2. HONORHT2 69 KV 515216 TO TENYSON2 69 KV 515217 CKT 1 b.3. LOAD 1 515217 b.4. HONORHT2 69 KV 515216 TO AGENCY 2 69 KV 515229 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_5TRIBES2__WELLSPA2 | 3 Phase fault 5TRIBES2 (515227) 69 kV Bus a. Apply fault at the 5TRIBES2 (515227) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHECOTA2 69 KV 515201 TO WELLS 2 69 KV 515202 CKT 1 b.2. LOAD 1 515202 b.3. CHECOTA2 69 KV 515201 TO 5TRIBES2 69 KV 515227 CKT 1 b.4. WELLS 2 69 KV 515202 TO WELLSPA2 69 KV 515215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_5TRIBES5__MUSKOGE5 | 3 Phase fault 5TRIBES5 (515228) 161 kV Bus a. Apply fault at the 5TRIBES5 (515228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TRIBES5 161 KV 515228 TO HANCOK-5 161 KV 515250 CKT 1 b.2. LOAD 1 515250 b.3. HANCOK-5 161 KV 515250 TO THRERVR5 161 KV 515640 CKT 1 b.4. LOAD 1 515640 b.5. MUSKOGE5 161 KV 515222 TO THRERVR5 161 KV 515640 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_5TRIBES5__PECANCK5 | 3 Phase fault 5TRIBES5 (515228) 161 kV Bus a. Apply fault at the 5TRIBES5 (515228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TRIBES5 161 KV 515228 TO PECANCK5 161 KV 515234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_77MEM | 3 Phase fault 77MEM-E4 (509735) 138 kV Bus a. Apply fault at the 77MEM-E4 (509735) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 77MEM-E4 138 KV 509735 TO 77MEMTP4 138 KV 509765 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_77MEM | 3 Phase fault 77MEM-W4 (509766) 138 kV Bus a. Apply fault at the 77MEM-W4 (509766) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 77MEM-W4 138 KV 509766 TO E.61ST-4 138 KV 509831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_77MEMTP4__81GARN | 3 Phase fault 77MEMTP4 (509765) 138 kV Bus a. Apply fault at the 77MEMTP4 (509765) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 77MEMTP4 138 KV 509765 TO 81GARN-4 138 KV 509855 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_7BLACKBERRY__NEOSHO_7 | 3 Phase fault 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY 345 KV 300739 TO NEOSHO 7 345 KV 532793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_7SAREPTA%__7EL_DORADO | 3 Phase fault 7SAREPTA% (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345 KV 337376 TO 7EL DORADO 345 KV 337562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_7SAREPTA%__LONGWD_7 | 3 Phase fault 7SAREPTA% (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345 KV 337376 TO LONGWD 7 345 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_7SPORTSMAN__GRDA1__7 | 3 Phase fault 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN 345 KV 300740 TO GRDA1 7 345 KV 512650 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_81GARN | 3 Phase fault 81GARN-4 (509855) 138 kV Bus a. Apply fault at the 81GARN-4 (509855) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81GARN-4 138 KV 509855 TO E_121ST4 138 KV 509889 CKT 1 b.2. LOAD 1 509889 b.3. 121LYNN4 138 KV 509869 TO E_121ST4 138 KV 509889 CKT 1 b.4. LOAD 1 509889 b.5. ONETA--4 138 KV 509806 TO 121LYNN4 138 KV 509869 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_81YALEN4__81YALTP4 | 3 Phase fault 81YALEN4 (509730) 138 kV Bus a. Apply fault at the 81YALEN4 (509730) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81YALEN4 138 KV 509730 TO 81YALTP4 138 KV 509809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_81YALES4__WARNTAP4 | 3 Phase fault 81YALES4 (509810) 138 kV Bus a. Apply fault at the 81YALES4 (509810) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81YALES4 138 KV 509810 TO WARNTAP4 138 KV 509858 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_81YALTP4__SHILETP4 | 3 Phase fault 81YALTP4 (509809) 138 kV Bus a. Apply fault at the 81YALTP4 (509809) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81YALTP4 138 KV 509809 TO SHILETP4 138 KV 509813 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_8ANO%__8P.HILL% | 3 Phase fault 8ANO% (337909) 500 kV Bus a. Apply fault at the 8ANO% (337909) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500 KV 337909 TO 8P.HILL% 500 KV 337922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_8ANO%__FTSMITH8 | 3 Phase fault 8ANO% (337909) 500 kV Bus a. Apply fault at the 8ANO% (337909) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500 KV 337909 TO FTSMITH8 500 KV 515305 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_8EL_DORADO%__8PANDA% | 3 Phase fault 8EL DORADO% (337561) 500 kV Bus a. Apply fault at the 8EL DORADO% (337561) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 500 KV 337561 TO 8PANDA% 500 KV 338440 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_8EL_DORADO%__8SHERIDAN% | 3 Phase fault 8EL DORADO% (337561) 500 kV Bus a. Apply fault at the 8EL DORADO% (337561) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 500 KV 337561 TO 8SHERIDAN% 500 KV 337643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_8HAPPYVALY%__8ANO% | 3 Phase fault 8HAPPYVALY% (337811) 500 kV Bus a. Apply fault at the 8HAPPYVALY% (337811) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8HAPPYVALY% 500 KV 337811 TO 8ANO% 500 KV 337909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_8MCNEIL%__8EL_DORADO% | 3 Phase fault 8MCNEIL% (337515) 500 kV Bus a. Apply fault at the 8MCNEIL% (337515) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MCNEIL% 500 KV 337515 TO 8EL DORADO% 500 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_8MCNEIL%__8ETTA% | 3 Phase fault 8MCNEIL% (337515) 500 kV Bus a. Apply fault at the 8MCNEIL% (337515) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MCNEIL% 500 KV 337515 TO 8ETTA% 500 KV 337754 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_8MT_OLIVE%__8EL_DORADO% | 3 Phase fault 8MT_OLIVE% (337368) 500 kV Bus a. Apply fault at the 8MT_OLIVE% (337368) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MT_OLIVE% 500 KV 337368 TO 8EL DORADO% 500 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_8MT_OLIVE%__LAYFLD8 | 3 Phase fault 8MT_OLIVE% (337368) 500 kV Bus a. Apply fault at the 8MT_OLIVE% (337368) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MT_OLIVE% 500 KV 337368 TO LAYFLD8 500 KV 509366 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_8SHERIDAN%__8MABELVALE% | 3 Phase fault 8SHERIDAN% (337643) 500 kV Bus a. Apply fault at the 8SHERIDAN% (337643) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHERIDAN% 500 KV 337643 TO 8MABELVALE% 500 KV 337808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_8SHERIDAN%__8MAGNETCOVE% | 3 Phase fault 8SHERIDAN% (337643) 500 kV Bus a. Apply fault at the 8SHERIDAN% (337643) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHERIDAN% 500 KV 337643 TO 8MAGNETCOVE% 500 KV 337763 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_8SHERIDAN%__8WHT_BLUFF% | 3 Phase fault 8SHERIDAN% (337643) 500 kV Bus a. Apply fault at the 8SHERIDAN% (337643) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHERIDAN% 500 KV 337643 TO 8WHT BLUFF% 500 KV 337651 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_8STERLING%__8EL_DORADO% | 3 Phase fault 8STERLING% (337420) 500 kV Bus a. Apply fault at the 8STERLING% (337420) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8STERLING% 500 KV 337420 TO 8EL DORADO% 500 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_8STERLING%__8PERRYVILLE% | 3 Phase fault 8STERLING% (337420) 500 kV Bus a. Apply fault at the 8STERLING% (337420) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8STERLING% 500 KV 337420 TO 8PERRYVILLE% 500 KV 337427 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_8STERLING2%__8STERLING% | 3 Phase fault 8STERLING2% (337413) 500 kV Bus a. Apply fault at the 8STERLING2% (337413) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8STERLING2% 500 KV 337413 TO 8STERLING% 500 KV 337420 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_A.A. | 3 Phase fault A.A.---4 (509784) 138 kV Bus a. Apply fault at the A.A.---4 (509784) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. A.A.---4 138 KV 509784 TO CDC-WT 4 138 KV 509842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_A.A. | 3 Phase fault A.A.---4 (509784) 138 kV Bus a. Apply fault at the A.A.---4 (509784) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. A.A.---4 138 KV 509784 TO MINGORD4 138 KV 509802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_A.A. | 3 Phase fault A.A.---4 (509784) 138 kV Bus a. Apply fault at the A.A.---4 (509784) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOHAWK 4 138 KV 509801 TO PPTAP 4 138 KV 509863 CKT 1 b.2. A.A.---4 138 KV 509784 TO MOHAWK 4 138 KV 509801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AGENCY_2__JAMESVL2 | 3 Phase fault AGENCY 2 (515229) 69 kV Bus a. Apply fault at the AGENCY 2 (515229) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AGENCY 2 69 KV 515229 TO JAMESVL2 69 KV 515240 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AGENCY_5__EUCLID_5 | 3 Phase fault AGENCY 5 (515230) 161 kV Bus a. Apply fault at the AGENCY 5 (515230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AGENCY 5 161 KV 515230 TO EUCLID 5 161 KV 515251 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AGENCY_5__PECANCK5 | 3 Phase fault AGENCY 5 (515230) 161 kV Bus a. Apply fault at the AGENCY 5 (515230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AGENCY 5 161 KV 515230 TO PECANCK5 161 KV 515234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ALWUETP4__ALLUWE_4 | 3 Phase fault ALWUETP4 (510429) 138 kV Bus a. Apply fault at the ALWUETP4 (510429) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALWUETP4 138 KV 510429 TO ALLUWE 4 138 KV 510430 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ANADARK2__CADDO__2 | 3 Phase fault ANADARK2 (520810) 69 kV Bus a. Apply fault at the ANADARK2 (520810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK2 69 KV 520810 TO CADDO 2 69 KV 520838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ANADARK4__CHERRYRD_4 | 3 Phase fault ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138 KV 520814 TO CHERRYRD 4 138 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ANADARK4__FLETCH | 3 Phase fault ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138 KV 520814 TO GEORGIA4 138 KV 520923 CKT 1 b.2. LOAD 1 520923 b.3. FLETCH-4 138 KV 520912 TO GEORGIA4 138 KV 520923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ANADARK4__TUTLETP4 | 3 Phase fault ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138 KV 520814 TO POCASET4 138 KV 521031 CKT 1 b.2. LOAD 1 521031 b.3. POCASET4 138 KV 521031 TO TUTLETP4 138 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ANDRCKT2__MAUDT__2 | 3 Phase fault ANDRCKT2 (509658) 69 kV Bus a. Apply fault at the ANDRCKT2 (509658) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUDT 2 69 KV 509653 TO MAUD 2 69 KV 509657 CKT 1 b.2. LOAD 1 509657 b.3. MAUD 2 69 KV 509657 TO ANDRCKT2 69 KV 509658 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ANDRCKT2__SPRNGHL2 | 3 Phase fault ANDRCKT2 (509658) 69 kV Bus a. Apply fault at the ANDRCKT2 (509658) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDRCKT2 69 KV 509658 TO SIMMS 2 69 KV 509659 CKT 1 b.2. LOAD 1 509659 b.3. SIMMS 2 69 KV 509659 TO SDEKALB2 69 KV 509660 CKT 1 b.4. LOAD 1 509660 b.5. SDEKALB2 69 KV 509660 TO WDEKALB2 69 KV 509661 CKT 1 b.6. LOAD 1 509661 b.7. WDEKALB2 69 KV 509661 TO SPRNGHL2 69 KV 509662 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ANDRSNC4__MUNZCTY4 | 3 Phase fault ANDRSNC4 (508050) 138 kV Bus a. Apply fault at the ANDRSNC4 (508050) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDRSNC4 138 KV 508050 TO BRYANML4 138 KV 508056 CKT 1 b.2. LOAD 1 508056 b.3. BRYANML4 138 KV 508056 TO MUNZCTY4 138 KV 508064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ARAPAHO2__HM | 3 Phase fault ARAPAHO2 (520815) 69 kV Bus a. Apply fault at the ARAPAHO2 (520815) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARAPAHO2 69 KV 520815 TO HM-BTTP2 69 KV 520942 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ARBUCKL4__VANOSTP4 | 3 Phase fault ARBUCKL4 (515117) 138 kV Bus a. Apply fault at the ARBUCKL4 (515117) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARBUCKL4 138 KV 515117 TO VANOSTP4 138 KV 515531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ARCADIA4__DANFRTH4 | 3 Phase fault ARCADIA4 (514907) 138 kV Bus a. Apply fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 138 KV 514907 TO RNDBARN4 138 KV 515461 CKT 1 b.2. LOAD 1 515461 b.3. BURGETT4 138 KV 514510 TO RNDBARN4 138 KV 515461 CKT 1 b.4. LOAD 1 515461 b.5. BURGETT4 138 KV 514510 TO DANFRTH4 138 KV 514833 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ARCADIA4__LGARBER4 | 3 Phase fault ARCADIA4 (514907) 138 kV Bus a. Apply fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 138 KV 514907 TO LGARBER4 138 KV 515465 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ARCADIA7__GEN | 3 Phase fault ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345 KV 514908 TO GEN-2017-133 345 KV 760032 CKT 4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ARCADIA7__REDBUD_7 | 3 Phase fault ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345 KV 514908 TO REDBUD 7 345 KV 514909 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ARCADIA7__SEMINOL7 | 3 Phase fault ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345 KV 514908 TO SEMINOL7 345 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ARSHILL4__FTHUMBG4 | 3 Phase fault ARSHILL4 (507711) 138 kV Bus a. Apply fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138 KV 507711 TO FTHUMBG4 138 KV 507731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ARSHILL4__LIEBERM4 | 3 Phase fault ARSHILL4 (507711) 138 kV Bus a. Apply fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138 KV 507711 TO LIEBERM4 138 KV 508806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ARSHILL4__MCWILLI4 | 3 Phase fault ARSHILL4 (507711) 138 kV Bus a. Apply fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138 KV 507711 TO MCWILLI4 138 KV 507742 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ARSHILL4__RAINES_4 | 3 Phase fault ARSHILL4 (507711) 138 kV Bus a. Apply fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138 KV 507711 TO RAINES 4 138 KV 507749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DIANA__4__NGPLTAP4 | 3 Phase fault DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 138 KV 508831 TO NGPLTAP4 138 KV 508837 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ARTVLTP4__ARTVILL4 | 3 Phase fault ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTVLTP4 138 KV 511537 TO ARTVILL4 138 KV 511538 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ASPEN__4__MOORLND4 | 3 Phase fault ASPEN 4 (520462) 138 kV Bus a. Apply fault at the ASPEN 4 (520462) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASPEN 4 138 KV 520462 TO MOORLND4 138 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_B.BOWTP4__CRAIGJT4 | 3 Phase fault B.BOWTP4 (510888) 138 kV Bus a. Apply fault at the B.BOWTP4 (510888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B.BOWTP4 138 KV 510888 TO CRAIGJT4 138 KV 510890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_B.BOW__4__B.BOWTP4 | 3 Phase fault B.BOW 4 (510864) 138 kV Bus a. Apply fault at the B.BOW 4 (510864) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B.BOW 4 138 KV 510864 TO B.BOWTP4 138 KV 510888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_B111 | 3 Phase fault B111---4 (509767) 138 kV Bus a. Apply fault at the B111---4 (509767) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B111---4 138 KV 509767 TO BA101ST4 138 KV 509768 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BA.N | 3 Phase fault BA.N-ST4 (509786) 138 kV Bus a. Apply fault at the BA.N-ST4 (509786) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.N-ST4 138 KV 509786 TO LLANETP4 138 KV 509804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BA.N | 3 Phase fault BA.N-ST4 (509786) 138 kV Bus a. Apply fault at the BA.N-ST4 (509786) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.N-ST4 138 KV 509786 TO ONETA--4 138 KV 509806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BA.NO | 3 Phase fault BA.NO-S4 (509721) 138 kV Bus a. Apply fault at the BA.NO-S4 (509721) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.NO-S4 138 KV 509721 TO BA.N-ST4 138 KV 509786 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BA101ST4__ONETA | 3 Phase fault BA101ST4 (509768) 138 kV Bus a. Apply fault at the BA101ST4 (509768) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101ST4 138 KV 509768 TO ONETA--4 138 KV 509806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BA101_S4__BA101ST4 | 3 Phase fault BA101 S4 (509737) 138 kV Bus a. Apply fault at the BA101 S4 (509737) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101 S4 138 KV 509737 TO BA101ST4 138 KV 509768 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BA81 | 3 Phase fault BA81---4 (509747) 138 kV Bus a. Apply fault at the BA81---4 (509747) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA81---4 138 KV 509747 TO BA101-N4 138 KV 509769 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BA81 | 3 Phase fault BA81---4 (509747) 138 kV Bus a. Apply fault at the BA81---4 (509747) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA81---4 138 KV 509747 TO FORD---4 138 KV 509772 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BADGER_7__BLUWND_7 | 3 Phase fault BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345 KV 515677 TO BLUWND 7 345 KV 515686 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BADGER_7__G16 | 3 Phase fault BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345 KV 515677 TO G16-003-TAP 345 KV 560071 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BADGER_7__GEN | 3 Phase fault BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345 KV 515677 TO GEN-2015-082 345 KV 585190 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BANNTAP4__E41ST_E4 | 3 Phase fault BANNTAP4 (509785) 138 kV Bus a. Apply fault at the BANNTAP4 (509785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANNTAP4 138 KV 509785 TO E41ST_E4 138 KV 509861 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BANN___2__LSORDTP2 | 3 Phase fault BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69 KV 508053 TO LSORDTP2 69 KV 508063 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BANN___2__SUGHLWT2 | 3 Phase fault BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69 KV 508053 TO REDLICK2 69 KV 508073 CKT 1 b.2. LOAD 1 508073 b.3. REDLICK2 69 KV 508073 TO RICHMND2 69 KV 508076 CKT 1 b.4. LOAD 1 508076 b.5. NW_TEXAR 2 69 KV 504109 TO RICHMND2 69 KV 508076 CKT 1 b.6. LOAD 1 508076 b.7. NW_TEXAR 2 69 KV 504109 TO SUGHLWT2 69 KV 508082 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BANN___2__TAYLOR_2 | 3 Phase fault BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69 KV 508053 TO KINGHWY2 69 KV 508061 CKT 1 b.2. LOAD 1 508061 b.3. KINGHWY2 69 KV 508061 TO TEXOPER2 69 KV 508087 CKT 1 b.4. LOAD 1 508087 b.5. TAYLOR 2 69 KV 508083 TO TEXOPER2 69 KV 508087 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DIANA__4__DIANASW4 | 3 Phase fault DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 138 KV 508831 TO DIANASW4 138 KV 509639 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BANN___4__SETEXAR4 | 3 Phase fault BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138 KV 508054 TO SETEXAR4 138 KV 508078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BANN___4__REDSPRG4 | 3 Phase fault BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138 KV 508054 TO REDSPRG4 138 KV 508075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BARITE | 3 Phase fault BARITE-RD 4 (504379) 138 kV Bus a. Apply fault at the BARITE-RD 4 (504379) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARITE-RD 4 138 KV 504379 TO BARITERDTP 4 138 KV 507463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BARNSAL4__MOUNDRD4 | 3 Phase fault BARNSAL4 (510388) 138 kV Bus a. Apply fault at the BARNSAL4 (510388) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARNSAL4 138 KV 510388 TO BARNPMP4 138 KV 510433 CKT 1 b.2. LOAD 1 510433 b.3. MOUNDRD4 138 KV 510395 TO BARNPMP4 138 KV 510433 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BAWATAP2__COWETAP2 | 3 Phase fault BAWATAP2 (509718) 69 kV Bus a. Apply fault at the BAWATAP2 (509718) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAWATAP2 69 KV 509718 TO COWETAP2 69 KV 509781 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BAWATAP2__T.S.E. | 3 Phase fault BAWATAP2 (509718) 69 kV Bus a. Apply fault at the BAWATAP2 (509718) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAWATAP2 69 KV 509718 TO T.S.E.-2 69 KV 509820 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BAWATER2__BAWATAP2 | 3 Phase fault BAWATER2 (509717) 69 kV Bus a. Apply fault at the BAWATER2 (509717) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAWATER2 69 KV 509717 TO BAWATAP2 69 KV 509718 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BCVI_HVB__SLKHILLS_4 | 3 Phase fault BCVI_HVB (520514) 138 kV Bus a. Apply fault at the BCVI_HVB (520514) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BCVI_HVB 138 KV 520514 TO SLKHILLS 4 138 KV 521103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BCV_SW_4__CHERRYRD_4 | 3 Phase fault BCV SW 4 (520513) 138 kV Bus a. Apply fault at the BCV SW 4 (520513) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BCV SW 4 138 KV 520513 TO CHERRYRD 4 138 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BC_SW__4__SLKHILLS_4 | 3 Phase fault BC SW 4 (520512) 138 kV Bus a. Apply fault at the BC SW 4 (520512) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BC SW 4 138 KV 520512 TO SLKHILLS 4 138 KV 521103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BEELINE4__BLUEBEL4 | 3 Phase fault BEELINE4 (515247) 138 kV Bus a. Apply fault at the BEELINE4 (515247) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONESTR4 138 KV 515245 TO BEELINE4 138 KV 515247 CKT 1 b.2. LOAD 1 515247 b.3. KELLYVL4 138 KV 515200 TO LONESTR4 138 KV 515245 CKT 1 b.4. LOAD 1 515245 b.5. KELLYVL4 138 KV 515200 TO BLUEBEL4 138 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BEELINE4__EXPGLNT4 | 3 Phase fault BEELINE4 (515247) 138 kV Bus a. Apply fault at the BEELINE4 (515247) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEELINE4 138 KV 515247 TO EXPGLNT4 138 KV 515473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BEELINE4__POLECTP4 | 3 Phase fault BEELINE4 (515247) 138 kV Bus a. Apply fault at the BEELINE4 (515247) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIBBENS4 138 KV 515237 TO BEELINE4 138 KV 515247 CKT 1 b.2. LOAD 1 515247 b.3. POLECTP4 138 KV 515218 TO TIBBENS4 138 KV 515237 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BELISLE4__38TH_ST4 | 3 Phase fault BELISLE4 (514844) 138 kV Bus a. Apply fault at the BELISLE4 (514844) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELISLE4 138 KV 514844 TO 38TH ST4 138 KV 514846 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BELISLE4__WESTERN4 | 3 Phase fault BELISLE4 (514844) 138 kV Bus a. Apply fault at the BELISLE4 (514844) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELISLE4 138 KV 514844 TO WESTERN4 138 KV 514869 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BEVYTAP5__FTSMTHE5 | 3 Phase fault BEVYTAP5 (515299) 161 kV Bus a. Apply fault at the BEVYTAP5 (515299) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVYTAP5 161 KV 515299 TO FTSMTHE5 161 KV 515300 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BING | 3 Phase fault BING-TP2 (511443) 69 kV Bus a. Apply fault at the BING-TP2 (511443) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BING-TP2 69 KV 511443 TO S.W.S.-2 69 KV 511476 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BINGERJ4__NIJECT_4 | 3 Phase fault BINGERJ4 (520827) 138 kV Bus a. Apply fault at the BINGERJ4 (520827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BINGERJ4 138 KV 520827 TO NIJECT 4 138 KV 521010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BINGERJ4__SICKLES4 | 3 Phase fault BINGERJ4 (520827) 138 kV Bus a. Apply fault at the BINGERJ4 (520827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BINGERJ4 138 KV 520827 TO SICKLES4 138 KV 521050 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BLANCH | 3 Phase fault BLANCH-2 (508801) 69 kV Bus a. Apply fault at the BLANCH-2 (508801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCH-2 69 KV 508801 TO LIEBERM2 69 KV 508805 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BLANCHD4__OU_SW_4 | 3 Phase fault BLANCHD4 (520828) 138 kV Bus a. Apply fault at the BLANCHD4 (520828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCHD4 138 KV 520828 TO OU SW 4 138 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BLOOMBG2__IPC_TAP2 | 3 Phase fault BLOOMBG2 (508055) 69 kV Bus a. Apply fault at the BLOOMBG2 (508055) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLOOMBG2 69 KV 508055 TO IPC TAP2 69 KV 508058 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BLUEBEL4__BOWDEN_4 | 3 Phase fault BLUEBEL4 (515242) 138 kV Bus a. Apply fault at the BLUEBEL4 (515242) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBEL4 138 KV 515242 TO BOWDEN 4 138 KV 515243 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BLUERIV4__PARKLN_4 | 3 Phase fault BLUERIV4 (515133) 138 kV Bus a. Apply fault at the BLUERIV4 (515133) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUERIV4 138 KV 515133 TO PARKLN 4 138 KV 515178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BORDER_____7__BECKHAM7 | 3 Phase fault BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345 KV 515458 TO BECKHAM7 345 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BORDER_____7__TUCO_INT___7 | 3 Phase fault BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345 KV 515458 TO TUCO_INT 7 345 KV 525832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BOWMAN_2__KNGINDT2 | 3 Phase fault BOWMAN 2 (514813) 69 kV Bus a. Apply fault at the BOWMAN 2 (514813) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOWMAN 2 69 KV 514813 TO KNGINDT2 69 KV 515625 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BOWMAN_2__OMKINGF2 | 3 Phase fault BOWMAN 2 (514813) 69 kV Bus a. Apply fault at the BOWMAN 2 (514813) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOWMAN 2 69 KV 514813 TO OMKINGF2 69 KV 529280 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BOWMAN_2__TURCRKT2 | 3 Phase fault BOWMAN 2 (514813) 69 kV Bus a. Apply fault at the BOWMAN 2 (514813) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOWMAN 2 69 KV 514813 TO TURCRKT2 69 KV 515517 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BRANDYBR__PIRKEY_4 | 3 Phase fault BRANDYBR (508596) 138 kV Bus a. Apply fault at the BRANDYBR (508596) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRANDYBR 138 KV 508596 TO EASTON 4 138 KV 509092 CKT 1 b.2. LOAD 1 509092 b.3. PIRKEY 4 138 KV 508562 TO EASTON 4 138 KV 509092 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BRCKWND4__BRECKNR4 | 3 Phase fault BRCKWND4 (514642) 138 kV Bus a. Apply fault at the BRCKWND4 (514642) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRCKWND4 138 KV 514642 TO BRECKNR4 138 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BRECKNR4__ENIDINT4 | 3 Phase fault BRECKNR4 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 138 KV 514815 TO ENIDINT4 138 KV 515383 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BRECKNR4__PLNSMEN4 | 3 Phase fault BRECKNR4 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 138 KV 514815 TO PLNSMEN4 138 KV 515641 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BRIDGCR4__SUNSHIN4 | 3 Phase fault BRIDGCR4 (520501) 138 kV Bus a. Apply fault at the BRIDGCR4 (520501) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRIDGCR4 138 KV 520501 TO SUNSHIN4 138 KV 521059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BRIDGCR4__TUTLETP4 | 3 Phase fault BRIDGCR4 (520501) 138 kV Bus a. Apply fault at the BRIDGCR4 (520501) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRIDGCR4 138 KV 520501 TO TUTLETP4 138 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BRISTOW4__BLUEBEL4 | 3 Phase fault BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 138 KV 515035 TO BLUEBEL4 138 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BRISTOW4__GRNWOOD4 | 3 Phase fault BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 138 KV 515035 TO GRNWOOD4 138 KV 515417 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BRISTOW4__KEYWEST4 | 3 Phase fault BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 138 KV 515035 TO KEYWEST4 138 KV 515048 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BRKN_BW4__BETHEL_4 | 3 Phase fault BRKN BW4 (505614) 138 kV Bus a. Apply fault at the BRKN BW4 (505614) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRKN BW4 138 KV 505614 TO BETHEL 4 138 KV 510928 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BRKN_BW4__CRAIGJT4 | 3 Phase fault BRKN BW4 (505614) 138 kV Bus a. Apply fault at the BRKN BW4 (505614) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRKN BW4 138 KV 505614 TO CRAIGJT4 138 KV 510890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BRKN_BW4__HOCHTWN4 | 3 Phase fault BRKN BW4 (505614) 138 kV Bus a. Apply fault at the BRKN BW4 (505614) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRKN BW4 138 KV 505614 TO HOCHTWN4 138 KV 520943 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BRYANML4__MUNZCTY4 | 3 Phase fault BRYANML4 (508056) 138 kV Bus a. Apply fault at the BRYANML4 (508056) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRYANML4 138 KV 508056 TO MUNZCTY4 138 KV 508064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BTLRJCT2__HM | 3 Phase fault BTLRJCT2 (520457) 69 kV Bus a. Apply fault at the BTLRJCT2 (520457) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BTLRJCT2 69 KV 520457 TO HM-BTTP2 69 KV 520942 CKT NO c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BUFFALO7__THISTLE7 | 3 Phase fault BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345 KV 532782 TO THISTLE7 345 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-221, GEN-2011-008, GEN-2017-121 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-221, GEN-2011-008, GEN-2017-121 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BUFORDR2__COOKVTP2 | 3 Phase fault BUFORDR2 (508287) 69 kV Bus a. Apply fault at the BUFORDR2 (508287) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFORDR2 69 KV 508287 TO COOKVTP2 69 KV 508338 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BUFORDR2__DEKALB_2 | 3 Phase fault BUFORDR2 (508287) 69 kV Bus a. Apply fault at the BUFORDR2 (508287) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFORDR2 69 KV 508287 TO DEKALB 2 69 KV 508289 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BUFORDR2__NAPLES_2 | 3 Phase fault BUFORDR2 (508287) 69 kV Bus a. Apply fault at the BUFORDR2 (508287) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFORDR2 69 KV 508287 TO NAPLES 2 69 KV 508307 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BULFOOT4__BULFTTP4 | 3 Phase fault BULFOOT4 (515960) 138 kV Bus a. Apply fault at the BULFOOT4 (515960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFOOT4 138 KV 515960 TO BULFTTP4 138 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BULFTTP4__DOVERSW4 | 3 Phase fault BULFTTP4 (520535) 138 kV Bus a. Apply fault at the BULFTTP4 (520535) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFTTP4 138 KV 520535 TO DOVERSW4 138 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BUNCHCK4__BRECKNR4 | 3 Phase fault BUNCHCK4 (514701) 138 kV Bus a. Apply fault at the BUNCHCK4 (514701) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 138 KV 514701 TO BRECKNR4 138 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BV | 3 Phase fault BV-COM-4 (510390) 138 kV Bus a. Apply fault at the BV-COM-4 (510390) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BV-COM-4 138 KV 510390 TO BV-SE--4 138 KV 510391 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BV | 3 Phase fault BV-COM-4 (510390) 138 kV Bus a. Apply fault at the BV-COM-4 (510390) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BV-COM-4 138 KV 510390 TO MOUNDRD4 138 KV 510395 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BV | 3 Phase fault BV-SE--4 (510391) 138 kV Bus a. Apply fault at the BV-SE--4 (510391) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BV-SE--4 138 KV 510391 TO BLUESTM4 138 KV 510394 CKT 1 b.2. LOAD 1 510394 b.3. BV-COM-4 138 KV 510390 TO BLUESTM4 138 KV 510394 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BV | 3 Phase fault BV-SE--4 (510391) 138 kV Bus a. Apply fault at the BV-SE--4 (510391) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NBVILLE4 138 KV 510386 TO BV-SE--4 138 KV 510391 CKT 1 b.2. LOAD 1 510391 b.3. NBVILLE4 138 KV 510386 TO COFFEYT4 138 KV 510422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BVRCNTY7__BADGER_7 | 3 Phase fault BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345 KV 515554 TO BADGER 7 345 KV 515677 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_C | 3 Phase fault C-RIVER4 (510946) 138 kV Bus a. Apply fault at the C-RIVER4 (510946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C-RIVER4 138 KV 510946 TO TALAWANDA 4 138 KV 510951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_C | 3 Phase fault C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 345 KV 515422 TO FIREWHL-TAP 345 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CADDO__2__WASHITA2 | 3 Phase fault CADDO 2 (520838) 69 kV Bus a. Apply fault at the CADDO 2 (520838) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CADDO 2 69 KV 520838 TO WASHITA2 69 KV 521088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CALRYTP2__MUSKOGE2 | 3 Phase fault CALRYTP2 (515211) 69 kV Bus a. Apply fault at the CALRYTP2 (515211) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALRYTP2 69 KV 515211 TO MUSKOGE2 69 KV 515221 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CANADN | 3 Phase fault CANADN-4 (514947) 138 kV Bus a. Apply fault at the CANADN-4 (514947) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADN-4 138 KV 514947 TO CANADNS4 138 KV 520842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CANADN7__FSHRTAP7 | 3 Phase fault CANADN7 (515605) 345 kV Bus a. Apply fault at the CANADN7 (515605) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANADN7 345 KV 515605 TO FSHRTAP7 345 KV 515610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CANADNS4__GOLDSBY4 | 3 Phase fault CANADNS4 (520842) 138 kV Bus a. Apply fault at the CANADNS4 (520842) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 138 KV 520842 TO GOLDSBY4 138 KV 520924 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CANA___4__CALUMET4 | 3 Phase fault CANA 4 (520502) 138 kV Bus a. Apply fault at the CANA 4 (520502) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANA 4 138 KV 520502 TO CALUMET4 138 KV 520839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CAN_GAS4__JENSEN_4 | 3 Phase fault CAN_GAS4 (511540) 138 kV Bus a. Apply fault at the CAN_GAS4 (511540) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 138 KV 511540 TO JENSEN 4 138 KV 514821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CARROLL6__DOLHILL6 | 3 Phase fault CARROLL6 (500140) 230 kV Bus a. Apply fault at the CARROLL6 (500140) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARROLL6 230 KV 500140 TO DOLHILL6 230 KV 500260 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CARSN | 3 Phase fault CARSN-N4 (509741) 138 kV Bus a. Apply fault at the CARSN-N4 (509741) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-N4 138 KV 509741 TO CARSONT4 138 KV 509865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CARSN | 3 Phase fault CARSN-S4 (509756) 138 kV Bus a. Apply fault at the CARSN-S4 (509756) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-S4 138 KV 509756 TO KENSH-W4 138 KV 509777 CKT 1 b.2. LOAD 1 509777 b.3. DENVR-C4 138 KV 509742 TO KENSH-W4 138 KV 509777 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CARSN | 3 Phase fault CARSN-S4 (509756) 138 kV Bus a. Apply fault at the CARSN-S4 (509756) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-S4 138 KV 509756 TO T.P.S.-4 138 KV 509788 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CARSN | 3 Phase fault CARSN-T4 (509739) 138 kV Bus a. Apply fault at the CARSN-T4 (509739) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-T4 138 KV 509739 TO UNIONAV4 138 KV 509740 CKT 1 b.2. LOAD 1 509740 b.3. UNIONAV4 138 KV 509740 TO CARSN-C4 138 KV 509749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CARSN | 3 Phase fault CARSN-T4 (509739) 138 kV Bus a. Apply fault at the CARSN-T4 (509739) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-T4 138 KV 509739 TO S.S.---4 138 KV 509815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CARTER_4__CHIKSAW4 | 3 Phase fault CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138 KV 515138 TO CHIKSAW4 138 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CARTER_4__HONEYCK4 | 3 Phase fault CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138 KV 515138 TO HONEYCK4 138 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CARTHGT4__LOGANSP4 | 3 Phase fault CARTHGT4 (509060) 138 kV Bus a. Apply fault at the CARTHGT4 (509060) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHGT4 138 KV 509060 TO LOGANSP4 138 KV 509071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CARTRCO4__GEN | 3 Phase fault CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138 KV 515561 TO GEN-2017-027 138 KV 588710 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CARTRCO4__ORIGINW4 | 3 Phase fault CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138 KV 515561 TO ORIGINW4 138 KV 515563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CASHION4__TWNLKJT4 | 3 Phase fault CASHION4 (520479) 138 kV Bus a. Apply fault at the CASHION4 (520479) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASHION4 138 KV 520479 TO TWNLKJT4 138 KV 520847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CATOOSA2__DAWSON | 3 Phase fault CATOOSA2 (509799) 69 kV Bus a. Apply fault at the CATOOSA2 (509799) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BCIRCLE2 69 KV 509794 TO CATOOSA2 69 KV 509799 CKT 1 b.2. DAWSON-2 69 KV 509791 TO BCIRCLE2 69 KV 509794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CATOOSA4__CDC | 3 Phase fault CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138 KV 509790 TO OWAS88_4 138 KV 509887 CKT 1 b.2. LOAD 1 509887 b.3. CDC-ET 4 138 KV 509839 TO OWAS88_4 138 KV 509887 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CATOOSA4__LLANETP4 | 3 Phase fault CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138 KV 509790 TO LLANETP4 138 KV 509804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CATOOSA4__PCATSAT4 | 3 Phase fault CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138 KV 509790 TO PCATSAT4 138 KV 509841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CATOOSA4__TERNITP4 | 3 Phase fault CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138 KV 509790 TO TERNITP4 138 KV 509835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CATSAGR5__COLINS_5 | 3 Phase fault CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ELMCRK 161 KV 300993 TO CATSAGR5 161 KV 512638 CKT 1 b.2. 5ELMCRK 161 KV 300993 TO COLINS 5 161 KV 512627 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CATSAGR5__MAID___5 | 3 Phase fault CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 161 KV 512638 TO MAID 5 161 KV 512648 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CDC | 3 Phase fault CDC-ET 4 (509839) 138 kV Bus a. Apply fault at the CDC-ET 4 (509839) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CDC-ET 4 138 KV 509839 TO OWAS88_4 138 KV 509887 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CDRDLTP4__OKEENE_4 | 3 Phase fault CDRDLTP4 (520848) 138 kV Bus a. Apply fault at the CDRDLTP4 (520848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CDRDLTP4 138 KV 520848 TO OKEENE 4 138 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CEDARLN4__SOONRTP4 | 3 Phase fault CEDARLN4 (514948) 138 kV Bus a. Apply fault at the CEDARLN4 (514948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARLN4 138 KV 514948 TO SOONRTP4 138 KV 514949 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CEDRDAL4__CDRDLTP4 | 3 Phase fault CEDRDAL4 (520507) 138 kV Bus a. Apply fault at the CEDRDAL4 (520507) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDRDAL4 138 KV 520507 TO CDRDLTP4 138 KV 520848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CEMRD_TP4__CMTRYRD4 | 3 Phase fault CEMRD_TP4 (511576) 138 kV Bus a. Apply fault at the CEMRD_TP4 (511576) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEMRD_TP4 138 KV 511576 TO CMTRYRD4 138 KV 515864 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CHAMSPR7__CLARKSV7 | 3 Phase fault CHAMSPR7 (506945) 345 kV Bus a. Apply fault at the CHAMSPR7 (506945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAMSPR7 345 KV 506945 TO CLARKSV7 345 KV 509745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055, GEN-2017-141 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055, GEN-2017-141 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CHAMSPR7__TONTITN7 | 3 Phase fault CHAMSPR7 (506945) 345 kV Bus a. Apply fault at the CHAMSPR7 (506945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAMSPR7 345 KV 506945 TO TONTITN7 345 KV 506959 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CHAPELH4__CHAPLHL4 | 3 Phase fault CHAPELH4 (508337) 138 kV Bus a. Apply fault at the CHAPELH4 (508337) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPELH4 138 KV 508337 TO CHAPLHL4 138 KV 509664 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CHCKSHA4__CKSHATP4 | 3 Phase fault CHCKSHA4 (520472) 138 kV Bus a. Apply fault at the CHCKSHA4 (520472) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHCKSHA4 138 KV 520472 TO CKSHATP4 138 KV 520473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CHEEKTP4__CHEEK_4 | 3 Phase fault CHEEKTP4 (515415) 138 kV Bus a. Apply fault at the CHEEKTP4 (515415) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHEEKTP4 138 KV 515415 TO CHEEK_4 138 KV 521125 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CHERYCK4__NORMHLL4 | 3 Phase fault CHERYCK4 (514957) 138 kV Bus a. Apply fault at the CHERYCK4 (514957) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERYCK4 138 KV 514957 TO NORMHLL4 138 KV 516097 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CHISHOLM7__BECKHAM7 | 3 Phase fault CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345 KV 511553 TO BECKHAM7 345 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CHISHOLM7__G16 | 3 Phase fault CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345 KV 511553 TO G16-037-TAP 345 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CHISHOM4__FAIRFLD4 | 3 Phase fault CHISHOM4 (515374) 138 kV Bus a. Apply fault at the CHISHOM4 (515374) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOM4 138 KV 515374 TO FAIRFLD4 138 KV 515468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CHOUTEAUCRK5__GEN | 3 Phase fault CHOUTEAUCRK5 (513570) 161 kV Bus a. Apply fault at the CHOUTEAUCRK5 (513570) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHOUTEAUCRK5 161 KV 513570 TO GEN-2017-061 161 KV 588990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CIMARON4__DVISION4 | 3 Phase fault CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYMAKR4 138 KV 514863 TO CIMARON4 138 KV 514898 CKT 1 b.2. DVISION4 138 KV 514853 TO HAYMAKR4 138 KV 514863 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CIMARON4__MCCLAIN4 | 3 Phase fault CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA 4 138 KV 514895 TO CIMARON4 138 KV 514898 CKT 1 b.2. SARA 4 138 KV 514895 TO MCCLAIN4 138 KV 514902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CIMARON4__MUSTANG4 | 3 Phase fault CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CZECHAL4 138 KV 514894 TO CIMARON4 138 KV 514898 CKT 1 b.2. XEROX 4 138 KV 514893 TO CZECHAL4 138 KV 514894 CKT 1 b.3. LOAD 1 514894 b.4. XEROX 4 138 KV 514893 TO MORGAN 4 138 KV 514896 CKT 1 b.5. LOAD 1 514896 b.6. MUSTANG4 138 KV 514861 TO MORGAN 4 138 KV 514896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CIMARON7__FSHRTAP7 | 3 Phase fault CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345 KV 514901 TO FSHRTAP7 345 KV 515610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MINCO5 trips on voltage protection settings | Disabling voltage protection settings for MINCO5prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CIMARON7__MATHWSN7 | 3 Phase fault CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345 KV 514901 TO MATHWSN7 345 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CIMARON7__NORMHLL7 | 3 Phase fault CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345 KV 514901 TO NORMHLL7 345 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CIP____4__CDC | 3 Phase fault CIP 4 (509714) 138 kV Bus a. Apply fault at the CIP 4 (509714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIP 4 138 KV 509714 TO CDC-ET 4 138 KV 509839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CIP____4__CDC____4 | 3 Phase fault CIP 4 (509714) 138 kV Bus a. Apply fault at the CIP 4 (509714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIP 4 138 KV 509714 TO CDC 4 138 KV 509715 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CKSHATP4__CORN_TP4 | 3 Phase fault CKSHATP4 (520473) 138 kV Bus a. Apply fault at the CKSHATP4 (520473) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CKSHATP4 138 KV 520473 TO CORN TP4 138 KV 520867 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CL | 3 Phase fault CL-AFTP4 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 138 KV 511446 TO ELKCTY-4 138 KV 511458 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CL | 3 Phase fault CL-AFTP4 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 138 KV 511446 TO HOB-JCT4 138 KV 511463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CLARKCOUNTY7__THISTLE7 | 3 Phase fault CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345 KV 539800 TO THISTLE7 345 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2011-008 trips on voltage protection settings | Disabling voltage protection settings for GEN-2011-008 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CLARKSV7__GEN | 3 Phase fault CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345 KV 509745 TO GEN-2017-140 345 KV 760389 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-141 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-141 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CLARKSV7__MUSKOGE7 | 3 Phase fault CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345 KV 509745 TO MUSKOGE7 345 KV 515224 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-141 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-141 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CLARKSV7__ONETA | 3 Phase fault CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345 KV 509745 TO ONETA--7 345 KV 509807 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-141 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-141 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CLARMR_5__CHOUTEAUCRK5 | 3 Phase fault CLARMR 5 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 161 KV 512651 TO CHOUTEAUCRK5 161 KV 513570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CLASSEN4__TROSPER4 | 3 Phase fault CLASSEN4 (514922) 138 kV Bus a. Apply fault at the CLASSEN4 (514922) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLASSEN4 138 KV 514922 TO CROSTWN4 138 KV 515851 CKT 1 b.2. LOAD 1 515851 b.3. LIGHTCK4 138 KV 514923 TO CROSTWN4 138 KV 515851 CKT 1 b.4. LOAD 1 515851 b.5. LIGHTCK4 138 KV 514923 TO TROSPER4 138 KV 514963 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CLEOSW_2__RNGWODJ2 | 3 Phase fault CLEOSW 2 (520855) 69 kV Bus a. Apply fault at the CLEOSW 2 (520855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOSW 2 69 KV 520855 TO RNGWODJ2 69 KV 521039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CLEVETP2__SO4TH__2 | 3 Phase fault CLEVETP2 (514722) 69 kV Bus a. Apply fault at the CLEVETP2 (514722) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVETP2 69 KV 514722 TO SO4TH 2 69 KV 514730 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CLEVLND7__G15 | 3 Phase fault CLEVLND7 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 345 KV 512694 TO G15-066T 345 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CLVLDSW4__AMBERTP4 | 3 Phase fault CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138 KV 520508 TO AMBERTP4 138 KV 520530 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CLVLDSW4__ANADARK4 | 3 Phase fault CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138 KV 520508 TO ANADARK4 138 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CLVLDSW4__COGAR__4 | 3 Phase fault CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138 KV 520508 TO COGAR 4 138 KV 520859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CMBLCRK4__CMBLTP_4 | 3 Phase fault CMBLCRK4 (515930) 138 kV Bus a. Apply fault at the CMBLCRK4 (515930) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMBLCRK4 138 KV 515930 TO CMBLTP 4 138 KV 520474 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CMBLTP_4__FOURCTP4 | 3 Phase fault CMBLTP 4 (520474) 138 kV Bus a. Apply fault at the CMBLTP 4 (520474) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMBLTP 4 138 KV 520474 TO FOURCTP4 138 KV 520545 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_COBRN_CREEK3__WHEELER____3 | 3 Phase fault COBRN_CREEK3 (523772) 115 kV Bus a. Apply fault at the COBRN_CREEK3 (523772) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COBRN_CREEK3 115 KV 523772 TO WHEELER 3 115 KV 523776 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_COFFEYT4__DEARING4 | 3 Phase fault COFFEYT4 (510422) 138 kV Bus a. Apply fault at the COFFEYT4 (510422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COFFEYT4 138 KV 510422 TO DEARING4 138 KV 533002 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_COLE___4__OU_SW_4 | 3 Phase fault COLE 4 (520861) 138 kV Bus a. Apply fault at the COLE 4 (520861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLE 4 138 KV 520861 TO OU SW 4 138 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_COLINS_5__CLARMR_5 | 3 Phase fault COLINS 5 (512627) 161 kV Bus a. Apply fault at the COLINS 5 (512627) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5KETONVL 161 KV 300997 TO COLINS 5 161 KV 512627 CKT 1 b.2. 5KETONVL 161 KV 300997 TO CLARMR 5 161 KV 512651 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_COMANC | 3 Phase fault COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69 KV 511436 TO L.E.S.-2 69 KV 511466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_COMANC | 3 Phase fault COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138 KV 511437 TO 112GORE4 138 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_COMANC | 3 Phase fault COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138 KV 511437 TO COMMTAP4 138 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_COMANC | 3 Phase fault COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138 KV 511437 TO L.E.S.-4 138 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_COMMTAP4__OMDUNCN4 | 3 Phase fault COMMTAP4 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMMTAP4 138 KV 511494 TO OMDUNCN4 138 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CORNVIL4__ALEX_BR4 | 3 Phase fault CORNVIL4 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138 KV 511449 TO ALEX BR4 138 KV 511516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CORNVIL4__CORN_TP4 | 3 Phase fault CORNVIL4 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138 KV 511449 TO CORN TP4 138 KV 520867 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CORNVIL4__LEONARD4 | 3 Phase fault CORNVIL4 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138 KV 511449 TO LEONARD4 138 KV 511575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CORNVIL4__MAUD___4 | 3 Phase fault CORNVIL4 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCHD4 138 KV 511508 TO MAUD 4 138 KV 515055 CKT 1 b.2. CORNVIL4 138 KV 511449 TO BLANCHD4 138 KV 511508 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CORNVIL4__N29CHIK4 | 3 Phase fault CORNVIL4 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138 KV 511449 TO N29CHIK4 138 KV 511502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CORNVIL4__NORGE | 3 Phase fault CORNVIL4 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138 KV 511449 TO NORGE--4 138 KV 511483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CORNVIL4__SANTAFE4 | 3 Phase fault CORNVIL4 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138 KV 511449 TO SANTAFE4 138 KV 511492 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CRAIGJT4__HOCHJCT4 | 3 Phase fault CRAIGJT4 (510890) 138 kV Bus a. Apply fault at the CRAIGJT4 (510890) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIGJT4 138 KV 510890 TO MTRIVER4 138 KV 521004 CKT 1 b.2. LOAD 1 521004 b.3. HOCHJCT4 138 KV 520823 TO MTRIVER4 138 KV 521004 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CRAIGJT4__MENA___4 | 3 Phase fault CRAIGJT4 (510890) 138 kV Bus a. Apply fault at the CRAIGJT4 (510890) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENA 4 138 KV 507436 TO GORDON TAP 4 138 KV 507461 CKT 1 b.2. LOAD A1 507461 b.3. GORDON TAP 4 138 KV 507461 TO CRAIGJT4 138 KV 510890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CRESENT4__GEN | 3 Phase fault CRESENT4 (515377) 138 kV Bus a. Apply fault at the CRESENT4 (515377) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESENT4 138 KV 515377 TO GEN-2016-032 138 KV 587210 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CRESENT4__TWNLKSW4 | 3 Phase fault CRESENT4 (515377) 138 kV Bus a. Apply fault at the CRESENT4 (515377) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESENT4 138 KV 515377 TO TWNLKSW4 138 KV 521073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CTNWOOD4__ARCADIA4 | 3 Phase fault CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138 KV 514827 TO ARCADIA4 138 KV 514907 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CTNWOOD4__CRESENT4 | 3 Phase fault CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138 KV 514827 TO CRESENT4 138 KV 515377 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CTNWOOD4__KETCHTP4 | 3 Phase fault CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138 KV 514827 TO LBRTYLK4 138 KV 515373 CKT 1 b.2. LOAD 1 515373 b.3. WATRLOO4 138 KV 514831 TO LBRTYLK4 138 KV 515373 CKT 1 b.4. LOAD 1 515373 b.5. WATRLOO4 138 KV 514831 TO WHITESB4 138 KV 515467 CKT 1 b.6. LOAD 1 515467 b.7. MITCHSB4 138 KV 515466 TO WHITESB4 138 KV 515467 CKT 1 b.8. LOAD 1 515467 b.9. KETCHTP4 138 KV 514828 TO MITCHSB4 138 KV 515466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CTNWOOD4__KINZE__4 | 3 Phase fault CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138 KV 514827 TO PINE ST4 138 KV 514829 CKT 1 b.2. LOAD 1 514829 b.3. LOAD 2 514829 b.4. PINE ST4 138 KV 514829 TO FITZGRD4 138 KV 514830 CKT 1 b.5. LOAD 1 514830 b.6. FITZGRD4 138 KV 514830 TO KINZE 4 138 KV 515008 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CTNWOOD4__LBRTYLK4 | 3 Phase fault CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138 KV 514827 TO LBRTYLK4 138 KV 515373 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CUSTDAY1_5__HERRON_5 | 3 Phase fault CUSTDAY1 5 (513590) 161 kV Bus a. Apply fault at the CUSTDAY1 5 (513590) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTDAY1 5 161 KV 513590 TO HERRON 5 161 KV 513591 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DANFRTH4__KETCH__4 | 3 Phase fault DANFRTH4 (514833) 138 kV Bus a. Apply fault at the DANFRTH4 (514833) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DANFRTH4 138 KV 514833 TO KETCH 4 138 KV 514834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DARENCT2__ALAMANC2 | 3 Phase fault DARENCT2 (509647) 69 kV Bus a. Apply fault at the DARENCT2 (509647) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DARENCT2 69 KV 509647 TO ALAMANC2 69 KV 509649 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DARENCT2__DARENCO2 | 3 Phase fault DARENCT2 (509647) 69 kV Bus a. Apply fault at the DARENCT2 (509647) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DARENCT2 69 KV 509647 TO DARENCO2 69 KV 509648 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DAWSON | 3 Phase fault DAWSON-4 (509792) 138 kV Bus a. Apply fault at the DAWSON-4 (509792) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSON-4 138 KV 509792 TO DAWSONT4 138 KV 509803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DAWSONT4__N21ST | 3 Phase fault DAWSONT4 (509803) 138 kV Bus a. Apply fault at the DAWSONT4 (509803) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONT4 138 KV 509803 TO N21ST--4 138 KV 509866 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DAYTON_4__HOBBYLO4 | 3 Phase fault DAYTON 4 (514892) 138 kV Bus a. Apply fault at the DAYTON 4 (514892) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAYTON 4 138 KV 514892 TO HOBBYLO4 138 KV 515338 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DEEPFKT2__DEEPFRK2 | 3 Phase fault DEEPFKT2 (514970) 69 kV Bus a. Apply fault at the DEEPFKT2 (514970) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEEPFKT2 69 KV 514970 TO DEEPFRK2 69 KV 514974 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DELWARE4__FARML__4 | 3 Phase fault DELWARE4 (510379) 138 kV Bus a. Apply fault at the DELWARE4 (510379) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELWARE4 138 KV 510379 TO FARML 4 138 KV 512734 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DELWARE7__N.E.S. | 3 Phase fault DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 345 KV 510380 TO N.E.S.-7 345 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DELWARE7__NEOSHO_7 | 3 Phase fault DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 345 KV 510380 TO NEOSHO 7 345 KV 532793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DENVR | 3 Phase fault DENVR-E4 (509743) 138 kV Bus a. Apply fault at the DENVR-E4 (509743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVR-E4 138 KV 509743 TO DENVTAP4 138 KV 509746 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DENVR | 3 Phase fault DENVR-W4 (509748) 138 kV Bus a. Apply fault at the DENVR-W4 (509748) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVR-W4 138 KV 509748 TO DENV_WTAP4 138 KV 509896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DENVTAP4__T.NO. | 3 Phase fault DENVTAP4 (509746) 138 kV Bus a. Apply fault at the DENVTAP4 (509746) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVTAP4 138 KV 509746 TO T.NO.--4 138 KV 509817 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DENVTAP4__W.ED. | 3 Phase fault DENVTAP4 (509746) 138 kV Bus a. Apply fault at the DENVTAP4 (509746) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVTAP4 138 KV 509746 TO W.ED.-E4 138 KV 509822 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DEQUEEN2__LOCKESB2 | 3 Phase fault DEQUEEN2 (507418) 69 kV Bus a. Apply fault at the DEQUEEN2 (507418) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEQUEEN2 69 KV 507418 TO LOCKESB2 69 KV 507422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DEQUEEN4__CRAIGJT4 | 3 Phase fault DEQUEEN4 (507419) 138 kV Bus a. Apply fault at the DEQUEEN4 (507419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEQUEEN4 138 KV 507419 TO CRAIGJT4 138 KV 510890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DEWEY__4__CANTNLK4 | 3 Phase fault DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138 KV 514787 TO CANTNLK4 138 KV 515964 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DEWEY__4__REDCLFT4 | 3 Phase fault DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138 KV 514787 TO REDCLFT4 138 KV 515533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DEWEY__4__TALOGA_4 | 3 Phase fault DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138 KV 514787 TO TALOGA 4 138 KV 521065 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DEWEY__4__TLGAWND4 | 3 Phase fault DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138 KV 514787 TO TLGAWND4 138 KV 515390 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DGRASSE4__MOORLND4 | 3 Phase fault DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138 KV 515853 TO MOORLND4 138 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DGRASSE4__ROSEVLY4 | 3 Phase fault DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138 KV 515853 TO ROSEVLY4 138 KV 520436 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DGRASSE7__THISTLE7 | 3 Phase fault DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 345 KV 515852 TO THISTLE7 345 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2011-008 trips on voltage protection settings | Disabling voltage protection settings for GEN-2011-008 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BANN___4__NWT | 3 Phase fault BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138 KV 508054 TO NWT-BNT4 138 KV 508070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ARSHILL4__STLGENS4 | 3 Phase fault ARSHILL4 (507711) 138 kV Bus a. Apply fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138 KV 507711 TO STLGENS4 138 KV 507789 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DILLARD4__WOLFCRK4 | 3 Phase fault DILLARD4 (515142) 138 kV Bus a. Apply fault at the DILLARD4 (515142) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DILLARD4 138 KV 515142 TO WOLFCRK4 138 KV 515143 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DOLHILL7__SW_SHV_7 | 3 Phase fault DOLHILL7 (500250) 345 kV Bus a. Apply fault at the DOLHILL7 (500250) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DOLHILL7 345 KV 500250 TO SW SHV 7 345 KV 507760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DOUGLTP4__CLASSEN4 | 3 Phase fault DOUGLTP4 (514868) 138 kV Bus a. Apply fault at the DOUGLTP4 (514868) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOUGLTP4 138 KV 514868 TO CLASSEN4 138 KV 514922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DOUGLTP4__WESTERN4 | 3 Phase fault DOUGLTP4 (514868) 138 kV Bus a. Apply fault at the DOUGLTP4 (514868) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOUGLTP4 138 KV 514868 TO WESTERN4 138 KV 514869 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DOVERSW2__HENESEY2 | 3 Phase fault DOVERSW2 (520881) 69 kV Bus a. Apply fault at the DOVERSW2 (520881) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW2 69 KV 520881 TO HENESEY2 69 KV 520940 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DOVERSW2__LACEY__2 | 3 Phase fault DOVERSW2 (520881) 69 kV Bus a. Apply fault at the DOVERSW2 (520881) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW2 69 KV 520881 TO LACEY 2 69 KV 520967 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DOVERSW4__GEN | 3 Phase fault DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138 KV 520882 TO GEN-2016-118 138 KV 587940 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DOVERSW4__GEN | 3 Phase fault DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138 KV 520882 TO GEN-2018-011 138 KV 762493 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DOVERSW4__KGFSJCT4 | 3 Phase fault DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKNGFSH4 138 KV 520603 TO DOVERSW4 138 KV 520882 CKT 1 b.2. KGFSJCT4 138 KV 520405 TO NKNGFSH4 138 KV 520603 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DOVERSW4__OKEENE_4 | 3 Phase fault DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138 KV 520882 TO OKEENE 4 138 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DOVERSW4__TWNLKSW4 | 3 Phase fault DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVER 4 138 KV 520879 TO DOVERSW4 138 KV 520882 CKT 1 b.2. TWNLAKE4 138 KV 520540 TO DOVER 4 138 KV 520879 CKT 1 b.3. LOAD 1 520879 b.4. TWNLAKE4 138 KV 520540 TO TWNLKSW4 138 KV 521073 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DOVERTP2__DOVERSW2 | 3 Phase fault DOVERTP2 (514772) 69 kV Bus a. Apply fault at the DOVERTP2 (514772) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERTP2 69 KV 514772 TO DOVERSW2 69 KV 520881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DOVERTP2__REDWING2 | 3 Phase fault DOVERTP2 (514772) 69 kV Bus a. Apply fault at the DOVERTP2 (514772) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERTP2 69 KV 514772 TO REDWING2 69 KV 515976 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DOVERTP2__TURCRKT2 | 3 Phase fault DOVERTP2 (514772) 69 kV Bus a. Apply fault at the DOVERTP2 (514772) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERTP2 69 KV 514772 TO TURCRKT2 69 KV 515517 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DRAPER_4__BARNES_4 | 3 Phase fault DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138 KV 514933 TO BARNES 4 138 KV 515003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DRAPER_4__GM_____4 | 3 Phase fault DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138 KV 514933 TO GM 4 138 KV 514961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DRAPER_4__MIDWEST4 | 3 Phase fault DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138 KV 514933 TO MIDWEST4 138 KV 514946 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DRAPER_4__SOONRTP4 | 3 Phase fault DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138 KV 514933 TO SOONRTP4 138 KV 514949 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DRAPER_7__NORMHLL7 | 3 Phase fault DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345 KV 514934 TO NORMHLL7 345 KV 516096 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DRAPER_7__SEMINOL7 | 3 Phase fault DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345 KV 514934 TO SEMINOL7 345 KV 515045 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DRYGULCH5__GEN | 3 Phase fault DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 161 KV 512629 TO GEN-2017-073 161 KV 589110 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DUGLASV2__DARENCT2 | 3 Phase fault DUGLASV2 (509645) 69 kV Bus a. Apply fault at the DUGLASV2 (509645) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUGLASV2 69 KV 509645 TO BLALOCK2 69 KV 509646 CKT 1 b.2. LOAD 1 509646 b.3. BLALOCK2 69 KV 509646 TO DARENCT2 69 KV 509647 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DUGLASV2__MAUDT__2 | 3 Phase fault DUGLASV2 (509645) 69 kV Bus a. Apply fault at the DUGLASV2 (509645) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUGLASV2 69 KV 509645 TO MAUDT 2 69 KV 509653 CKT NO c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DUGLASV2__ROACH__2 | 3 Phase fault DUGLASV2 (509645) 69 kV Bus a. Apply fault at the DUGLASV2 (509645) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUGLASV2 69 KV 509645 TO NLINDEN2 69 KV 509652 CKT 1 b.2. LOAD 1 509652 b.3. NLINDEN2 69 KV 509652 TO ROACH 2 69 KV 509668 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DUNCAN | 3 Phase fault DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138 KV 511453 TO OMDUNCN4 138 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DVISION4__HAYMAKR4 | 3 Phase fault DVISION4 (514853) 138 kV Bus a. Apply fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 138 KV 514853 TO HAYMAKR4 138 KV 514863 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DVISION4__HEFNER_4 | 3 Phase fault DVISION4 (514853) 138 kV Bus a. Apply fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKESID4 138 KV 514849 TO DVISION4 138 KV 514853 CKT 1 b.2. LOAD 1 514853 b.3. HEFNER 4 138 KV 514848 TO LAKESID4 138 KV 514849 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DVISION4__MUSTANG4 | 3 Phase fault DVISION4 (514853) 138 kV Bus a. Apply fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 138 KV 514853 TO MUSTANG4 138 KV 514861 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DVISION4__NORTWST4 | 3 Phase fault DVISION4 (514853) 138 kV Bus a. Apply fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 138 KV 514853 TO RICHRDS4 138 KV 514862 CKT 1 b.2. LOAD 1 514862 b.3. RICHRDS4 138 KV 514862 TO PIEDMNT4 138 KV 514864 CKT 1 b.4. LOAD 1 514864 b.5. PIEDMNT4 138 KV 514864 TO NORTWST4 138 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DVISION4__RICHRDS4 | 3 Phase fault DVISION4 (514853) 138 kV Bus a. Apply fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 138 KV 514853 TO RICHRDS4 138 KV 514862 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DX | 3 Phase fault DX----W2 (509796) 69 kV Bus a. Apply fault at the DX----W2 (509796) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DX----W2 69 KV 509796 TO S.S.---2 69 KV 509816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_EAGLCHF2__RNGWODJ2 | 3 Phase fault EAGLCHF2 (520890) 69 kV Bus a. Apply fault at the EAGLCHF2 (520890) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLCHF2 69 KV 520890 TO RNGWODJ2 69 KV 521039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_EKNGFSH4__EKFSHTP4 | 3 Phase fault EKNGFSH4 (520484) 138 kV Bus a. Apply fault at the EKNGFSH4 (520484) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EKNGFSH4 138 KV 520484 TO EKFSHTP4 138 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ELRENO_CIMARON | 3 Phase fault EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138 KV 514819 TO CIMARON4 138 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ELRENO_JENSENT | 3 Phase fault EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138 KV 514819 TO JENSENT4 138 KV 514820 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ELRENO_ROMNOSE | 3 Phase fault EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138 KV 514819 TO OMEGA 4 138 KV 515962 CKT 1 b.2. LOAD 1 515962 b.3. ROMNOSE4 138 KV 514823 TO OMEGA 4 138 KV 515962 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ELKCITY6__CHISHOLM6 | 3 Phase fault ELKCITY6 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 230 KV 511490 TO CHISHOLM6 230 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ELKCTY_CLINTJC4 | 3 Phase fault ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 138 KV 511458 TO CLINTJC4 138 KV 511485 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ELKCTY_FALCNRD | 3 Phase fault ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 138 KV 511458 TO FALCNRD4 138 KV 511511 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ELKCTY_REDHLSW | 3 Phase fault ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 138 KV 511458 TO REDHLSW4 138 KV 521116 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_EMPIRE_4__FLETCH | 3 Phase fault EMPIRE 4 (520900) 138 kV Bus a. Apply fault at the EMPIRE 4 (520900) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMPIRE 4 138 KV 520900 TO FLETCH-4 138 KV 520912 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ENID___2__SO4TH__2 | 3 Phase fault ENID 2 (514727) 69 kV Bus a. Apply fault at the ENID 2 (514727) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENID 2 69 KV 514727 TO SO4TH 2 69 KV 514730 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ERLSBOR2__FRSTHIL2 | 3 Phase fault ERLSBOR2 (515073) 69 kV Bus a. Apply fault at the ERLSBOR2 (515073) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ERLSBOR2 69 KV 515073 TO FRSTHIL2 69 KV 515074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_EUFREST2__WELLSPA2 | 3 Phase fault EUFREST2 (515214) 69 kV Bus a. Apply fault at the EUFREST2 (515214) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUFREST2 69 KV 515214 TO WELLSPA2 69 KV 515215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_EXCLART4__EXPCLAR4 | 3 Phase fault EXCLART4 (510401) 138 kV Bus a. Apply fault at the EXCLART4 (510401) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXCLART4 138 KV 510401 TO EXPCLAR4 138 KV 510405 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_EXCLART4__G17 | 3 Phase fault EXCLART4 (510401) 138 kV Bus a. Apply fault at the EXCLART4 (510401) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXCLART4 138 KV 510401 TO G17-077-TAP 138 KV 589154 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_EXPLGLN4__EXPGLNT4 | 3 Phase fault EXPLGLN4 (515248) 138 kV Bus a. Apply fault at the EXPLGLN4 (515248) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXPLGLN4 138 KV 515248 TO EXPGLNT4 138 KV 515473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_EYLAU__4__BUCHANN4 | 3 Phase fault EYLAU 4 (509655) 138 kV Bus a. Apply fault at the EYLAU 4 (509655) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EYLAU 4 138 KV 509655 TO BUCHANN4 138 KV 509656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FAIRVEW2__OKEENE_2 | 3 Phase fault FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69 KV 520909 TO OKEENE 2 69 KV 521015 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FAIRVEW2__OMFAIRV2 | 3 Phase fault FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69 KV 520909 TO OMFAIRV2 69 KV 529343 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FAIRVEW2__RNGWODJ2 | 3 Phase fault FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69 KV 520909 TO RNGWODJ2 69 KV 521039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FIXCT4__FIXICO_4 | 3 Phase fault FIXCT4 (510877) 138 kV Bus a. Apply fault at the FIXCT4 (510877) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIXCT4 138 KV 510877 TO FIXICO 4 138 KV 515078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FIXCT4__WELETK4 | 3 Phase fault FIXCT4 (510877) 138 kV Bus a. Apply fault at the FIXCT4 (510877) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIXCT4 138 KV 510877 TO WELETK4 138 KV 510902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FLETCHR4__FLE_TAP4 | 3 Phase fault FLETCHR4 (511422) 138 kV Bus a. Apply fault at the FLETCHR4 (511422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR4 138 KV 511422 TO FLE TAP4 138 KV 511423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FLE_TAP4__G16 | 3 Phase fault FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138 KV 511423 TO G16-097-TAP 138 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FLE_TAP4__L.E.S. | 3 Phase fault FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138 KV 511423 TO L.E.S.-4 138 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FLOURNY2__PINESRD2 | 3 Phase fault FLOURNY2 (507726) 69 kV Bus a. Apply fault at the FLOURNY2 (507726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 69 KV 507726 TO PINESRD2 69 KV 507747 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FLOURNY2__WASKOM_2 | 3 Phase fault FLOURNY2 (507726) 69 kV Bus a. Apply fault at the FLOURNY2 (507726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 69 KV 507726 TO WASKOM 2 69 KV 508839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FLOURNY2__WOOLWTP2 | 3 Phase fault FLOURNY2 (507726) 69 kV Bus a. Apply fault at the FLOURNY2 (507726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 69 KV 507726 TO WOOLWTP2 69 KV 507770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FOREMAN2__DEQUEEN2 | 3 Phase fault FOREMAN2 (507421) 69 kV Bus a. Apply fault at the FOREMAN2 (507421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORMANR2 69 KV 507407 TO FOREMAN2 69 KV 507421 CKT 1 b.2. LOAD 1 507421 b.3. DEQUEEN 2 69 KV 504120 TO FORMANR2 69 KV 507407 CKT 1 b.4. LOAD A1 507407 b.5. DEQUEEN 2 69 KV 504120 TO DEQUEEN2 69 KV 507418 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FOREMAN2__FOREMAG2 | 3 Phase fault FOREMAN2 (507421) 69 kV Bus a. Apply fault at the FOREMAN2 (507421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOREMAN2 69 KV 507421 TO FOREMAG2 69 KV 507440 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FOREMAN2__PATTERS2 | 3 Phase fault FOREMAN2 (507421) 69 kV Bus a. Apply fault at the FOREMAN2 (507421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOREMAN2 69 KV 507421 TO PATTERS2 69 KV 507429 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FOURCTP4__FOURCNT4 | 3 Phase fault FOURCTP4 (520545) 138 kV Bus a. Apply fault at the FOURCTP4 (520545) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOURCTP4 138 KV 520545 TO FOURCNT4 138 KV 520546 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FOURCTP4__TWNLKJT4 | 3 Phase fault FOURCTP4 (520545) 138 kV Bus a. Apply fault at the FOURCTP4 (520545) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOURCTP4 138 KV 520545 TO TWNLKJT4 138 KV 520847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FRMNTAP4__FAIRMON4 | 3 Phase fault FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138 KV 514709 TO FAIRMON4 138 KV 514712 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FRMNTAP4__SO4TH__4 | 3 Phase fault FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138 KV 514709 TO SO4TH 4 138 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FRMNTAP4__WOODRNG4 | 3 Phase fault FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138 KV 514709 TO WOODRNG4 138 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FRNKLNS4__CANADNS4 | 3 Phase fault FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRNKLNS4 138 KV 520917 TO LIDDELL4 138 KV 520975 CKT 1 b.2. LOAD 1 520975 b.3. NOBLE4 138 KV 520400 TO LIDDELL4 138 KV 520975 CKT 1 b.4. LOAD 1 520975 b.5. NOBLE4 138 KV 520400 TO CANADNS4 138 KV 520842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FRNKLNS4__OU_SW_4 | 3 Phase fault FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ACME 4 138 KV 520802 TO FRNKLNS4 138 KV 520917 CKT 1 b.2. ACME 4 138 KV 520802 TO WNORMAN4 138 KV 521095 CKT 1 b.3. LOAD 1 521095 b.4. LAMAR4 138 KV 520403 TO WNORMAN4 138 KV 521095 CKT 1 b.5. LOAD 1 521095 b.6. LAMAR4 138 KV 520403 TO OU SW 4 138 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FRNKLNS4__PINK_SW4 | 3 Phase fault FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLN4 138 KV 520913 TO FRNKLNS4 138 KV 520917 CKT 1 b.2. FRANKLN4 138 KV 520913 TO PINK SW4 138 KV 521028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FRNKLNS4__SUNSHIN4 | 3 Phase fault FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRNKLNS4 138 KV 520917 TO WMOORE 4 138 KV 521123 CKT 1 b.2. LOAD 1 521123 b.3. BAILEY4 138 KV 520401 TO WMOORE 4 138 KV 521123 CKT 1 b.4. LOAD 1 521123 b.5. BAILEY4 138 KV 520401 TO SUNSHIN4 138 KV 521059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FROGVIL4__HUGO_PP4 | 3 Phase fault FROGVIL4 (520918) 138 kV Bus a. Apply fault at the FROGVIL4 (520918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FROGVIL4 138 KV 520918 TO HUGO PP4 138 KV 520948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FRSTHIL4__STRLGTP4 | 3 Phase fault FRSTHIL4 (515075) 138 kV Bus a. Apply fault at the FRSTHIL4 (515075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRSTHIL4 138 KV 515075 TO STRLGTP4 138 KV 515286 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FTSMTHE5__COLONY_5 | 3 Phase fault FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5 (515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161 KV 515300 TO COLONY 5 161 KV 515345 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FTSMTHE5__FTSMTHW5 | 3 Phase fault FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5 (515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161 KV 515300 TO FTSMTHW5 161 KV 515301 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FTSMTHE5__QUANXTP5 | 3 Phase fault FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5 (515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161 KV 515300 TO QUANXTP5 161 KV 515310 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FTSMTHW5__ARKOMA_5 | 3 Phase fault FTSMTHW5 (515301) 161 kV Bus a. Apply fault at the FTSMTHW5 (515301) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 161 KV 515301 TO ARKOMA 5 161 KV 515306 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FT_GIB_5__OKAYGR_5 | 3 Phase fault FT GIB 5 (505560) 161 kV Bus a. Apply fault at the FT GIB 5 (505560) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FT GIB 5 161 KV 505560 TO OKAYGR 5 161 KV 512640 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FULTONE4__21STTAP4 | 3 Phase fault FULTONE4 (509797) 138 kV Bus a. Apply fault at the FULTONE4 (509797) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FULTONE4 138 KV 509797 TO S21ST--4 138 KV 509808 CKT 1 b.2. LOAD 1 509808 b.3. S21ST--4 138 KV 509808 TO 21STTAP4 138 KV 509828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FULTONW4__KENSH | 3 Phase fault FULTONW4 (509829) 138 kV Bus a. Apply fault at the FULTONW4 (509829) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FULTONW4 138 KV 509829 TO KENSH-E-TP4 138 KV 509830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FULTON____3__HOPE___3 | 3 Phase fault FULTON 3 (503912) 115 kV Bus a. Apply fault at the FULTON 3 (503912) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FULTON 3 115 KV 503912 TO HOPE 3 115 KV 507453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_G07621119 | 3 Phase fault G07621119-20 (515599) 345 kV Bus a. Apply fault at the G07621119-20 (515599) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G07621119-20 345 KV 515599 TO GREAT_WESTRN 345 KV 585410 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_G07621119 | 3 Phase fault G07621119-20 (515599) 345 kV Bus a. Apply fault at the G07621119-20 (515599) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G07621119-20 345 KV 515599 TO PRSIMN_CRK1 345 KV 585430 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_G15 | 3 Phase fault G15-066T (560056) 345 kV Bus a. Apply fault at the G15-066T (560056) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G15-066T 345 KV 560056 TO GEN-2015-066 345 KV 585040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_G16 | 3 Phase fault G16-003-TAP (560071) 345 kV Bus a. Apply fault at the G16-003-TAP (560071) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP 345 KV 560071 TO GEN-2017-011 345 KV 588560 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_G16 | 3 Phase fault G16-037-TAP (560078) 345 kV Bus a. Apply fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345 KV 560078 TO GEN-2016-037 345 KV 587230 CKT 1 | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_G16 | 3 Phase fault G16-091-TAP (587744) 345 kV Bus a. Apply fault at the G16-091-TAP (587744) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-091-TAP 345 KV 587744 TO GEN-2016-095 345 KV 587770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_G16133G16146__G16133_345GS | 3 Phase fault G16133G16146 (588039) 345 kV Bus a. Apply fault at the G16133G16146 (588039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16133G16146 345 KV 588039 TO G16133_345GS 345 KV 588040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_G17-009_NESHO | 3 Phase fault G17-009-TAP (532777) 345 kV Bus a. Apply fault at the G17-009-TAP (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP 345 KV 532777 TO NEOSHO 7 345 KV 532793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_G17-092_FIREWHLTAP | 3 Phase fault G17-092-SWYD (588838) 345 kV Bus a. Apply fault at the G17-092-SWYD (588838) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-092-SWYD 345 KV 588838 TO FIREWHL-TAP 345 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_G17_151_G18-015 | 3 Phase fault G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345 KV 762216 TO G18-015-TAP 345 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GLASMTN4__MOORLND4 | 3 Phase fault GLASMTN4 (514788) 138 kV Bus a. Apply fault at the GLASMTN4 (514788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLASMTN4 138 KV 514788 TO MOORLND4 138 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GLENWD_4__IMO____4 | 3 Phase fault GLENWD 4 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 138 KV 514734 TO IMO 4 138 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GOLDSBY4__OU_SW_4 | 3 Phase fault GOLDSBY4 (520924) 138 kV Bus a. Apply fault at the GOLDSBY4 (520924) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOLDSBY4 138 KV 520924 TO OU SW 4 138 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GORE___5__EUFAULA5 | 3 Phase fault GORE 5 (505552) 161 kV Bus a. Apply fault at the GORE 5 (505552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161 KV 505552 TO EUFAULA5 161 KV 505570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GORE___5__MUSKTAP5 | 3 Phase fault GORE 5 (505552) 161 kV Bus a. Apply fault at the GORE 5 (505552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161 KV 505552 TO MUSKTAP5 161 KV 505558 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GORE___5__TENKIL_5 | 3 Phase fault GORE 5 (505552) 161 kV Bus a. Apply fault at the GORE 5 (505552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161 KV 505552 TO TENKIL 5 161 KV 505566 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GORE___5__WEBFALL5 | 3 Phase fault GORE 5 (505552) 161 kV Bus a. Apply fault at the GORE 5 (505552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161 KV 505552 TO WEBFALL5 161 KV 505554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GORE___5__WELEETK5 | 3 Phase fault GORE 5 (505552) 161 kV Bus a. Apply fault at the GORE 5 (505552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161 KV 505552 TO WELEETK5 161 KV 505590 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRACMNT4__ANADARK4 | 3 Phase fault GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138 KV 515802 TO ANADARK4 138 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN trips on voltage protection settings | Disabling voltage protection settings for BLUCAN prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRACMNT4__WASHITA4 | 3 Phase fault GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138 KV 515802 TO WASHITA4 138 KV 521089 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRACMNT7__G16 | 3 Phase fault GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345 KV 515800 TO G16-037-TAP 345 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRACMNT7__G16 | 3 Phase fault GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345 KV 515800 TO G16-091-TAP 345 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRACMNT7__GEN | 3 Phase fault GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345 KV 515800 TO GEN-2015-093 345 KV 563269 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRANNIS___2__DEQUEEN2 | 3 Phase fault GRANNIS 2 (504129) 69 kV Bus a. Apply fault at the GRANNIS 2 (504129) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANNIS 2 69 KV 504129 TO DEQUEEN2 69 KV 507418 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRAPEVINE__6__NICHOLS____6 | 3 Phase fault GRAPEVINE 6 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 230 KV 523771 TO NICHOLS 6 230 KV 524044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRAPEVINE__6__WHEELER____6 | 3 Phase fault GRAPEVINE 6 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 230 KV 523771 TO WHEELER 6 230 KV 523777 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA1__5__CHOUTEAUCRK5 | 3 Phase fault GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 161 KV 512656 TO CHOUTEAUCRK5 161 KV 513570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA1__5__MAID___5 | 3 Phase fault GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 161 KV 512656 TO WMAIN ST5 161 KV 512742 CKT 1 b.2. LOAD 1 512742 b.3. WMAIN ST5 161 KV 512742 TO NWMAID5 161 KV 512757 CKT 1 b.4. LOAD 1 512757 b.5. NWMAID5 161 KV 512757 TO GERALDGAY5 161 KV 512760 CKT 1 b.6. LOAD 1 512760 b.7. MAID 5 161 KV 512648 TO GERALDGAY5 161 KV 512760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA1__5__WAGNOR_5 | 3 Phase fault GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 161 KV 512656 TO WAGNOR 5 161 KV 512700 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA1__7__GREC_TAP5 | 3 Phase fault GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 345 KV 512650 TO GREC TAP5 345 KV 512865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA1__7__TONECE7 | 3 Phase fault GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 345 KV 512650 TO TONECE7 345 KV 512750 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDGVTP4__MEEKRSW4 | 3 Phase fault GRDGVTP4 (520526) 138 kV Bus a. Apply fault at the GRDGVTP4 (520526) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDGVTP4 138 KV 520526 TO MEEKRSW4 138 KV 520994 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GREAT_WESTRN__COWBOY_RIDGE | 3 Phase fault GREAT_WESTRN (585410) 345 kV Bus a. Apply fault at the GREAT_WESTRN (585410) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GREAT_WESTRN 345 KV 585410 TO COWBOY_RIDGE 345 KV 585420 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GREC_TAP5__IGLOOV_7 | 3 Phase fault GREC TAP5 (512865) 345 kV Bus a. Apply fault at the GREC TAP5 (512865) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GREC TAP5 345 KV 512865 TO IGLOOV 7 345 KV 513596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRTWSRN7__GUTHRIE7 | 3 Phase fault GRTWSRN7 (515825) 345 kV Bus a. Apply fault at the GRTWSRN7 (515825) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRTWSRN7 345 KV 515825 TO GUTHRIE7 345 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HAMMTAP4__HAMMETT4 | 3 Phase fault HAMMTAP4 (515046) 138 kV Bus a. Apply fault at the HAMMTAP4 (515046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMMTAP4 138 KV 515046 TO HAMMETT4 138 KV 520951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HAMMTAP4__LINCOLN4 | 3 Phase fault HAMMTAP4 (515046) 138 kV Bus a. Apply fault at the HAMMTAP4 (515046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMMTAP4 138 KV 515046 TO LINCOLN4 138 KV 515442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HARPER2__ANADARK2 | 3 Phase fault HARPER2 (520440) 69 kV Bus a. Apply fault at the HARPER2 (520440) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER2 69 KV 520440 TO ANADARK2 69 KV 520810 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HARRISN4__KNOXLEE4 | 3 Phase fault HARRISN4 (508544) 138 kV Bus a. Apply fault at the HARRISN4 (508544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRISN4 138 KV 508544 TO KNOXLEE4 138 KV 508548 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HARTSIS4__S_SHV__4 | 3 Phase fault HARTSIS4 (507735) 138 kV Bus a. Apply fault at the HARTSIS4 (507735) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARTSIS4 138 KV 507735 TO S SHV 4 138 KV 507755 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HEFNER_4__TENESTP4 | 3 Phase fault HEFNER 4 (514848) 138 kV Bus a. Apply fault at the HEFNER 4 (514848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILSHIR4 138 KV 514836 TO HEFNER 4 138 KV 514848 CKT 1 b.2. WILSHIR4 138 KV 514836 TO TENNESE4 138 KV 514838 CKT 1 b.3. LOAD 1 514838 b.4. TENESTP4 138 KV 514837 TO TENNESE4 138 KV 514838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HENESEY4__BULFTTP4 | 3 Phase fault HENESEY4 (514774) 138 kV Bus a. Apply fault at the HENESEY4 (514774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 138 KV 514774 TO BULFTTP4 138 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HENESEY4__DOVERSW4 | 3 Phase fault HENESEY4 (514774) 138 kV Bus a. Apply fault at the HENESEY4 (514774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 138 KV 514774 TO DOVERSW4 138 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HERRON_5__IGLOOV1_5 | 3 Phase fault HERRON 5 (513591) 161 kV Bus a. Apply fault at the HERRON 5 (513591) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HERRON 5 161 KV 513591 TO IGLOOV1 5 161 KV 513593 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HERRON_5__IGLOOV2_5 | 3 Phase fault HERRON 5 (513591) 161 kV Bus a. Apply fault at the HERRON 5 (513591) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HERRON 5 161 KV 513591 TO IGLOOV2 5 161 KV 513595 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HIGHLND4__PINK_SW4 | 3 Phase fault HIGHLND4 (520941) 138 kV Bus a. Apply fault at the HIGHLND4 (520941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGHLND4 138 KV 520941 TO PINK SW4 138 KV 521028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HLTOPTP__BEELINE2 | 3 Phase fault HLTOPTP (514200) 69 kV Bus a. Apply fault at the HLTOPTP (514200) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLTOPTP 69 KV 514200 TO BEELINE2 69 KV 515246 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HOB | 3 Phase fault HOB-JCT4 (511463) 138 kV Bus a. Apply fault at the HOB-JCT4 (511463) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT4 138 KV 511463 TO MARTHA 4 138 KV 511564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HOB | 3 Phase fault HOB-JCT4 (511463) 138 kV Bus a. Apply fault at the HOB-JCT4 (511463) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT4 138 KV 511463 TO RKY_RDG4 138 KV 511554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HOBBYLO4__CHEMTRN4 | 3 Phase fault HOBBYLO4 (515338) 138 kV Bus a. Apply fault at the HOBBYLO4 (515338) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBYLO4 138 KV 515338 TO CHEMTRN4 138 KV 515367 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HOCHJCT4__DOMINJCT4 | 3 Phase fault HOCHJCT4 (520823) 138 kV Bus a. Apply fault at the HOCHJCT4 (520823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOCHJCT4 138 KV 520823 TO DOMINJCT4 138 KV 521195 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HOCHJCT4__HOCHTWN4 | 3 Phase fault HOCHJCT4 (520823) 138 kV Bus a. Apply fault at the HOCHJCT4 (520823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOCHJCT4 138 KV 520823 TO HOCHTWN4 138 KV 520943 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HOLLYWD4__INDNHIL4 | 3 Phase fault HOLLYWD4 (514953) 138 kV Bus a. Apply fault at the HOLLYWD4 (514953) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLLYWD4 138 KV 514953 TO INDNHIL4 138 KV 514954 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HOOKS__2__LSORDTP2 | 3 Phase fault HOOKS 2 (508057) 69 kV Bus a. Apply fault at the HOOKS 2 (508057) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOKS 2 69 KV 508057 TO LSORDTP2 69 KV 508063 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HOOKS__2__REDRVR | 3 Phase fault HOOKS 2 (508057) 69 kV Bus a. Apply fault at the HOOKS 2 (508057) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOKS 2 69 KV 508057 TO REDRVR-2 69 KV 508074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HOPESWI3__HOPE___3 | 3 Phase fault HOPESWI3 (507452) 115 kV Bus a. Apply fault at the HOPESWI3 (507452) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOPESWI3 115 KV 507452 TO HOPE 3 115 KV 507453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HSLEAST2__DEEPFKT2 | 3 Phase fault HSLEAST2 (514927) 69 kV Bus a. Apply fault at the HSLEAST2 (514927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69 KV 514927 TO GRNPAST2 69 KV 514971 CKT 1 b.2. LOAD 1 514971 b.3. DEEPFKT2 69 KV 514970 TO GRNPAST2 69 KV 514971 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HSLEAST2__HSLWEST2 | 3 Phase fault HSLEAST2 (514927) 69 kV Bus a. Apply fault at the HSLEAST2 (514927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69 KV 514927 TO HSLWEST2 69 KV 514937 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HSLEAST2__MCLOUDT2 | 3 Phase fault HSLEAST2 (514927) 69 kV Bus a. Apply fault at the HSLEAST2 (514927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69 KV 514927 TO MCLOUDT2 69 KV 515504 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HSLEAST2__TXSTELA2 | 3 Phase fault HSLEAST2 (514927) 69 kV Bus a. Apply fault at the HSLEAST2 (514927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69 KV 514927 TO TXSTELA2 69 KV 514985 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HSL____4__GEN | 3 Phase fault HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138 KV 514941 TO GEN-2018-029 138 KV 762647 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HSL____4__HAMMTAP4 | 3 Phase fault HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138 KV 514941 TO HAMMTAP4 138 KV 515046 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HSL____4__JONESSB4 | 3 Phase fault HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138 KV 514941 TO JONESSB4 138 KV 515480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HSL____4__RENO___4 | 3 Phase fault HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138 KV 514941 TO MIDWAY 4 138 KV 514966 CKT 1 b.2. LOAD 1 514966 b.3. NE10TH 4 138 KV 514964 TO MIDWAY 4 138 KV 514966 CKT 1 b.4. LOAD 1 514966 b.5. NE10TH 4 138 KV 514964 TO RENO 4 138 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HSL____4__SE15TH_4 | 3 Phase fault HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138 KV 514941 TO SE15TH 4 138 KV 514993 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HSL____4__SQUIRCK4 | 3 Phase fault HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138 KV 514941 TO DALE 4 138 KV 514987 CKT 1 b.2. LOAD 1 514987 b.3. DALE 4 138 KV 514987 TO SQUIRCK4 138 KV 515059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HUGO | 3 Phase fault HUGO---4 (510901) 138 kV Bus a. Apply fault at the HUGO---4 (510901) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGO---4 138 KV 510901 TO VALIANT4 138 KV 510918 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HUGOITC4__HUGO_PP4 | 3 Phase fault HUGOITC4 (520560) 138 kV Bus a. Apply fault at the HUGOITC4 (520560) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOITC4 138 KV 520560 TO HUGO PP4 138 KV 520948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HUGO_PP4__GEN | 3 Phase fault HUGO PP4 (520948) 138 kV Bus a. Apply fault at the HUGO PP4 (520948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGO PP4 138 KV 520948 TO GEN-2017-023 138 KV 588670 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HUGO_PP4__VALLANT4 | 3 Phase fault HUGO PP4 (520948) 138 kV Bus a. Apply fault at the HUGO PP4 (520948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGO PP4 138 KV 520948 TO VALLANT4 138 KV 521079 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HUGO___7__G17 | 3 Phase fault HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 345 KV 521157 TO G17-075-TAP 345 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HUNTERS7__CHSHLMV7 | 3 Phase fault HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 345 KV 515476 TO CHSHLMV7 345 KV 515477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HUNTERS7__RENFROW7 | 3 Phase fault HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 345 KV 515476 TO RENFROW7 345 KV 515543 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HWY20 | 3 Phase fault HWY20-T4 (509821) 138 kV Bus a. Apply fault at the HWY20-T4 (509821) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HWY20-T4 138 KV 509821 TO WLDCT_HIL4 138 KV 509897 CKT 1 b.2. LOAD 1 509897 b.3. HWY20--4 138 KV 509798 TO WLDCT_HIL4 138 KV 509897 CKT 1 b.4. LOAD 1 509897 b.5. HWY20--4 138 KV 509798 TO OMHOMNY4 138 KV 529306 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_INOLATP4__CATOOSA4 | 3 Phase fault INOLATP4 (509752) 138 kV Bus a. Apply fault at the INOLATP4 (509752) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INOLATP4 138 KV 509752 TO CATOOSA4 138 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_INOLATP4__EXCLART4 | 3 Phase fault INOLATP4 (509752) 138 kV Bus a. Apply fault at the INOLATP4 (509752) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INOLATP4 138 KV 509752 TO ROCKPT-4 138 KV 510437 CKT 1 b.2. LOAD 1 510437 b.3. CHOUTEA4 138 KV 510373 TO ROCKPT-4 138 KV 510437 CKT 1 b.4. LOAD 1 510437 b.5. CHOUTEA4 138 KV 510373 TO EXCLART4 138 KV 510401 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_INOLA__4__INOLATP4 | 3 Phase fault INOLA 4 (509736) 138 kV Bus a. Apply fault at the INOLA 4 (509736) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INOLA 4 138 KV 509736 TO INOLATP4 138 KV 509752 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_IODINE_4__MOORLND4 | 3 Phase fault IODINE 4 (520957) 138 kV Bus a. Apply fault at the IODINE 4 (520957) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IODINE 4 138 KV 520957 TO MOORLND4 138 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_IPC_TAP2__IPC____2 | 3 Phase fault IPC TAP2 (508058) 69 kV Bus a. Apply fault at the IPC TAP2 (508058) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC TAP2 69 KV 508058 TO IPC 2 69 KV 508092 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_IPC_T__4__CASSTP4 | 3 Phase fault IPC T 4 (508059) 138 kV Bus a. Apply fault at the IPC T 4 (508059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138 KV 508059 TO CASSTP4 138 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_IPC_T__4__IPC____4 | 3 Phase fault IPC T 4 (508059) 138 kV Bus a. Apply fault at the IPC T 4 (508059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138 KV 508059 TO IPC 4 138 KV 508095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_JEFFRSN4__LAKEPIN4 | 3 Phase fault JEFFRSN4 (508835) 138 kV Bus a. Apply fault at the JEFFRSN4 (508835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138 KV 508835 TO LAKEPIN4 138 KV 509624 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_JEFFRSN4__WILKES_4 | 3 Phase fault JEFFRSN4 (508835) 138 kV Bus a. Apply fault at the JEFFRSN4 (508835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138 KV 508835 TO WILKES 4 138 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_JENSENT4__CIMARON4 | 3 Phase fault JENSENT4 (514820) 138 kV Bus a. Apply fault at the JENSENT4 (514820) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSENT4 138 KV 514820 TO CIMARON4 138 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_JENSENT4__JENSEN_4 | 3 Phase fault JENSENT4 (514820) 138 kV Bus a. Apply fault at the JENSENT4 (514820) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSENT4 138 KV 514820 TO JENSEN 4 138 KV 514821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_JENSEN_4__EL_RENO4 | 3 Phase fault JENSEN 4 (514821) 138 kV Bus a. Apply fault at the JENSEN 4 (514821) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSEN 4 138 KV 514821 TO EL RENO4 138 KV 520893 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_JNSKAMO4__ARCADIA4 | 3 Phase fault JNSKAMO4 (514906) 138 kV Bus a. Apply fault at the JNSKAMO4 (514906) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 138 KV 514906 TO ARCADIA4 138 KV 514907 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_JNSKAMO4__HSL____4 | 3 Phase fault JNSKAMO4 (514906) 138 kV Bus a. Apply fault at the JNSKAMO4 (514906) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 138 KV 514906 TO HSL 4 138 KV 514941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_JOHNCO_4__CANEYCK4 | 3 Phase fault JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138 KV 514808 TO CANEYCK4 138 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_JOHNCO_4__RUSSET | 3 Phase fault JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138 KV 514808 TO RUSSET-4 138 KV 515120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_JOHNCO_4__SXMLCKT4 | 3 Phase fault JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138 KV 514808 TO SXMLCKT4 138 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_JOHNCO_7__DMNDSPG7 | 3 Phase fault JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345 KV 514809 TO DMNDSPG7 345 KV 516006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_JOHNCO_7__GEN | 3 Phase fault JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345 KV 514809 TO GEN-2017-149 345 KV 760830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_JOHNCO_7__SUNNYSD7 | 3 Phase fault JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345 KV 514809 TO SUNNYSD7 345 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_JONESSB4__LGARBER4 | 3 Phase fault JONESSB4 (515480) 138 kV Bus a. Apply fault at the JONESSB4 (515480) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHTWOOD4 138 KV 514842 TO JONESSB4 138 KV 515480 CKT 1 b.2. CHTWOOD4 138 KV 514842 TO LGARBER4 138 KV 515465 CKT 1 b.3. LOAD 1 515465 b.4. ARCADIA4 138 KV 514907 TO LGARBER4 138 KV 515465 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_KANSATP5__KANSAS_5 | 3 Phase fault KANSATP5 (512714) 161 kV Bus a. Apply fault at the KANSATP5 (512714) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KANSATP5 161 KV 512714 TO KANSAS 5 161 KV 512716 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_KELLYAV4__MEMRIAL4 | 3 Phase fault KELLYAV4 (514501) 138 kV Bus a. Apply fault at the KELLYAV4 (514501) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLYAV4 138 KV 514501 TO MEMRIAL4 138 KV 514835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_KENSH | 3 Phase fault KENSH-E4 (509744) 138 kV Bus a. Apply fault at the KENSH-E4 (509744) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENSH-E4 138 KV 509744 TO ZUNIS-N4 138 KV 509827 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_KENTUKT2__44&SUNL2 | 3 Phase fault KENTUKT2 (514977) 69 kV Bus a. Apply fault at the KENTUKT2 (514977) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENTUKT2 69 KV 514977 TO SAGE 2 69 KV 514978 CKT 1 b.2. LOAD 1 514978 b.3. SAGE 2 69 KV 514978 TO 44&SUNL2 69 KV 514979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_KERR_GR5__KANSATP5 | 3 Phase fault KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161 KV 512635 TO 412SUB 5 161 KV 512637 CKT 1 b.2. LOAD 1 512637 b.3. 412SUB 5 161 KV 512637 TO KANSATP5 161 KV 512714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_KERR_GR5__KERR_BRK1_5 | 3 Phase fault KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161 KV 512635 TO KERR BRK1 5 161 KV 512770 CKT Z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_KERR_GR5__MAID___5 | 3 Phase fault KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161 KV 512635 TO MAID 5 161 KV 512648 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_KERR_GR5__PENSA__5 | 3 Phase fault KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161 KV 512635 TO PENSA 5 161 KV 512654 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_KERR_GR5__SALNCRK5 | 3 Phase fault KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161 KV 512635 TO SALNCRK5 161 KV 512805 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_KETCHTP4__KETCH__4 | 3 Phase fault KETCHTP4 (514828) 138 kV Bus a. Apply fault at the KETCHTP4 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 138 KV 514828 TO KETCH 4 138 KV 514834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_KETCHTP4__NORTWST4 | 3 Phase fault KETCHTP4 (514828) 138 kV Bus a. Apply fault at the KETCHTP4 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 138 KV 514828 TO NORTWST4 138 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_KETCH__4__FAIRFLD4 | 3 Phase fault KETCH 4 (514834) 138 kV Bus a. Apply fault at the KETCH 4 (514834) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCH 4 138 KV 514834 TO FAIRFLD4 138 KV 515468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_KEYSTON4__WEKIWA | 3 Phase fault KEYSTON4 (505610) 138 kV Bus a. Apply fault at the KEYSTON4 (505610) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON4 138 KV 505610 TO WEKIWA-4 138 KV 509757 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_KGFSHSW4__CALUMET4 | 3 Phase fault KGFSHSW4 (520533) 138 kV Bus a. Apply fault at the KGFSHSW4 (520533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSHSW4 138 KV 520533 TO CONCHO 4 138 KV 520865 CKT 1 b.2. LOAD 1 520865 b.3. CALUMET4 138 KV 520839 TO CONCHO 4 138 KV 520865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_KGFSHSW4__CMBLTP_4 | 3 Phase fault KGFSHSW4 (520533) 138 kV Bus a. Apply fault at the KGFSHSW4 (520533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSHSW4 138 KV 520533 TO REEDING4 138 KV 521037 CKT 1 b.2. LOAD 1 521037 b.3. CMBLTP 4 138 KV 520474 TO REEDING4 138 KV 521037 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_KGFSHSW4__EKFSHTP4 | 3 Phase fault KGFSHSW4 (520533) 138 kV Bus a. Apply fault at the KGFSHSW4 (520533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSHSW4 138 KV 520533 TO EKFSHTP4 138 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_KGFSJCT4__EKFSHTP4 | 3 Phase fault KGFSJCT4 (520405) 138 kV Bus a. Apply fault at the KGFSJCT4 (520405) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSJCT4 138 KV 520405 TO EKFSHTP4 138 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_KINZEGR4__KINZE__4 | 3 Phase fault KINZEGR4 (512710) 138 kV Bus a. Apply fault at the KINZEGR4 (512710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZEGR4 138 KV 512710 TO KINZE 4 138 KV 515008 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_KINZE__4__UNVRSTY4 | 3 Phase fault KINZE 4 (515008) 138 kV Bus a. Apply fault at the KINZE 4 (515008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZE 4 138 KV 515008 TO UNVRSTY4 138 KV 515181 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_KIPUMPT2__FTOWSON2 | 3 Phase fault KIPUMPT2 (510876) 69 kV Bus a. Apply fault at the KIPUMPT2 (510876) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KIPUMPT2 69 KV 510876 TO FTOWSON2 69 KV 510917 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_KIPUMPT2__VALIANT2 | 3 Phase fault KIPUMPT2 (510876) 69 kV Bus a. Apply fault at the KIPUMPT2 (510876) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KIPUMPT2 69 KV 510876 TO VALIANT2 69 KV 510910 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_KI_PMPN2__KIPUMPT2 | 3 Phase fault KI PMPN2 (510875) 69 kV Bus a. Apply fault at the KI PMPN2 (510875) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KI PMPN2 69 KV 510875 TO KIPUMPT2 69 KV 510876 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_KNGFSHR7__FSHRTAP7 | 3 Phase fault KNGFSHR7 (515600) 345 kV Bus a. Apply fault at the KNGFSHR7 (515600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KNGFSHR7 345 KV 515600 TO FSHRTAP7 345 KV 515610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-045 trips on voltage protection settings | Disabling voltage protection settings for GEN-2016-045 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_KNOBHIL4__DGRASSE4 | 3 Phase fault KNOBHIL4 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 138 KV 514795 TO DGRASSE4 138 KV 515853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_KNOXLEE4__BRANDYBR | 3 Phase fault KNOXLEE4 (508548) 138 kV Bus a. Apply fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138 KV 508548 TO BRANDYBR 138 KV 508596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_KNOXLEE4__CHEROKE4 | 3 Phase fault KNOXLEE4 (508548) 138 kV Bus a. Apply fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138 KV 508548 TO CHEROKE4 138 KV 509059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_KNOXLEE4__MONROER4 | 3 Phase fault KNOXLEE4 (508548) 138 kV Bus a. Apply fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138 KV 508548 TO MONROER4 138 KV 509073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_KNOXLEE4__OAK2HIL4 | 3 Phase fault KNOXLEE4 (508548) 138 kV Bus a. Apply fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138 KV 508548 TO OAK2HIL4 138 KV 509078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_KNOXLEE4__SOTXEST4 | 3 Phase fault KNOXLEE4 (508548) 138 kV Bus a. Apply fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138 KV 508548 TO SOTXEST4 138 KV 508570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_L.E.S._LGOREN2 | 3 Phase fault L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69 KV 511466 TO LGORE-N2 69 KV 511469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_L.E.S._LGORES2 | 3 Phase fault L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69 KV 511466 TO LGORE-S2 69 KV 511470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_L.E.S._ARTVLTP4 | 3 Phase fault L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138 KV 511467 TO SHERID4 138 KV 511474 CKT 1 b.2. LOAD 1 511474 b.3. SHERID4 138 KV 511474 TO ARTVLTP4 138 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_L.E.S._COMMTAP4 | 3 Phase fault L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138 KV 511467 TO COMMTAP4 138 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_L.E.S._ELGINJT4 | 3 Phase fault L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138 KV 511467 TO ELGINJT4 138 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_L.E.S._SHERID4 | 3 Phase fault L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138 KV 511467 TO SHERID4 138 KV 511474 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_L.E.S._G16-091-TAP | 3 Phase fault L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345 KV 511468 TO G16-091-TAP 345 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_L.E.S._G17-171-TAP | 3 Phase fault L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345 KV 511468 TO G17-171-TAP 345 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LEASIDE_4__LOGANSP4 | 3 Phase fault LEASIDE 4 (507793) 138 kV Bus a. Apply fault at the LEASIDE 4 (507793) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEASIDE 4 138 KV 507793 TO STONWAL4 138 KV 509052 CKT 1 b.2. LOAD 1 509052 b.3. KEATCHI4 138 KV 509050 TO STONWAL4 138 KV 509052 CKT 1 b.4. LOAD 1 509052 b.5. KEATCHI4 138 KV 509050 TO GEORPAC4 138 KV 509064 CKT 1 b.6. GEORPAC4 138 KV 509064 TO LOGANSP4 138 KV 509071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LEONARD4__MLCLMRD4 | 3 Phase fault LEONARD4 (511575) 138 kV Bus a. Apply fault at the LEONARD4 (511575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEONARD4 138 KV 511575 TO MLCLMRD4 138 KV 515933 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LGYEAR_112GORE | 3 Phase fault LG-YEAR4 (511428) 138 kV Bus a. Apply fault at the LG-YEAR4 (511428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-YEAR4 138 KV 511428 TO 112GORE4 138 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LIEBERM2__OILCITY2 | 3 Phase fault LIEBERM2 (508805) 69 kV Bus a. Apply fault at the LIEBERM2 (508805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM2 69 KV 508805 TO OILCITY2 69 KV 508812 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LIEBERM4__G16 | 3 Phase fault LIEBERM4 (508806) 138 kV Bus a. Apply fault at the LIEBERM4 (508806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138 KV 508806 TO G16-167-TAP 138 KV 588404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LIEBERM4__JEFFRSN4 | 3 Phase fault LIEBERM4 (508806) 138 kV Bus a. Apply fault at the LIEBERM4 (508806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138 KV 508806 TO IPCJEFF4 138 KV 508833 CKT 1 b.2. LOAD 1 508833 b.3. IPCJEFF4 138 KV 508833 TO JEFFRSN4 138 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LIEBERM4__LONGWD_4 | 3 Phase fault LIEBERM4 (508806) 138 kV Bus a. Apply fault at the LIEBERM4 (508806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138 KV 508806 TO LONGWD 4 138 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LINCOLN4__MEEKRSW4 | 3 Phase fault LINCOLN4 (515442) 138 kV Bus a. Apply fault at the LINCOLN4 (515442) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINCOLN4 138 KV 515442 TO MEEKER 4 138 KV 520464 CKT 1 b.2. LOAD 1 520464 b.3. MEEKER 4 138 KV 520464 TO MEEKRSW4 138 KV 520994 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LINCOLN4__WOLVRNT4 | 3 Phase fault LINCOLN4 (515442) 138 kV Bus a. Apply fault at the LINCOLN4 (515442) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JACKTWN4 138 KV 515051 TO LINCOLN4 138 KV 515442 CKT 1 b.2. JACKTWN4 138 KV 515051 TO WOLVRNT4 138 KV 515532 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LINTNRD4__NBENTON4 | 3 Phase fault LINTNRD4 (508807) 138 kV Bus a. Apply fault at the LINTNRD4 (508807) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINTNRD4 138 KV 508807 TO NBENTON4 138 KV 508811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LINWOOD4__POWELL_4 | 3 Phase fault LINWOOD4 (507738) 138 kV Bus a. Apply fault at the LINWOOD4 (507738) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINWOOD4 138 KV 507738 TO POWELL 4 138 KV 507748 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LITTLAX2__LITLAXT2 | 3 Phase fault LITTLAX2 (514951) 69 kV Bus a. Apply fault at the LITTLAX2 (514951) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTLAX2 69 KV 514951 TO LITLAXT2 69 KV 515502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LLANE_LLANET | 3 Phase fault LLANE-E4 (509728) 138 kV Bus a. Apply fault at the LLANE-E4 (509728) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LLANE-E4 138 KV 509728 TO LLAN ET4 138 KV 509771 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LLANE_LLANWT | 3 Phase fault LLANE-W4 (509720) 138 kV Bus a. Apply fault at the LLANE-W4 (509720) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LLANE-W4 138 KV 509720 TO LLAN WT4 138 KV 509770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LLAN_ET4__CATOOSA4 | 3 Phase fault LLAN ET4 (509771) 138 kV Bus a. Apply fault at the LLAN ET4 (509771) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LLAN ET4 138 KV 509771 TO CATOOSA4 138 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LLAN_WT4__DAWSONT4 | 3 Phase fault LLAN WT4 (509770) 138 kV Bus a. Apply fault at the LLAN WT4 (509770) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LLAN WT4 138 KV 509770 TO DAWSONT4 138 KV 509803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LLAN_WT4__LLANETP4 | 3 Phase fault LLAN WT4 (509770) 138 kV Bus a. Apply fault at the LLAN WT4 (509770) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LLAN WT4 138 KV 509770 TO LLANETP4 138 KV 509804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LNEOAK_4__NORTWST4 | 3 Phase fault LNEOAK 4 (514873) 138 kV Bus a. Apply fault at the LNEOAK 4 (514873) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNEOAK 4 138 KV 514873 TO NORTWST4 138 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LOCKESB2__NASHVIL2 | 3 Phase fault LOCKESB2 (507422) 69 kV Bus a. Apply fault at the LOCKESB2 (507422) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOCKESB2 69 KV 507422 TO NASHVIL2 69 KV 507426 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LONEGRV4__CHEEKTP4 | 3 Phase fault LONEGRV4 (515144) 138 kV Bus a. Apply fault at the LONEGRV4 (515144) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONEGRV4 138 KV 515144 TO CHEEKTP4 138 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LONGVHT4__WHITNEY4 | 3 Phase fault LONGVHT4 (508554) 138 kV Bus a. Apply fault at the LONGVHT4 (508554) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGVHT4 138 KV 508554 TO WHITNEY4 138 KV 508575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LONGWD_4__FLOURNY4 | 3 Phase fault LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 138 KV 508808 TO OAKPH 4 138 KV 508816 CKT 1 b.2. LOAD 1 508816 b.3. FLOURNY4 138 KV 507727 TO OAKPH 4 138 KV 508816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LONGWD_4__RAINES_4 | 3 Phase fault LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORAM 4 138 KV 507774 TO LONGWD 4 138 KV 508808 CKT 1 b.2. RAINES 4 138 KV 507749 TO NORAM 4 138 KV 507774 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LONGWD_4__SABMINT4 | 3 Phase fault LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SABMINT4 138 KV 508566 TO SEMRSHL4 138 KV 508569 CKT 1 b.2. LOAD 1 508569 b.3. SCOTTSV4 138 KV 508567 TO SEMRSHL4 138 KV 508569 CKT 1 b.4. LOAD 1 508569 b.5. SCOTTSV4 138 KV 508567 TO LONGWD 4 138 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LONGWD_7__GEN | 3 Phase fault LONGWD 7 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345 KV 508809 TO GEN-2018-050 345 KV 762845 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LONGWD_7__WILKES_7 | 3 Phase fault LONGWD 7 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345 KV 508809 TO WILKES 7 345 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LSORDTP2__LSORD__2 | 3 Phase fault LSORDTP2 (508063) 69 kV Bus a. Apply fault at the LSORDTP2 (508063) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSORDTP2 69 KV 508063 TO LSORD 2 69 KV 508093 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LSSOUTH4__DIANA__4 | 3 Phase fault LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138 KV 508297 TO DIANA 4 138 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LSSOUTH4__PITTSB_4 | 3 Phase fault LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138 KV 508297 TO PITTSB_4 138 KV 508313 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LSSOUTH4__WILKES_4 | 3 Phase fault LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138 KV 508297 TO WILKES 4 138 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LTLRLKT2__TXPLSTP2 | 3 Phase fault LTLRLKT2 (514983) 69 kV Bus a. Apply fault at the LTLRLKT2 (514983) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LTLRLKT2 69 KV 514983 TO TXPLSTP2 69 KV 515516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LWS_112GORE | 3 Phase fault LWS-NTP4 (511471) 138 kV Bus a. Apply fault at the LWS-NTP4 (511471) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS-NTP4 138 KV 511471 TO 112GORE4 138 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LWSTAP_4__L.E.S. | 3 Phase fault LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138 KV 511439 TO L.E.S.-4 138 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LWSTAP_4__RPPAPER4 | 3 Phase fault LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138 KV 511439 TO RPPAPER4 138 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LWS___S4__LWSTAP_4 | 3 Phase fault LWS S4 (511431) 138 kV Bus a. Apply fault at the LWS S4 (511431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS S4 138 KV 511431 TO LWSTAP 4 138 KV 511439 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LYDIA__7__VALIANT7 | 3 Phase fault LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345 KV 508298 TO VALIANT7 345 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LYDIA__7__WELSH__7 | 3 Phase fault LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345 KV 508298 TO WELSH 7 345 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MACOCTP2__LITLAXT2 | 3 Phase fault MACOCTP2 (514956) 69 kV Bus a. Apply fault at the MACOCTP2 (514956) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MACOCTP2 69 KV 514956 TO LITLAXT2 69 KV 515502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MAIDTP2__GRDA1_2 | 3 Phase fault MAIDTP2 (512625) 69 kV Bus a. Apply fault at the MAIDTP2 (512625) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIDTP2 69 KV 512625 TO GRDA1 2 69 KV 512727 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MAID___2__AMERCAST_S2 | 3 Phase fault MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 69 KV 512626 TO AMERCAST S2 69 KV 512681 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MAID___2__REDDEN_2 | 3 Phase fault MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 69 KV 512626 TO REDDEN 2 69 KV 512698 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MAID___5__5CDRCRST | 3 Phase fault MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 161 KV 512648 TO LOCSTGVKM 5 161 KV 513050 CKT 1 b.2. LOAD 1 513050 b.3. 5CDRCRST 161 KV 301344 TO LOCSTGVKM 5 161 KV 513050 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MAID___5__GERALDGAY5 | 3 Phase fault MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 161 KV 512648 TO GERALDGAY5 161 KV 512760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MAID___5__GRDA1__5 | 3 Phase fault MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 161 KV 512648 TO GRDA1 5 161 KV 512656 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MAID___5__PENSA__5 | 3 Phase fault MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 161 KV 512629 TO MAID 5 161 KV 512648 CKT 1 b.2. DRYGULCH5 161 KV 512629 TO PENSA 5 161 KV 512654 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MARSHL_JEFFRSN | 3 Phase fault MARSHL-4 (508557) 138 kV Bus a. Apply fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138 KV 508557 TO JEFFRSN4 138 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MARSHL_PIRKEY | 3 Phase fault MARSHL-4 (508557) 138 kV Bus a. Apply fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138 KV 508557 TO PIRKEY 4 138 KV 508562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MARSHL_4__CTNWOOD4 | 3 Phase fault MARSHL 4 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138 KV 514733 TO CTNWOOD4 138 KV 514827 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MARSHL_4__MARSHAL4 | 3 Phase fault MARSHL 4 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138 KV 514733 TO MARSHAL4 138 KV 521006 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MATHWSN7__REDNGTN7 | 3 Phase fault MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345 KV 515497 TO REDNGTN7 345 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MATHWSN7__TRAVERSE3 | 3 Phase fault MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345 KV 515497 TO TRAVERSE3 345 KV 900001 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119, GEN-2016-045, GEN-2016-053 trips on voltage protection settings | Disabling voltage protection settings for GEN-2016-119, GEN-2016-045, GEN-2016-053 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MAUDT__2__REDWATR2 | 3 Phase fault MAUDT 2 (509653) 69 kV Bus a. Apply fault at the MAUDT 2 (509653) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUDT 2 69 KV 509653 TO REDWATR2 69 KV 509667 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MAUD___2__ERLSBOR2 | 3 Phase fault MAUD 2 (515054) 69 kV Bus a. Apply fault at the MAUD 2 (515054) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 2 69 KV 515054 TO ERLSBOR2 69 KV 515073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MAUD___2__KNAWATP2 | 3 Phase fault MAUD 2 (515054) 69 kV Bus a. Apply fault at the MAUD 2 (515054) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 2 69 KV 515054 TO KNAWATP2 69 KV 515496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MAUD___2__LTRIVRT2 | 3 Phase fault MAUD 2 (515054) 69 kV Bus a. Apply fault at the MAUD 2 (515054) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 2 69 KV 515054 TO LTRIVRT2 69 KV 515503 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MAUD___4__FIXCT4 | 3 Phase fault MAUD 4 (515055) 138 kV Bus a. Apply fault at the MAUD 4 (515055) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EARLSBORO 4 138 KV 510948 TO MAUD 4 138 KV 515055 CKT 1 b.2. FIXCT4 138 KV 510877 TO EARLSBORO 4 138 KV 510948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MAUD___4__FRSTHIL4 | 3 Phase fault MAUD 4 (515055) 138 kV Bus a. Apply fault at the MAUD 4 (515055) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 4 138 KV 515055 TO FRSTHIL4 138 KV 515075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MAYO_LLANET | 3 Phase fault MAYO--N4 (509779) 138 kV Bus a. Apply fault at the MAYO--N4 (509779) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYO--N4 138 KV 509779 TO E41ST_W4 138 KV 509886 CKT 1 b.2. LOAD 1 509886 b.3. LLAN ET4 138 KV 509771 TO E41ST_W4 138 KV 509886 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MAYO_BANNTP4 | 3 Phase fault MAYO--S4 (509780) 138 kV Bus a. Apply fault at the MAYO--S4 (509780) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYO--S4 138 KV 509780 TO BANNTAP4 138 KV 509785 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MCALEST4__TALAWANDA__4 | 3 Phase fault MCALEST4 (510908) 138 kV Bus a. Apply fault at the MCALEST4 (510908) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCALEST4 138 KV 510908 TO TALAWANDA 4 138 KV 510951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MCALESTIND_4__TALAWANDA__4 | 3 Phase fault MCALESTIND 4 (510909) 138 kV Bus a. Apply fault at the MCALESTIND 4 (510909) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCALESTIND 4 138 KV 510909 TO TALAWANDA 4 138 KV 510951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MCCLAIN4__NORMHLL4 | 3 Phase fault MCCLAIN4 (514902) 138 kV Bus a. Apply fault at the MCCLAIN4 (514902) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCLAIN4 138 KV 514902 TO NORMHLL4 138 KV 516097 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MCLOUDT2__SINCPNT2 | 3 Phase fault MCLOUDT2 (515504) 69 kV Bus a. Apply fault at the MCLOUDT2 (515504) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCLOUDT2 69 KV 515504 TO SINCPNT2 69 KV 515642 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MCLOUD_2__MCLOUDT2 | 3 Phase fault MCLOUD 2 (515065) 69 kV Bus a. Apply fault at the MCLOUD 2 (515065) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCLOUD 2 69 KV 515065 TO MCLOUDT2 69 KV 515504 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MEEKRSW4__WREDHIL4 | 3 Phase fault MEEKRSW4 (520994) 138 kV Bus a. Apply fault at the MEEKRSW4 (520994) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEEKRSW4 138 KV 520994 TO WREDHIL4 138 KV 521097 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MEMRIAL4__DANFRTH4 | 3 Phase fault MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTERN4 138 KV 514832 TO MEMRIAL4 138 KV 514835 CKT 1 b.2. LOAD 1 514835 b.3. EASTERN4 138 KV 514832 TO HAFERSB4 138 KV 515469 CKT 1 b.4. LOAD 1 515469 b.5. DANFRTH4 138 KV 514833 TO HAFERSB4 138 KV 515469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MEMRIAL4__JONESSB4 | 3 Phase fault MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138 KV 514835 TO BRYANT 4 138 KV 514839 CKT 1 b.2. LOAD 1 514839 b.3. BRYANT 4 138 KV 514839 TO ACORN 4 138 KV 515459 CKT 1 b.4. LOAD 1 515459 b.5. ACORN 4 138 KV 515459 TO JONESSB4 138 KV 515480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MEMRIAL4__REMPKTP4 | 3 Phase fault MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLYAV4 138 KV 514501 TO MEMRIAL4 138 KV 514835 CKT 1 b.2. LOAD 1 514835 b.3. KELLYAV4 138 KV 514501 TO REMPKTP4 138 KV 514872 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MEMRIAL4__SKYLINE4 | 3 Phase fault MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138 KV 514835 TO SKYLINE4 138 KV 514850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MEMRIAL4__TENESTP4 | 3 Phase fault MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138 KV 514835 TO TENESTP4 138 KV 514837 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MENOTAP4__IMO____4 | 3 Phase fault MENOTAP4 (514789) 138 kV Bus a. Apply fault at the MENOTAP4 (514789) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENOTAP4 138 KV 514789 TO IMO 4 138 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MIDWEST4__FRNKLNS4 | 3 Phase fault MIDWEST4 (514946) 138 kV Bus a. Apply fault at the MIDWEST4 (514946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWEST4 138 KV 514946 TO FRNKLNS4 138 KV 520917 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MIDWEST4__HOLLYWD4 | 3 Phase fault MIDWEST4 (514946) 138 kV Bus a. Apply fault at the MIDWEST4 (514946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWEST4 138 KV 514946 TO HOLLYWD4 138 KV 514953 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MINCO__7__CIMARON7 | 3 Phase fault MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345 KV 514801 TO CIMARON7 345 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MINCO__7__GEN-2017-233 | 3 Phase fault MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345 KV 514801 TO GEN-2017-233 345 KV 761250 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MINCO__7__GRACMNT7 | 3 Phase fault MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345 KV 514801 TO GRACMNT7 345 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MINCO__7__MCNOWND7 | 3 Phase fault MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345 KV 514801 TO MCNOWND7 345 KV 515444 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MINCO__7__MNCWND37 | 3 Phase fault MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345 KV 514801 TO MNCWND37 345 KV 515549 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MINCO__7__NORMHLL7 | 3 Phase fault MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345 KV 514801 TO NORMHLL7 345 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MINGO_21STTAP | 3 Phase fault MINGO-N4 (509760) 138 kV Bus a. Apply fault at the MINGO-N4 (509760) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGO-N4 138 KV 509760 TO 21STTAP4 138 KV 509828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MINGO_MAYON4 | 3 Phase fault MINGO-N4 (509760) 138 kV Bus a. Apply fault at the MINGO-N4 (509760) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGO-N4 138 KV 509760 TO MAYO--N4 138 KV 509779 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MINGO_MAYOS4 | 3 Phase fault MINGO-S4 (509761) 138 kV Bus a. Apply fault at the MINGO-S4 (509761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGO-S4 138 KV 509761 TO MAYO--S4 138 KV 509780 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MINGO_TSE4 | 3 Phase fault MINGO-S4 (509761) 138 kV Bus a. Apply fault at the MINGO-S4 (509761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGO-S4 138 KV 509761 TO T.S.E.-4 138 KV 509811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MINGORD4__CATOOSA4 | 3 Phase fault MINGORD4 (509802) 138 kV Bus a. Apply fault at the MINGORD4 (509802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSN-N4 138 KV 509787 TO MINGORD4 138 KV 509802 CKT 1 b.2. LOAD 1 509802 b.3. DAWSN-N4 138 KV 509787 TO 141PINE4 138 KV 509892 CKT 1 b.4. LOAD 1 509892 b.5. SPNKY CK4 138 KV 509722 TO 141PINE4 138 KV 509892 CKT 1 b.6. LOAD 1 509892 b.7. SPNKY CK4 138 KV 509722 TO CATOOSA4 138 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MOORE__2__FRNKLNS2 | 3 Phase fault MOORE 2 (520489) 69 kV Bus a. Apply fault at the MOORE 2 (520489) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE 2 69 KV 520489 TO FRNKLNS2 69 KV 520916 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MOORLND4__GEN-2016-020 | 3 Phase fault MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND4 138 KV 520999 TO GEN-2016-020 138 KV 587140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MOUNDRD4__ELIZACK4 | 3 Phase fault MOUNDRD4 (510395) 138 kV Bus a. Apply fault at the MOUNDRD4 (510395) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUNDRD4 138 KV 510395 TO ELIZACK4 138 KV 510435 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MRIETA_2__ROCKYPT4 | 3 Phase fault MRIETA 2 (515160) 138 kV Bus a. Apply fault at the MRIETA 2 (515160) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 2 138 KV 515160 TO ROCKYPT4 138 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MSKPORT5__MSKPTAP5 | 3 Phase fault MSKPORT5 (515184) 161 kV Bus a. Apply fault at the MSKPORT5 (515184) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSKPORT5 161 KV 515184 TO MSKPTAP5 161 KV 515232 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MSKPTAP5__EUCLID_5 | 3 Phase fault MSKPTAP5 (515232) 161 kV Bus a. Apply fault at the MSKPTAP5 (515232) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSKPTAP5 161 KV 515232 TO EUCLID 5 161 KV 515251 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MUNZCTY4__DUGLASV4 | 3 Phase fault MUNZCTY4 (508064) 138 kV Bus a. Apply fault at the MUNZCTY4 (508064) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138 KV 508064 TO DUGLASV4 138 KV 509666 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MUNZCTY4__WILKES_4 | 3 Phase fault MUNZCTY4 (508064) 138 kV Bus a. Apply fault at the MUNZCTY4 (508064) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138 KV 508064 TO WILKES 4 138 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MUSKOGE5__MSKPTAP5 | 3 Phase fault MUSKOGE5 (515222) 161 kV Bus a. Apply fault at the MUSKOGE5 (515222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKOGE5 161 KV 515222 TO MSKPTAP5 161 KV 515232 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MUSKOGE5__TAHLQH_5 | 3 Phase fault MUSKOGE5 (515222) 161 kV Bus a. Apply fault at the MUSKOGE5 (515222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKOGE5 161 KV 515222 TO KETOWAH5 161 KV 516027 CKT 1 b.2. LOAD 1 516027 b.3. 7CLANS 5 161 KV 515956 TO KETOWAH5 161 KV 516027 CKT 1 b.4. LOAD 1 516027 b.5. TAHLQH 5 161 KV 512655 TO 7CLANS 5 161 KV 515956 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MUSKOGE7__FIREWHL | 3 Phase fault MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345 KV 515224 TO FIREWHL-TAP 345 KV 588839 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MUSKOGE7__FTSMITH7 | 3 Phase fault MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345 KV 515224 TO FTSMITH7 345 KV 515302 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MUSKOGE7__PECANCK7 | 3 Phase fault MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345 KV 515224 TO PECANCK7 345 KV 515235 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MUSKTAP5__FT_GIB_5 | 3 Phase fault MUSKTAP5 (505558) 161 kV Bus a. Apply fault at the MUSKTAP5 (505558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKTAP5 161 KV 505558 TO FT GIB 5 161 KV 505560 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MUSKTAP5__MUSKOGE5 | 3 Phase fault MUSKTAP5 (505558) 161 kV Bus a. Apply fault at the MUSKTAP5 (505558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKTAP5 161 KV 505558 TO MUSKOGE5 161 KV 515222 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MUSTANG4__DAYTON_4 | 3 Phase fault MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138 KV 514861 TO DAYTON 4 138 KV 514892 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MUSTANG4__DOUGLTP4 | 3 Phase fault MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138 KV 514861 TO COUNCIL4 138 KV 514865 CKT 1 b.2. LOAD 1 514865 b.3. COUNCIL4 138 KV 514865 TO WESTOAK4 138 KV 514866 CKT 1 b.4. LOAD 1 514866 b.5. WESTOAK4 138 KV 514866 TO MERIDAN4 138 KV 514867 CKT 1 b.6. LOAD 1 514867 b.7. MERIDAN4 138 KV 514867 TO DOUGLTP4 138 KV 514868 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MUSTANG4__GEN-2018-026 | 3 Phase fault MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138 KV 514861 TO GEN-2018-026 138 KV 762614 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MUSTANG4__MORGAN_4 | 3 Phase fault MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138 KV 514861 TO MORGAN 4 138 KV 514896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MUSTANG4__SW_5TH_4 | 3 Phase fault MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138 KV 514861 TO SW 5TH 4 138 KV 514920 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_N.E.S._ALWUETP4 | 3 Phase fault N.E.S.-4 (510396) 138 kV Bus a. Apply fault at the N.E.S.-4 (510396) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.E.S.-4 138 KV 510396 TO HAWTHRN4 138 KV 510413 CKT 1 b.2. LOAD 1 510413 b.3. CHELSA4 138 KV 510410 TO HAWTHRN4 138 KV 510413 CKT 1 b.4. LOAD 1 510413 b.5. CHELSA4 138 KV 510410 TO ALWUETP4 138 KV 510429 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_N.E.S._BVSE4 | 3 Phase fault N.E.S.-4 (510396) 138 kV Bus a. Apply fault at the N.E.S.-4 (510396) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATOVA 4 138 KV 510384 TO N.E.S.-4 138 KV 510396 CKT 1 b.2. LOAD 1 510396 b.3. WATOVA 4 138 KV 510384 TO NOWATA-4 138 KV 510397 CKT 1 b.4. LOAD 1 510397 b.5. BV-SE--4 138 KV 510391 TO NOWATA-4 138 KV 510397 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_N.E.S._CLARMR | 3 Phase fault N.E.S.-4 (510396) 138 kV Bus a. Apply fault at the N.E.S.-4 (510396) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.E.S.-4 138 KV 510396 TO OOLOGAHKM 4 138 KV 513124 CKT 1 b.2. LOAD 1 513124 b.3. CLARMR 4 138 KV 512707 TO OOLOGAHKM 4 138 KV 513124 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_N.E.S._PCATSAT | 3 Phase fault N.E.S.-4 (510396) 138 kV Bus a. Apply fault at the N.E.S.-4 (510396) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCATSAT4 138 KV 509841 TO OWASO2_4 138 KV 509843 CKT 1 b.2. LOAD 1 509843 b.3. OWASO2_4 138 KV 509843 TO N.E.S.-4 138 KV 510396 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_N.E.S._TERNITP4 | 3 Phase fault N.E.S.-4 (510396) 138 kV Bus a. Apply fault at the N.E.S.-4 (510396) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARTOK4 138 KV 509864 TO N.E.S.-4 138 KV 510396 CKT 1 b.2. LOAD 1 510396 b.3. VERDIGS4 138 KV 509854 TO CLARTOK4 138 KV 509864 CKT 1 b.4. LOAD 1 509864 b.5. TERNITP4 138 KV 509835 TO VERDIGS4 138 KV 509854 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NASH___4__ALUMAX_4 | 3 Phase fault NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138 KV 508049 TO ALUMAX 4 138 KV 508091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NASH___4__BANN___4 | 3 Phase fault NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138 KV 508049 TO BANN 4 138 KV 508054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NASH___4__NWTXARK4 | 3 Phase fault NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138 KV 508049 TO NWTXARK4 138 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NBENTON4__G16 | 3 Phase fault NBENTON4 (508811) 138 kV Bus a. Apply fault at the NBENTON4 (508811) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NBENTON4 138 KV 508811 TO G16-167-TAP 138 KV 588404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NE10TH_4__RENO___4 | 3 Phase fault NE10TH 4 (514964) 138 kV Bus a. Apply fault at the NE10TH 4 (514964) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE10TH 4 138 KV 514964 TO RENO 4 138 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NE30TH_2__DEEPFKT2 | 3 Phase fault NE30TH 2 (514969) 69 kV Bus a. Apply fault at the NE30TH 2 (514969) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE30TH 2 69 KV 514969 TO DEEPFKT2 69 KV 514970 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NE30TH_2__RENO___2 | 3 Phase fault NE30TH 2 (514969) 69 kV Bus a. Apply fault at the NE30TH 2 (514969) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE30TH 2 69 KV 514969 TO RENO 2 69 KV 514972 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NE45TAP4__RUSHING4 | 3 Phase fault NE45TAP4 (515062) 138 kV Bus a. Apply fault at the NE45TAP4 (515062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE45TAP4 138 KV 515062 TO RUSHING4 138 KV 515064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NE45TAP4__WOLVRNT4 | 3 Phase fault NE45TAP4 (515062) 138 kV Bus a. Apply fault at the NE45TAP4 (515062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCK CK4 138 KV 515058 TO NE45TAP4 138 KV 515062 CKT 1 b.2. MOBIL 4 138 KV 515057 TO ROCK CK4 138 KV 515058 CKT 1 b.3. LOAD 1 515058 b.4. MOBIL 4 138 KV 515057 TO WOLVRNT4 138 KV 515532 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NEKOOSA2__HOLOX__2 | 3 Phase fault NEKOOSA2 (508065) 69 kV Bus a. Apply fault at the NEKOOSA2 (508065) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEKOOSA2 69 KV 508065 TO HOLOX 2 69 KV 508094 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NEKOSAT2__HOLOX__2 | 3 Phase fault NEKOSAT2 (508066) 69 kV Bus a. Apply fault at the NEKOSAT2 (508066) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEKOSAT2 69 KV 508066 TO HOLOX 2 69 KV 508094 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NEKOSAT2__SUGHLET2 | 3 Phase fault NEKOSAT2 (508066) 69 kV Bus a. Apply fault at the NEKOSAT2 (508066) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEKOSAT2 69 KV 508066 TO SUGHLET2 69 KV 508081 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NEOSHO_7__G17 | 3 Phase fault NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 345 KV 532793 TO G17-209-TAP 345 KV 760921 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NEOSHO_7__GEN | 3 Phase fault NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 345 KV 532793 TO GEN-2018-032 345 KV 762680 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NEWBOST2__DEKALB_2 | 3 Phase fault NEWBOST2 (508067) 69 kV Bus a. Apply fault at the NEWBOST2 (508067) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWBOST2 69 KV 508067 TO DEKALB 2 69 KV 508289 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NEWBOST2__NNBOSTN2 | 3 Phase fault NEWBOST2 (508067) 69 kV Bus a. Apply fault at the NEWBOST2 (508067) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWBOST2 69 KV 508067 TO NNBOSTN2 69 KV 508068 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NEWBOST2__REDRVR | 3 Phase fault NEWBOST2 (508067) 69 kV Bus a. Apply fault at the NEWBOST2 (508067) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWBOST2 69 KV 508067 TO REDRVR-2 69 KV 508074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NNBOSTN4__ANDRSNC4 | 3 Phase fault NNBOSTN4 (508069) 138 kV Bus a. Apply fault at the NNBOSTN4 (508069) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN4 138 KV 508069 TO RIFFIN REC4 138 KV 508104 CKT 1 b.2. LOAD 1 508104 b.3. ANDRSNC4 138 KV 508050 TO RIFFIN REC4 138 KV 508104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NNBOSTN4__G18 | 3 Phase fault NNBOSTN4 (508069) 138 kV Bus a. Apply fault at the NNBOSTN4 (508069) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN4 138 KV 508069 TO G18-003-TAP 138 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NORTWST7__ARCADIA7 | 3 Phase fault NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345 KV 514880 TO ARCADIA7 345 KV 514908 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NORTWST7__CIMARON7 | 3 Phase fault NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345 KV 514880 TO CIMARON7 345 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NORTWST7__MATHWSN7 | 3 Phase fault NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345 KV 514880 TO MATHWSN7 345 KV 515497 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NORTWST7__SPRNGCK7 | 3 Phase fault NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345 KV 514880 TO SPRNGCK7 345 KV 514881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NSHVILR2__NASHVIL2 | 3 Phase fault NSHVILR2 (507413) 69 kV Bus a. Apply fault at the NSHVILR2 (507413) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NSHVILR2 69 KV 507413 TO NASHVIL2 69 KV 507426 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NWT-BNT4_G18-003-TAP | 3 Phase fault NWT-BNT4 (508070) 138 kV Bus a. Apply fault at the NWT-BNT4 (508070) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138 KV 508070 TO G18-003-TAP 138 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NWT-BNT4_NWTXARX4 | 3 Phase fault NWT-BNT4 (508070) 138 kV Bus a. Apply fault at the NWT-BNT4 (508070) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138 KV 508070 TO NWTXARK4 138 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NWTXARK4__SUGARHL4 | 3 Phase fault NWTXARK4 (508071) 138 kV Bus a. Apply fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 138 KV 508071 TO SUGARHL4 138 KV 508080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NWTXARK7__LYDIA__7 | 3 Phase fault NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345 KV 508072 TO LYDIA 7 345 KV 508298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NWTXARK7__VALIANT7 | 3 Phase fault NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345 KV 508072 TO VALIANT7 345 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NWTXARK7__WELSH__7 | 3 Phase fault NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345 KV 508072 TO WELSH 7 345 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_O.K.U._G17-151-TAP | 3 Phase fault O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345 KV 511456 TO G17-151TAP 345 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_O.K.U._G18-015-Tap | 3 Phase fault O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345 KV 511456 TO G18-015-TAP 345 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_O.K.U._GEN-2017-033 | 3 Phase fault O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345 KV 511456 TO GEN-2017-033 345 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_O.K.U._L.E.S. | 3 Phase fault O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345 KV 511456 TO L.E.S.-7 345 KV 511468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_O.K.U._OKLAUN HVDC | 3 Phase fault O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345 KV 511456 TO OKLAUN HVDC7 345 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OAKCRK_4__DRAPER_4 | 3 Phase fault OAKCRK 4 (514960) 138 kV Bus a. Apply fault at the OAKCRK 4 (514960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKCRK 4 138 KV 514960 TO WILDMRY4 138 KV 514984 CKT 1 b.2. LOAD 1 514984 b.3. WILDMRY4 138 KV 514984 TO AIRDEPT4 138 KV 515457 CKT 1 b.4. LOAD 1 515457 b.5. GM 4 138 KV 514961 TO AIRDEPT4 138 KV 515457 CKT 1 b.6. LOAD 1 515457 b.7. DRAPER 4 138 KV 514933 TO GM 4 138 KV 514961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OAKCRK_4__INDNHIL4 | 3 Phase fault OAKCRK 4 (514960) 138 kV Bus a. Apply fault at the OAKCRK 4 (514960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE 4 138 KV 514955 TO OAKCRK 4 138 KV 514960 CKT 1 b.2. MOORE 4 138 KV 514955 TO INDIANH4 138 KV 515380 CKT 1 b.3. LOAD 1 515380 b.4. INDNHIL4 138 KV 514954 TO INDIANH4 138 KV 515380 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OAKCRK_4__SELNDTP4 | 3 Phase fault OAKCRK 4 (514960) 138 kV Bus a. Apply fault at the OAKCRK 4 (514960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKCRK 4 138 KV 514960 TO SELNDTP4 138 KV 515965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OAKS_OASETP | 3 Phase fault OAKS--E4 (509846) 138 kV Bus a. Apply fault at the OAKS--E4 (509846) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKS--E4 138 KV 509846 TO OAKSETP4 138 KV 509850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OAKSWTP4__SAPLPRD4 | 3 Phase fault OAKSWTP4 (509848) 138 kV Bus a. Apply fault at the OAKSWTP4 (509848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKSWTP4 138 KV 509848 TO SAPLPRD4 138 KV 509871 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OAKS__W4__OAKSWTP4 | 3 Phase fault OAKS W4 (509727) 138 kV Bus a. Apply fault at the OAKS W4 (509727) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKS W4 138 KV 509727 TO OAKSWTP4 138 KV 509848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OAKTRET4__SOONRTP4 | 3 Phase fault OAKTRET4 (514930) 138 kV Bus a. Apply fault at the OAKTRET4 (514930) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKTRET4 138 KV 514930 TO SOONRTP4 138 KV 514949 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OGMARTN2__DX | 3 Phase fault OGMARTN2 (509751) 69 kV Bus a. Apply fault at the OGMARTN2 (509751) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGMARTN2 69 KV 509751 TO DX----E2 69 KV 509795 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OGMARTN2__T.P.S. | 3 Phase fault OGMARTN2 (509751) 69 kV Bus a. Apply fault at the OGMARTN2 (509751) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLPIP2 69 KV 509750 TO OGMARTN2 69 KV 509751 CKT 1 b.2. LOAD 1 509751 b.3. WILLPIP2 69 KV 509750 TO T.P.S.-2 69 KV 509789 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKAYGR_5__WAGNOR_5 | 3 Phase fault OKAYGR 5 (512640) 161 kV Bus a. Apply fault at the OKAYGR 5 (512640) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAYGR 5 161 KV 512640 TO WAGNOR 5 161 KV 512700 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKAY___2__NASHVIL2 | 3 Phase fault OKAY 2 (507427) 69 kV Bus a. Apply fault at the OKAY 2 (507427) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWAYR2 69 KV 507410 TO TOLETTE2 69 KV 507415 CKT 1 b.2. LOAD A1 507415 b.3. TOLETTE2 69 KV 507415 TO OKAY 2 69 KV 507427 CKT 1 b.4. LOAD 1 507427 b.5. MIDWAYR2 69 KV 507410 TO NASHVIL2 69 KV 507426 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKAY___4__TURK___4 | 3 Phase fault OKAY 4 (507428) 138 kV Bus a. Apply fault at the OKAY 4 (507428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAY 4 138 KV 507428 TO TURK 4 138 KV 507454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKEENE_2__TALOGA_2 | 3 Phase fault OKEENE 2 (521015) 69 kV Bus a. Apply fault at the OKEENE 2 (521015) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANTON-2 69 KV 520843 TO OKEENE 2 69 KV 521015 CKT 1 b.2. LOAD 1 521015 b.3. CANTON-2 69 KV 520843 TO TALOGA 2 69 KV 521064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKMULGE4__EC.HEN | 3 Phase fault OKMULGE4 (510898) 138 kV Bus a. Apply fault at the OKMULGE4 (510898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKMULGE4 138 KV 510898 TO EC.HEN-4 138 KV 510923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKMULGE4__KELCO_4 | 3 Phase fault OKMULGE4 (510898) 138 kV Bus a. Apply fault at the OKMULGE4 (510898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKMULGE4 138 KV 510898 TO KELCO 4 138 KV 510931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OMAHA__2__DUGLASV2 | 3 Phase fault OMAHA 2 (509644) 69 kV Bus a. Apply fault at the OMAHA 2 (509644) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMAHA 2 69 KV 509644 TO DUGLASV2 69 KV 509645 CKT NO c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ONETA_121LYNN | 3 Phase fault ONETA--4 (509806) 138 kV Bus a. Apply fault at the ONETA--4 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 138 KV 509806 TO 121LYNN4 138 KV 509869 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ONETA_BA81 | 3 Phase fault ONETA--4 (509806) 138 kV Bus a. Apply fault at the ONETA--4 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101-N4 138 KV 509769 TO ONETA--4 138 KV 509806 CKT 1 b.2. LOAD 1 509806 b.3. BA81---4 138 KV 509747 TO BA101-N4 138 KV 509769 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ONETA_BANNTAP4 | 3 Phase fault ONETA--4 (509806) 138 kV Bus a. Apply fault at the ONETA--4 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 138 KV 509806 TO BA_71ST4 138 KV 509891 CKT 1 b.2. LOAD 1 509891 b.3. BANNTAP4 138 KV 509785 TO BA_71ST4 138 KV 509891 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ONETA_NES | 3 Phase fault ONETA--7 (509807) 345 kV Bus a. Apply fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 345 KV 509807 TO N.E.S.-7 345 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ONETA_OEC | 3 Phase fault ONETA--7 (509807) 345 kV Bus a. Apply fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 345 KV 509807 TO OEC 7 345 KV 509836 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ORU_ETP4__WARNTAP4 | 3 Phase fault ORU ETP4 (509849) 138 kV Bus a. Apply fault at the ORU ETP4 (509849) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU ETP4 138 KV 509849 TO WARNTAP4 138 KV 509858 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ORU___E4__ORU_ETP4 | 3 Phase fault ORU E4 (509738) 138 kV Bus a. Apply fault at the ORU E4 (509738) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU E4 138 KV 509738 TO ORU ETP4 138 KV 509849 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ORU___W4__ORU | 3 Phase fault ORU W4 (509732) 138 kV Bus a. Apply fault at the ORU W4 (509732) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU W4 138 KV 509732 TO ORU-WTP4 138 KV 509853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OTTER__4__ARMFTWD4 | 3 Phase fault OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138 KV 514708 TO ARMFTWD4 138 KV 515694 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OTTER__4__WOODRNG4 | 3 Phase fault OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138 KV 514708 TO WOODRNG4 138 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OTTER__4__WRVALLY4 | 3 Phase fault OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138 KV 514708 TO WRVALLY4 138 KV 514713 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OWASO1_4__OWASOTP4 | 3 Phase fault OWASO1_4 (509726) 138 kV Bus a. Apply fault at the OWASO1_4 (509726) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OWASO1_4 138 KV 509726 TO OWASOTP4 138 KV 509844 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OWASOTP4__N.E.S. | 3 Phase fault OWASOTP4 (509844) 138 kV Bus a. Apply fault at the OWASOTP4 (509844) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OWAS1094 138 KV 509860 TO N.E.S.-4 138 KV 510396 CKT 1 b.2. LOAD 1 510396 b.3. OWASOTP4 138 KV 509844 TO OWAS1094 138 KV 509860 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PAOLI | 3 Phase fault PAOLI- 4 (515100) 138 kV Bus a. Apply fault at the PAOLI- 4 (515100) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAOLI- 4 138 KV 515100 TO CHIGLEY4 138 KV 515114 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PAOLI | 3 Phase fault PAOLI- 4 (515100) 138 kV Bus a. Apply fault at the PAOLI- 4 (515100) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAOLI- 4 138 KV 515100 TO MAYSVIL4 138 KV 515124 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PARADSE4__CHERRYRD_4 | 3 Phase fault PARADSE4 (521024) 138 kV Bus a. Apply fault at the PARADSE4 (521024) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARADSE4 138 KV 521024 TO CHERRYRD 4 138 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PARKLN_4__LKKONWA4 | 3 Phase fault PARKLN 4 (515178) 138 kV Bus a. Apply fault at the PARKLN 4 (515178) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKLN 4 138 KV 515178 TO LKKONWA4 138 KV 515977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PARKLN_4__SOTHADA4 | 3 Phase fault PARKLN 4 (515178) 138 kV Bus a. Apply fault at the PARKLN 4 (515178) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKLN 4 138 KV 515178 TO SOTHADA4 138 KV 515318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PARKMEDTP__COLNSGR2 | 3 Phase fault PARKMEDTP (512703) 69 kV Bus a. Apply fault at the PARKMEDTP (512703) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKMEDTP 69 KV 512703 TO COLNSGR2 69 KV 512870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PATTERS2__NEKOOSA2 | 3 Phase fault PATTERS2 (507429) 69 kV Bus a. Apply fault at the PATTERS2 (507429) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS2 69 KV 507429 TO NEKOOSA2 69 KV 508065 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PATTERS2__NEKOSAT2 | 3 Phase fault PATTERS2 (507429) 69 kV Bus a. Apply fault at the PATTERS2 (507429) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS2 69 KV 507429 TO ASHDOWN2 69 KV 508051 CKT 1 b.2. LOAD 1 508051 b.3. ASHDOWN2 69 KV 508051 TO NEKOSAT2 69 KV 508066 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PATTERS4__BARITERDTP_4 | 3 Phase fault PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOCKSBRG 4 138 KV 504123 TO PATTERS4 138 KV 507431 CKT 1 b.2. LOCKSBRG 4 138 KV 504123 TO BARITERDTP 4 138 KV 507463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PATTERS4__CRAIGJT4 | 3 Phase fault PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHDWN_W 4 138 KV 504124 TO PATTERS4 138 KV 507431 CKT 1 b.2. ASHDWN_W 4 138 KV 504124 TO CRAIGJT4 138 KV 510890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PATTERS4__NWTXARK4 | 3 Phase fault PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS4 138 KV 507431 TO NWTXARK4 138 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PATTERS4__OKAY___4 | 3 Phase fault PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHDWNR4 138 KV 507402 TO OKAY 4 138 KV 507428 CKT 1 b.2. ASHDWNR4 138 KV 507402 TO PATTERS4 138 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PATTERS4__SNASHVL4 | 3 Phase fault PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS4 138 KV 507431 TO SNASHVL4 138 KV 507434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PAWNSW4__GLENCOKM_4 | 3 Phase fault PAWNSW4 (512749) 138 kV Bus a. Apply fault at the PAWNSW4 (512749) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAWNSW4 138 KV 512749 TO GLENCOKM 4 138 KV 513095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PCATSAT4__PCATOSA4 | 3 Phase fault PCATSAT4 (509841) 138 kV Bus a. Apply fault at the PCATSAT4 (509841) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCATSAT4 138 KV 509841 TO BIRDCREE-4 138 KV 509899 CKT 1 b.2. LOAD 1 509899 b.3. PCATOSA4 138 KV 509725 TO BIRDCREE-4 138 KV 509899 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PEARLHL2__ROACH__2 | 3 Phase fault PEARLHL2 (509651) 69 kV Bus a. Apply fault at the PEARLHL2 (509651) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEARLHL2 69 KV 509651 TO ROACH 2 69 KV 509668 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PEARSNT2__MAUD___2 | 3 Phase fault PEARSNT2 (515053) 69 kV Bus a. Apply fault at the PEARSNT2 (515053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEARSNT2 69 KV 515053 TO MAUD 2 69 KV 515054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PECANCK4__BRISTOW4 | 3 Phase fault PECANCK4 (515233) 138 kV Bus a. Apply fault at the PECANCK4 (515233) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK4 138 KV 515233 TO BEGGS 4 138 KV 515249 CKT 1 b.2. LOAD 1 515249 b.3. BRISTOW4 138 KV 515035 TO BEGGS 4 138 KV 515249 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PECANCK7__GEN | 3 Phase fault PECANCK7 (515235) 345 kV Bus a. Apply fault at the PECANCK7 (515235) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECANCK7 345 KV 515235 TO GEN-2018-048 345 KV 762823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-141 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-141 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PENN___2__KENTUKT2 | 3 Phase fault PENN 2 (514924) 69 kV Bus a. Apply fault at the PENN 2 (514924) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENN 2 69 KV 514924 TO KENTUKT2 69 KV 514977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PENN___4__36&MER_4 | 3 Phase fault PENN 4 (514925) 138 kV Bus a. Apply fault at the PENN 4 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRAIRPT4 138 KV 514889 TO PENN 4 138 KV 514925 CKT 1 b.2. LOAD 1 514925 b.3. 36&MER 4 138 KV 514888 TO WRAIRPT4 138 KV 514889 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PENN___4__OAKCRK_4 | 3 Phase fault PENN 4 (514925) 138 kV Bus a. Apply fault at the PENN 4 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENN 4 138 KV 514925 TO SANTAFE4 138 KV 514926 CKT 1 b.2. LOAD 1 514926 b.3. SANTAFE4 138 KV 514926 TO OAKCRK 4 138 KV 514960 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PENSA__5__KETCHUM5 | 3 Phase fault PENSA 5 (512654) 161 kV Bus a. Apply fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 5 161 KV 512654 TO KETCHUM5 161 KV 512669 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PERDUE_4__DIANA__4 | 3 Phase fault PERDUE 4 (508351) 138 kV Bus a. Apply fault at the PERDUE 4 (508351) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERDUE 4 138 KV 508351 TO DIANA 4 138 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PERSIMN7__GUTHRIE7 | 3 Phase fault PERSIMN7 (515951) 345 kV Bus a. Apply fault at the PERSIMN7 (515951) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PERSIMN7 345 KV 515951 TO GUTHRIE7 345 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PETTY__4__CHAPELH4 | 3 Phase fault PETTY 4 (508310) 138 kV Bus a. Apply fault at the PETTY 4 (508310) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PETTY 4 138 KV 508310 TO CHAPELH4 138 KV 508337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PIC4__CDRDLTP4 | 3 Phase fault PIC4 (520425) 138 kV Bus a. Apply fault at the PIC4 (520425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIC4 138 KV 520425 TO CDRDLTP4 138 KV 520848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PIC4__MOORLND4 | 3 Phase fault PIC4 (520425) 138 kV Bus a. Apply fault at the PIC4 (520425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIC4 138 KV 520425 TO MOORLND4 138 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PIEDMNT4__NORTWST4 | 3 Phase fault PIEDMNT4 (514864) 138 kV Bus a. Apply fault at the PIEDMNT4 (514864) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIEDMNT4 138 KV 514864 TO NORTWST4 138 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PINERTP2__WASHITA2 | 3 Phase fault PINERTP2 (521027) 69 kV Bus a. Apply fault at the PINERTP2 (521027) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PINERTP2 69 KV 521027 TO WASHITA2 69 KV 521088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PINK_SW4__SHAWNEE4 | 3 Phase fault PINK SW4 (521028) 138 kV Bus a. Apply fault at the PINK SW4 (521028) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PINK SW4 138 KV 521028 TO SHAWNEE4 138 KV 521048 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PINK___4__PINK_SW4 | 3 Phase fault PINK 4 (520494) 138 kV Bus a. Apply fault at the PINK 4 (520494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PINK 4 138 KV 520494 TO PINK SW4 138 KV 521028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PINTAIL7__KINGWD_7 | 3 Phase fault PINTAIL7 (516010) 345 kV Bus a. Apply fault at the PINTAIL7 (516010) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PINTAIL7 345 KV 516010 TO KINGWD 7 345 KV 516019 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PIRKEY_4__SABMINT4 | 3 Phase fault PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138 KV 508562 TO SABMINT4 138 KV 508566 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PIRKEY_4__WHITNEY4 | 3 Phase fault PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138 KV 508562 TO HALLSVLS4 138 KV 508595 CKT 1 b.2. LOAD 1 508595 b.3. WHITNEY4 138 KV 508575 TO HALLSVLS4 138 KV 508595 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PIRKEY_7__DIANA__7 | 3 Phase fault PIRKEY 7 (508563) 345 kV Bus a. Apply fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345 KV 508563 TO DIANA 7 345 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PIRKEY_7__LEBROCK7 | 3 Phase fault PIRKEY 7 (508563) 345 kV Bus a. Apply fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345 KV 508563 TO LEBROCK7 345 KV 508572 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PITTSB_CRIVER | 3 Phase fault PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345 KV 510907 TO C-RIVER7 345 KV 515422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PITTSB_JOHNCO | 3 Phase fault PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345 KV 510907 TO JOHNCO 7 345 KV 514809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PITTSB_KIOWA | 3 Phase fault PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345 KV 510907 TO KIOWA 7 345 KV 510925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PITTSB_SEMINOL | 3 Phase fault PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345 KV 510907 TO SEMINOL7 345 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PITTSB_VALIANT | 3 Phase fault PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345 KV 510907 TO VALIANT7 345 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_POLECTP4__HICKORY4 | 3 Phase fault POLECTP4 (515218) 138 kV Bus a. Apply fault at the POLECTP4 (515218) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POLECTP4 138 KV 515218 TO HICKORY4 138 KV 515244 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_POLECTP4__POLECAT4 | 3 Phase fault POLECTP4 (515218) 138 kV Bus a. Apply fault at the POLECTP4 (515218) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POLECTP4 138 KV 515218 TO POLECAT4 138 KV 515219 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_POOLVIL4__CARTRCO4 | 3 Phase fault POOLVIL4 (515130) 138 kV Bus a. Apply fault at the POOLVIL4 (515130) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POOLVIL4 138 KV 515130 TO CARTRCO4 138 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_POWELL_4__SW_SHV_4 | 3 Phase fault POWELL 4 (507748) 138 kV Bus a. Apply fault at the POWELL 4 (507748) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POWELL 4 138 KV 507748 TO SW SHV 4 138 KV 507759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PP_YARCHT | 3 Phase fault PP----E4 (509818) 138 kV Bus a. Apply fault at the PP----E4 (509818) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PP----E4 138 KV 509818 TO YARCHT 4 138 KV 509862 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PP_P&PWTP4 | 3 Phase fault PP----W4 (509805) 138 kV Bus a. Apply fault at the PP----W4 (509805) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PP----W4 138 KV 509805 TO P&P WTP4 138 KV 509851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PPTAP__4__46ST | 3 Phase fault PPTAP 4 (509863) 138 kV Bus a. Apply fault at the PPTAP 4 (509863) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PPTAP 4 138 KV 509863 TO 46ST-TP-4 138 KV 509900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_QUAILCK4__LNEOAK_4 | 3 Phase fault QUAILCK4 (514851) 138 kV Bus a. Apply fault at the QUAILCK4 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 138 KV 514851 TO LNEOAK 4 138 KV 514873 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_QUAILCK4__NORTWST4 | 3 Phase fault QUAILCK4 (514851) 138 kV Bus a. Apply fault at the QUAILCK4 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNEOAK 4 138 KV 514873 TO NORTWST4 138 KV 514879 CKT 1 b.2. QUAILCK4 138 KV 514851 TO LNEOAK 4 138 KV 514873 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_QUAILCK4__SLVRLAK4 | 3 Phase fault QUAILCK4 (514851) 138 kV Bus a. Apply fault at the QUAILCK4 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 138 KV 514851 TO SLVRLAK4 138 KV 514852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_R.S.S_5DELT | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138 KV 509783 TO 52DELWT4 138 KV 509814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_R.S.S._KIMCLRK4 | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 136YALE4 138 KV 509775 TO R.S.S.-4 138 KV 509783 CKT 1 b.2. 136YALE4 138 KV 509775 TO KIMCLRK4 138 KV 509845 CKT 1 b.3. LOAD 1 509845 b.4. B111---4 138 KV 509767 TO KIMCLRK4 138 KV 509845 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_R.S.S._EXPGLNT4 | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138 KV 509783 TO EXPGLNT4 138 KV 515473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_R.S.S._OAKSETP4 | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138 KV 509783 TO OAKSETP4 138 KV 509850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_R.S.S._EXP_OKM4 | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138 KV 509783 TO EXP_OKM4 138 KV 510904 CKT 1 b.2. LOAD 1 510904 b.3. OKMULGE4 138 KV 510898 TO EXP_OKM4 138 KV 510904 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_R.S.S._ORU-WTP4 | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138 KV 509783 TO ORU-WTP4 138 KV 509853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_R.S.S._ORU ETP4 | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138 KV 509783 TO ORU ETP4 138 KV 509849 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_R.S.S._RSST2 | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138 KV 509783 TO RSS T2 4 138 KV 509875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_R.S.S._COGENT | 3 Phase fault R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345 KV 509782 TO COGENT 7 345 KV 509834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on frequency protection settings | Disabling frequency protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_R.S.S._G16133G16146 | 3 Phase fault R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345 KV 509782 TO G16133G16146 345 KV 588039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_R.S.S._ONETA | 3 Phase fault R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345 KV 509782 TO ONETA--7 345 KV 509807 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_R.S.S._PECANCK7 | 3 Phase fault R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345 KV 509782 TO PECANCK7 345 KV 515235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_R.S.S._REDBUD | 3 Phase fault R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345 KV 509782 TO REDBUD 7 345 KV 514909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_R.S.S._SAPLPRD | 3 Phase fault R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345 KV 509782 TO SAPLPRD7 345 KV 509870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on frequency protection settings | Disabling frequency protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_RATLIFF4__CARTRCO4 | 3 Phase fault RATLIFF4 (515129) 138 kV Bus a. Apply fault at the RATLIFF4 (515129) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RATLIFF4 138 KV 515129 TO CARTRCO4 138 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_REDBAYOU_6__DOLHILL6 | 3 Phase fault REDBAYOU_6 (500255) 230 kV Bus a. Apply fault at the REDBAYOU_6 (500255) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBAYOU_6 230 KV 500255 TO DOLHILL6 230 KV 500260 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_REDBDPLN4__LEONARD4 | 3 Phase fault REDBDPLN4 (511573) 138 kV Bus a. Apply fault at the REDBDPLN4 (511573) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBDPLN4 138 KV 511573 TO LEONARD4 138 KV 511575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_REDCLFT4__REDCLF_4 | 3 Phase fault REDCLFT4 (515533) 138 kV Bus a. Apply fault at the REDCLFT4 (515533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDCLFT4 138 KV 515533 TO REDCLF 4 138 KV 515863 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_REDNGTN7__REDDIRT7 | 3 Phase fault REDNGTN7 (515875) 345 kV Bus a. Apply fault at the REDNGTN7 (515875) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDNGTN7 345 KV 515875 TO REDDIRT7 345 KV 515877 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_REDSPRG4__EYLAU__4 | 3 Phase fault REDSPRG4 (508075) 138 kV Bus a. Apply fault at the REDSPRG4 (508075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDSPRG4 138 KV 508075 TO EYLAU 4 138 KV 509655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_REDSPRG4__IPC_T__4 | 3 Phase fault REDSPRG4 (508075) 138 kV Bus a. Apply fault at the REDSPRG4 (508075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC-DOM4 138 KV 508060 TO REDSPRG4 138 KV 508075 CKT 1 b.2. LOAD 1 508075 b.3. IPC T 4 138 KV 508059 TO IPC-DOM4 138 KV 508060 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_REDWATR4__EYLAU__4 | 3 Phase fault REDWATR4 (509654) 138 kV Bus a. Apply fault at the REDWATR4 (509654) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDWATR4 138 KV 509654 TO EYLAU 4 138 KV 509655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_REMPKTP4__REMNGPK4 | 3 Phase fault REMPKTP4 (514872) 138 kV Bus a. Apply fault at the REMPKTP4 (514872) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REMPKTP4 138 KV 514872 TO REMNGPK4 138 KV 514874 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_RENO___2__SUNNYLN2 | 3 Phase fault RENO 2 (514972) 69 kV Bus a. Apply fault at the RENO 2 (514972) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 2 69 KV 514972 TO SUNNYLN2 69 KV 514980 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_RENO___4__WASHPRK4 | 3 Phase fault RENO 4 (514973) 138 kV Bus a. Apply fault at the RENO 4 (514973) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 4 138 KV 514973 TO WASHPRK4 138 KV 515156 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_RICHRDS4__PIEDMNT4 | 3 Phase fault RICHRDS4 (514862) 138 kV Bus a. Apply fault at the RICHRDS4 (514862) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHRDS4 138 KV 514862 TO PIEDMNT4 138 KV 514864 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ROCKYPT4__SPRNDAL4 | 3 Phase fault ROCKYPT4 (515164) 138 kV Bus a. Apply fault at the ROCKYPT4 (515164) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT4 138 KV 515164 TO SPRNDAL4 138 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ROKHILL4__NEWPROS4 | 3 Phase fault ROKHILL4 (509083) 138 kV Bus a. Apply fault at the ROKHILL4 (509083) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL4 138 KV 509083 TO NEWPROS4 138 KV 509102 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ROKHILL4__TATUM__4 | 3 Phase fault ROKHILL4 (509083) 138 kV Bus a. Apply fault at the ROKHILL4 (509083) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL4 138 KV 509083 TO TATUM 4 138 KV 509087 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ROMNOSE4__GEARYTP4 | 3 Phase fault ROMNOSE4 (514823) 138 kV Bus a. Apply fault at the ROMNOSE4 (514823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROMNOSE4 138 KV 514823 TO GEARYTP4 138 KV 515931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_RSS_T1_4__R.S.S. | 3 Phase fault RSS T1 4 (509773) 138 kV Bus a. Apply fault at the RSS T1 4 (509773) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T1 4 138 KV 509773 TO R.S.S.-4 138 KV 509783 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on frequency protection settings | Disabling frequency protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_RUSHSPR7__GEN | 3 Phase fault RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345 KV 511571 TO GEN-2018-055 345 KV 762900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_RVRFANT2__MUSKOGE2 | 3 Phase fault RVRFANT2 (515210) 69 kV Bus a. Apply fault at the RVRFANT2 (515210) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RVRFANT2 69 KV 515210 TO MUSKOGE2 69 KV 515221 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_RVRSID_2__MUSKOGE2 | 3 Phase fault RVRSID 2 (515205) 69 kV Bus a. Apply fault at the RVRSID 2 (515205) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RVRSID 2 69 KV 515205 TO MUSKOGE2 69 KV 515221 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_S.HIL_E4__SHILETP4 | 3 Phase fault S.HIL E4 (509731) 138 kV Bus a. Apply fault at the S.HIL E4 (509731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HIL E4 138 KV 509731 TO SHILETP4 138 KV 509813 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_S.S._BLUEBEL4 | 3 Phase fault S.S.---4 (509815) 138 kV Bus a. Apply fault at the S.S.---4 (509815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRATTV-4 138 KV 509758 TO S.S.---4 138 KV 509815 CKT 1 b.2. LOAD 1 509815 b.3. PRATTV-4 138 KV 509758 TO BLUEBEL4 138 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on frequency protection settings | Disabling frequency protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_S.S._DENV_WTAP | 3 Phase fault S.S.---4 (509815) 138 kV Bus a. Apply fault at the S.S.---4 (509815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---4 138 KV 509815 TO DENV_WTAP4 138 KV 509896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on frequency protection settings | Disabling frequency protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_S.S._HWY20-T | 3 Phase fault S.S.---4 (509815) 138 kV Bus a. Apply fault at the S.S.---4 (509815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---4 138 KV 509815 TO HWY20-T4 138 KV 509821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on frequency protection settings | Disabling frequency protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_S.S._WED-TAP4 | 3 Phase fault S.S.---4 (509815) 138 kV Bus a. Apply fault at the S.S.---4 (509815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---4 138 KV 509815 TO WED-TAP4 138 KV 509823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on frequency protection settings | Disabling frequency protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_S.W.S._ANADARK | 3 Phase fault S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138 KV 511477 TO ANADARK4 138 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN trips on voltage protection settings | Disabling voltage protection settings for BLUCAN prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_S.W.S._CORNVIL4 | 3 Phase fault S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VERDEN 4 138 KV 511421 TO S.W.S.-4 138 KV 511477 CKT 1 b.2. VERDEN 4 138 KV 511421 TO N29CHIK4 138 KV 511502 CKT 1 b.3. LOAD 1 511502 b.4. CORNVIL4 138 KV 511449 TO N29CHIK4 138 KV 511502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN trips on voltage protection settings | Disabling voltage protection settings for BLUCAN prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_S.W.S._ELGINJT4 | 3 Phase fault S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138 KV 511477 TO ELSWORTH 4 138 KV 511563 CKT 1 b.2. LOAD 1 511563 b.3. LOAD 2 511563 b.4. ELGINJT4 138 KV 511486 TO ELSWORTH 4 138 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN trips on voltage protection settings | Disabling voltage protection settings for BLUCAN prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_S.W.S._G16-097-TAP | 3 Phase fault S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138 KV 511477 TO G16-097-TAP 138 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN trips on voltage protection settings | Disabling voltage protection settings for BLUCAN prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_S.W.S._HOBJCT | 3 Phase fault S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNEG-4 138 KV 511445 TO S.W.S.-4 138 KV 511477 CKT 1 b.2. CARNEG-4 138 KV 511445 TO HOB-JCT4 138 KV 511463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN trips on voltage protection settings | Disabling voltage protection settings for BLUCAN prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_S.W.S._WASHITA | 3 Phase fault S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138 KV 511477 TO WASHITA4 138 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_S52DEL_4__52DELTP4 | 3 Phase fault S52DEL 4 (509716) 138 kV Bus a. Apply fault at the S52DEL 4 (509716) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S52DEL 4 138 KV 509716 TO 52DELTP4 138 KV 509776 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SABMINT4__SABINEM4 | 3 Phase fault SABMINT4 (508566) 138 kV Bus a. Apply fault at the SABMINT4 (508566) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SABMINT4 138 KV 508566 TO SABINEM4 138 KV 508577 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SALINA_5__SALNCRK5 | 3 Phase fault SALINA 5 (512686) 161 kV Bus a. Apply fault at the SALINA 5 (512686) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINA 5 161 KV 512686 TO SALNCRK5 161 KV 512805 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SALISAW5__GORE___5 | 3 Phase fault SALISAW5 (505550) 161 kV Bus a. Apply fault at the SALISAW5 (505550) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALISAW5 161 KV 505550 TO GORE 5 161 KV 505552 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SAPLPRD4__DENV_WTAP4 | 3 Phase fault SAPLPRD4 (509871) 138 kV Bus a. Apply fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 138 KV 509871 TO DENV_WTAP4 138 KV 509896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SAPLPRD4__R.S.S. | 3 Phase fault SAPLPRD4 (509871) 138 kV Bus a. Apply fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENKS--4 138 KV 509759 TO SAPLPRD4 138 KV 509871 CKT 1 b.2. 116JENK4 138 KV 509753 TO JENKS--4 138 KV 509759 CKT 1 b.3. LOAD 1 509759 b.4. 116JENK4 138 KV 509753 TO R.S.S.-4 138 KV 509783 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on frequency protection settings | Disabling frequency protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SAPULPA2__BEELINE2 | 3 Phase fault SAPULPA2 (515236) 69 kV Bus a. Apply fault at the SAPULPA2 (515236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPULPA2 69 KV 515236 TO BEELINE2 69 KV 515246 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SARA_RD4__SUNSHIN4 | 3 Phase fault SARA RD4 (521005) 138 kV Bus a. Apply fault at the SARA RD4 (521005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA RD4 138 KV 521005 TO SUNSHIN4 138 KV 521059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SARA___4__MCCLAIN4 | 3 Phase fault SARA 4 (514895) 138 kV Bus a. Apply fault at the SARA 4 (514895) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA 4 138 KV 514895 TO MCCLAIN4 138 KV 514902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SAWYER4__HUGO_PP4 | 3 Phase fault SAWYER4 (520411) 138 kV Bus a. Apply fault at the SAWYER4 (520411) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAWYER4 138 KV 520411 TO HUGO PP4 138 KV 520948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SCOFCTY4__COFFEYT4 | 3 Phase fault SCOFCTY4 (510378) 138 kV Bus a. Apply fault at the SCOFCTY4 (510378) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOFCTY4 138 KV 510378 TO COFFEYT4 138 KV 510422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SDIERKS2__DIERKSR2 | 3 Phase fault SDIERKS2 (507432) 69 kV Bus a. Apply fault at the SDIERKS2 (507432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SDIERKS2 69 KV 507432 TO DIERKSR2 69 KV 507437 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SDIERKS4__BARITERDTP_4 | 3 Phase fault SDIERKS4 (507433) 138 kV Bus a. Apply fault at the SDIERKS4 (507433) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SDIERKS4 138 KV 507433 TO BARITERDTP 4 138 KV 507463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SE15TH_4__BARNES_4 | 3 Phase fault SE15TH 4 (514993) 138 kV Bus a. Apply fault at the SE15TH 4 (514993) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SE15TH 4 138 KV 514993 TO BARNES 4 138 KV 515003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SE15TH_4__TINKER54 | 3 Phase fault SE15TH 4 (514993) 138 kV Bus a. Apply fault at the SE15TH 4 (514993) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDAL4 138 KV 514986 TO SE15TH 4 138 KV 514993 CKT 1 b.2. LOAD 1 514993 b.3. GLENDAL4 138 KV 514986 TO TINKER74 138 KV 515959 CKT 1 b.4. LOAD 1 515959 b.5. TINKER64 138 KV 515806 TO TINKER74 138 KV 515959 CKT 1 b.6. LOAD 1 515959 b.7. TINKER54 138 KV 514994 TO TINKER64 138 KV 515806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SELNDTP4__SELNDFL4 | 3 Phase fault SELNDTP4 (515965) 138 kV Bus a. Apply fault at the SELNDTP4 (515965) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SELNDTP4 138 KV 515965 TO SELNDFL4 138 KV 515966 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SELNDTP4__TROSPER4 | 3 Phase fault SELNDTP4 (515965) 138 kV Bus a. Apply fault at the SELNDTP4 (515965) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DISCVRY4 138 KV 514962 TO SELNDTP4 138 KV 515965 CKT 1 b.2. FOSTER 4 138 KV 514959 TO DISCVRY4 138 KV 514962 CKT 1 b.3. LOAD 1 514962 b.4. FOSTER 4 138 KV 514959 TO NEWDOMI4 138 KV 515387 CKT 1 b.5. LOAD 1 515387 b.6. TROSPER4 138 KV 514963 TO NEWDOMI4 138 KV 515387 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SEMINOL4__LKKONWA4 | 3 Phase fault SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138 KV 515044 TO LKKONWA4 138 KV 515977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SEMINOL4__MAUD___4 | 3 Phase fault SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138 KV 515044 TO MAUD 4 138 KV 515055 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SEMINOL4__PAOLI | 3 Phase fault SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138 KV 515044 TO PAOLI- 4 138 KV 515100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SEMINOL4__VANOSTP4 | 3 Phase fault SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138 KV 515044 TO VANOSTP4 138 KV 515531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SEMINOL7__FIREWHL | 3 Phase fault SEMINOL7 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 345 KV 515045 TO FIREWHL-TAP 345 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SEQUOYAHJ4__ANADARK4 | 3 Phase fault SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138 KV 520422 TO ANADARK4 138 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SEQUOYAHJ4__CKSHATP4 | 3 Phase fault SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138 KV 520422 TO CKSHATP4 138 KV 520473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SEQUOYAHJ4__SEQOYAH4 | 3 Phase fault SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138 KV 520422 TO SEQOYAH4 138 KV 520547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SETEXAR2__TEXARK_2 | 3 Phase fault SETEXAR2 (508077) 69 kV Bus a. Apply fault at the SETEXAR2 (508077) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETEXAR2 69 KV 508077 TO TEXARK 2 69 KV 508086 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SETEXAR4__MANDEVILTP4 | 3 Phase fault SETEXAR4 (508078) 138 kV Bus a. Apply fault at the SETEXAR4 (508078) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETEXAR4 138 KV 508078 TO MANDEVILTP4 138 KV 508105 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SFOREMAN__4__NNBOSTN4 | 3 Phase fault SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4 (504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 138 KV 504029 TO NNBOSTN4 138 KV 508069 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SFOREMAN__4__PATTERS4 | 3 Phase fault SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4 (504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 138 KV 504029 TO PATTERS4 138 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SHAWNEE2__SINCPNT2 | 3 Phase fault SHAWNEE2 (515068) 69 kV Bus a. Apply fault at the SHAWNEE2 (515068) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHAWNEE2 69 KV 515068 TO SINCPNT2 69 KV 515642 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SHILETP4__ORU | 3 Phase fault SHILETP4 (509813) 138 kV Bus a. Apply fault at the SHILETP4 (509813) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHILETP4 138 KV 509813 TO ORU-WTP4 138 KV 509853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SILSPWW5__KANSATP5 | 3 Phase fault SILSPWW5 (512642) 161 kV Bus a. Apply fault at the SILSPWW5 (512642) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILSPWW5 161 KV 512642 TO KANSATP5 161 KV 512714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SINCPAN2__SINCPNT2 | 3 Phase fault SINCPAN2 (515072) 69 kV Bus a. Apply fault at the SINCPAN2 (515072) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SINCPAN2 69 KV 515072 TO SINCPNT2 69 KV 515642 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SKELTON7__GEN | 3 Phase fault SKELTON7 (515990) 345 kV Bus a. Apply fault at the SKELTON7 (515990) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SKELTON7 345 KV 515990 TO GEN-2016-128 345 KV 588190 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SKYLINE4__FAIRFLD4 | 3 Phase fault SKYLINE4 (514850) 138 kV Bus a. Apply fault at the SKYLINE4 (514850) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SKYLINE4 138 KV 514850 TO CHISHOM4 138 KV 515374 CKT 1 b.2. LOAD 1 515374 b.3. CHISHOM4 138 KV 515374 TO FAIRFLD4 138 KV 515468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SKYLINE4__QUAILCK4 | 3 Phase fault SKYLINE4 (514850) 138 kV Bus a. Apply fault at the SKYLINE4 (514850) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SKYLINE4 138 KV 514850 TO QUAILCK4 138 KV 514851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SLVRLAK4__DVISION4 | 3 Phase fault SLVRLAK4 (514852) 138 kV Bus a. Apply fault at the SLVRLAK4 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 138 KV 514852 TO DVISION4 138 KV 514853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SLVRLAK4__NORTWST4 | 3 Phase fault SLVRLAK4 (514852) 138 kV Bus a. Apply fault at the SLVRLAK4 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 138 KV 514852 TO BRADEN 4 138 KV 514854 CKT 1 b.2. LOAD 1 514854 b.3. BRADEN 4 138 KV 514854 TO NORTWST4 138 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SMITHCO4__DAYTON_4 | 3 Phase fault SMITHCO4 (514891) 138 kV Bus a. Apply fault at the SMITHCO4 (514891) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMITHCO4 138 KV 514891 TO DAYTON 4 138 KV 514892 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SO4TH__2__CHSTNTT2 | 3 Phase fault SO4TH 2 (514730) 69 kV Bus a. Apply fault at the SO4TH 2 (514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 69 KV 514730 TO CHSTNTT2 69 KV 515456 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SO4TH__4__BRECKNR4 | 3 Phase fault SO4TH 4 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138 KV 514731 TO BRECKNR4 138 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SO4TH__4__IMO____4 | 3 Phase fault SO4TH 4 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138 KV 514731 TO IMO 4 138 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SOONER_7__G15 | 3 Phase fault SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345 KV 514803 TO G15-066T 345 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SOONER_7__G16 | 3 Phase fault SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345 KV 514803 TO G16-119-TAP 345 KV 587804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SOONER_7__PINTAIL7 | 3 Phase fault SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345 KV 514803 TO PINTAIL7 345 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SOONER_7__RANCHRD7 | 3 Phase fault SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345 KV 514803 TO RANCHRD7 345 KV 515576 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SOONER_7__THUNDER7 | 3 Phase fault SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345 KV 514803 TO THUNDER7 345 KV 515894 CKT 1 | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SOUTHRD4__ROMNOSE4 | 3 Phase fault SOUTHRD4 (514822) 138 kV Bus a. Apply fault at the SOUTHRD4 (514822) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOUTHRD4 138 KV 514822 TO ROMNOSE4 138 KV 514823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SPNKY_CK4__CATOOSA4 | 3 Phase fault SPNKY CK4 (509722) 138 kV Bus a. Apply fault at the SPNKY CK4 (509722) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPNKY CK4 138 KV 509722 TO CATOOSA4 138 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SPPMAINBUS__WELSH__7 | 3 Phase fault SPPMAINBUS (5917) 345 kV Bus a. Apply fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPPMAIN345 KV 5917 TO WELSH 7 345 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SPRHILL4__DIANA__4 | 3 Phase fault SPRHILL4 (508571) 138 kV Bus a. Apply fault at the SPRHILL4 (508571) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRHILL4 138 KV 508571 TO DIANA 4 138 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SQUIRCK4__NE45TAP4 | 3 Phase fault SQUIRCK4 (515059) 138 kV Bus a. Apply fault at the SQUIRCK4 (515059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQUIRCK4 138 KV 515059 TO INGLEWD4 138 KV 515060 CKT 1 b.2. LOAD 1 515060 b.3. INGLEWD4 138 KV 515060 TO STGREG 4 138 KV 515061 CKT 1 b.4. LOAD 1 515061 b.5. STGREG 4 138 KV 515061 TO NE45TAP4 138 KV 515062 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SQUIRCK4__STRLGTP4 | 3 Phase fault SQUIRCK4 (515059) 138 kV Bus a. Apply fault at the SQUIRCK4 (515059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQUIRCK4 138 KV 515059 TO STRLGTP4 138 KV 515286 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_STALOGA2__PUTNAM_2 | 3 Phase fault STALOGA2 (520454) 69 kV Bus a. Apply fault at the STALOGA2 (520454) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STALOGA2 69 KV 520454 TO PUTNAM 2 69 KV 521033 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_STNWAL_4__REMPKTP4 | 3 Phase fault STNWAL 4 (514870) 138 kV Bus a. Apply fault at the STNWAL 4 (514870) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNWAL 4 138 KV 514870 TO REMPKTP4 138 KV 514872 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_STNWAL_4__RENO___4 | 3 Phase fault STNWAL 4 (514870) 138 kV Bus a. Apply fault at the STNWAL 4 (514870) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNWAL 4 138 KV 514870 TO OUMED 4 138 KV 514875 CKT 1 b.2. LOAD 1 514875 b.3. OUMED 4 138 KV 514875 TO GATEWAY4 138 KV 515963 CKT 1 b.4. LOAD 1 515963 b.5. WASHPRK4 138 KV 515156 TO GATEWAY4 138 KV 515963 CKT 1 b.6. LOAD 1 515963 b.7. RENO 4 138 KV 514973 TO WASHPRK4 138 KV 515156 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_STRLGTP4__STERLNG4 | 3 Phase fault STRLGTP4 (515286) 138 kV Bus a. Apply fault at the STRLGTP4 (515286) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STRLGTP4 138 KV 515286 TO STERLNG4 138 KV 520449 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_STUBMAN4__HOLLYWD4 | 3 Phase fault STUBMAN4 (514952) 138 kV Bus a. Apply fault at the STUBMAN4 (514952) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STUBMAN4 138 KV 514952 TO HOLLYWD4 138 KV 514953 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SUGARHL2__SUGHLET2 | 3 Phase fault SUGARHL2 (508079) 69 kV Bus a. Apply fault at the SUGARHL2 (508079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGARHL2 69 KV 508079 TO SUGHLET2 69 KV 508081 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SUGARHL2__SUGHLWT2 | 3 Phase fault SUGARHL2 (508079) 69 kV Bus a. Apply fault at the SUGARHL2 (508079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGARHL2 69 KV 508079 TO SUGHLWT2 69 KV 508082 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SUGHLET2__TEXARK_2 | 3 Phase fault SUGHLET2 (508081) 69 kV Bus a. Apply fault at the SUGHLET2 (508081) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGHLET2 69 KV 508081 TO TEX12ST2 69 KV 508084 CKT 1 b.2. LOAD 1 508084 b.3. TEX12ST2 69 KV 508084 TO WASHST 2 69 KV 508088 CKT 1 b.4. LOAD 1 508088 b.5. TEXARK 2 69 KV 508086 TO WASHST 2 69 KV 508088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SUGHLWT2__TEX39ST2 | 3 Phase fault SUGHLWT2 (508082) 69 kV Bus a. Apply fault at the SUGHLWT2 (508082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGHLWT2 69 KV 508082 TO TEX39ST2 69 KV 508085 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SUMMERG2__LEASIDE_2 | 3 Phase fault SUMMERG2 (507758) 69 kV Bus a. Apply fault at the SUMMERG2 (507758) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMERG2 69 KV 507758 TO LEASIDE 2 69 KV 507794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SUNNYLN2__TINKER32 | 3 Phase fault SUNNYLN2 (514980) 69 kV Bus a. Apply fault at the SUNNYLN2 (514980) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYLN2 69 KV 514980 TO TINKER32 69 KV 514981 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SUNNYSD4__ARDWEST4 | 3 Phase fault SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNIROY 4 138 KV 515137 TO ARDWEST4 138 KV 515372 CKT 1 b.2. LOAD 1 515372 b.3. SUNNYSD4 138 KV 515135 TO UNIROY 4 138 KV 515137 CKT 1 b.4. LOAD 1 515137 b.5. CARTER 4 138 KV 515138 TO ARDWEST4 138 KV 515372 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SUNNYSD4__CARTRCO4 | 3 Phase fault SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138 KV 515135 TO CARTRCO4 138 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SUNNYSD4__LONEGRV4 | 3 Phase fault SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138 KV 515135 TO LONEGRV4 138 KV 515144 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SUNNYSD4__ROCKYPT4 | 3 Phase fault SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138 KV 515135 TO ROCKYPT4 138 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SUNNYSD7__G17 | 3 Phase fault SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345 KV 515136 TO G17-075-TAP 345 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SUNNYSD7__GEN | 3 Phase fault SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345 KV 515136 TO GEN-2017-167 345 KV 761859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SW134TP4__MCCLAIN4 | 3 Phase fault SW134TP4 (514876) 138 kV Bus a. Apply fault at the SW134TP4 (514876) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW134TP4 138 KV 514876 TO MCCLAIN4 138 KV 514902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SW134TP4__NORMHLL4 | 3 Phase fault SW134TP4 (514876) 138 kV Bus a. Apply fault at the SW134TP4 (514876) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW134TP4 138 KV 514876 TO SOGATE 4 138 KV 514928 CKT 1 b.2. LOAD 1 514928 b.3. SOGATE 4 138 KV 514928 TO TURNER 4 138 KV 514992 CKT 1 b.4. LOAD 1 514992 b.5. TURNER 4 138 KV 514992 TO NORMHLL4 138 KV 516097 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SW134TP4__PENN___4 | 3 Phase fault SW134TP4 (514876) 138 kV Bus a. Apply fault at the SW134TP4 (514876) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW134TP4 138 KV 514876 TO WESTMOR4 138 KV 514887 CKT 1 b.2. LOAD 1 514887 b.3. WESTMOR4 138 KV 514887 TO PENN 4 138 KV 514925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SWEETWT6__BUFFCK6 | 3 Phase fault SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230 KV 511541 TO BUFFCK6 230 KV 511542 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SWEETWT6__CHISHOLM6 | 3 Phase fault SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230 KV 511541 TO CHISHOLM6 230 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SWEETWT6__DEMPSEY6 | 3 Phase fault SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230 KV 511541 TO DEMPSEY6 230 KV 511544 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SWEETWT6__ROARK6 | 3 Phase fault SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230 KV 511541 TO ROARK6 230 KV 511547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SWEETWT6__STLN | 3 Phase fault SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230 KV 511541 TO STLN-DEMARC6 230 KV 523779 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SWISHER____6__TUCO_INT___6 | 3 Phase fault SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230 KV 525213 TO TUCO_INT 6 230 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SW_5TH_2__38TH_ST2 | 3 Phase fault SW 5TH 2 (514919) 69 kV Bus a. Apply fault at the SW 5TH 2 (514919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAY AVE2 69 KV 514913 TO SW 5TH 2 69 KV 514919 CKT 1 b.2. 38TH ST2 69 KV 514845 TO MAY AVE2 69 KV 514913 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SW_5TH_2__KENTUKT2 | 3 Phase fault SW 5TH 2 (514919) 69 kV Bus a. Apply fault at the SW 5TH 2 (514919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW 5TH 2 69 KV 514919 TO SW22ND 2 69 KV 514975 CKT 1 b.2. LOAD 1 514975 b.3. SW22ND 2 69 KV 514975 TO KENTUKY2 69 KV 514976 CKT 1 b.4. LOAD 1 514976 b.5. KENTUKY2 69 KV 514976 TO KENTUKT2 69 KV 514977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SW_5TH_4__CLASSEN4 | 3 Phase fault SW 5TH 4 (514920) 138 kV Bus a. Apply fault at the SW 5TH 4 (514920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW 5TH 4 138 KV 514920 TO CLASSEN4 138 KV 514922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SW_64TH2__PENN___2 | 3 Phase fault SW 64TH2 (514918) 69 kV Bus a. Apply fault at the SW 64TH2 (514918) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW 64TH2 69 KV 514918 TO PENN 2 69 KV 514924 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SW_SHV_4__FLOURNY4 | 3 Phase fault SW SHV 4 (507759) 138 kV Bus a. Apply fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENMOTR4 138 KV 507732 TO SW SHV 4 138 KV 507759 CKT 1 b.2. FLOURNY4 138 KV 507727 TO GENMOTR4 138 KV 507732 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SW_SHV_4__LEASIDE_4 | 3 Phase fault SW SHV 4 (507759) 138 kV Bus a. Apply fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW SHV 4 138 KV 507759 TO LEASIDE 4 138 KV 507793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SW_SHV_4__ROKHILL4 | 3 Phase fault SW SHV 4 (507759) 138 kV Bus a. Apply fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRIDGE4 138 KV 507757 TO SW SHV 4 138 KV 507759 CKT 1 b.2. SPRIDGE4 138 KV 507757 TO WLNTSPRINGS4 138 KV 509103 CKT 1 b.3. LOAD 1 509103 b.4. ROKHILL4 138 KV 509083 TO WLNTSPRINGS4 138 KV 509103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SW_SHV_7__DIANA__7 | 3 Phase fault SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345 KV 507760 TO DIANA 7 345 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SW_SHV_7__LONGWD_7 | 3 Phase fault SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345 KV 507760 TO LONGWD 7 345 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_S_SHV__4__CEDARGR4 | 3 Phase fault S SHV 4 (507755) 138 kV Bus a. Apply fault at the S SHV 4 (507755) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138 KV 507755 TO CEDARGR4 138 KV 507771 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_S_SHV__4__SW_SHV_4 | 3 Phase fault S SHV 4 (507755) 138 kV Bus a. Apply fault at the S SHV 4 (507755) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138 KV 507755 TO SW SHV 4 138 KV 507759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_S_SHV__4__WALLAKE4 | 3 Phase fault S SHV 4 (507755) 138 kV Bus a. Apply fault at the S SHV 4 (507755) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138 KV 507755 TO WALLAKE4 138 KV 507765 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_S_SHV__4__WESTELC4 | 3 Phase fault S SHV 4 (507755) 138 kV Bus a. Apply fault at the S SHV 4 (507755) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138 KV 507755 TO WESTELC4 138 KV 507767 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TCONCO_CEMRD_TP4 | 3 Phase fault T-CONCO4 (511424) 138 kV Bus a. Apply fault at the T-CONCO4 (511424) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T-CONCO4 138 KV 511424 TO CEMRD_TP4 138 KV 511576 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_T.NO._46STTP4 | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO 46ST-TP-4 138 KV 509900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_T.NO._BARNSAL4 | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO SKIATOK4 138 KV 509884 CKT 1 b.2. LOAD 1 509884 b.3. SKIATOK4 138 KV 509884 TO BARNSAL4 138 KV 510388 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_T.NO._CDC-ET4 | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO CDC-ET 4 138 KV 509839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_T.NO._CDC-WT4 | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO CDC-WT 4 138 KV 509842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_T.NO._NES | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO N.E.S.-4 138 KV 510396 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_T.NO._OWASOTP | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO OWASOTP4 138 KV 509844 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_T.NO._P&PWTP4 | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO P&P WTP4 138 KV 509851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_T.NO._TNO24 | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO T.NO.2-4 138 KV 509895 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_T.NO._CLEVLND7 | 3 Phase fault T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345 KV 509852 TO CLEVLND7 345 KV 512694 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_T.NO._IGLOOV7 | 3 Phase fault T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345 KV 509852 TO IGLOOV 7 345 KV 513596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_T.NO._NES7 | 3 Phase fault T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345 KV 509852 TO N.E.S.-7 345 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_T.NO.2_GEN-2018-028 | 3 Phase fault T.NO.2-4 (509895) 138 kV Bus a. Apply fault at the T.NO.2-4 (509895) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.2-4 138 KV 509895 TO GEN-2018-028 138 KV 762636 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_T.P.S._52DELWT | 3 Phase fault T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138 KV 509788 TO 52DELWT4 138 KV 509814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on frequency protection settings | Disabling frequency protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_T.P.S._CARSN-T4 | 3 Phase fault T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 36&OLY-4 138 KV 509724 TO T.P.S.-4 138 KV 509788 CKT 1 b.2. LOAD 1 509788 b.3. 36&OLY-4 138 KV 509724 TO CARSN-T4 138 KV 509739 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on frequency protection settings | Disabling frequency protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_T.P.S._GEN-2018-027 | 3 Phase fault T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138 KV 509788 TO GEN-2018-027 138 KV 762625 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_T.P.S._OAKSETP4 | 3 Phase fault T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138 KV 509788 TO OAKSETP4 138 KV 509850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on frequency protection settings | Disabling frequency protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_T.P.S._OAKSWTP4 | 3 Phase fault T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138 KV 509788 TO OAKSWTP4 138 KV 509848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on frequency protection settings | Disabling frequency protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_T.P.S._SAPLPRD | 3 Phase fault T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138 KV 509788 TO 72ELWOD4 138 KV 509888 CKT 1 b.2. LOAD 1 509888 b.3. SAPLPRD4 138 KV 509871 TO 72ELWOD4 138 KV 509888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on frequency protection settings | Disabling frequency protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_T.S.E._21STTAP4 | 3 Phase fault T.S.E.-4 (509811) 138 kV Bus a. Apply fault at the T.S.E.-4 (509811) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.S.E.-4 138 KV 509811 TO 21STTAP4 138 KV 509828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_T.S.E._E61ST | 3 Phase fault T.S.E.-4 (509811) 138 kV Bus a. Apply fault at the T.S.E.-4 (509811) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.S.E.-4 138 KV 509811 TO E.61ST-4 138 KV 509831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_T.S.E._KENSHETP4 | 3 Phase fault T.S.E.-4 (509811) 138 kV Bus a. Apply fault at the T.S.E.-4 (509811) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.S.E.-4 138 KV 509811 TO KENSH-E-TP4 138 KV 509830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_T.S.E._SHUD4 | 3 Phase fault T.S.E.-4 (509811) 138 kV Bus a. Apply fault at the T.S.E.-4 (509811) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.S.E.-4 138 KV 509811 TO S.HUD.-4 138 KV 509833 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TAHLQH_5__BRIGSKM_5 | 3 Phase fault TAHLQH 5 (512655) 161 kV Bus a. Apply fault at the TAHLQH 5 (512655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 161 KV 512655 TO BRIGSKM 5 161 KV 513044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TAHLQH_5__HWY59TP5 | 3 Phase fault TAHLQH 5 (512655) 161 kV Bus a. Apply fault at the TAHLQH 5 (512655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 161 KV 512655 TO HWY59TP5 161 KV 515527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TALOGA_2__HMBTTP | 3 Phase fault TALOGA 2 (521064) 69 kV Bus a. Apply fault at the TALOGA 2 (521064) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STALOGA2 69 KV 520454 TO TALOGA 2 69 KV 521064 CKT 1 b.2. STALOGA2 69 KV 520454 TO PUTNAM 2 69 KV 521033 CKT 1 b.3. LOAD 1 521033 b.4. HM-BTTP2 69 KV 520942 TO PUTNAM 2 69 KV 521033 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TALOGA_2__WOODWRD2 | 3 Phase fault TALOGA 2 (521064) 69 kV Bus a. Apply fault at the TALOGA 2 (521064) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALOGA 2 69 KV 521064 TO VICI 2 69 KV 521082 CKT 1 b.2. LOAD 1 521082 b.3. VICI 2 69 KV 521082 TO WOODWRD2 69 KV 521096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TALOGA_4__MOORLND4 | 3 Phase fault TALOGA 4 (521065) 138 kV Bus a. Apply fault at the TALOGA 4 (521065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEILING4 138 KV 520553 TO TALOGA 4 138 KV 521065 CKT 1 b.2. SEILING4 138 KV 520553 TO MOORLND4 138 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TATONGA7__CRSRDSW7 | 3 Phase fault TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345 KV 515407 TO CRSRDSW7 345 KV 515448 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TATONGA7__MAMTHPW7 | 3 Phase fault TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345 KV 515407 TO MAMTHPW7 345 KV 515585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TATONGA7__MATHWSN7 | 3 Phase fault TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345 KV 515407 TO MATHWSN7 345 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TATONGA7__SLNGWND7 | 3 Phase fault TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345 KV 515407 TO SLNGWND7 345 KV 515582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TAYLOR_2__TEX39ST2 | 3 Phase fault TAYLOR 2 (508083) 69 kV Bus a. Apply fault at the TAYLOR 2 (508083) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 2 69 KV 508083 TO TEX39ST2 69 KV 508085 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TAYLOR_2__TEXARK_2 | 3 Phase fault TAYLOR 2 (508083) 69 kV Bus a. Apply fault at the TAYLOR 2 (508083) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 2 69 KV 508083 TO TEXARK 2 69 KV 508086 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TECUMSH2__FRSTHIL2 | 3 Phase fault TECUMSH2 (515071) 69 kV Bus a. Apply fault at the TECUMSH2 (515071) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECUMSH2 69 KV 515071 TO FRSTHIL2 69 KV 515074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TENESTP4__84TH_ST4 | 3 Phase fault TENESTP4 (514837) 138 kV Bus a. Apply fault at the TENESTP4 (514837) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TENESTP4 138 KV 514837 TO 84TH ST4 138 KV 514843 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TERNIT_TERNITP4 | 3 Phase fault TER-NIT4 (509723) 138 kV Bus a. Apply fault at the TER-NIT4 (509723) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TER-NIT4 138 KV 509723 TO PCATOSA4 138 KV 509725 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TERNIT_TERNITP4 | 3 Phase fault TER-NIT4 (509723) 138 kV Bus a. Apply fault at the TER-NIT4 (509723) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TER-NIT4 138 KV 509723 TO TERNITP4 138 KV 509835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TERNITP4__VERDIGS4 | 3 Phase fault TERNITP4 (509835) 138 kV Bus a. Apply fault at the TERNITP4 (509835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERNITP4 138 KV 509835 TO VERDIGS4 138 KV 509854 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TERRYRD7__G17_171_TAP | 3 Phase fault TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345 KV 511568 TO G17-171-TAP 345 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TERRYRD7__RSHSPR1_MPT1 | 3 Phase fault TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345 KV 511568 TO RSHSPR1_MPT1 345 KV 511979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TERRYRD7__RUSHSPR7 | 3 Phase fault TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345 KV 511568 TO RUSHSPR7 345 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TERRYRD7__SUNNYSD7 | 3 Phase fault TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345 KV 511568 TO SUNNYSD7 345 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TEXARK_2__IPC_TAP2 | 3 Phase fault TEXARK 2 (508086) 69 kV Bus a. Apply fault at the TEXARK 2 (508086) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S_TEXARK 2 69 KV 504117 TO PLEASHL2 69 KV 508048 CKT 1 b.2. LOAD 1 508048 b.3. S_TEXARK 2 69 KV 504117 TO TEXARK 2 69 KV 508086 CKT 1 b.4. LOAD 1 508086 b.5. PLEASHL2 69 KV 508048 TO IPC TAP2 69 KV 508058 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_THISTLE7__GEN_2017-018 | 3 Phase fault THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345 KV 539801 TO GEN-2017-018 345 KV 588630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2011-008 trips on voltage protection settings | Disabling voltage protection settings for GEN-2011-008 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_THISTLE7__GEN-2018-049 | 3 Phase fault THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345 KV 539801 TO GEN-2018-049 345 KV 762834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 GEN-2011-008 trips on voltage protection settings | Lower acceleration to 0.2 Disabling voltage protection settings for GEN-2011-008 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TINKER54__BARNES_4 | 3 Phase fault TINKER54 (514994) 138 kV Bus a. Apply fault at the TINKER54 (514994) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TINKER54 138 KV 514994 TO BARNES 4 138 KV 515003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TOLK_______6__TUCO_INT___6 | 3 Phase fault TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230 KV 525531 TO TUCO_INT 6 230 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TROSPER4__RENO___4 | 3 Phase fault TROSPER4 (514963) 138 kV Bus a. Apply fault at the TROSPER4 (514963) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROSPER4 138 KV 514963 TO RENO 4 138 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TUCO_INT___6__ANTELOPE_1_6 | 3 Phase fault TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230 KV 525830 TO ANTELOPE_1 6 230 KV 525840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TUCO_INT___6__CARLISLE___6 | 3 Phase fault TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230 KV 525830 TO CARLISLE 6 230 KV 526161 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TUCO_INT___6__HALE_WNDCL16 | 3 Phase fault TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230 KV 525830 TO HALE_WNDCL16 230 KV 525957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TUCO_INT___6__JONES______6 | 3 Phase fault TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230 KV 525830 TO JONES 6 230 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TUCO_INT___7__ELK_CT1 | 3 Phase fault TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345 KV 525832 TO ELK_CT1 345 KV 525850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TUCO_INT___7__G17 | 3 Phase fault TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345 KV 525832 TO G17-151TAP 345 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TUCO_INT___7__YOAKUM_345 | 3 Phase fault TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345 KV 525832 TO YOAKUM_345 345 KV 526936 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TURCRK_2__TURCRKT2 | 3 Phase fault TURCRK 2 (514735) 69 kV Bus a. Apply fault at the TURCRK 2 (514735) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURCRK 2 69 KV 514735 TO TURCRKT2 69 KV 515517 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TURK___3__HOPE___3 | 3 Phase fault TURK 3 (507456) 115 kV Bus a. Apply fault at the TURK 3 (507456) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCNAB 3 115 KV 504122 TO TURK 3 115 KV 507456 CKT 1 b.2. MCNAB 3 115 KV 504122 TO HOPE 3 115 KV 507453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TURK___4__MANDEVILTP4 | 3 Phase fault TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 4 138 KV 507454 TO MANDEVILTP4 138 KV 508105 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TURK___4__SUGARHL4 | 3 Phase fault TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 4 138 KV 507454 TO SUGARHL4 138 KV 508080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TURK___7__NWTXARK7 | 3 Phase fault TURK 7 (507455) 345 kV Bus a. Apply fault at the TURK 7 (507455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURK 7 345 KV 507455 TO NWTXARK7 345 KV 508072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TUTCONT4__CEMRD_TP4 | 3 Phase fault TUTCONT4 (511425) 138 kV Bus a. Apply fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTCONT4 138 KV 511425 TO CEMRD_TP4 138 KV 511576 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2014-020 trips on frequency protection settings | Disabling frequency protection settings for GEN-2014-020 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TUTCONT4__CIMARON4 | 3 Phase fault TUTCONT4 (511425) 138 kV Bus a. Apply fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTCONT4 138 KV 511425 TO CIMARON4 138 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2014-020 trips on frequency protection settings | Disabling frequency protection settings for GEN-2014-020 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TUTCONT4__LEONARD4 | 3 Phase fault TUTCONT4 (511425) 138 kV Bus a. Apply fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTCONT4 138 KV 511425 TO TUTTLE4 138 KV 511501 CKT 1 b.2. LOAD 1 511501 b.3. TUTTLE4 138 KV 511501 TO LEONARD4 138 KV 511575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2014-020 trips on frequency protection settings | Disabling frequency protection settings for GEN-2014-020 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TUTTLE_4__TUTLETP4 | 3 Phase fault TUTTLE 4 (520496) 138 kV Bus a. Apply fault at the TUTTLE 4 (520496) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTTLE 4 138 KV 520496 TO TUTLETP4 138 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TWNLKJT4__TWNLKSW4 | 3 Phase fault TWNLKJT4 (520847) 138 kV Bus a. Apply fault at the TWNLKJT4 (520847) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWNLKJT4 138 KV 520847 TO TWNLKSW4 138 KV 521073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TXPLSTE2__TXPLSTP2 | 3 Phase fault TXPLSTE2 (514989) 69 kV Bus a. Apply fault at the TXPLSTE2 (514989) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXPLSTE2 69 KV 514989 TO TXPLSTP2 69 KV 515516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TXSTELA2__LITLAXT2 | 3 Phase fault TXSTELA2 (514985) 69 kV Bus a. Apply fault at the TXSTELA2 (514985) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXSTELA2 69 KV 514985 TO LITLAXT2 69 KV 515502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TXSTELA2__TXPLSTP2 | 3 Phase fault TXSTELA2 (514985) 69 kV Bus a. Apply fault at the TXSTELA2 (514985) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXSTELA2 69 KV 514985 TO TXPLSTP2 69 KV 515516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_VWEYCO4_VALIANT4 | 3 Phase fault V-WEYCO4 (510866) 138 kV Bus a. Apply fault at the V-WEYCO4 (510866) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. V-WEYCO4 138 KV 510866 TO VALIANT4 138 KV 510918 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_VALIANT4__B.BOWTP4 | 3 Phase fault VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IDABEL-4 138 KV 510886 TO VALIANT4 138 KV 510918 CKT 1 b.2. IDABEL-4 138 KV 510886 TO B.BOWTP4 138 KV 510888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_VALIANT4__HUGO_PP4 | 3 Phase fault VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 138 KV 510918 TO HUGO PP4 138 KV 520948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_VALIANT7__HUGO___7 | 3 Phase fault VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345 KV 510911 TO HUGO 7 345 KV 521157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_VANCE__2__SO4TH__2 | 3 Phase fault VANCE 2 (514718) 69 kV Bus a. Apply fault at the VANCE 2 (514718) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANCE 2 69 KV 514718 TO SO4TH 2 69 KV 514730 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_VANOSS_4__PARKLN_4 | 3 Phase fault VANOSS 4 (515174) 138 kV Bus a. Apply fault at the VANOSS 4 (515174) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANOSS 4 138 KV 515174 TO PARKLN 4 138 KV 515178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_VANOSS_4__VANOSTP4 | 3 Phase fault VANOSS 4 (515174) 138 kV Bus a. Apply fault at the VANOSS 4 (515174) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANOSS 4 138 KV 515174 TO VANOSTP4 138 KV 515531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_VINITA_VINITAJC2 | 3 Phase fault VINITA-2 (510404) 69 kV Bus a. Apply fault at the VINITA-2 (510404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINITA-2 69 KV 510404 TO VINTAJC2 69 KV 510418 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_VINTAJC4__ALWUETP4 | 3 Phase fault VINTAJC4 (510417) 138 kV Bus a. Apply fault at the VINTAJC4 (510417) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC4 138 KV 510417 TO ALWUETP4 138 KV 510429 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_VINTAJC4__HOC404_4 | 3 Phase fault VINTAJC4 (510417) 138 kV Bus a. Apply fault at the VINTAJC4 (510417) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC4 138 KV 510417 TO HOC404 4 138 KV 547486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_W.ED._CARSONT4 | 3 Phase fault W.ED.-W4 (509832) 138 kV Bus a. Apply fault at the W.ED.-W4 (509832) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W.ED.-W4 138 KV 509832 TO CARSONT4 138 KV 509865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WARNTAP4__77MEMW4 | 3 Phase fault WARNTAP4 (509858) 138 kV Bus a. Apply fault at the WARNTAP4 (509858) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 96YALE-4 138 KV 509847 TO WARNTAP4 138 KV 509858 CKT 1 b.2. 77MEM-W4 138 KV 509766 TO 96YALE-4 138 KV 509847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WARWICK4__BELLCOW4 | 3 Phase fault WARWICK4 (515047) 138 kV Bus a. Apply fault at the WARWICK4 (515047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARWICK4 138 KV 515047 TO BELLCOW4 138 KV 515369 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WARWICK4__TRYON_4 | 3 Phase fault WARWICK4 (515047) 138 kV Bus a. Apply fault at the WARWICK4 (515047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARWICK4 138 KV 515047 TO TRYON 4 138 KV 515675 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WARWICK4__WFROSST4 | 3 Phase fault WARWICK4 (515047) 138 kV Bus a. Apply fault at the WARWICK4 (515047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARWICK4 138 KV 515047 TO WFROSST4 138 KV 515366 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WASHITA4__BINGERJ4 | 3 Phase fault WASHITA4 (521089) 138 kV Bus a. Apply fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEY 4 138 KV 521017 TO WASHITA4 138 KV 521089 CKT 1 b.2. BINGERJ4 138 KV 520827 TO ONEY 4 138 KV 521017 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WASHITA4__SLKHILLS_4 | 3 Phase fault WASHITA4 (521089) 138 kV Bus a. Apply fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 138 KV 521089 TO SLKHILLS 4 138 KV 521103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN trips on voltage protection settings | Disabling voltage protection settings for BLUCAN prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WATLANT4__CASSTP4 | 3 Phase fault WATLANT4 (508090) 138 kV Bus a. Apply fault at the WATLANT4 (508090) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138 KV 508090 TO CASSTP4 138 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WATLANT4__WILKES_4 | 3 Phase fault WATLANT4 (508090) 138 kV Bus a. Apply fault at the WATLANT4 (508090) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138 KV 508090 TO WILKES 4 138 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WATNGSW4__CALUMET4 | 3 Phase fault WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138 KV 520536 TO CALUMET4 138 KV 520839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WATNGSW4__FAY____4 | 3 Phase fault WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138 KV 520536 TO WATONGA4 138 KV 521091 CKT 1 b.2. LOAD 1 521091 b.3. FAY 4 138 KV 520538 TO WATONGA4 138 KV 521091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WATNGSW4__KGFSHSW4 | 3 Phase fault WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138 KV 520536 TO OMEGA 4 138 KV 520964 CKT 1 b.2. LOAD 1 520964 b.3. PARKCOM4 138 KV 520475 TO OMEGA 4 138 KV 520964 CKT 1 b.4. LOAD 1 520964 b.5. PARKCOM4 138 KV 520475 TO KGFSHSW4 138 KV 520533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WATNGSW4__OKEENE_4 | 3 Phase fault WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138 KV 520536 TO OKEENE 4 138 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WAUKOTP4__HENESEY4 | 3 Phase fault WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 138 KV 514710 TO HENESEY4 138 KV 514774 CKT 1 b.2. LOAD 1 514774 b.3. WAUKOMI4 138 KV 514710 TO WAUKOTP4 138 KV 514711 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WAUKOTP4__SO4TH__4 | 3 Phase fault WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138 KV 514711 TO SO4TH 4 138 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WAUKOTP4__WOODRNG4 | 3 Phase fault WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138 KV 514711 TO WOODRNG4 138 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WCITYTP2__VALIANT2 | 3 Phase fault WCITYTP2 (510870) 69 kV Bus a. Apply fault at the WCITYTP2 (510870) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WCITYTP2 69 KV 510870 TO VALIANT2 69 KV 510910 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WED_CARSON4 | 3 Phase fault WED-TAP4 (509823) 138 kV Bus a. Apply fault at the WED-TAP4 (509823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WED-TAP4 138 KV 509823 TO CARSONT4 138 KV 509865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WEKIWA_GEN_2010_055 | 3 Phase fault WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138 KV 509757 TO GEN-2010-055 138 KV 560389 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WEKIWA_P&PWTP4 | 3 Phase fault WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138 KV 509757 TO P&P WTP4 138 KV 509851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WEKIWA_SS4 | 3 Phase fault WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEFFD-4 138 KV 509812 TO S.S.---4 138 KV 509815 CKT 1 b.2. LOAD 1 509815 b.3. WEKIWA-4 138 KV 509757 TO SHEFFD-4 138 KV 509812 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on frequency protection settings | Disabling frequency protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WEKIWA_SHEFFD | 3 Phase fault WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138 KV 509757 TO SHEFFD-4 138 KV 509812 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on frequency protection settings | Disabling frequency protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WEKIWA_SILCTYGR4 | 3 Phase fault WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138 KV 509757 TO SILVCTYGR4 138 KV 512726 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on frequency protection settings | Disabling frequency protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WEKIWA_WEDTAP4 | 3 Phase fault WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138 KV 509757 TO WED-TAP4 138 KV 509823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WEKIWA_SAPLPRD | 3 Phase fault WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345 KV 509755 TO SAPLPRD7 345 KV 509870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WEKIWA_SOONER | 3 Phase fault WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345 KV 509755 TO SOONER 7 345 KV 514803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WEKIWA_TNO7 | 3 Phase fault WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345 KV 509755 TO T.NO.--7 345 KV 509852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WELLSPA2__ONAPA__2 | 3 Phase fault WELLSPA2 (515215) 69 kV Bus a. Apply fault at the WELLSPA2 (515215) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELLSPA2 69 KV 515215 TO ONAPA 2 69 KV 521020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WELSHRE4__WILKES_4 | 3 Phase fault WELSHRE4 (508355) 138 kV Bus a. Apply fault at the WELSHRE4 (508355) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELSHRE4 138 KV 508355 TO WILKES 4 138 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WELSH__7__DIANA__7 | 3 Phase fault WELSH 7 (508359) 345 kV Bus a. Apply fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345 KV 508359 TO DIANA 7 345 KV 508832 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WELSH__7__WILKES_7 | 3 Phase fault WELSH 7 (508359) 345 kV Bus a. Apply fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345 KV 508359 TO WILKES 7 345 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WESTELC4__LEASIDE_4 | 3 Phase fault WESTELC4 (507767) 138 kV Bus a. Apply fault at the WESTELC4 (507767) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTELC4 138 KV 507767 TO LEASIDE 4 138 KV 507793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WESTERN4__STNWAL_4 | 3 Phase fault WESTERN4 (514869) 138 kV Bus a. Apply fault at the WESTERN4 (514869) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTERN4 138 KV 514869 TO STNWAL 4 138 KV 514870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WESTHSE4__INDNHIL4 | 3 Phase fault WESTHSE4 (514904) 138 kV Bus a. Apply fault at the WESTHSE4 (514904) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTHSE4 138 KV 514904 TO INDNHIL4 138 KV 514954 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFROSST4__LINCOLN4 | 3 Phase fault WFROSST4 (515366) 138 kV Bus a. Apply fault at the WFROSST4 (515366) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WFROSST4 138 KV 515366 TO LINCOLN4 138 KV 515442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFROSST4__RSSVILE4 | 3 Phase fault WFROSST4 (515366) 138 kV Bus a. Apply fault at the WFROSST4 (515366) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WFROSST4 138 KV 515366 TO RSSVILE4 138 KV 521107 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WHEELER____3__HOWARD_____3 | 3 Phase fault WHEELER 3 (523776) 115 kV Bus a. Apply fault at the WHEELER 3 (523776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 3 115 KV 523776 TO HOWARD 3 115 KV 523797 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WHEELER____6__STLN | 3 Phase fault WHEELER 6 (523777) 230 kV Bus a. Apply fault at the WHEELER 6 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 230 KV 523777 TO STLN-DEMARC6 230 KV 523779 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WHIRLPO4__CDC | 3 Phase fault WHIRLPO4 (509840) 138 kV Bus a. Apply fault at the WHIRLPO4 (509840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHIRLPO4 138 KV 509840 TO CDC-WT 4 138 KV 509842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WHITNEY4__EASTEX_4 | 3 Phase fault WHITNEY4 (508575) 138 kV Bus a. Apply fault at the WHITNEY4 (508575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY4 138 KV 508575 TO EASTEX 4 138 KV 508582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WHORSE_HWY20 | 3 Phase fault WHORSE-4 (509754) 138 kV Bus a. Apply fault at the WHORSE-4 (509754) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHORSE-4 138 KV 509754 TO HWY20-T4 138 KV 509821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WILKES_4__CHAPELH4 | 3 Phase fault WILKES 4 (508840) 138 kV Bus a. Apply fault at the WILKES 4 (508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPELH4 138 KV 508337 TO WELSHRE4 138 KV 508355 CKT 1 b.2. LOAD 1 508355 b.3. WELSHRE4 138 KV 508355 TO WILKES 4 138 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WINDFRM4__MOORLND4 | 3 Phase fault WINDFRM4 (515785) 138 kV Bus a. Apply fault at the WINDFRM4 (515785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 138 KV 515785 TO MOORLND4 138 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WLNUTCK4__PAOLI | 3 Phase fault WLNUTCK4 (515097) 138 kV Bus a. Apply fault at the WLNUTCK4 (515097) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WLNUTCK4 138 KV 515097 TO PAOLI- 4 138 KV 515100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WODWRD_2__WOODWRD2 | 3 Phase fault WODWRD 2 (514782) 69 kV Bus a. Apply fault at the WODWRD 2 (514782) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WODWRD 2 69 KV 514782 TO WOODWRD2 69 KV 521096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WOLFCRK4__CHEEKTP4 | 3 Phase fault WOLFCRK4 (515143) 138 kV Bus a. Apply fault at the WOLFCRK4 (515143) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK4 138 KV 515143 TO CHEEKTP4 138 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WOLVERN4__WOLVRNT4 | 3 Phase fault WOLVERN4 (515056) 138 kV Bus a. Apply fault at the WOLVERN4 (515056) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLVERN4 138 KV 515056 TO WOLVRNT4 138 KV 515532 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WOODRNG4__MARSHL_4 | 3 Phase fault WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 138 KV 514714 TO MARSHL 4 138 KV 514733 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WOODRNG7__GEN-2017-164 | 3 Phase fault WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345 KV 514715 TO GEN-2017-164 345 KV 762321 CKT 1 | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WOODRNG7__HUNTERS7 | 3 Phase fault WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345 KV 514715 TO HUNTERS7 345 KV 515476 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WOODRNG7__PINTAIL7 | 3 Phase fault WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345 KV 514715 TO PINTAIL7 345 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WOODRNG7__REDNGTN7 | 3 Phase fault WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345 KV 514715 TO REDNGTN7 345 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WOODRNG7__SKELTON7 | 3 Phase fault WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345 KV 514715 TO SKELTON7 345 KV 515990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WOODWRD2__CRTSJCT2 | 3 Phase fault WOODWRD2 (521096) 69 kV Bus a. Apply fault at the WOODWRD2 (521096) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD2 69 KV 521096 TO CRTSJCT2 69 KV 521197 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WOODWRD2__FARGOJCT2 | 3 Phase fault WOODWRD2 (521096) 69 kV Bus a. Apply fault at the WOODWRD2 (521096) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD2 69 KV 521096 TO FARGOJCT2 69 KV 521196 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WOODWRD4__CENT___4 | 3 Phase fault WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138 KV 514785 TO CENT 4 138 KV 515363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WOODWRD4__WINDFRM4 | 3 Phase fault WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138 KV 514785 TO WINDFRM4 138 KV 515785 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WOODWRD4__WWRDEHV4 | 3 Phase fault WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138 KV 514785 TO WWRDEHV4 138 KV 515376 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WRNMED_WRNMEDT4 | 3 Phase fault WRN-MED4 (509729) 138 kV Bus a. Apply fault at the WRN-MED4 (509729) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRN-MED4 138 KV 509729 TO WRNMEDT4 138 KV 509764 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WRNMEDT4__81YALTP4 | 3 Phase fault WRNMEDT4 (509764) 138 kV Bus a. Apply fault at the WRNMEDT4 (509764) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRNMEDT4 138 KV 509764 TO 81YALTP4 138 KV 509809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WRNMEDT4__S.HUD. | 3 Phase fault WRNMEDT4 (509764) 138 kV Bus a. Apply fault at the WRNMEDT4 (509764) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRNMEDT4 138 KV 509764 TO S.HUD.-4 138 KV 509833 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WWRDEHV4__KEENAN_4 | 3 Phase fault WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138 KV 515376 TO KEENAN 4 138 KV 515394 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WWRDEHV4__OUSPRT_4 | 3 Phase fault WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138 KV 515376 TO OUSPRT 4 138 KV 515398 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WWRDEHV4__REDCLFT4 | 3 Phase fault WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IODINE-4 138 KV 514796 TO WWRDEHV4 138 KV 515376 CKT 1 b.2. IODINE-4 138 KV 514796 TO REDCLFT4 138 KV 515533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WWRDEHV4__WWDPST_4 | 3 Phase fault WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138 KV 515376 TO WWDPST 4 138 KV 515425 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WWRDEHV7__BECKHAM7 | 3 Phase fault WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345 KV 515375 TO BECKHAM7 345 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WWRDEHV7__DGRASSE7 | 3 Phase fault WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345 KV 515375 TO DGRASSE7 345 KV 515852 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WWRDEHV7__G07621119 | 3 Phase fault WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345 KV 515375 TO G07621119-20 345 KV 515599 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WWRDEHV7__G16 | 3 Phase fault WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345 KV 515375 TO G16-003-TAP 345 KV 560071 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WWRDEHV7__GUTHRIE7 | 3 Phase fault WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345 KV 515375 TO GUTHRIE7 345 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WWRDEHV7__TATONGA7 | 3 Phase fault WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345 KV 515375 TO TATONGA7 345 KV 515407 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_YARCH_YARCHT4 | 3 Phase fault YARCH-N4 (509825) 138 kV Bus a. Apply fault at the YARCH-N4 (509825) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YARCH-N4 138 KV 509825 TO YARCHT 4 138 KV 509862 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_YARCH_PPTAP | 3 Phase fault YARCH-S4 (509824) 138 kV Bus a. Apply fault at the YARCH-S4 (509824) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YARCH-S4 138 KV 509824 TO KENSH-E-TP4 138 KV 509830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_YARCHT_4__PPTAP__4 | 3 Phase fault YARCHT 4 (509862) 138 kV Bus a. Apply fault at the YARCHT 4 (509862) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YARCHT 4 138 KV 509862 TO PPTAP 4 138 KV 509863 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_YOAKUM_345__HOBBS_INT__7 | 3 Phase fault YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345 KV 526936 TO HOBBS_INT 7 345 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ZUNIS_FULTONW4 | 3 Phase fault ZUNIS-N4 (509827) 138 kV Bus a. Apply fault at the ZUNIS-N4 (509827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ZUNIS-N4 138 KV 509827 TO FULTONW4 138 KV 509829 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_38TH_ST2__514846 | 3 Phase fault 38TH ST2 (514845) 69 kV Bus a. Apply fault at the 38TH ST2 (514845) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 38TH ST2 514845 TO 38TH ST4 514846 TO 38TH ST1 515768 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_4MURFBORO__337673 | 3 Phase fault 4MURFBORO (337672) 138 kV Bus a. Apply fault at the 4MURFBORO (337672) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MURFBORO 337672 TO 3MURFBORO.S! 337673 TO 1MURFBORO 337671 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_5TRIBES2__515228 | 3 Phase fault 5TRIBES2 (515227) 69 kV Bus a. Apply fault at the 5TRIBES2 (515227) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TRIBES2 515227 TO 5TRIBES5 515228 TO 5TRIBES1 515723 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_8ANO%__337912 | 3 Phase fault 8ANO% (337909) 500 kV Bus a. Apply fault at the 8ANO% (337909) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 337909 TO 5ANO% 337912 TO 1ANO AUX 337913 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_8EL_DORADO%__337539 | 3 Phase fault 8EL DORADO% (337561) 500 kV Bus a. Apply fault at the 8EL DORADO% (337561) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 337561 TO 3EL DORADO! 337539 TO 1EL DORADO3 337566 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_8EL_DORADO%__337562 | 3 Phase fault 8EL DORADO% (337561) 500 kV Bus a. Apply fault at the 8EL DORADO% (337561) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 337561 TO 7EL DORADO 337562 TO 1EL DORADO2 337565 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_8STERLING%__337415 | 3 Phase fault 8STERLING% (337420) 500 kV Bus a. Apply fault at the 8STERLING% (337420) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8STERLING% 337420 TO 3STERLING% 337415 TO 1STERLING3 337412 CKT 3 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AGENCY_2__515230 | 3 Phase fault AGENCY 2 (515229) 69 kV Bus a. Apply fault at the AGENCY 2 (515229) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AGENCY 2 515229 TO AGENCY 5 515230 TO AGENCY 1 515701 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ANADARK4__520810 | 3 Phase fault ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 520814 TO ANADARK2 520810 TO ADRKTERT 521181 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ARCADIA4__514908 | 3 Phase fault ARCADIA4 (514907) 138 kV Bus a. Apply fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 514907 TO ARCADIA7 514908 TO ARCADI31 515704 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ARSHILL2__507711 | 3 Phase fault ARSHILL2 (507710) 69 kV Bus a. Apply fault at the ARSHILL2 (507710) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL2 507710 TO ARSHILL4 507711 TO ARSH2-1 507714 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BANN___2__508054 | 3 Phase fault BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 508053 TO BANN 4 508054 TO BANN1-1 508097 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BEELINE2__515247 | 3 Phase fault BEELINE2 (515246) 69 kV Bus a. Apply fault at the BEELINE2 (515246) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEELINE2 515246 TO BEELINE4 515247 TO BEELINE1 515705 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BLUEBEL2__515242 | 3 Phase fault BLUEBEL2 (515241) 69 kV Bus a. Apply fault at the BLUEBEL2 (515241) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBEL2 515241 TO BLUEBEL4 515242 TO BLUEBEL1 515706 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BRISTOW2__515035 | 3 Phase fault BRISTOW2 (515034) 69 kV Bus a. Apply fault at the BRISTOW2 (515034) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW2 515034 TO BRISTOW4 515035 TO BRISTOW1 515709 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_BV_XFMR | 3 Phase fault BV-COM-2 (510389) 69 kV Bus a. Apply fault at the BV-COM-2 (510389) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BV-COM-2 510389 TO BV-COM-4 510390 TO BVCOM3-1 510372 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CRIVER_XFMR | 3 Phase fault C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 515422 TO C-RIVER4 510946 TO C-RIVER1 510947 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CANADNS4__520841 | 3 Phase fault CANADNS4 (520842) 138 kV Bus a. Apply fault at the CANADNS4 (520842) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 520842 TO CANADNS2 520841 TO CANTERT 521164 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CATOOSA2__509790 | 3 Phase fault CATOOSA2 (509799) 69 kV Bus a. Apply fault at the CATOOSA2 (509799) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA2 509799 TO CATOOSA4 509790 TO CATOO1-1 509867 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CATSAGR5__509790 | 3 Phase fault CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 512638 TO CATOOSA4 509790 TO 512835 CKT 3 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CHAMSPR5__506945 | 3 Phase fault CHAMSPR5 (506944) 161 kV Bus a. Apply fault at the CHAMSPR5 (506944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAMSPR5 506944 TO CHAMSPR7 506945 TO CHAMSPR1 506919 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CHISHOLM6__511553 | 3 Phase fault CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6 (511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CIMARON4__514901 | 3 Phase fault CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 514898 TO CIMARON7 514901 TO CIMARO21 515715 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CLARMR_5__512679 | 3 Phase fault CLARMR 5 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 512651 TO CLARMR 2 512679 TO CLARMR2 512815 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CLARMR_5__512707 | 3 Phase fault CLARMR 5 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 512651 TO CLARMR 4 512707 TO CLARMR4 512813 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CLEVLND7__512729 | 3 Phase fault CLEVLND7 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 512694 TO CLEVLND 4 512729 TO CLEVLND1 512817 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_COLINS_5__512705 | 3 Phase fault COLINS 5 (512627) 161 kV Bus a. Apply fault at the COLINS 5 (512627) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINS 5 512627 TO COLLINS4 512705 TO COLLIN1 1 512838 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_COLNSGR2__512627 | 3 Phase fault COLNSGR2 (512870) 69 kV Bus a. Apply fault at the COLNSGR2 (512870) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLNSGR2 512870 TO COLINS 5 512627 TO COLLIN3 1 512840 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_CORNVIL2__511449 | 3 Phase fault CORNVIL2 (511450) 69 kV Bus a. Apply fault at the CORNVIL2 (511450) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL2 511450 TO CORNVIL4 511449 TO CORNV2-1 511418 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DAWSON_XFMR | 3 Phase fault DAWSON-2 (509791) 69 kV Bus a. Apply fault at the DAWSON-2 (509791) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSON-2 509791 TO DAWSON-4 509792 TO DAWSN3-1 509877 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DELWARE4__510380 | 3 Phase fault DELWARE4 (510379) 138 kV Bus a. Apply fault at the DELWARE4 (510379) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELWARE4 510379 TO DELWARE7 510380 TO DELAWAR1 510370 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DEQUEEN2__507419 | 3 Phase fault DEQUEEN2 (507418) 69 kV Bus a. Apply fault at the DEQUEEN2 (507418) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEQUEEN2 507418 TO DEQUEEN4 507419 TO DQUEN1-1 507441 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DGRASSE4__515852 | 3 Phase fault DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 515853 TO DGRASSE7 515852 TO DGRASSE1 515854 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DIANA__4__508832 | 3 Phase fault DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 508831 TO DIANA 7 508832 TO DIANA-N1 508845 CKT 3 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DOVERSW4__520881 | 3 Phase fault DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 520882 TO DOVERSW2 520881 TO DVRTERT 521166 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_DRAPER_4__514934 | 3 Phase fault DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 514933 TO DRAPER 7 514934 TO DRAPER21 515792 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ELGINJT2__511486 | 3 Phase fault ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2 (511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ELKCTY_XFMR | 3 Phase fault ELKCTY-2 (511459) 69 kV Bus a. Apply fault at the ELKCTY-2 (511459) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-2 511459 TO ELKCTY-4 511458 TO ELKC4-1 511493 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ELKCTY_XFMR | 3 Phase fault ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 511458 TO ELKCITY6 511490 TO ELKC2-1 511482 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ELRENO_2__514819 | 3 Phase fault ELRENO 2 (514818) 69 kV Bus a. Apply fault at the ELRENO 2 (514818) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELRENO 2 514818 TO EL-RENO4 514819 TO EL RENO1 515722 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FLETCH_XFMR | 3 Phase fault FLETCH-4 (520912) 138 kV Bus a. Apply fault at the FLETCH-4 (520912) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCH-4 520912 TO FLETCHR2 520911 TO FLCHTERT 521168 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FLOURNY2__507727 | 3 Phase fault FLOURNY2 (507726) 69 kV Bus a. Apply fault at the FLOURNY2 (507726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 507726 TO FLOURNY4 507727 TO FLOURNY1 507740 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FRNKLNS4__520916 | 3 Phase fault FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRNKLNS4 520917 TO FRNKLNS2 520916 TO FRNKTERT 521169 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FRSTHIL2__515075 | 3 Phase fault FRSTHIL2 (515074) 69 kV Bus a. Apply fault at the FRSTHIL2 (515074) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRSTHIL2 515074 TO FRSTHIL4 515075 TO FRSTHIL1 515725 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FTSMITH7__515305 | 3 Phase fault FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 515302 TO FTSMITH8 515305 TO FTSMTH11 515726 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FTSMTHE5__515305 | 3 Phase fault FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5 (515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 515300 TO FTSMITH8 515305 TO FTSMTH31 515727 CKT 3 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FTSMTHW5__515302 | 3 Phase fault FTSMTHW5 (515301) 161 kV Bus a. Apply fault at the FTSMTHW5 (515301) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 515301 TO FTSMITH7 515302 TO FTSMTH51 515728 CKT 5 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_FTSMTHW5__515305 | 3 Phase fault FTSMTHW5 (515301) 161 kV Bus a. Apply fault at the FTSMTHW5 (515301) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 515301 TO FTSMITH8 515305 TO FTSMTH41 515791 CKT 4 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GORE___5__512644 | 3 Phase fault GORE 5 (505552) 161 kV Bus a. Apply fault at the GORE 5 (505552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 505552 TO GORE GR2 512644 TO GORTER1 512832 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRACMNT4__515800 | 3 Phase fault GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRAPEVINE__6__523770 | 3 Phase fault GRAPEVINE 6 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 523771 TO GRAPEVINE 3 523770 TO GRAPEVN_TR11 523769 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA1__5__512727 | 3 Phase fault GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 512656 TO GRDA1 2 512727 TO GRDA1 1 512816 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA1__7__512656 | 3 Phase fault GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 512650 TO GRDA1 5 512656 TO GRDA2 1 512826 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRTWSRN7__515820 | 3 Phase fault GRTWSRN7 (515825) 345 kV Bus a. Apply fault at the GRTWSRN7 (515825) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRTWSRN7 515825 TO GRTWSL11 515820 TO GRTWST11 515860 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRTWSRN7__515823 | 3 Phase fault GRTWSRN7 (515825) 345 kV Bus a. Apply fault at the GRTWSRN7 (515825) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRTWSRN7 515825 TO GRTWSL21 515823 TO GRTWST21 515824 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HOB_XFMR | 3 Phase fault HOB-JCT2 (511464) 69 kV Bus a. Apply fault at the HOB-JCT2 (511464) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT2 511464 TO HOB-JCT4 511463 TO HOBJT1-1 511417 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HOC404_5__547486 | 3 Phase fault HOC404 5 (547487) 161 kV Bus a. Apply fault at the HOC404 5 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 547487 TO HOC404 4 547486 TO HOC404A1 547715 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HSLWEST2__514941 | 3 Phase fault HSLWEST2 (514937) 69 kV Bus a. Apply fault at the HSLWEST2 (514937) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLWEST2 514937 TO HSL 4 514941 TO HSL 1 515731 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HUGO_XFMR | 3 Phase fault HUGO---2 (510893) 69 kV Bus a. Apply fault at the HUGO---2 (510893) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGO---2 510893 TO HUGO---4 510901 TO HUGO4-1 510859 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_HUGO___7__520560 | 3 Phase fault HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 521157 TO HUGOITC4 520560 TO HUGO TERTA 521189 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_IGLOOV_7__513593 | 3 Phase fault IGLOOV 7 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 513596 TO IGLOOV1 5 513593 TO IGLOTER1 1 513592 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_IGLOOV_7__513595 | 3 Phase fault IGLOOV 7 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 513596 TO IGLOOV2 5 513595 TO IGLOTER2 1 513594 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_IMO____2__514790 | 3 Phase fault IMO 2 (514721) 69 kV Bus a. Apply fault at the IMO 2 (514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 514721 TO IMO 4 514790 TO IMO 1 515788 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_JOHNCO_4__514809 | 3 Phase fault JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 514808 TO JOHNCO 7 514809 TO JOHNCO11 514810 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_KEENAN_1__515394 | 3 Phase fault KEENAN 1 (515393) 34.5 kV Bus a. Apply fault at the KEENAN 1 (515393) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEENAN 1 515393 TO KEENAN 4 515394 TO KEENAN T 515392 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_KNOXLEE2__508548 | 3 Phase fault KNOXLEE2 (508547) 69 kV Bus a. Apply fault at the KNOXLEE2 (508547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE2 508547 TO KNOXLEE4 508548 TO KXLEE-1 508584 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_L.E.S._XFMR | 3 Phase fault L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_L.E.S._XFMR | 3 Phase fault L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LEASIDE_2__507793 | 3 Phase fault LEASIDE 2 (507794) 69 kV Bus a. Apply fault at the LEASIDE 2 (507794) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEASIDE 2 507794 TO LEASIDE 4 507793 TO LEASIDE 1-1 507795 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LIEBERM2__508806 | 3 Phase fault LIEBERM2 (508805) 69 kV Bus a. Apply fault at the LIEBERM2 (508805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM2 508805 TO LIEBERM4 508806 TO LBMN3-1 508822 CKT 3 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LOGANSP2__509071 | 3 Phase fault LOGANSP2 (509070) 69 kV Bus a. Apply fault at the LOGANSP2 (509070) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGANSP2 509070 TO LOGANSP4 509071 TO 509094 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LONGWD_4__508809 | 3 Phase fault LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 508808 TO LONGWD 7 508809 TO LONGW1-1 508819 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_LSSOUTH2__508297 | 3 Phase fault LSSOUTH2 (508296) 69 kV Bus a. Apply fault at the LSSOUTH2 (508296) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH2 508296 TO LSSOUTH4 508297 TO LSS-1 508325 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MAID___5__512626 | 3 Phase fault MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 512648 TO MAID 2 512626 TO MAITER2 1 512837 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MANDEVILTP4__504363 | 3 Phase fault MANDEVILTP4 (508105) 138 kV Bus a. Apply fault at the MANDEVILTP4 (508105) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANDEVILTP4 508105 TO NE-TEXARK2 504363 TO NE-TEXARK1 504364 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MARAUTO2__508557 | 3 Phase fault MARAUTO2 (508576) 69 kV Bus a. Apply fault at the MARAUTO2 (508576) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARAUTO2 508576 TO MARSHL-4 508557 TO MRSH4#21 508592 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MAUD___4__515054 | 3 Phase fault MAUD 4 (515055) 138 kV Bus a. Apply fault at the MAUD 4 (515055) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 4 515055 TO MAUD 2 515054 TO MAUD 1 515736 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MENA___2__507436 | 3 Phase fault MENA 2 (508301) 69 kV Bus a. Apply fault at the MENA 2 (508301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENA 2 508301 TO MENA 4 507436 TO MENA3-1 507438 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MOORLND4__520995 | 3 Phase fault MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND4 520999 TO MOORLND2 520995 TO MLNDTERT 521180 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MSTANG_2__514861 | 3 Phase fault MSTANG 2 (514860) 69 kV Bus a. Apply fault at the MSTANG 2 (514860) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTANG 2 514860 TO MUSTANG4 514861 TO MUSTANG1 515740 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MSTNG10G__514861 | 3 Phase fault MSTNG10G (515672) 13.8 kV Bus a. Apply fault at the MSTNG10G (515672) 13.8 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTNG10G 515672 TO MUSTANG4 514861 TO MSTNG11G 515673 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MSTNG_8G__514861 | 3 Phase fault MSTNG 8G (515670) 13.8 kV Bus a. Apply fault at the MSTNG 8G (515670) 13.8 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTNG 8G 515670 TO MUSTANG4 514861 TO MSTNG 9G 515671 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_MUSKOGE2__515222 | 3 Phase fault MUSKOGE2 (515221) 69 kV Bus a. Apply fault at the MUSKOGE2 (515221) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKOGE2 515221 TO MUSKOGE5 515222 TO MUSKOG41 515797 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NBENTON2__508811 | 3 Phase fault NBENTON2 (508810) 69 kV Bus a. Apply fault at the NBENTON2 (508810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NBENTON2 508810 TO NBENTON4 508811 TO NBENTON1 508823 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NEOSHO_7__532937 | 3 Phase fault NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 532793 TO NEOSHO 5 532937 TO N345 2 1 532825 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NEOSHO_7__533021 | 3 Phase fault NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 532793 TO NEOSHO 4 533021 TO N345 1 1 532824 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NNBOSTN2__508069 | 3 Phase fault NNBOSTN2 (508068) 69 kV Bus a. Apply fault at the NNBOSTN2 (508068) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN2 508068 TO NNBOSTN4 508069 TO NNBT2-1 508099 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NORMHLL7__516097 | 3 Phase fault NORMHLL7 (516096) 345 kV Bus a. Apply fault at the NORMHLL7 (516096) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORMHLL7 516096 TO NORMHLL4 516097 TO NORMHL21 516099 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NORTWST4__514880 | 3 Phase fault NORTWST4 (514879) 138 kV Bus a. Apply fault at the NORTWST4 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTWST4 514879 TO NORTWST7 514880 TO NORTWS31 515743 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_NWTXARK4__508072 | 3 Phase fault NWTXARK4 (508071) 138 kV Bus a. Apply fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 508071 TO NWTXARK7 508072 TO NWTEX2-1 508101 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKAY___2__507428 | 3 Phase fault OKAY 2 (507427) 69 kV Bus a. Apply fault at the OKAY 2 (507427) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAY 2 507427 TO OKAY 4 507428 TO OKAY1-1 507442 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKEENE_4__521015 | 3 Phase fault OKEENE 4 (521016) 138 kV Bus a. Apply fault at the OKEENE 4 (521016) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKEENE 4 521016 TO OKEENE 2 521015 TO OKENTERT 521173 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ONETA_XFMR | 3 Phase fault ONETA--4 (509806) 138 kV Bus a. Apply fault at the ONETA--4 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 509806 TO ONETA--7 509807 TO ONETA1-1 509881 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OUSPRT_1__515398 | 3 Phase fault OUSPRT 1 (515397) 34.5 kV Bus a. Apply fault at the OUSPRT 1 (515397) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OUSPRT 1 515397 TO OUSPRT 4 515398 TO OUSPRT T 515396 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PALIOGE2__515100 | 3 Phase fault PALIOGE2 (515099) 69 kV Bus a. Apply fault at the PALIOGE2 (515099) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PALIOGE2 515099 TO PAOLI- 4 515100 TO PAOLI 1 515746 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PARKLN_2__515178 | 3 Phase fault PARKLN 2 (515177) 69 kV Bus a. Apply fault at the PARKLN 2 (515177) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKLN 2 515177 TO PARKLN 4 515178 TO PARKLN21 515748 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PATTERS2__507431 | 3 Phase fault PATTERS2 (507429) 69 kV Bus a. Apply fault at the PATTERS2 (507429) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS2 507429 TO PATTERS4 507431 TO PATTN2-1 507444 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PECANCK4__515234 | 3 Phase fault PECANCK4 (515233) 138 kV Bus a. Apply fault at the PECANCK4 (515233) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK4 515233 TO PECANCK5 515234 TO PECANC31 515750 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PECANCK5__515235 | 3 Phase fault PECANCK5 (515234) 161 kV Bus a. Apply fault at the PECANCK5 (515234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK5 515234 TO PECANCK7 515235 TO PECANC21 515759 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PENN___2__514925 | 3 Phase fault PENN 2 (514924) 69 kV Bus a. Apply fault at the PENN 2 (514924) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENN 2 514924 TO PENN 4 514925 TO PENN 1 515751 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PENSA__5__512628 | 3 Phase fault PENSA 5 (512654) 161 kV Bus a. Apply fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 5 512654 TO PENSA 2 512628 TO PENSA 1 512841 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_PIRKEY_4__508563 | 3 Phase fault PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY2-1 508588 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_R.S.S.XFMR | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 509783 TO RSS NG3 511844 TO RSS NG4 511845 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_REDBUD1S__514909 | 3 Phase fault REDBUD1S (514899) 18 kV Bus a. Apply fault at the REDBUD1S (514899) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD1S 514899 TO REDBUD 7 514909 TO REDBUD1G 514910 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_REDBUD2S__514909 | 3 Phase fault REDBUD2S (514900) 18 kV Bus a. Apply fault at the REDBUD2S (514900) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD2S 514900 TO REDBUD 7 514909 TO REDBUD2G 514911 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_REDBUD3S__514909 | 3 Phase fault REDBUD3S (514905) 18 kV Bus a. Apply fault at the REDBUD3S (514905) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD3S 514905 TO REDBUD 7 514909 TO REDBUD3G 514912 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_REDBUD4S__514909 | 3 Phase fault REDBUD4S (514940) 18 kV Bus a. Apply fault at the REDBUD4S (514940) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD4S 514940 TO REDBUD 7 514909 TO REDBUD4G 514942 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_RENO___2__514973 | 3 Phase fault RENO 2 (514972) 69 kV Bus a. Apply fault at the RENO 2 (514972) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 2 514972 TO RENO 4 514973 TO RENO 1 515753 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ROCKYPT2__515164 | 3 Phase fault ROCKYPT2 (515163) 69 kV Bus a. Apply fault at the ROCKYPT2 (515163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 515163 TO ROCKYPT4 515164 TO ROCKYPT1 515754 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_ROKHILL2__509083 | 3 Phase fault ROKHILL2 (509082) 69 kV Bus a. Apply fault at the ROKHILL2 (509082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL2 509082 TO ROKHILL4 509083 TO RKHIL2-1 509091 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_RSS_T1_4__509782 | 3 Phase fault RSS T1 4 (509773) 138 kV Bus a. Apply fault at the RSS T1 4 (509773) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T1 4 509773 TO R.S.S.-7 509782 TO RSST1 T1 509882 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on frequency protection settings | Disabling frequency protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_RSS_T2_4__509782 | 3 Phase fault RSS T2 4 (509875) 138 kV Bus a. Apply fault at the RSS T2 4 (509875) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T2 4 509875 TO R.S.S.-7 509782 TO RSST2 T1 509876 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on frequency protection settings | Disabling frequency protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_RUSHING2__515064 | 3 Phase fault RUSHING2 (515063) 69 kV Bus a. Apply fault at the RUSHING2 (515063) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSHING2 515063 TO RUSHING4 515064 TO RUSHING1 515755 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_RUSHSPR7__511965 | 3 Phase fault RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 511571 TO RUSHSPRW1-1 511965 TO RUSHSPR1-1 511572 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_S.S._XFMR | 3 Phase fault S.S.---2 (509816) 69 kV Bus a. Apply fault at the S.S.---2 (509816) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---2 509816 TO S.S.---4 509815 TO SS6-1 509878 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on frequency protection settings | Disabling frequency protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_S.W.S.2_XFMR | 3 Phase fault S.W.S.-2 (511476) 69 kV Bus a. Apply fault at the S.W.S.-2 (511476) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-2 511476 TO S.W.S.-4 511477 TO SWS#1--1 511413 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN trips on voltage protection settings | Disabling voltage protection settings for BLUCAN prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_S.W.S.4_XFMR | 3 Phase fault S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 511477 TO SWS NG4 511849 TO SWS NG5 511850 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN trips on voltage protection settings | Disabling voltage protection settings for BLUCAN prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SAPLPRD4__509870 | 3 Phase fault SAPLPRD4 (509871) 138 kV Bus a. Apply fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 509871 TO SAPLPRD7 509870 TO SAPLPRD1 509872 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on frequency protection settings | Disabling frequency protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SDIERKS2__507433 | 3 Phase fault SDIERKS2 (507432) 69 kV Bus a. Apply fault at the SDIERKS2 (507432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SDIERKS2 507432 TO SDIERKS4 507433 TO SDRKS1-1 507446 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SEMINOL4__515045 | 3 Phase fault SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 515044 TO SEMINOL7 515045 TO SEMINO21 515757 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SETEXAR2__508078 | 3 Phase fault SETEXAR2 (508077) 69 kV Bus a. Apply fault at the SETEXAR2 (508077) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETEXAR2 508077 TO SETEXAR4 508078 TO SETEX1-1 508102 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SFOREMAN__4__504030 | 3 Phase fault SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4 (504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 504029 TO SFORE_1 2 504030 TO SFORE_T1 1 504031 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SKELTON7__515991 | 3 Phase fault SKELTON7 (515990) 345 kV Bus a. Apply fault at the SKELTON7 (515990) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SKELTON7 515990 TO SKELTL11 515991 TO SKELTT11 515992 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SO4TH__2__514731 | 3 Phase fault SO4TH 2 (514730) 69 kV Bus a. Apply fault at the SO4TH 2 (514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 514730 TO SO4TH 4 514731 TO SO4TH 1 515758 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SOONER_4__514803 | 3 Phase fault SOONER 4 (514802) 138 kV Bus a. Apply fault at the SOONER 4 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 4 514802 TO SOONER 7 514803 TO SOONER 1 515760 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SUGARHL2__508080 | 3 Phase fault SUGARHL2 (508079) 69 kV Bus a. Apply fault at the SUGARHL2 (508079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGARHL2 508079 TO SUGARHL4 508080 TO SHILL1-1 508103 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SUNNYSD4__515136 | 3 Phase fault SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SUNNYSD7__515135 | 3 Phase fault SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SW_5TH_2__514920 | 3 Phase fault SW 5TH 2 (514919) 69 kV Bus a. Apply fault at the SW 5TH 2 (514919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW 5TH 2 514919 TO SW 5TH 4 514920 TO SW 5TH 1 515763 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SW_SHV_7__507759 | 3 Phase fault SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV1-1 507778 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_S_SHV__2__507755 | 3 Phase fault S SHV 2 (507754) 69 kV Bus a. Apply fault at the S SHV 2 (507754) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 2 507754 TO S SHV 4 507755 TO SSHV2-1 507776 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_T.NO.2_XFMR | 3 Phase fault T.NO.2-4 (509895) 138 kV Bus a. Apply fault at the T.NO.2-4 (509895) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.2-4 509895 TO T.NO.--7 509852 TO TNO2-1 509894 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2010-055 trips on voltage protection settings | Disabling voltage protection settings for GEN-2010-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_T.P.S._XFMR | 3 Phase fault T.P.S.-2 (509789) 69 kV Bus a. Apply fault at the T.P.S.-2 (509789) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-2 509789 TO T.P.S.-4 509788 TO TPS5-1 509880 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_T.S.E._XFMR | 3 Phase fault T.S.E.-2 (509820) 69 kV Bus a. Apply fault at the T.S.E.-2 (509820) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.S.E.-2 509820 TO T.S.E.-4 509811 TO TSE3-1 509873 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TAHLQH_5__512647 | 3 Phase fault TAHLQH 5 (512655) 161 kV Bus a. Apply fault at the TAHLQH 5 (512655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 512655 TO TAHLQH 2 512647 TO TAHLQH1 512851 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TALOGA_4__521064 | 3 Phase fault TALOGA 4 (521065) 138 kV Bus a. Apply fault at the TALOGA 4 (521065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALOGA 4 521065 TO TALOGA 2 521064 TO TLGTERT 521178 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_THISTLE7__539804 | 3 Phase fault THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 539801 TO THISTLE4 539804 TO THISTLE T1 539802 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2011-008 trips on voltage protection settings | Disabling voltage protection settings for GEN-2011-008 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TUCO_INT___6__525828 | 3 Phase fault TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 525830 TO TUCO_INT 3 525828 TO TUCO_TR4 1 525821 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TUCO_INT___7__525830 | 3 Phase fault TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 525832 TO TUCO_INT 6 525830 TO TUCO_TR2 1 525825 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TURK___3__507454 | 3 Phase fault TURK 3 (507456) 115 kV Bus a. Apply fault at the TURK 3 (507456) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 3 507456 TO TURK 4 507454 TO TURK1 1 507458 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_TURK___4__507455 | 3 Phase fault TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 4 507454 TO TURK 7 507455 TO TURK 1 507457 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_VALIANT2__510918 | 3 Phase fault VALIANT2 (510910) 69 kV Bus a. Apply fault at the VALIANT2 (510910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT2 510910 TO VALIANT4 510918 TO VALN1-1 510937 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_VALIANT4__510911 | 3 Phase fault VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 510918 TO VALIANT7 510911 TO VALN3-1 510939 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_VINTAJC2__510417 | 3 Phase fault VINTAJC2 (510418) 69 kV Bus a. Apply fault at the VINTAJC2 (510418) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC2 510418 TO VINTAJC4 510417 TO VINJT1-1 510367 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WAGNOR_5__512697 | 3 Phase fault WAGNOR 5 (512700) 161 kV Bus a. Apply fault at the WAGNOR 5 (512700) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAGNOR 5 512700 TO WAGNOR 2 512697 TO WAGNOR1 512818 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WASHITA4__521088 | 3 Phase fault WASHITA4 (521089) 138 kV Bus a. Apply fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 521089 TO WASHITA2 521088 TO WASHTERT 521179 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WATLANT2__508090 | 3 Phase fault WATLANT2 (508089) 69 kV Bus a. Apply fault at the WATLANT2 (508089) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT2 508089 TO WATLANT4 508090 TO WATL2-1 508046 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WEKIWA_XFMR | 3 Phase fault WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 509757 TO WEKIWA-7 509755 TO WEKIW1-1 509879 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WHEELER____6__523776 | 3 Phase fault WHEELER 6 (523777) 230 kV Bus a. Apply fault at the WHEELER 6 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 523777 TO WHEELER 3 523776 TO WHEELER_TR11 523774 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WHITNEY2__508575 | 3 Phase fault WHITNEY2 (508574) 69 kV Bus a. Apply fault at the WHITNEY2 (508574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY2 508574 TO WHITNEY4 508575 TO WHIT2-1 508590 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WILKES_4__508841 | 3 Phase fault WILKES 4 (508840) 138 kV Bus a. Apply fault at the WILKES 4 (508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 508840 TO WILKES 7 508841 TO WILKES-1 508826 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WOODRNG4__514715 | 3 Phase fault WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 514714 TO WOODRNG7 514715 TO WOODRNG1 515770 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WOODWRD4__514782 | 3 Phase fault WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 514785 TO WODWRD 2 514782 TO WOODWR21 515771 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WWRDEHV4__515375 | 3 Phase fault WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_YOAKUM_345__526935 | 3 Phase fault YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 526936 TO YOAKUM 6 526935 TO YOAKUM_TR1 526937 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKGE_All_10_P2_3_CLEOCOR4 | Apply single-phase fault at CLEOCOR4 (514778) 138 kV Bus for 6 cycles and DISCONNECT LINE 514778 TO 515562 CKT 1 and DISCONNECT LINE 515562 TO 514789 CKT 1 and DISCONNECT LINE 514789 TO 514790 CKT 1 and DISCONNECT LINE 514778 TO 514788 CKT 1 and DISCONNECT LINE 514788 TO 520999 CKT 1 and DISCONNECT LOAD 1 514788 and DISCONNECT LOAD 2 514788 and DISCONNECT LOAD 1 514789 and DISCONNECT LOAD 1 515553 and DISCONNECT 514788 and DISCONNECT 514789 and DISCONNECT 515553 and DISCONNECT 515562 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKGE_All_11_P2_3_BEEDISCONNECT LINE4 | Apply single-phase fault at BEELINE4 (515247) 138 kV Bus for 6 cycles and DISCONNECT 515705 and DISCONNECT LINE 515247 TO 515473 CKT 1 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKGE_All_12_P2_4_MUSKOGE5 | Apply single-phase fault at MUSKOGE5 (515222) 161 kV Bus for 6 cycles and DISCONNECT LINE 505558 TO 515222 CKT 1 and DISCONNECT LINE 515222 TO 515232 CKT 1 and DISCONNECT LINE 515222 TO 515640 CKT 1 and DISCONNECT LINE 515222 TO 516027 CKT 1 and DISCONNECT 515797 and DISCONNECT 515739 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKGE_All_6_P2_2_MCCLAIN4 | Apply single-phase fault at MCCLAIN4 (514902) 138 kV Bus for 6 cycles and DISCONNECT LINE 514902 TO 514998 CKT 1 and DISCONNECT LINE 514902 TO 514999 CKT 1 and DISCONNECT GENERATOR 1 514998 and DISCONNECT LOAD S1 514998 and DISCONNECT 514998 and DISCONNECT GENERATOR 1 514999 and DISCONNECT LOAD S1 514999 and DISCONNECT 514999 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKGE_All_7_P2_2_BRISTOW4 | Apply single-phase fault at BRISTOW4 (515035) 138 kV Bus for 6 cycles and DISCONNECT LINE 515035 TO 515048 CKT 1 and DISCONNECT LINE 515035 TO 515242 CKT 1 and DISCONNECT LINE 515035 TO 515249 CKT 1 and DISCONNECT LINE 515035 TO 515417 CKT 1 and DISCONNECT 515709 and DISCONNECT LOAD 1 515035 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKGE_All_8_P2_2_MASSARD5 | Apply single-phase fault at MASSARD5 (515343) 161 kV Bus for 6 cycles and DISCONNECT LINE 515293 TO 515343 CKT 1 and DISCONNECT LINE 515311 TO 515343 CKT 1 and DISCONNECT LINE 515341 TO 515343 CKT 1 and DISCONNECT LINE 515343 TO 515523 CKT 1 and DISCONNECT 515735 and DISCONNECT LOAD 1 515343 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKGE_All_9_P2_3_CLEOCOR4 | Apply single-phase fault at CLEOCOR4 (514778) 138 kV Bus for 6.0 cycles, clear fault and DISCONNECT LINE 514778 TO 515562 CKT 1 and DISCONNECT LINE 515562 TO 514789 CKT 1 and DISCONNECT LINE 514789 TO 514790 CKT 1 and DISCONNECT LINE 514778 TO 514788 CKT 1 and DISCONNECT LINE 514788 TO 520999 CKT 1 Apply single-phase fault at CLEOCOR4 (514778) 138 kV Bus for 20.0 cycles and CLOSE LINE 514778 TO 515562 CKT 1 and CLOSE LINE 515562 TO 514789 CKT 1 and CLOSE LINE 514789 TO 514790 CKT 1 and CLOSE LINE 514778 TO 514788 CKT 1 and CLOSE LINE 514788 TO 520999 CKT 1 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_34_P2_2_PAOLI4 | Apply single-phase fault at PAOLI 4 (521023) 138 kV Bus for 6 cycles and DISCONNECT 521023 and DISCONNECT 521174 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_35_P2_3_ANADARK4 | Apply single-phase fault at ANADARK4 (520814) 138 kV Bus for 6 cycles and DISCONNECT GENERATOR 1 521101 and DISCONNECT GENERATOR 1 521102 and DISCONNECT GENERATOR 1 521110 and DISCONNECT GENERATOR 1 521111 and DISCONNECT GENERATOR 1 521112 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_36_P2_3_WASHITA4 | Apply single-phase fault at WASHITA4 (521089) 138 kV Bus for 6 cycles and DISCONNECT LINE 515802 TO 521089 CKT 1 and DISCONNECT LINE 515802 TO 521089 CKT 2 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_37_P2_3_WASHITA4 | Apply single-phase fault at WASHITA4 (521089) 138 kV Bus for 6 cycles and DISCONNECT LINE 511477 TO 521089 CKT 1 and DISCONNECT LINE 515802 TO 521089 CKT 2 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_38_P2_3_WASHITA4 | Apply single-phase fault at WASHITA4 (521089) 138 kV Bus for 6 cycles and DISCONNECT LINE 515802 TO 521089 CKT 1 and DISCONNECT LINE 521089 TO 521017 CKT 1 and DISCONNECT LOAD 1 520468 and DISCONNECT LOAD 1 520503 and DISCONNECT LOAD 1 520856 and DISCONNECT LOAD 1 520950 and DISCONNECT LOAD 1 521010 and DISCONNECT LOAD 2 521010 and DISCONNECT LOAD 1 521017 and DISCONNECT LOAD 1 521050 and DISCONNECT LOAD 1 521092 and DISCONNECT 520468 and DISCONNECT 520503 and DISCONNECT 520827 and DISCONNECT 520856 and DISCONNECT 520950 and DISCONNECT 521010 and DISCONNECT 521017 and DISCONNECT 521050 and DISCONNECT 521092 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_39_P2_3_FRNKLNS4 | Apply single-phase fault at FRNKLNS4 (520917) 138 kV Bus for 6 cycles and DISCONNECT 514946 and DISCONNECT LINE 520917 TO 520913 CKT 1 and DISCONNECT LINE 521028 TO 520913 CKT 1 and DISCONNECT LOAD 1 520913 and DISCONNECT 520913 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_40_P2_3_FRNKLNS4 | Apply single-phase fault at FRNKLNS4 (520917) 138 kV Bus for 6 cycles and DISCONNECT 514946 and DISCONNECT LINE 520917 TO 520975 CKT 1 and DISCONNECT LINE 520400 TO 520975 CKT 1 and DISCONNECT LINE 520400 TO 520842 CKT 1 and DISCONNECT LOAD 1 520400 and DISCONNECT LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_41_P2_3_CANADNS4 | Apply single-phase fault at CANADNS4 (520842) 138 kV Bus for 6 cycles and DISCONNECT 514947 and DISCONNECT LINE 520842 TO 520400 CKT 1 and DISCONNECT LINE 520975 TO 520400 CKT 1 and DISCONNECT LINE 520917 TO 520975 CKT 1 and DISCONNECT LOAD 1 520400 and DISCONNECT LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_42_P2_3_CANADNS4 | Apply single-phase fault at CANADNS4 (520842) 138 kV Bus for 6 cycles and DISCONNECT 514947 and DISCONNECT LINE 520842 TO 520924 CKT 1 and DISCONNECT LINE 521104 TO 520924 CKT 1 and DISCONNECT LOAD 1 520924 and DISCONNECT 520924 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_43_P2_3_PHAROAH4 | Apply single-phase fault at PHAROAH4 (521026) 138 kV Bus for 6 cycles and DISCONNECT LINE 300686 TO 521026 CKT 1 and DISCONNECT LINE 301553 TO 521026 CKT 1 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_44_P2_4_HUGOPP4 | Apply single-phase fault at HUGO PP4 (520948) 138 kV Bus for 6 cycles and DISCONNECT LINE 520948 TO 520411 CKT 1 and DISCONNECT LINE 521036 TO 520411 CKT 1 and DISCONNECT LINE 521036 TO 520874 CKT 1 and DISCONNECT LINE 520968 TO 520874 CKT 1 and DISCONNECT LINE 520968 TO 510887 CKT 1 and DISCONNECT LINE 505602 TO 505600 CKT 1 and DISCONNECT LINE 521074 TO 505600 CKT 1 and DISCONNECT LINE 521074 TO 520448 CKT 1 and DISCONNECT LINE 521074 TO 510887 CKT 1 and DISCONNECT LOAD 1 515370 and DISCONNECT LOAD 1 515568 and DISCONNECT LOAD 1 520463 and DISCONNECT LOAD 1 520483 and DISCONNECT LOAD 1 520497 and DISCONNECT LOAD 1 520918 and DISCONNECT LOAD 1 521077 and DISCONNECT LOAD 1 521115 and DISCONNECT 515370 and DISCONNECT 515568 and DISCONNECT 520463 and DISCONNECT 520483 and DISCONNECT 520497 and DISCONNECT 520826 and DISCONNECT 520884 and DISCONNECT 520918 and DISCONNECT 521049 and DISCONNECT 521077 and DISCONNECT 521098 and DISCONNECT 521115 and DISCONNECT LOAD 1 520411 and DISCONNECT LOAD 1 520874 and DISCONNECT LOAD 1 520968 and DISCONNECT LOAD 1 521036 and DISCONNECT 520411 and DISCONNECT 520874 and DISCONNECT 520968 and DISCONNECT 521036 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_45_P2_4_HUGOPP4 | Apply single-phase fault at HUGO PP4 (520948) 138 kV Bus for 6 cycles and DISCONNECT LINE 520948 TO 900000 CKT 1 and DISCONNECT GENERATOR 1 520947 and DISCONNECT LINE 520834 TO 900001 CKT 1 and DISCONNECT LINE 520947 TO 520948 CKT 1 and DISCONNECT LOAD F1 520947 and DISCONNECT LOAD V1 520947 and DISCONNECT 520947 and DISCONNECT LOAD 1 520419 and DISCONNECT LOAD 1 520466 and DISCONNECT LOAD 1 520834 and DISCONNECT LOAD 1 520946 and DISCONNECT LOAD 1 521079 and DISCONNECT 520419 and DISCONNECT 520466 and DISCONNECT 520834 and DISCONNECT 520946 and DISCONNECT 520953 and DISCONNECT 521079 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_46_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 520996 TO 520999 CKT 1 and DISCONNECT LINE 520998 TO 520999 CKT 1 and DISCONNECT GENERATOR 1 520996 and DISCONNECT LOAD F1 520996 and DISCONNECT LOAD V1 520996 and DISCONNECT 520996 and DISCONNECT GENERATOR 1 520998 and DISCONNECT LOAD F1 520998 and DISCONNECT LOAD V1 520998 and DISCONNECT 520998 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_47_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 515853 TO 520999 CKT 1 and DISCONNECT LOAD 1 520553 and DISCONNECT 520553 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_48_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 520999 TO 520425 CKT 1 and DISCONNECT LINE 520848 TO 520425 CKT 1 and DISCONNECT LINE 520848 TO 521016 CKT 1 and DISCONNECT LOAD 1 520425 and DISCONNECT LOAD 1 520507 and DISCONNECT 520425 and DISCONNECT 520507 and DISCONNECT 520848 and DISCONNECT LINE 520920 TO 520957 CKT 1 and DISCONNECT LINE 520999 TO 520957 CKT 1 and DISCONNECT LOAD 1 520957 and DISCONNECT 520957 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_49_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 515785 TO 520999 CKT 1 and Open DISCONNECT LINE 520999 to 520462 ckt 1 and DISCONNECT LINE 520462 TO 520500 CKT 1 and DISCONNECT LINE 521128 TO 520500 CKT 1 and DISCONNECT LINE 521128 TO 521001 CKT 1 and DISCONNECT LOAD 1 520462 and DISCONNECT LOAD 1 520492 and DISCONNECT LOAD 1 520500 and DISCONNECT 520462 and DISCONNECT 520492 and DISCONNECT 520500 and DISCONNECT 521128 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_67_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6.0 cycles and DISCONNECT LINE 520996 TO 520999 CKT 1 and DISCONNECT GENERATOR 1 520996 and DISCONNECT LOAD F1 520996 and DISCONNECT LOAD V1 520996 and DISCONNECT 520996 Run fault at MOORLND4 (520999) 138 kV Bus for 9.0 cycles, clear fault and DISCONNECT LINE 520998 TO 520999 CKT 1 and DISCONNECT GENERATOR 1 520998 and DISCONNECT LOAD F1 520998 and DISCONNECT LOAD V1 520998 and DISCONNECT 520998 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_74_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 520999 TO 515853 CKT 1 and DISCONNECT LINE 520436 TO 515853 CKT 1 and DISCONNECT LOAD 1 520553 and DISCONNECT 520553 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer |  | Apply single-phase fault at ANADARK4 (520814) 138 kV Bus 6 cycles and DISCONNECT LINE 521031 TO 520814 CKT 1 and DISCONNECT BUS | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKGE_All_10_P2_3_CLEOCOR4 | Apply single-phase fault at CLEOCOR4 (514778) 138 kV Bus for 6 cycles and DISCONNECT LINE 514778 TO 515562 CKT 1 and DISCONNECT LINE 515562 TO 514789 CKT 1 and DISCONNECT LINE 514789 TO 514790 CKT 1 and DISCONNECT LINE 514778 TO 514788 CKT 1 and DISCONNECT LINE 514788 TO 520999 CKT 1 and DISCONNECT LOAD 1 514788 and DISCONNECT LOAD 2 514788 and DISCONNECT LOAD 1 514789 and DISCONNECT LOAD 1 515553 and DISCONNECT 514788 and DISCONNECT 514789 and DISCONNECT 515553 and DISCONNECT 515562 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKGE_All_11_P2_3_BEEDISCONNECT LINE4 | Apply single-phase fault at BEELINE4 (515247) 138 kV Bus for 6 cycles and DISCONNECT 515705 and DISCONNECT LINE 515247 TO 515473 CKT 1 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKGE_All_12_P2_4_MUSKOGE5 | Apply single-phase fault at MUSKOGE5 (515222) 161 kV Bus for 6 cycles and DISCONNECT LINE 505558 TO 515222 CKT 1 and DISCONNECT LINE 515222 TO 515232 CKT 1 and DISCONNECT LINE 515222 TO 515640 CKT 1 and DISCONNECT LINE 515222 TO 516027 CKT 1 and DISCONNECT 515797 and DISCONNECT 515739 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKGE_All_6_P2_2_MCCLAIN4 | Apply single-phase fault at MCCLAIN4 (514902) 138 kV Bus for 6 cycles and DISCONNECT LINE 514902 TO 514998 CKT 1 and DISCONNECT LINE 514902 TO 514999 CKT 1 and DISCONNECT GENERATOR 1 514998 and DISCONNECT LOAD S1 514998 and DISCONNECT 514998 and DISCONNECT GENERATOR 1 514999 and DISCONNECT LOAD S1 514999 and DISCONNECT 514999 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKGE_All_7_P2_2_BRISTOW4 | Apply single-phase fault at BRISTOW4 (515035) 138 kV Bus for 6 cycles and DISCONNECT LINE 515035 TO 515048 CKT 1 and DISCONNECT LINE 515035 TO 515242 CKT 1 and DISCONNECT LINE 515035 TO 515249 CKT 1 and DISCONNECT LINE 515035 TO 515417 CKT 1 and DISCONNECT 515709 and DISCONNECT LOAD 1 515035 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKGE_All_8_P2_2_MASSARD5 | Apply single-phase fault at MASSARD5 (515343) 161 kV Bus for 6 cycles and DISCONNECT LINE 515293 TO 515343 CKT 1 and DISCONNECT LINE 515311 TO 515343 CKT 1 and DISCONNECT LINE 515341 TO 515343 CKT 1 and DISCONNECT LINE 515343 TO 515523 CKT 1 and DISCONNECT 515735 and DISCONNECT LOAD 1 515343 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKGE_All_9_P2_3_CLEOCOR4 | Apply single-phase fault at CLEOCOR4 (514778) 138 kV Bus for 6.0 cycles, clear fault and DISCONNECT LINE 514778 TO 515562 CKT 1 and DISCONNECT LINE 515562 TO 514789 CKT 1 and DISCONNECT LINE 514789 TO 514790 CKT 1 and DISCONNECT LINE 514778 TO 514788 CKT 1 and DISCONNECT LINE 514788 TO 520999 CKT 1 Apply single-phase fault at CLEOCOR4 (514778) 138 kV Bus for 20.0 cycles and CLOSE LINE 514778 TO 515562 CKT 1 and CLOSE LINE 515562 TO 514789 CKT 1 and CLOSE LINE 514789 TO 514790 CKT 1 and CLOSE LINE 514778 TO 514788 CKT 1 and CLOSE LINE 514788 TO 520999 CKT 1 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_34_P2_2_PAOLI4 | Apply single-phase fault at PAOLI 4 (521023) 138 kV Bus for 6 cycles and DISCONNECT 521023 and DISCONNECT 521174 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_35_P2_3_ANADARK4 | Apply single-phase fault at ANADARK4 (520814) 138 kV Bus for 6 cycles and DISCONNECT GENERATOR 1 521101 and DISCONNECT GENERATOR 1 521102 and DISCONNECT GENERATOR 1 521110 and DISCONNECT GENERATOR 1 521111 and DISCONNECT GENERATOR 1 521112 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_36_P2_3_WASHITA4 | Apply single-phase fault at WASHITA4 (521089) 138 kV Bus for 6 cycles and DISCONNECT LINE 515802 TO 521089 CKT 1 and DISCONNECT LINE 515802 TO 521089 CKT 2 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_37_P2_3_WASHITA4 | Apply single-phase fault at WASHITA4 (521089) 138 kV Bus for 6 cycles and DISCONNECT LINE 511477 TO 521089 CKT 1 and DISCONNECT LINE 515802 TO 521089 CKT 2 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_38_P2_3_WASHITA4 | Apply single-phase fault at WASHITA4 (521089) 138 kV Bus for 6 cycles and DISCONNECT LINE 515802 TO 521089 CKT 1 and DISCONNECT LINE 521089 TO 521017 CKT 1 and DISCONNECT LOAD 1 520468 and DISCONNECT LOAD 1 520503 and DISCONNECT LOAD 1 520856 and DISCONNECT LOAD 1 520950 and DISCONNECT LOAD 1 521010 and DISCONNECT LOAD 2 521010 and DISCONNECT LOAD 1 521017 and DISCONNECT LOAD 1 521050 and DISCONNECT LOAD 1 521092 and DISCONNECT 520468 and DISCONNECT 520503 and DISCONNECT 520827 and DISCONNECT 520856 and DISCONNECT 520950 and DISCONNECT 521010 and DISCONNECT 521017 and DISCONNECT 521050 and DISCONNECT 521092 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_39_P2_3_FRNKLNS4 | Apply single-phase fault at FRNKLNS4 (520917) 138 kV Bus for 6 cycles and DISCONNECT 514946 and DISCONNECT LINE 520917 TO 520913 CKT 1 and DISCONNECT LINE 521028 TO 520913 CKT 1 and DISCONNECT LOAD 1 520913 and DISCONNECT 520913 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_40_P2_3_FRNKLNS4 | Apply single-phase fault at FRNKLNS4 (520917) 138 kV Bus for 6 cycles and DISCONNECT 514946 and DISCONNECT LINE 520917 TO 520975 CKT 1 and DISCONNECT LINE 520400 TO 520975 CKT 1 and DISCONNECT LINE 520400 TO 520842 CKT 1 and DISCONNECT LOAD 1 520400 and DISCONNECT LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_41_P2_3_CANADNS4 | Apply single-phase fault at CANADNS4 (520842) 138 kV Bus for 6 cycles and DISCONNECT 514947 and DISCONNECT LINE 520842 TO 520400 CKT 1 and DISCONNECT LINE 520975 TO 520400 CKT 1 and DISCONNECT LINE 520917 TO 520975 CKT 1 and DISCONNECT LOAD 1 520400 and DISCONNECT LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_42_P2_3_CANADNS4 | Apply single-phase fault at CANADNS4 (520842) 138 kV Bus for 6 cycles and DISCONNECT 514947 and DISCONNECT LINE 520842 TO 520924 CKT 1 and DISCONNECT LINE 521104 TO 520924 CKT 1 and DISCONNECT LOAD 1 520924 and DISCONNECT 520924 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_43_P2_3_PHAROAH4 | Apply single-phase fault at PHAROAH4 (521026) 138 kV Bus for 6 cycles and DISCONNECT LINE 300686 TO 521026 CKT 1 and DISCONNECT LINE 301553 TO 521026 CKT 1 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_44_P2_4_HUGOPP4 | Apply single-phase fault at HUGO PP4 (520948) 138 kV Bus for 6 cycles and DISCONNECT LINE 520948 TO 520411 CKT 1 and DISCONNECT LINE 521036 TO 520411 CKT 1 and DISCONNECT LINE 521036 TO 520874 CKT 1 and DISCONNECT LINE 520968 TO 520874 CKT 1 and DISCONNECT LINE 520968 TO 510887 CKT 1 and DISCONNECT LINE 505602 TO 505600 CKT 1 and DISCONNECT LINE 521074 TO 505600 CKT 1 and DISCONNECT LINE 521074 TO 520448 CKT 1 and DISCONNECT LINE 521074 TO 510887 CKT 1 and DISCONNECT LOAD 1 515370 and DISCONNECT LOAD 1 515568 and DISCONNECT LOAD 1 520463 and DISCONNECT LOAD 1 520483 and DISCONNECT LOAD 1 520497 and DISCONNECT LOAD 1 520918 and DISCONNECT LOAD 1 521077 and DISCONNECT LOAD 1 521115 and DISCONNECT 515370 and DISCONNECT 515568 and DISCONNECT 520463 and DISCONNECT 520483 and DISCONNECT 520497 and DISCONNECT 520826 and DISCONNECT 520884 and DISCONNECT 520918 and DISCONNECT 521049 and DISCONNECT 521077 and DISCONNECT 521098 and DISCONNECT 521115 and DISCONNECT LOAD 1 520411 and DISCONNECT LOAD 1 520874 and DISCONNECT LOAD 1 520968 and DISCONNECT LOAD 1 521036 and DISCONNECT 520411 and DISCONNECT 520874 and DISCONNECT 520968 and DISCONNECT 521036 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_45_P2_4_HUGOPP4 | Apply single-phase fault at HUGO PP4 (520948) 138 kV Bus for 6 cycles and DISCONNECT LINE 520948 TO 900000 CKT 1 and DISCONNECT GENERATOR 1 520947 and DISCONNECT LINE 520834 TO 900001 CKT 1 and DISCONNECT LINE 520947 TO 520948 CKT 1 and DISCONNECT LOAD F1 520947 and DISCONNECT LOAD V1 520947 and DISCONNECT 520947 and DISCONNECT LOAD 1 520419 and DISCONNECT LOAD 1 520466 and DISCONNECT LOAD 1 520834 and DISCONNECT LOAD 1 520946 and DISCONNECT LOAD 1 521079 and DISCONNECT 520419 and DISCONNECT 520466 and DISCONNECT 520834 and DISCONNECT 520946 and DISCONNECT 520953 and DISCONNECT 521079 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_46_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 520996 TO 520999 CKT 1 and DISCONNECT LINE 520998 TO 520999 CKT 1 and DISCONNECT GENERATOR 1 520996 and DISCONNECT LOAD F1 520996 and DISCONNECT LOAD V1 520996 and DISCONNECT 520996 and DISCONNECT GENERATOR 1 520998 and DISCONNECT LOAD F1 520998 and DISCONNECT LOAD V1 520998 and DISCONNECT 520998 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_47_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 515853 TO 520999 CKT 1 and DISCONNECT LOAD 1 520553 and DISCONNECT 520553 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_48_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 520999 TO 520425 CKT 1 and DISCONNECT LINE 520848 TO 520425 CKT 1 and DISCONNECT LINE 520848 TO 521016 CKT 1 and DISCONNECT LOAD 1 520425 and DISCONNECT LOAD 1 520507 and DISCONNECT 520425 and DISCONNECT 520507 and DISCONNECT 520848 and DISCONNECT LINE 520920 TO 520957 CKT 1 and DISCONNECT LINE 520999 TO 520957 CKT 1 and DISCONNECT LOAD 1 520957 and DISCONNECT 520957 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_49_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 515785 TO 520999 CKT 1 and Open DISCONNECT LINE 520999 to 520462 ckt 1 and DISCONNECT LINE 520462 TO 520500 CKT 1 and DISCONNECT LINE 521128 TO 520500 CKT 1 and DISCONNECT LINE 521128 TO 521001 CKT 1 and DISCONNECT LOAD 1 520462 and DISCONNECT LOAD 1 520492 and DISCONNECT LOAD 1 520500 and DISCONNECT 520462 and DISCONNECT 520492 and DISCONNECT 520500 and DISCONNECT 521128 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_67_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6.0 cycles and DISCONNECT LINE 520996 TO 520999 CKT 1 and DISCONNECT GENERATOR 1 520996 and DISCONNECT LOAD F1 520996 and DISCONNECT LOAD V1 520996 and DISCONNECT 520996 Run fault at MOORLND4 (520999) 138 kV Bus for 9.0 cycles, clear fault and DISCONNECT LINE 520998 TO 520999 CKT 1 and DISCONNECT GENERATOR 1 520998 and DISCONNECT LOAD F1 520998 and DISCONNECT LOAD V1 520998 and DISCONNECT 520998 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_74_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 520999 TO 515853 CKT 1 and DISCONNECT LINE 520436 TO 515853 CKT 1 and DISCONNECT LOAD 1 520553 and DISCONNECT 520553 | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer |  | Apply single-phase fault at ANADARK4 (520814) 138 kV Bus 6 cycles and DISCONNECT LINE 521031 TO 520814 CKT 1 and DISCONNECT BUS | P2_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_10_P4_SWShreveport | Apply single-phase fault on SW SHV7 345.0 KV 507760 TO DIANA7 345.0 KV 508832 CKT 1, near SW SHV 7 for 5 cycles with stuck breaker at SW SHV 7 (507760) 345 kV Bus. Clear Fault after 10 cycles and trip SW SHV7 345.0 KV 507760 TO LONGWD7 345.0 KV 508809 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are subm
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_3_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO NWTXARK7 345.0 KV 508072 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO WILKES7 345.0 KV 508841 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are subm
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_4_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 2 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are subm
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_5_P4_Wilkes | Apply single-phase fault on LINE 508841 TO 508809 CKT 1, near WILKES 7 for 5 cycles with stuck breaker at WILKES 7 (508841) 345 kV Bus. Clear Fault after 10 cycles and trip LINE 508841 TO 508359 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_6_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO PIRKEY7 345.0 KV 508563 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are subm
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_7_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO WELSH7 345.0 KV 508359 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are subm
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_8_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO WILKES7 345.0 KV 508841 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_82_P4_Oneta | Apply single-phase fault on ONETA7 345.0 KV 509807 TO RSS7 345.0 KV 509782 CKT 1, near ONETA--7 for 5 cycles with stuck breaker at ONETA--7 (509807) 345 kV Bus. Clear Fault after 10 cycles and trip ONETA7 345.0 KV 509807 TO CLARKSV7 345.0 KV 509745 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_83_P4_Riverside | Apply single-phase fault on RSS7 345.0 KV 509782 TO REDBUD7 345.0 KV 514909 CKT 1, near R.S.S.-7 for 5 cycles with stuck breaker at R.S.S.-7 (509782) 345 kV Bus. Clear Fault after 10 cycles and trip RSS7 345.0 KV 509782 TO SAPLPRD7 345.0 KV 509870 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_84_P4_SantaFe | Apply single-phase fault on SANTAFE4 345.0 KV 511492 TO CORNVIL4 345.0 KV 511449 CKT 1, near SANTAFE4 for 5 cycles with stuck breaker at SANTAFE4 (511492) 138 kV Bus. Clear Fault after 10 cycles and trip SANTAFE4 345.0 KV 511492 TO RUSHSPT4 345.0 KV 511491 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_9_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO 7SAREPTA% 345.0 KV 337376 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_46_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_47_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_48_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_49_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_50_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_51_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_52_P4_IGLOOV7 | Apply single-phase fault on and DISCONNECT 527964, near IGLOOV 7 for 15 cycles with stuck breaker at IGLOOV 7 (513596) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_53_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_54_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_55_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_56_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_57_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_58_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_59_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_60_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_61_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_62_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_63_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_64_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_65_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_66_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_67_P4_KERRGR3 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR3 for 15 cycles with stuck breaker at KERR GR3 (512634) 115 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_68_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_69_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_70_P4_KETCHUM5 | Apply single-phase fault on and DISCONNECT 527964, near KETCHUM5 for 15 cycles with stuck breaker at KETCHUM5 (512669) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_71_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_72_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_73_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_74_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_75_P4_SALNCRK5 | Apply single-phase fault on and DISCONNECT 527964, near SALNCRK5 for 15 cycles with stuck breaker at SALNCRK5 (512805) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_76_P4_TONECE5 | Apply single-phase fault on and DISCONNECT 527964, near TONECE5 for 15 cycles with stuck breaker at TONECE5 (512751) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_77_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_GRDA_All_78_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKGE_All_16_P4_2_BVRCNTY7 | Apply single-phase fault on and DISCONNECT 527964, near BVRCNTY7 for 16 cycles with stuck breaker at BVRCNTY7 (515554) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKGE_All_17_P4_2_WINDFRM4 | Apply single-phase fault on and DISCONNECT 527964, near WINDFRM4 for 16 cycles with stuck breaker at WINDFRM4 (515785) 138 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKGE_All_18_P4_2_SUNNYSD7 | Apply single-phase fault on and DISCONNECT 527964, near SUNNYSD7 for 16 cycles with stuck breaker at SUNNYSD7 (515136) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKGE_All_19_P4_2_DRAPER4 | Apply single-phase fault on and DISCONNECT 527964, near DRAPER 4 for 16 cycles with stuck breaker at DRAPER 4 (514933) 138 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKGE_All_20_P4_2_WAUKOTP4 | Apply single-phase fault on LINE 514711 TO 514731 CKT 1 and LINE 514710 TO 514711 CKT 1, near WAUKOTP4 for 6 cycles with stuck breaker at WAUKOTP4 (514711) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514711 TO 514714 CKT 1 and LINE 514709 TO 514712 CKT 1 and LINE 514709 TO 514714 CKT 1 and LINE 514709 TO 514731 CKT 1 and DISCONNECT 514711 and DISCONNECT 514709 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKGE_All_21_P4_2_JOHNCO7 | Apply single-phase fault on and DISCONNECT 527964, near JOHNCO 7 for 16 cycles with stuck breaker at JOHNCO 7 (514809) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKGE_All_22_P4_2_GRACMNT7 | Apply single-phase fault on and DISCONNECT 527964, near GRACMNT7 for 16 cycles with stuck breaker at GRACMNT7 (515800) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKGE_All_23_P4_2_OPENSKY7 | Apply single-phase fault on and DISCONNECT 527964, near OPENSKY7 for 16 cycles with stuck breaker at OPENSKY7 (515621) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKGE_All_24_P4_2_PECANCK7 | Apply single-phase fault on and DISCONNECT 527964, near PECANCK7 for 16 cycles with stuck breaker at PECANCK7 (515235) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKGE_All_25_P4_2_RANCHRD7 | Apply single-phase fault on and DISCONNECT 527964, near RANCHRD7 for 16 cycles with stuck breaker at RANCHRD7 (515576) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKGE_All_26_P4_2_REDBUD7 | Apply single-phase fault on and DISCONNECT 527964, near REDBUD 7 for 16 cycles with stuck breaker at REDBUD 7 (514909) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKGE_All_27_P4_2_FTSMITH8 | Apply single-phase fault on and DISCONNECT 527964, near FTSMITH8 for 16 cycles with stuck breaker at FTSMITH8 (515305) 500 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKGE_All_28_P4_3_SEMINOL7 | Apply single-phase fault on and DISCONNECT 527964, near SEMINOL7 for 16 cycles with stuck breaker at SEMINOL7 (515045) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKGE_All_29_P4_3_SOONER7 | Apply single-phase fault on and DISCONNECT 527964, near SOONER 7 for 16 cycles with stuck breaker at SOONER 7 (514803) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKGE_All_30_P4_2_NORTWST7 | Apply single-phase fault on and DISCONNECT 527964, near NORTWST7 for 16 cycles with stuck breaker at NORTWST7 (514880) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKGE_All_31_P4_2_BORDER7 | Apply single-phase fault on and DISCONNECT 527964, near BORDER 7 for 16 cycles with stuck breaker at BORDER 7 (515458) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_OKGE_All_35_P4_6_SO4TH4 | Apply single-phase fault on LINE 514731 TO 514790 CKT 1 and LINE 514711 TO 514731 CKT 1, near SO4TH 4 for 6 cycles with stuck breaker at SO4TH 4 (514731) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514709 TO 514731 CKT 1 and LINE 514731 TO 514815 CKT 1 and DISCONNECT 515758 and LOAD 1 514731 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SPA_All_10_P4_2_BullShoals | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SPA_All_11_P4_2_BullShoals | Apply single-phase fault on LINE 338104 TO 338121 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338121 and drop LOAD 1 338122 and drop LOAD 1 338124 and DISCONNECT 338121 and DISCONNECT 338122 and DISCONNECT 338123 and DISCONNECT 338124 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SPA_All_12_P4_2_BullShoals | Apply single-phase fault on LINE 300095 TO 301057 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and trip DISCONNECT 505462 and trip DISCONNECT 505464 and trip DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SPA_All_13_P4_2_TableRock | Apply single-phase fault on LINE 505461 TO 338110 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SPA_All_14_P4_2_TableRock | Apply single-phase fault on LINE 300130 TO 300727 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SPA_All_15_P4_2_TableRock | Apply single-phase fault on LINE 338099 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SPA_All_16_P4_2_TableRock | Apply single-phase fault on LINE 505496 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SPA_All_17_P4_2_TableRock | Apply single-phase fault on LINE 547497 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SPA_All_18_P4_2_TableRock | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and trip LINE 505474 TO 300735 CKT 1 and DISCONNECT 505473 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SPA_All_19_P4_2_Norfork | Apply single-phase fault on LINE 505460 TO 300081 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SPA_All_20_P4_2_Norfork | Apply single-phase fault on LINE 505461 TO 504440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SPA_All_21_P4_2_Norfork | Apply single-phase fault on LINE 301549 TO 505448 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SPA_All_22_P4_2_Norfork | Apply single-phase fault on LINE 338132 TO 338129 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338130 and drop LOAD 1 338131 and DISCONNECT 338130 and DISCONNECT 338131 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SPA_All_23_P4_2_Norfork | Apply single-phase fault on LINE 505442 TO 505440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338220 and drop LOAD A1 504080 and DISCONNECT 338220 and DISCONNECT 504080 and DISCONNECT 504081 and DISCONNECT 504082 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SPA_All_24_P4_2_Norfork | Apply single-phase fault on LINE 301121 TO 505458 CKT 1, near NORFORK2 for 5 cycles with stuck breaker at NORFORK2 (505450) 69 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505450 and drop LOAD A1 504448 and drop LOAD 1 505458 and DISCONNECT 504448 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505458 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SPA_All_7_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505468 and DISCONNECT 505470 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SPA_All_8_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505468 and DISCONNECT 505470 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_SPA_All_9_P4_2_BullShoalsWest | Apply single-phase fault on LINE 338110 TO 505461 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and DISCONNECT 505468 and DISCONNECT 505470 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_50_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520422 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_51_P4_2_ANADARK4 | Apply single-phase fault on LINE 521059 TO 520501 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 520814 CKT 1 and LINE 520812 TO 520814 CKT 1 and LINE 520814 TO 520923 CKT 1 and trip GENERATOR 1 520812 and drop LOAD F1 520812 and drop LOAD V1 520812 and DISCONNECT 520812 and drop LOAD 1 520496 and drop LOAD 1 520501 and drop LOAD 1 521031 and DISCONNECT 520496 and DISCONNECT 520501 and DISCONNECT 521031 and DISCONNECT 521072 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_52_P4_2_ANADARK4 | Apply single-phase fault on LINE 521129 TO 521024 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 511477 TO 520814 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_53_P4_2_CANADNS4 | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near CANADNS4 for 6 cycles with stuck breaker at CANADNS4 (520842) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 514947 TO 520842 CKT 1 and LINE 520842 TO 514947 CKT 1 and drop LOAD 1 520924 and DISCONNECT 520924 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_54_P4_2_FRNKLNS4 | Apply single-phase fault on LINE 520842 TO 514947 CKT 1, near FRNKLNS4 for 6 cycles with stuck breaker at FRNKLNS4 (520917) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 514946 and LINE 520917 TO 514946 CKT 1 and drop LOAD 1 520400 and drop LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_55_P4_2_FTSUPLY4 | Apply single-phase fault on LINE 520922 TO 520920 CKT 1 and trip GENERATOR 1 521145 and DISCONNECT 520922 and DISCONNECT 521141 and DISCONNECT 521144 and DISCONNECT 521145 and DISCONNECT 521151, near FTSUPLY4 for 6 cycles with stuck breaker at FTSUPLY4 (520920) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and LINE 520920 TO 520957 CKT 1 and drop LOAD 1 520957 and DISCONNECT 520957 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_56_P4_2_HUGOPP4 | Apply single-phase fault on LINE 510887 TO 520448 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 505602 TO 521044 CKT 1 and drop LOAD 1 515370 and drop LOAD 1 515568 and drop LOAD 1 520463 and drop LOAD 1 520483 and drop LOAD 1 520497 and drop LOAD 1 520918 and drop LOAD 1 521077 and drop LOAD 1 521115 and DISCONNECT 515370 and DISCONNECT 515568 and DISCONNECT 520463 and DISCONNECT 520483 and DISCONNECT 520497 and DISCONNECT 520826 and DISCONNECT 520884 and DISCONNECT 520918 and DISCONNECT 521049 and DISCONNECT 521077 and DISCONNECT 521098 and DISCONNECT 521115 and drop LOAD 1 520411 and drop LOAD 1 520874 and drop LOAD 1 520968 and drop LOAD 1 521036 and DISCONNECT 520411 and DISCONNECT 520874 and DISCONNECT 520968 and DISCONNECT 521036 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_57_P4_2_HUGOPP4 | Apply single-phase fault on LINE 521194 TO 521195 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 520948 TO 521079 CKT 1 and trip GENERATOR 1 520947 and drop LOAD F1 520947 and drop LOAD V1 520947 and DISCONNECT 520947 and drop LOAD 1 520419 and drop LOAD 1 520466 and drop LOAD 1 520834 and drop LOAD 1 520946 and drop LOAD 1 521079 and DISCONNECT 520419 and DISCONNECT 520466 and DISCONNECT 520834 and DISCONNECT 520946 and DISCONNECT 520953 and DISCONNECT 521079 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_58_P4_2_MARIETTAS4 | Apply single-phase fault on LINE 515150 TO 514808 CKT 1, near MARIETA4 for 6 cycles with stuck breaker at MARIETA4 (520988) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520988 TO 515160 CKT 1 and LINE 520981 TO 520864 CKT 1 and drop LOAD 1 520455 and drop LOAD 1 520487 and drop LOAD 1 520488 and drop LOAD 1 520511 and drop LOAD 1 520901 and drop LOAD 1 521038 and drop LOAD 1 521061 and drop LOAD 1 521066 and DISCONNECT 520455 and DISCONNECT 520467 and DISCONNECT 520487 and DISCONNECT 520488 and DISCONNECT 520511 and DISCONNECT 520901 and DISCONNECT 520939 and DISCONNECT 520972 and DISCONNECT 521038 and DISCONNECT 521061 and DISCONNECT 521066 and DISCONNECT 521067 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_59_P4_2_NOELSW4 | Apply single-phase fault on LINE 521200 TO 520431 CKT 1, near NOELSW 4 for 6 cycles with stuck breaker at NOELSW 4 (520430) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520436 TO 515853 CKT 1 and LINE 520430 TO 520437 CKT 1 and drop LOAD 1 520431 and drop LOAD 1 520437 and drop LOAD 2 520437 and DISCONNECT 520431 and DISCONNECT 520437 and drop LOAD 1 520436 and drop LOAD 1 520601 and DISCONNECT 520436 and DISCONNECT 520601 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_60_P4_2_OKEENE4 | Apply single-phase fault on LINE 520882 TO 521016 CKT 1, near OKEENE 4 for 6 cycles with stuck breaker at OKEENE 4 (521016) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and drop LOAD 1 520425 and drop LOAD 1 520507 and DISCONNECT 520425 and DISCONNECT 520848 and DISCONNECT 520507 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_61_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 520510 CKT 1 and LINE 511449 TO 511483 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_62_P4_2_PHAROAH4 | Apply single-phase fault on LINE 300686 TO 300137 CKT 1, near PHAROAH4 for 6 cycles with stuck breaker at PHAROAH4 (521026) 138 kV Bus. Clear Fault after 9 cycles and trip DISCONNECT 301553 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_63_P4_2_TWNLKSW4 | Apply single-phase fault on LINE 520882 TO 520535 CKT 1, near TWNLKSW4 for 6 cycles with stuck breaker at TWNLKSW4 (521073) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520533 TO 520865 CKT 1 and LINE 521073 TO 520540 CKT Z1 and drop LOAD 1 520879 and drop LOAD 1 520540 and DISCONNECT 520879 and DISCONNECT 520540 and drop LOAD 1 521037 and drop LOAD 1 515930 and drop LOAD 1 520546 and drop LOAD 1 520479 and DISCONNECT 521037 and DISCONNECT 520474 and DISCONNECT 515930 and DISCONNECT 520545 and DISCONNECT 520546 and DISCONNECT 520847 and DISCONNECT 520479 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_64_P4_2_WAKTASW4 | Apply single-phase fault on LINE 515544 TO 515546 CKT 1, near WAKTASW4 for 6 cycles with stuck breaker at WAKTASW4 (520434) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 520434 and drop LOAD 1 520409 and drop LOAD 1A 520409 and DISCONNECT 520409 and DISCONNECT 520435 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_65_P4_2_WASHITA4 | Apply single-phase fault on LINE 511485 TO 520856 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 1 and LINE 521089 TO 521017 CKT 1 and drop LOAD 1 520468 and drop LOAD 1 520503 and drop LOAD 1 520856 and drop LOAD 1 520950 and drop LOAD 1 521010 and drop LOAD 2 521010 and drop LOAD 1 521017 and drop LOAD 1 521050 and drop LOAD 1 521092 and DISCONNECT 520468 and DISCONNECT 520503 and DISCONNECT 520827 and DISCONNECT 520856 and DISCONNECT 520950 and DISCONNECT 521010 and DISCONNECT 521017 and DISCONNECT 521050 and DISCONNECT 521092 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_66_P4_2_WASHITA4 | Apply single-phase fault on LINE 515802 TO 521089 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 2 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_75_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 and LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520923 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_WFEC_All_76_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 511449 TO 511502 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_10_P4_SWShreveport | Apply single-phase fault on SW SHV7 345.0 KV 507760 TO DIANA7 345.0 KV 508832 CKT 1, near SW SHV 7 for 5 cycles with stuck breaker at SW SHV 7 (507760) 345 kV Bus. Clear Fault after 10 cycles and trip SW SHV7 345.0 KV 507760 TO LONGWD7 345.0 KV 508809 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_3_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO NWTXARK7 345.0 KV 508072 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO WILKES7 345.0 KV 508841 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_4_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 2 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_5_P4_Wilkes | Apply single-phase fault on LINE 508841 TO 508809 CKT 1, near WILKES 7 for 5 cycles with stuck breaker at WILKES 7 (508841) 345 kV Bus. Clear Fault after 10 cycles and trip LINE 508841 TO 508359 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_6_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO PIRKEY7 345.0 KV 508563 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_7_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO WELSH7 345.0 KV 508359 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_8_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO WILKES7 345.0 KV 508841 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_82_P4_Oneta | Apply single-phase fault on ONETA7 345.0 KV 509807 TO RSS7 345.0 KV 509782 CKT 1, near ONETA--7 for 5 cycles with stuck breaker at ONETA--7 (509807) 345 kV Bus. Clear Fault after 10 cycles and trip ONETA7 345.0 KV 509807 TO CLARKSV7 345.0 KV 509745 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_83_P4_Riverside | Apply single-phase fault on RSS7 345.0 KV 509782 TO REDBUD7 345.0 KV 514909 CKT 1, near R.S.S.-7 for 5 cycles with stuck breaker at R.S.S.-7 (509782) 345 kV Bus. Clear Fault after 10 cycles and trip RSS7 345.0 KV 509782 TO SAPLPRD7 345.0 KV 509870 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_84_P4_SantaFe | Apply single-phase fault on SANTAFE4 345.0 KV 511492 TO CORNVIL4 345.0 KV 511449 CKT 1, near SANTAFE4 for 5 cycles with stuck breaker at SANTAFE4 (511492) 138 kV Bus. Clear Fault after 10 cycles and trip SANTAFE4 345.0 KV 511492 TO RUSHSPT4 345.0 KV 511491 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_9_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO 7SAREPTA% 345.0 KV 337376 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_46_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_47_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_48_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_49_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_50_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_51_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_52_P4_IGLOOV7 | Apply single-phase fault on and DISCONNECT 527964, near IGLOOV 7 for 15 cycles with stuck breaker at IGLOOV 7 (513596) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_53_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_54_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_55_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_56_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_57_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_58_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_59_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_60_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_61_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_62_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_63_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_64_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_65_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_66_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_67_P4_KERRGR3 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR3 for 15 cycles with stuck breaker at KERR GR3 (512634) 115 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_68_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_69_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_70_P4_KETCHUM5 | Apply single-phase fault on and DISCONNECT 527964, near KETCHUM5 for 15 cycles with stuck breaker at KETCHUM5 (512669) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_71_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_72_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_73_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_74_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_75_P4_SALNCRK5 | Apply single-phase fault on and DISCONNECT 527964, near SALNCRK5 for 15 cycles with stuck breaker at SALNCRK5 (512805) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_76_P4_TONECE5 | Apply single-phase fault on and DISCONNECT 527964, near TONECE5 for 15 cycles with stuck breaker at TONECE5 (512751) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_77_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_GRDA_All_78_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKGE_All_16_P4_2_BVRCNTY7 | Apply single-phase fault on and DISCONNECT 527964, near BVRCNTY7 for 16 cycles with stuck breaker at BVRCNTY7 (515554) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKGE_All_17_P4_2_WINDFRM4 | Apply single-phase fault on and DISCONNECT 527964, near WINDFRM4 for 16 cycles with stuck breaker at WINDFRM4 (515785) 138 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKGE_All_18_P4_2_SUNNYSD7 | Apply single-phase fault on and DISCONNECT 527964, near SUNNYSD7 for 16 cycles with stuck breaker at SUNNYSD7 (515136) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKGE_All_19_P4_2_DRAPER4 | Apply single-phase fault on and DISCONNECT 527964, near DRAPER 4 for 16 cycles with stuck breaker at DRAPER 4 (514933) 138 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for 2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKGE_All_20_P4_2_WAUKOTP4 | Apply single-phase fault on LINE 514711 TO 514731 CKT 1 and LINE 514710 TO 514711 CKT 1, near WAUKOTP4 for 6 cycles with stuck breaker at WAUKOTP4 (514711) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514711 TO 514714 CKT 1 and LINE 514709 TO 514712 CKT 1 and LINE 514709 TO 514714 CKT 1 and LINE 514709 TO 514731 CKT 1 and DISCONNECT 514711 and DISCONNECT 514709 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKGE_All_21_P4_2_JOHNCO7 | Apply single-phase fault on and DISCONNECT 527964, near JOHNCO 7 for 16 cycles with stuck breaker at JOHNCO 7 (514809) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKGE_All_22_P4_2_GRACMNT7 | Apply single-phase fault on and DISCONNECT 527964, near GRACMNT7 for 16 cycles with stuck breaker at GRACMNT7 (515800) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKGE_All_23_P4_2_OPENSKY7 | Apply single-phase fault on and DISCONNECT 527964, near OPENSKY7 for 16 cycles with stuck breaker at OPENSKY7 (515621) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKGE_All_24_P4_2_PECANCK7 | Apply single-phase fault on and DISCONNECT 527964, near PECANCK7 for 16 cycles with stuck breaker at PECANCK7 (515235) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKGE_All_25_P4_2_RANCHRD7 | Apply single-phase fault on and DISCONNECT 527964, near RANCHRD7 for 16 cycles with stuck breaker at RANCHRD7 (515576) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKGE_All_26_P4_2_REDBUD7 | Apply single-phase fault on and DISCONNECT 527964, near REDBUD 7 for 16 cycles with stuck breaker at REDBUD 7 (514909) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKGE_All_27_P4_2_FTSMITH8 | Apply single-phase fault on and DISCONNECT 527964, near FTSMITH8 for 16 cycles with stuck breaker at FTSMITH8 (515305) 500 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for 2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKGE_All_28_P4_3_SEMINOL7 | Apply single-phase fault on and DISCONNECT 527964, near SEMINOL7 for 16 cycles with stuck breaker at SEMINOL7 (515045) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKGE_All_29_P4_3_SOONER7 | Apply single-phase fault on and DISCONNECT 527964, near SOONER 7 for 16 cycles with stuck breaker at SOONER 7 (514803) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKGE_All_30_P4_2_NORTWST7 | Apply single-phase fault on and DISCONNECT 527964, near NORTWST7 for 16 cycles with stuck breaker at NORTWST7 (514880) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKGE_All_31_P4_2_BORDER7 | Apply single-phase fault on and DISCONNECT 527964, near BORDER 7 for 16 cycles with stuck breaker at BORDER 7 (515458) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_OKGE_All_35_P4_6_SO4TH4 | Apply single-phase fault on LINE 514731 TO 514790 CKT 1 and LINE 514711 TO 514731 CKT 1, near SO4TH 4 for 6 cycles with stuck breaker at SO4TH 4 (514731) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514709 TO 514731 CKT 1 and LINE 514731 TO 514815 CKT 1 and DISCONNECT 515758 and LOAD 1 514731 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SPA_All_10_P4_2_BullShoals | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SPA_All_11_P4_2_BullShoals | Apply single-phase fault on LINE 338104 TO 338121 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338121 and drop LOAD 1 338122 and drop LOAD 1 338124 and DISCONNECT 338121 and DISCONNECT 338122 and DISCONNECT 338123 and DISCONNECT 338124 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SPA_All_12_P4_2_BullShoals | Apply single-phase fault on LINE 300095 TO 301057 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and trip DISCONNECT 505462 and trip DISCONNECT 505464 and trip DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SPA_All_13_P4_2_TableRock | Apply single-phase fault on LINE 505461 TO 338110 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SPA_All_14_P4_2_TableRock | Apply single-phase fault on LINE 300130 TO 300727 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SPA_All_15_P4_2_TableRock | Apply single-phase fault on LINE 338099 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SPA_All_16_P4_2_TableRock | Apply single-phase fault on LINE 505496 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SPA_All_17_P4_2_TableRock | Apply single-phase fault on LINE 547497 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SPA_All_18_P4_2_TableRock | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and trip LINE 505474 TO 300735 CKT 1 and DISCONNECT 505473 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SPA_All_19_P4_2_Norfork | Apply single-phase fault on LINE 505460 TO 300081 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SPA_All_20_P4_2_Norfork | Apply single-phase fault on LINE 505461 TO 504440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SPA_All_21_P4_2_Norfork | Apply single-phase fault on LINE 301549 TO 505448 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SPA_All_22_P4_2_Norfork | Apply single-phase fault on LINE 338132 TO 338129 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338130 and drop LOAD 1 338131 and DISCONNECT 338130 and DISCONNECT 338131 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SPA_All_23_P4_2_Norfork | Apply single-phase fault on LINE 505442 TO 505440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338220 and drop LOAD A1 504080 and DISCONNECT 338220 and DISCONNECT 504080 and DISCONNECT 504081 and DISCONNECT 504082 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SPA_All_24_P4_2_Norfork | Apply single-phase fault on LINE 301121 TO 505458 CKT 1, near NORFORK2 for 5 cycles with stuck breaker at NORFORK2 (505450) 69 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505450 and drop LOAD A1 504448 and drop LOAD 1 505458 and DISCONNECT 504448 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505458 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SPA_All_7_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505468 and DISCONNECT 505470 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SPA_All_8_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505468 and DISCONNECT 505470 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_SPA_All_9_P4_2_BullShoalsWest | Apply single-phase fault on LINE 338110 TO 505461 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and DISCONNECT 505468 and DISCONNECT 505470 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_50_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520422 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_51_P4_2_ANADARK4 | Apply single-phase fault on LINE 521059 TO 520501 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 520814 CKT 1 and LINE 520812 TO 520814 CKT 1 and LINE 520814 TO 520923 CKT 1 and trip GENERATOR 1 520812 and drop LOAD F1 520812 and drop LOAD V1 520812 and DISCONNECT 520812 and drop LOAD 1 520496 and drop LOAD 1 520501 and drop LOAD 1 521031 and DISCONNECT 520496 and DISCONNECT 520501 and DISCONNECT 521031 and DISCONNECT 521072 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_52_P4_2_ANADARK4 | Apply single-phase fault on LINE 521129 TO 521024 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 511477 TO 520814 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_53_P4_2_CANADNS4 | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near CANADNS4 for 6 cycles with stuck breaker at CANADNS4 (520842) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 514947 TO 520842 CKT 1 and LINE 520842 TO 514947 CKT 1 and drop LOAD 1 520924 and DISCONNECT 520924 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_54_P4_2_FRNKLNS4 | Apply single-phase fault on LINE 520842 TO 514947 CKT 1, near FRNKLNS4 for 6 cycles with stuck breaker at FRNKLNS4 (520917) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 514946 and LINE 520917 TO 514946 CKT 1 and drop LOAD 1 520400 and drop LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_55_P4_2_FTSUPLY4 | Apply single-phase fault on LINE 520922 TO 520920 CKT 1 and trip GENERATOR 1 521145 and DISCONNECT 520922 and DISCONNECT 521141 and DISCONNECT 521144 and DISCONNECT 521145 and DISCONNECT 521151, near FTSUPLY4 for 6 cycles with stuck breaker at FTSUPLY4 (520920) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and LINE 520920 TO 520957 CKT 1 and drop LOAD 1 520957 and DISCONNECT 520957 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_56_P4_2_HUGOPP4 | Apply single-phase fault on LINE 510887 TO 520448 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 505602 TO 521044 CKT 1 and drop LOAD 1 515370 and drop LOAD 1 515568 and drop LOAD 1 520463 and drop LOAD 1 520483 and drop LOAD 1 520497 and drop LOAD 1 520918 and drop LOAD 1 521077 and drop LOAD 1 521115 and DISCONNECT 515370 and DISCONNECT 515568 and DISCONNECT 520463 and DISCONNECT 520483 and DISCONNECT 520497 and DISCONNECT 520826 and DISCONNECT 520884 and DISCONNECT 520918 and DISCONNECT 521049 and DISCONNECT 521077 and DISCONNECT 521098 and DISCONNECT 521115 and drop LOAD 1 520411 and drop LOAD 1 520874 and drop LOAD 1 520968 and drop LOAD 1 521036 and DISCONNECT 520411 and DISCONNECT 520874 and DISCONNECT 520968 and DISCONNECT 521036 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-023 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-023 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_57_P4_2_HUGOPP4 | Apply single-phase fault on LINE 521194 TO 521195 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 520948 TO 521079 CKT 1 and trip GENERATOR 1 520947 and drop LOAD F1 520947 and drop LOAD V1 520947 and DISCONNECT 520947 and drop LOAD 1 520419 and drop LOAD 1 520466 and drop LOAD 1 520834 and drop LOAD 1 520946 and drop LOAD 1 521079 and DISCONNECT 520419 and DISCONNECT 520466 and DISCONNECT 520834 and DISCONNECT 520946 and DISCONNECT 520953 and DISCONNECT 521079 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_58_P4_2_MARIETTAS4 | Apply single-phase fault on LINE 515150 TO 514808 CKT 1, near MARIETA4 for 6 cycles with stuck breaker at MARIETA4 (520988) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520988 TO 515160 CKT 1 and LINE 520981 TO 520864 CKT 1 and drop LOAD 1 520455 and drop LOAD 1 520487 and drop LOAD 1 520488 and drop LOAD 1 520511 and drop LOAD 1 520901 and drop LOAD 1 521038 and drop LOAD 1 521061 and drop LOAD 1 521066 and DISCONNECT 520455 and DISCONNECT 520467 and DISCONNECT 520487 and DISCONNECT 520488 and DISCONNECT 520511 and DISCONNECT 520901 and DISCONNECT 520939 and DISCONNECT 520972 and DISCONNECT 521038 and DISCONNECT 521061 and DISCONNECT 521066 and DISCONNECT 521067 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_59_P4_2_NOELSW4 | Apply single-phase fault on LINE 521200 TO 520431 CKT 1, near NOELSW 4 for 6 cycles with stuck breaker at NOELSW 4 (520430) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520436 TO 515853 CKT 1 and LINE 520430 TO 520437 CKT 1 and drop LOAD 1 520431 and drop LOAD 1 520437 and drop LOAD 2 520437 and DISCONNECT 520431 and DISCONNECT 520437 and drop LOAD 1 520436 and drop LOAD 1 520601 and DISCONNECT 520436 and DISCONNECT 520601 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_60_P4_2_OKEENE4 | Apply single-phase fault on LINE 520882 TO 521016 CKT 1, near OKEENE 4 for 6 cycles with stuck breaker at OKEENE 4 (521016) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and drop LOAD 1 520425 and drop LOAD 1 520507 and DISCONNECT 520425 and DISCONNECT 520848 and DISCONNECT 520507 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_61_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 520510 CKT 1 and LINE 511449 TO 511483 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_62_P4_2_PHAROAH4 | Apply single-phase fault on LINE 300686 TO 300137 CKT 1, near PHAROAH4 for 6 cycles with stuck breaker at PHAROAH4 (521026) 138 kV Bus. Clear Fault after 9 cycles and trip DISCONNECT 301553 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_63_P4_2_TWNLKSW4 | Apply single-phase fault on LINE 520882 TO 520535 CKT 1, near TWNLKSW4 for 6 cycles with stuck breaker at TWNLKSW4 (521073) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520533 TO 520865 CKT 1 and LINE 521073 TO 520540 CKT Z1 and drop LOAD 1 520879 and drop LOAD 1 520540 and DISCONNECT 520879 and DISCONNECT 520540 and drop LOAD 1 521037 and drop LOAD 1 515930 and drop LOAD 1 520546 and drop LOAD 1 520479 and DISCONNECT 521037 and DISCONNECT 520474 and DISCONNECT 515930 and DISCONNECT 520545 and DISCONNECT 520546 and DISCONNECT 520847 and DISCONNECT 520479 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_64_P4_2_WAKTASW4 | Apply single-phase fault on LINE 515544 TO 515546 CKT 1, near WAKTASW4 for 6 cycles with stuck breaker at WAKTASW4 (520434) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 520434 and drop LOAD 1 520409 and drop LOAD 1A 520409 and DISCONNECT 520409 and DISCONNECT 520435 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_65_P4_2_WASHITA4 | Apply single-phase fault on LINE 511485 TO 520856 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 1 and LINE 521089 TO 521017 CKT 1 and drop LOAD 1 520468 and drop LOAD 1 520503 and drop LOAD 1 520856 and drop LOAD 1 520950 and drop LOAD 1 521010 and drop LOAD 2 521010 and drop LOAD 1 521017 and drop LOAD 1 521050 and drop LOAD 1 521092 and DISCONNECT 520468 and DISCONNECT 520503 and DISCONNECT 520827 and DISCONNECT 520856 and DISCONNECT 520950 and DISCONNECT 521010 and DISCONNECT 521017 and DISCONNECT 521050 and DISCONNECT 521092 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_66_P4_2_WASHITA4 | Apply single-phase fault on LINE 515802 TO 521089 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 2 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_75_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 and LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520923 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_WFEC_All_76_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 511449 TO 511502 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | 21STTAP4_508911 | a. Apply single-phase fault on a.1. 21STTAP4 138.0 KV 509828 TO 509811 CKT 1 b. with stuck breaker near 21STTAP4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. 21STTAP4 138.0 KV 509828 TO MINGO-N4 138.0 KV 509760 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | 36MER_4_515338 | a. Apply single-phase fault on a.1. 36&MER 4 138.0 KV 514888 TO HOBBYLO4 138.0 KV 515338 CKT 1 b. with stuck breaker near 36&MER 4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. 36&MER 4 138.0 KV 514888 TO SW 5TH 4 138.0 KV 514920 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | 52DELTP4_509811 | a. Apply single-phase fault on a.1. 52DELTP4 138.0 KV 509776 TO 36LEWIS4 138.0 KV 509800 CKT 1 a.2. LOAD 1 509800 a.3. 36LEWIS4 138.0 KV 509800 TO T.P.S.-4 138.0 KV 509788 CKT 1 b. with stuck breaker near 52DELTP4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. 52DELTP4 138.0 KV 509776 TO T.S.E.-4 138.0 KV 509811 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | 52DELWT4_509788 | a. Apply single-phase fault on a.1. 52DELWT4 138.0 KV 509814 TO T.P.S.-4 138.0 KV 509788 CKT 1 b. with stuck breaker near 52DELWT4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. R.S.S.-4 138.0 KV 509783 TO 52DELWT4 138.0 KV 509814 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | 7SAREPTA_337562 | a. Apply single-phase fault on a.1. 7SAREPTA% 345.0 KV 337376 TO 7EL DORADO 345.0 KV 337562 CKT 1 b. with stuck breaker near 7SAREPTA%345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. 7SAREPTA% 345.0 KV 337376 TO LONGWD 7 345.0 KV 508809 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are subm
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | ARCADIA4_514833 | a. Apply single-phase fault on a.1. DANFRTH4 138.0 KV 514833 TO BURGETT4 138.0 KV 514510 CKT 1 a.2. LOAD 1 514510 a.3. BURGETT4 138.0 KV 514510 TO RNDBARN4 138.0 KV 515461 CKT 1 a.4. LOAD 1 515461 a.5. RNDBARN4 138.0 KV 515461 TO ARCADIA4 138.0 KV 514907 CKT 1 b. with stuck breaker near ARCADIA4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. ARCADIA4 138.0 KV 514907 TO JNSKAMO4 138.0 KV 514906 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | ARCADIA7_514880 | a. Apply single-phase fault on a.1. ARCADIA7 345.0 KV 514908 TO NORTWST7 345.0 KV 514880 CKT 1 b. with stuck breaker near ARCADIA7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. ARCADIA7 345.0 KV 514908 TO REDBUD 7 345.0 KV 514909 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | BARNES_4_514994.0 | a. Apply single-phase fault on a.1. BARNES 4 138.0 KV 515003 TO TINKER54 138.0 KV 514994 CKT 1 b. with stuck breaker near BARNES 4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. BARNES 4 138.0 KV 515003 TO DRAPER 4 138.0 KV 514933 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | BECKHAM7_511553 | a. Apply single-phase fault on a.1. BECKHAM7 345.0 KV 516059 TO CHISHOLM7 345.0 KV 511553 CKT 1 b. with stuck breaker near BECKHAM7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. BECKHAM7 345.0 KV 516059 TO BORDER 7 345.0 KV 515458 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | CATOOSA4_509752 | a. Apply single-phase fault on a.1. CATOOSA4 138.0 KV 509790 TO INOLATP4 138.0 KV 509752 CKT 1 b. with stuck breaker near CATOOSA4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. CATOOSA4 138.0 KV 509790 TO LLANETP4 138.0 KV 509804 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | CIMARON4_514853 | a. Apply single-phase fault on a.1. CIMARON4 138.0 KV 514898 TO HAYMAKR4 138.0 KV 514863 CKT 1 a.2. LOAD 1 514863 a.3. HAYMAKR4 138.0 KV 514863 TO DVISION4 138.0 KV 514853 CKT 1 b. with stuck breaker near CIMARON4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. CIMARON4 138.0 KV 514898 TO CZECHAL4 138.0 KV 514894 CKT 1 c.2. LOAD 1 514894 c.3. CZECHAL4 138.0 KV 514894 TO XEROX 4 138.0 KV 514893 CKT 1 c.4. LOAD 1 514893 c.5. XEROX 4 138.0 KV 514893 TO MORGAN 4 138.0 KV 514896 CKT 1 c.6. LOAD 1 514896 c.7. MORGAN 4 138.0 KV 514896 TO MUSTANG4 138.0 KV 514861 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | CLASSEN4_514920.0 | a. Apply single-phase fault on a.1. CLASSEN4 138.0 KV 514922 TO SW 5TH 4 138.0 KV 514920 CKT 1 b. with stuck breaker near CLASSEN4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. CLASSEN4 138.0 KV 514922 TO CROSTWN4 138.0 KV 515851 CKT 1 c.2. LOAD 1 515851 c.3. CROSTWN4 138.0 KV 515851 TO LIGHTCK4 138.0 KV 514923 CKT 1 c.4. LOAD 1 514923 c.5. LIGHTCK4 138.0 KV 514923 TO TROSPER4 138.0 KV 514963 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | DOUGLTP4_514861 | a. Apply single-phase fault on a.1. MUSTANG4 138.0 KV 514861 TO COUNCIL4 138.0 KV 514865 CKT 1 a.2. LOAD 1 514865 a.3. COUNCIL4 138.0 KV 514865 TO WESTOAK4 138.0 KV 514866 CKT 1 a.4. LOAD 1 514866 a.5. MERIDAN4 138.0 KV 514867 TO WESTOAK4 138.0 KV 514866 CKT 1 a.6. LOAD 1 514866 a.7. MERIDAN4 138.0 KV 514867 TO DOUGLTP4 138.0 KV 514868 CKT 1 b. with stuck breaker near DOUGLTP4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. DOUGLTP4 138.0 KV 514868 TO WESTERN4 138.0 KV 514869 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG, GEN-2018-029 trips on frequency protection settings | Disabling frequency protection settings for BCV WTG, GEN-2018-029 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | DOVERSW4_520405 | a. Apply single-phase fault on a.1. DOVERSW4 138.0 KV 520882 TO NKNGFSH4 138.0 KV 520603 CKT 1 a.2. LOAD 1A 520603 a.3. LOAD 1B 520603 a.4. NKNGFSH4 138.0 KV 520603 TO KGFSJCT4 138.0 KV 520405 CKT 1 b. with stuck breaker near DOVERSW4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. DOVERSW4 138.0 KV 520882 TO DOVER 4 138.0 KV 520879 CKT 1 c.2. LOAD 1 520879 c.3. DOVER 4 138.0 KV 520879 TO TWNLAKE4 138.0 KV 520540 CKT 1 c.4. LOAD 1 520540 c.5. TWNLAKE4 138.0 KV 520540 TO TWNLKSW4 138.0 KV 521073 CKT Z1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | DVISION4_514848 | a. Apply single-phase fault on a.1. DVISION4 138.0 KV 514853 TO LAKESID4 138.0 KV 514849 CKT 1 a.2. LOAD 1 514849 a.3. LAKESID4 138.0 KV 514849 TO HEFNER 4 138.0 KV 514848 CKT 1 b. with stuck breaker near DVISION4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. CIMARON4 138.0 KV 514898 TO HAYMAKR4 138.0 KV 514863 CKT 1 c.2. LOAD 1 514863 c.3. HAYMAKR4 138.0 KV 514863 TO DVISION4 138.0 KV 514853 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FIREWHL_TAP_515422 | a. Apply single-phase fault on a.1. FIREWHL-TAP 345.0 KV 588839 TO C-RIVER7 345.0 KV 515422 CKT 1 b. with stuck breaker near FIREWHL-TAP345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. FIREWHL-TAP 345.0 KV 588839 TO MUSKOGE7 345.0 KV 515224 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | GRACMNT7_514801 | a. Apply single-phase fault on a.1. GRACMNT7 345.0 KV 515800 TO MINCO 7 345.0 KV 514801 CKT 1 b. with stuck breaker near GRACMNT7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. GRACMNT7 345.0 KV 515800 TO G16-091-TAP 345.0 KV 587744 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | HENESEY4_520882.0 | a. Apply single-phase fault on a.1. HENESEY4 138.0 KV 514774 TO DOVERSW4 138.0 KV 520882 CKT 1 b. with stuck breaker near HENESEY4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. HENESEY4 138.0 KV 514774 TO WAUKOMI4 138.0 KV 514710 CKT 1 c.2. LOAD 1 514710 c.3. HENESEY4 138.0 KV 514774 TO WAUKOMI4 138.0 KV 514710 CKT 1 c.4. LOAD 1 514710 c.5. WAUKOMI4 138.0 KV 514710 TO WAUKOTP4 138.0 KV 514711 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | HSL_4_515046 | a. Apply single-phase fault on a.1. HSL 4 138.0 KV 514941 TO HAMMTAP4 138.0 KV 515046 CKT 1 b. with stuck breaker near HSL 4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. HSL 4 138.0 KV 514941 TO JNSKAMO4 138.0 KV 514906 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | JNSKAMO4_514907 | a. Apply single-phase fault on a.1. JNSKAMO4 138.0 KV 514906 TO ARCADIA4 138.0 KV 514907 CKT 1 b. with stuck breaker near JNSKAMO4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. JNSKAMO4 138.0 KV 514906 TO 4MEMORALT 138.0 KV 300136 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-029, GEN-2017-154 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-029, GEN-2017-154 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | JONESSB4_514835 | a. Apply single-phase fault on a.1. MEMRIAL4 138.0 KV 514835 TO BRYANT 4 138.0 KV 514839 CKT 1 a.2. LOAD 1 514839 a.3. BRYANT 4 138.0 KV 514839 TO ACORN 4 138.0 KV 515459 CKT 1 a.4. LOAD 1 515459 a.5. ACORN 4 138.0 KV 515459 TO JONESSB4 138.0 KV 515480 CKT 1 b. with stuck breaker near JONESSB4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. JONESSB4 138.0 KV 515480 TO CHTWOOD4 138.0 KV 514842 CKT 1 c.2. LOAD 1 514842 c.3. CHTWOOD4 138.0 KV 514842 TO LGARBER4 138.0 KV 515465 CKT 1 c.4. LOAD 1 515465 c.5. LGARBER4 138.0 KV 515465 TO ARCADIA4 138.0 KV 514907 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-154 trips on voltage protection settings | Disabling frequency protection settings for GEN-2017-154 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | KENSH_E_TP4_509829 | a. Apply single-phase fault on a.1. KENSH-E-TP4 138.0 KV 509830 TO FULTONW4 138.0 KV 509829 CKT 1 b. with stuck breaker near KENSH-E-TP4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. KENSH-E-TP4 138.0 KV 509830 TO T.S.E.-4 138.0 KV 509811 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | LLANETP4_509786 | a. Apply single-phase fault on a.1. LLANETP4 138.0 KV 509804 TO BA.N-ST4 138.0 KV 509786 CKT 1 b. with stuck breaker near LLANETP4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. LLANETP4 138.0 KV 509804 TO CATOOSA4 138.0 KV 509790 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | LONGWD_7_508841 | a. Apply single-phase fault on a.1. LONGWD 7 345.0 KV 508809 TO WILKES 7 345.0 KV 508841 CKT 1 b. with stuck breaker near LONGWD 7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. LONGWD 7 345.0 KV 508809 TO SW SHV 7 345.0 KV 507760 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are subm
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | MEMRIAL4_514837 | a. Apply single-phase fault on a.1. MEMRIAL4 138.0 KV 514835 TO TENESTP4 138.0 KV 514837 CKT 1 b. with stuck breaker near MEMRIAL4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. MEMRIAL4 138.0 KV 514835 TO BRYANT 4 138.0 KV 514839 CKT 1 c.2. LOAD 1 514839 c.3. BRYANT 4 138.0 KV 514839 TO ACORN 4 138.0 KV 515459 CKT 1 c.4. LOAD 1 515459 c.5. ACORN 4 138.0 KV 515459 TO JONESSB4 138.0 KV 515480 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | MINCO_7_514901 | a. Apply single-phase fault on a.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 b. with stuck breaker near MINCO 7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. MINCO 7 345.0 KV 514801 TO NORMHLL7 345.0 KV 516096 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | MUSKOGE7_515302 | a. Apply single-phase fault on a.1. MUSKOGE7 345.0 KV 515224 TO CLARKSV7 345.0 KV 509745 CKT 1 b. with stuck breaker near MUSKOGE7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. MUSKOGE7 345.0 KV 515224 TO FTSMITH7 345.0 KV 515302 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | MUSTANG4_514920 | a. Apply single-phase fault on a.1. MUSTANG4 138.0 KV 514861 TO SW 5TH 4 138.0 KV 514920 CKT 1 b. with stuck breaker near MUSTANG4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. MUSTANG4 138.0 KV 514861 TO COUNCIL4 138.0 KV 514865 CKT 1 c.2. LOAD 1 514865 c.3. COUNCIL4 138.0 KV 514865 TO WESTOAK4 138.0 KV 514866 CKT 1 c.4. LOAD 1 514866 c.5. MERIDAN4 138.0 KV 514867 TO WESTOAK4 138.0 KV 514866 CKT 1 c.6. LOAD 1 514866 c.7. MERIDAN4 138.0 KV 514867 TO DOUGLTP4 138.0 KV 514868 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | NES4_510385 | a. Apply single-phase fault on a.1. N.E.S.-4 138.0 KV 510396 TO RICE CK4 138.0 KV 510385 CKT 1 a.2. LOAD M1 510385 a.3. RICE CK4 138.0 KV 510385 TO BV-SE--4 138.0 KV 510391 CKT 1 b. with stuck breaker near N.E.S.-4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. N.E.S.-4 138.0 KV 510396 TO HAWTHRN4 138.0 KV 510413 CKT 1 c.2. LOAD 1 510413 c.3. HAWTHRN4 138.0 KV 510413 TO CHELSA4 138.0 KV 510410 CKT 1 c.4. LOAD 1 510410 c.5. CHELSA4 138.0 KV 510410 TO ALWUETP4 138.0 KV 510429 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | NNBOSTN4_762431.0 | a. Apply single-phase fault on a.1. NNBOSTN4 138.0 KV 508069 TO G18-003-TAP 138.0 KV 762431 CKT 1 b. with stuck breaker near NNBOSTN4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. NNBOSTN4 138.0 KV 508069 TO 508104 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | NWTXARK4_508049 | a. Apply single-phase fault on a.1. NWTXARK4 138.0 KV 508071 TO NASH 4 138.0 KV 508049 CKT 1 b. with stuck breaker near NWTXARK4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. NWT-BNT4 138.0 KV 508070 TO NWTXARK4 138.0 KV 508071 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | NWT_BNT4_508071 | a. Apply single-phase fault on a.1. NWT-BNT4 138.0 KV 508070 TO NWTXARK4 138.0 KV 508071 CKT 1 b. with stuck breaker near NWT-BNT4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. NWT-BNT4 138.0 KV 508070 TO BANN 4 138.0 KV 508054 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | OKEENE_4_520536.0 | a. Apply single-phase fault on a.1. OKEENE 4 138.0 KV 521016 TO WATNGSW4 138.0 KV 520536 CKT 1 b. with stuck breaker near OKEENE 4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. OKEENE 4 138.0 KV 521016 TO DOVERSW4 138.0 KV 520882 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | PATTERS4_504124.0 | a. Apply single-phase fault on a.1. PATTERS4 138.0 KV 507431 TO ASHDWN_W 4 138.0 KV 504124 CKT 1 a.2. LOAD A1 504124 a.3. ASHDWN_W 4 138.0 KV 504124 TO CRAIGJT4 138.0 KV 510890 CKT 1 b. with stuck breaker near PATTERS4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. PATTERS4 138.0 KV 507431 TO SNASHVL4 138.0 KV 507434 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | PECANCK5_515230 | a. Apply single-phase fault on a.1. PECANCK5 161.0 KV 515234 TO AGENCY 5 161.0 KV 515230 CKT 1 b. with stuck breaker near PECANCK5161 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. PECANCK5 161.0 KV 515234 TO 5TRIBES5 161.0 KV 515228 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | PECANCK7_509782 | a. Apply single-phase fault on a.1. PECANCK7 345.0 KV 515235 TO R.S.S.-7 345.0 KV 509782 CKT 1 b. with stuck breaker near PECANCK7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. PECANCK7 345.0 KV 515235 TO MUSKOGE7 345.0 KV 515224 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | RENO_4_514941 | a. Apply single-phase fault on a.1. RENO 4 138.0 KV 514973 TO DUNJEE 4 138.0 KV 514884 CKT 1 a.2. LOAD 1 514884 a.3. DUNJEE 4 138.0 KV 514884 TO HSL 4 138.0 KV 514941 CKT 1 b. with stuck breaker near RENO 4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. RENO 4 138.0 KV 514973 TO NE10TH 4 138.0 KV 514964 CKT 1 c.2. LOAD 1 514964 c.3. NE10TH 4 138.0 KV 514964 TO MIDWAY 4 138.0 KV 514966 CKT 1 c.4. LOAD 1 514966 c.5. MIDWAY 4 138.0 KV 514966 TO HSL 4 138.0 KV 514941 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-154, GEN-2018-029 trips on voltage protection settings | Disabling frequency protection settings for GEN-2017-154, GEN-2018-029 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | SAPLPRD4_509896 | a. Apply single-phase fault on a.1. SAPLPRD4 138.0 KV 509871 TO DENV_WTAP4 138.0 KV 509896 CKT 1 b. with stuck breaker near SAPLPRD4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. SAPLPRD4 138.0 KV 509871 TO OAKSWTP4 138.0 KV 509848 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | SE15TH_4_514941 | a. Apply single-phase fault on a.1. SE15TH 4 138.0 KV 514993 TO HSL 4 138.0 KV 514941 CKT 1 b. with stuck breaker near SE15TH 4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. SE15TH 4 138.0 KV 514993 TO GLENDAL4 138.0 KV 514986 CKT 1 c.2. LOAD 1 514986 c.3. GLENDAL4 138.0 KV 514986 TO TINKER74 138.0 KV 515959 CKT 1 c.4. LOAD 1 515959 c.5. TINKER74 138.0 KV 515959 TO TINKER64 138.0 KV 515806 CKT 1 c.6. LOAD 1 515806 c.7. TINKER64 138.0 KV 515806 TO TINKER54 138.0 KV 514994 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | SEMINOL7_510907 | a. Apply single-phase fault on a.1. SEMINOL7 345.0 KV 515045 TO PITTSB-7 345.0 KV 510907 CKT 1 b. with stuck breaker near SEMINOL7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. SEMINOL7 345.0 KV 515045 TO ARCADIA7 345.0 KV 514908 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | SKYLINE4_514851 | a. Apply single-phase fault on a.1. SKYLINE4 138.0 KV 514850 TO QUAILCK4 138.0 KV 514851 CKT 1 b. with stuck breaker near SKYLINE4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. SKYLINE4 138.0 KV 514850 TO MEMRIAL4 138.0 KV 514835 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | SUGARHL4_507454 | a. Apply single-phase fault on a.1. SUGARHL4 138.0 KV 508080 TO TURK 4 138.0 KV 507454 CKT 1 b. with stuck breaker near SUGARHL4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. SUGARHL4 138.0 KV 508080 TO NWTXARK4 138.0 KV 508071 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | SUNNYSD7_511568 | a. Apply single-phase fault on a.1. SUNNYSD7 345.0 KV 515136 TO TERRYRD7 345.0 KV 511568 CKT 1 b. with stuck breaker near SUNNYSD7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. SUNNYSD7 345.0 KV 515136 TO G17-075-TAP 345.0 KV 560088 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | SW_5TH_4_514922 | a. Apply single-phase fault on a.1. SW 5TH 4 138.0 KV 514920 TO CLASSEN4 138.0 KV 514922 CKT 1 b. with stuck breaker near SW 5TH 4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. SW 5TH 4 138.0 KV 514920 TO MUSTANG4 138.0 KV 514861 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | SW_SHV_7_508809 | a. Apply single-phase fault on a.1. SW SHV 7 345.0 KV 507760 TO LONGWD 7 345.0 KV 508809 CKT 1 b. with stuck breaker near SW SHV 7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. SW SHV 7 345.0 KV 507760 TO DOLHILL7 345.0 KV 500250 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are subm
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | TNO4_509895 | a. Apply single-phase fault on a.1. T.NO.--4 138.0 KV 509817 TO T.NO.2-4 138.0 KV 509895 CKT 1 b. with stuck breaker near T.NO.--4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. T.NO.--4 138.0 KV 509817 TO CDC-WT 4 138.0 KV 509842 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | TPS4_509800 | a. Apply single-phase fault on a.1. T.P.S.-4 138.0 KV 509788 TO 36LEWIS4 138.0 KV 509800 CKT 1 a.2. LOAD 1 509800 a.3. 36LEWIS4 138.0 KV 509800 TO 52DELTP4 138.0 KV 509776 CKT 1 b. with stuck breaker near T.P.S.-4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. T.P.S.-4 138.0 KV 509788 TO 36&OLY-4 138.0 KV 509724 CKT 1 c.2. LOAD 1 509724 c.3. 36&OLY-4 138.0 KV 509724 TO CARSN-T4 138.0 KV 509739 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | TSE4_509828 | a. Apply single-phase fault on a.1. T.S.E.-4 138.0 KV 509811 TO 21STTAP4 138.0 KV 509828 CKT 1 b. with stuck breaker near T.S.E.-4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. T.S.E.-4 138.0 KV 509811 TO 52DELTP4 138.0 KV 509776 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | TWNLKSW4_520847 | a. Apply single-phase fault on a.1. TWNLKSW4 138.0 KV 521073 TO TWNLKJT4 138.0 KV 520847 CKT 1 b. with stuck breaker near TWNLKSW4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. DOVERSW4 138.0 KV 520882 TO DOVER 4 138.0 KV 520879 CKT 1 c.2. LOAD 1 520879 c.3. DOVER 4 138.0 KV 520879 TO TWNLAKE4 138.0 KV 520540 CKT 1 c.4. LOAD 1 520540 c.5. TWNLAKE4 138.0 KV 520540 TO TWNLKSW4 138.0 KV 521073 CKT Z1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | WESTERN4_514870 | a. Apply single-phase fault on a.1. WESTERN4 138.0 KV 514869 TO STNWAL 4 138.0 KV 514870 CKT 1 b. with stuck breaker near WESTERN4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. WESTERN4 138.0 KV 514869 TO DOUGLTP4 138.0 KV 514868 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | WILKES_7_508809 | a. Apply single-phase fault on a.1. WILKES 7 345.0 KV 508841 TO LONGWD 7 345.0 KV 508809 CKT 1 b. with stuck breaker near WILKES 7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. WILKES 7 345.0 KV 508841 TO WELSH 7 345.0 KV 508359 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are subm
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | WWRDEHV7_515852 | a. Apply single-phase fault on a.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 1 b. with stuck breaker near WWRDEHV7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | 21STTAP4_508911 | a. Apply single-phase fault on a.1. 21STTAP4 138.0 KV 509828 TO 509811 CKT 1 b. with stuck breaker near 21STTAP4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. 21STTAP4 138.0 KV 509828 TO MINGO-N4 138.0 KV 509760 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | 36MER_4_515338 | a. Apply single-phase fault on a.1. 36&MER 4 138.0 KV 514888 TO HOBBYLO4 138.0 KV 515338 CKT 1 b. with stuck breaker near 36&MER 4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. 36&MER 4 138.0 KV 514888 TO SW 5TH 4 138.0 KV 514920 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | 52DELTP4_509811 | a. Apply single-phase fault on a.1. 52DELTP4 138.0 KV 509776 TO 36LEWIS4 138.0 KV 509800 CKT 1 a.2. LOAD 1 509800 a.3. 36LEWIS4 138.0 KV 509800 TO T.P.S.-4 138.0 KV 509788 CKT 1 b. with stuck breaker near 52DELTP4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. 52DELTP4 138.0 KV 509776 TO T.S.E.-4 138.0 KV 509811 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | 52DELWT4_509788 | a. Apply single-phase fault on a.1. 52DELWT4 138.0 KV 509814 TO T.P.S.-4 138.0 KV 509788 CKT 1 b. with stuck breaker near 52DELWT4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. R.S.S.-4 138.0 KV 509783 TO 52DELWT4 138.0 KV 509814 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | 7SAREPTA_337562 | a. Apply single-phase fault on a.1. 7SAREPTA% 345.0 KV 337376 TO 7EL DORADO 345.0 KV 337562 CKT 1 b. with stuck breaker near 7SAREPTA%345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. 7SAREPTA% 345.0 KV 337376 TO LONGWD 7 345.0 KV 508809 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | ARCADIA4_514833 | a. Apply single-phase fault on a.1. DANFRTH4 138.0 KV 514833 TO BURGETT4 138.0 KV 514510 CKT 1 a.2. LOAD 1 514510 a.3. BURGETT4 138.0 KV 514510 TO RNDBARN4 138.0 KV 515461 CKT 1 a.4. LOAD 1 515461 a.5. RNDBARN4 138.0 KV 515461 TO ARCADIA4 138.0 KV 514907 CKT 1 b. with stuck breaker near ARCADIA4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. ARCADIA4 138.0 KV 514907 TO JNSKAMO4 138.0 KV 514906 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | ARCADIA7_514880 | a. Apply single-phase fault on a.1. ARCADIA7 345.0 KV 514908 TO NORTWST7 345.0 KV 514880 CKT 1 b. with stuck breaker near ARCADIA7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. ARCADIA7 345.0 KV 514908 TO REDBUD 7 345.0 KV 514909 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | BARNES_4_514994.0 | a. Apply single-phase fault on a.1. BARNES 4 138.0 KV 515003 TO TINKER54 138.0 KV 514994 CKT 1 b. with stuck breaker near BARNES 4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. BARNES 4 138.0 KV 515003 TO DRAPER 4 138.0 KV 514933 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | BECKHAM7_511553 | a. Apply single-phase fault on a.1. BECKHAM7 345.0 KV 516059 TO CHISHOLM7 345.0 KV 511553 CKT 1 b. with stuck breaker near BECKHAM7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. BECKHAM7 345.0 KV 516059 TO BORDER 7 345.0 KV 515458 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | CATOOSA4_509752 | a. Apply single-phase fault on a.1. CATOOSA4 138.0 KV 509790 TO INOLATP4 138.0 KV 509752 CKT 1 b. with stuck breaker near CATOOSA4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. CATOOSA4 138.0 KV 509790 TO LLANETP4 138.0 KV 509804 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | CIMARON4_514853 | a. Apply single-phase fault on a.1. CIMARON4 138.0 KV 514898 TO HAYMAKR4 138.0 KV 514863 CKT 1 a.2. LOAD 1 514863 a.3. HAYMAKR4 138.0 KV 514863 TO DVISION4 138.0 KV 514853 CKT 1 b. with stuck breaker near CIMARON4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. CIMARON4 138.0 KV 514898 TO CZECHAL4 138.0 KV 514894 CKT 1 c.2. LOAD 1 514894 c.3. CZECHAL4 138.0 KV 514894 TO XEROX 4 138.0 KV 514893 CKT 1 c.4. LOAD 1 514893 c.5. XEROX 4 138.0 KV 514893 TO MORGAN 4 138.0 KV 514896 CKT 1 c.6. LOAD 1 514896 c.7. MORGAN 4 138.0 KV 514896 TO MUSTANG4 138.0 KV 514861 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | CLASSEN4_514920.0 | a. Apply single-phase fault on a.1. CLASSEN4 138.0 KV 514922 TO SW 5TH 4 138.0 KV 514920 CKT 1 b. with stuck breaker near CLASSEN4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. CLASSEN4 138.0 KV 514922 TO CROSTWN4 138.0 KV 515851 CKT 1 c.2. LOAD 1 515851 c.3. CROSTWN4 138.0 KV 515851 TO LIGHTCK4 138.0 KV 514923 CKT 1 c.4. LOAD 1 514923 c.5. LIGHTCK4 138.0 KV 514923 TO TROSPER4 138.0 KV 514963 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | DOUGLTP4_514861 | a. Apply single-phase fault on a.1. MUSTANG4 138.0 KV 514861 TO COUNCIL4 138.0 KV 514865 CKT 1 a.2. LOAD 1 514865 a.3. COUNCIL4 138.0 KV 514865 TO WESTOAK4 138.0 KV 514866 CKT 1 a.4. LOAD 1 514866 a.5. MERIDAN4 138.0 KV 514867 TO WESTOAK4 138.0 KV 514866 CKT 1 a.6. LOAD 1 514866 a.7. MERIDAN4 138.0 KV 514867 TO DOUGLTP4 138.0 KV 514868 CKT 1 b. with stuck breaker near DOUGLTP4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. DOUGLTP4 138.0 KV 514868 TO WESTERN4 138.0 KV 514869 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | DOVERSW4_520405 | a. Apply single-phase fault on a.1. DOVERSW4 138.0 KV 520882 TO NKNGFSH4 138.0 KV 520603 CKT 1 a.2. LOAD 1A 520603 a.3. LOAD 1B 520603 a.4. NKNGFSH4 138.0 KV 520603 TO KGFSJCT4 138.0 KV 520405 CKT 1 b. with stuck breaker near DOVERSW4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. DOVERSW4 138.0 KV 520882 TO DOVER 4 138.0 KV 520879 CKT 1 c.2. LOAD 1 520879 c.3. DOVER 4 138.0 KV 520879 TO TWNLAKE4 138.0 KV 520540 CKT 1 c.4. LOAD 1 520540 c.5. TWNLAKE4 138.0 KV 520540 TO TWNLKSW4 138.0 KV 521073 CKT Z1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | DVISION4_514848 | a. Apply single-phase fault on a.1. DVISION4 138.0 KV 514853 TO LAKESID4 138.0 KV 514849 CKT 1 a.2. LOAD 1 514849 a.3. LAKESID4 138.0 KV 514849 TO HEFNER 4 138.0 KV 514848 CKT 1 b. with stuck breaker near DVISION4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. CIMARON4 138.0 KV 514898 TO HAYMAKR4 138.0 KV 514863 CKT 1 c.2. LOAD 1 514863 c.3. HAYMAKR4 138.0 KV 514863 TO DVISION4 138.0 KV 514853 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FIREWHL_TAP_515422 | a. Apply single-phase fault on a.1. FIREWHL-TAP 345.0 KV 588839 TO C-RIVER7 345.0 KV 515422 CKT 1 b. with stuck breaker near FIREWHL-TAP345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. FIREWHL-TAP 345.0 KV 588839 TO MUSKOGE7 345.0 KV 515224 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | GRACMNT7_514801 | a. Apply single-phase fault on a.1. GRACMNT7 345.0 KV 515800 TO MINCO 7 345.0 KV 514801 CKT 1 b. with stuck breaker near GRACMNT7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. GRACMNT7 345.0 KV 515800 TO G16-091-TAP 345.0 KV 587744 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | HENESEY4_520882.0 | a. Apply single-phase fault on a.1. HENESEY4 138.0 KV 514774 TO DOVERSW4 138.0 KV 520882 CKT 1 b. with stuck breaker near HENESEY4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. HENESEY4 138.0 KV 514774 TO WAUKOMI4 138.0 KV 514710 CKT 1 c.2. LOAD 1 514710 c.3. HENESEY4 138.0 KV 514774 TO WAUKOMI4 138.0 KV 514710 CKT 1 c.4. LOAD 1 514710 c.5. WAUKOMI4 138.0 KV 514710 TO WAUKOTP4 138.0 KV 514711 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | HSL_4_515046 | a. Apply single-phase fault on a.1. HSL 4 138.0 KV 514941 TO HAMMTAP4 138.0 KV 515046 CKT 1 b. with stuck breaker near HSL 4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. HSL 4 138.0 KV 514941 TO JNSKAMO4 138.0 KV 514906 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | JNSKAMO4_514907 | a. Apply single-phase fault on a.1. JNSKAMO4 138.0 KV 514906 TO ARCADIA4 138.0 KV 514907 CKT 1 b. with stuck breaker near JNSKAMO4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. JNSKAMO4 138.0 KV 514906 TO 4MEMORALT 138.0 KV 300136 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | JONESSB4_514835 | a. Apply single-phase fault on a.1. MEMRIAL4 138.0 KV 514835 TO BRYANT 4 138.0 KV 514839 CKT 1 a.2. LOAD 1 514839 a.3. BRYANT 4 138.0 KV 514839 TO ACORN 4 138.0 KV 515459 CKT 1 a.4. LOAD 1 515459 a.5. ACORN 4 138.0 KV 515459 TO JONESSB4 138.0 KV 515480 CKT 1 b. with stuck breaker near JONESSB4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. JONESSB4 138.0 KV 515480 TO CHTWOOD4 138.0 KV 514842 CKT 1 c.2. LOAD 1 514842 c.3. CHTWOOD4 138.0 KV 514842 TO LGARBER4 138.0 KV 515465 CKT 1 c.4. LOAD 1 515465 c.5. LGARBER4 138.0 KV 515465 TO ARCADIA4 138.0 KV 514907 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | KENSH_E_TP4_509829 | a. Apply single-phase fault on a.1. KENSH-E-TP4 138.0 KV 509830 TO FULTONW4 138.0 KV 509829 CKT 1 b. with stuck breaker near KENSH-E-TP4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. KENSH-E-TP4 138.0 KV 509830 TO T.S.E.-4 138.0 KV 509811 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | LLANETP4_509786 | a. Apply single-phase fault on a.1. LLANETP4 138.0 KV 509804 TO BA.N-ST4 138.0 KV 509786 CKT 1 b. with stuck breaker near LLANETP4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. LLANETP4 138.0 KV 509804 TO CATOOSA4 138.0 KV 509790 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | LONGWD_7_508841 | a. Apply single-phase fault on a.1. LONGWD 7 345.0 KV 508809 TO WILKES 7 345.0 KV 508841 CKT 1 b. with stuck breaker near LONGWD 7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. LONGWD 7 345.0 KV 508809 TO SW SHV 7 345.0 KV 507760 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | MEMRIAL4_514837 | a. Apply single-phase fault on a.1. MEMRIAL4 138.0 KV 514835 TO TENESTP4 138.0 KV 514837 CKT 1 b. with stuck breaker near MEMRIAL4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. MEMRIAL4 138.0 KV 514835 TO BRYANT 4 138.0 KV 514839 CKT 1 c.2. LOAD 1 514839 c.3. BRYANT 4 138.0 KV 514839 TO ACORN 4 138.0 KV 515459 CKT 1 c.4. LOAD 1 515459 c.5. ACORN 4 138.0 KV 515459 TO JONESSB4 138.0 KV 515480 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | MINCO_7_514901 | a. Apply single-phase fault on a.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 b. with stuck breaker near MINCO 7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. MINCO 7 345.0 KV 514801 TO NORMHLL7 345.0 KV 516096 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | MUSKOGE7_515302 | a. Apply single-phase fault on a.1. MUSKOGE7 345.0 KV 515224 TO CLARKSV7 345.0 KV 509745 CKT 1 b. with stuck breaker near MUSKOGE7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. MUSKOGE7 345.0 KV 515224 TO FTSMITH7 345.0 KV 515302 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | MUSTANG4_514920 | a. Apply single-phase fault on a.1. MUSTANG4 138.0 KV 514861 TO SW 5TH 4 138.0 KV 514920 CKT 1 b. with stuck breaker near MUSTANG4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. MUSTANG4 138.0 KV 514861 TO COUNCIL4 138.0 KV 514865 CKT 1 c.2. LOAD 1 514865 c.3. COUNCIL4 138.0 KV 514865 TO WESTOAK4 138.0 KV 514866 CKT 1 c.4. LOAD 1 514866 c.5. MERIDAN4 138.0 KV 514867 TO WESTOAK4 138.0 KV 514866 CKT 1 c.6. LOAD 1 514866 c.7. MERIDAN4 138.0 KV 514867 TO DOUGLTP4 138.0 KV 514868 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | NES4_510385 | a. Apply single-phase fault on a.1. N.E.S.-4 138.0 KV 510396 TO RICE CK4 138.0 KV 510385 CKT 1 a.2. LOAD M1 510385 a.3. RICE CK4 138.0 KV 510385 TO BV-SE--4 138.0 KV 510391 CKT 1 b. with stuck breaker near N.E.S.-4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. N.E.S.-4 138.0 KV 510396 TO HAWTHRN4 138.0 KV 510413 CKT 1 c.2. LOAD 1 510413 c.3. HAWTHRN4 138.0 KV 510413 TO CHELSA4 138.0 KV 510410 CKT 1 c.4. LOAD 1 510410 c.5. CHELSA4 138.0 KV 510410 TO ALWUETP4 138.0 KV 510429 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | NNBOSTN4_762431.0 | a. Apply single-phase fault on a.1. NNBOSTN4 138.0 KV 508069 TO G18-003-TAP 138.0 KV 762431 CKT 1 b. with stuck breaker near NNBOSTN4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. NNBOSTN4 138.0 KV 508069 TO 508104 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | NWTXARK4_508049 | a. Apply single-phase fault on a.1. NWTXARK4 138.0 KV 508071 TO NASH 4 138.0 KV 508049 CKT 1 b. with stuck breaker near NWTXARK4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. NWT-BNT4 138.0 KV 508070 TO NWTXARK4 138.0 KV 508071 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | NWT_BNT4_508071 | a. Apply single-phase fault on a.1. NWT-BNT4 138.0 KV 508070 TO NWTXARK4 138.0 KV 508071 CKT 1 b. with stuck breaker near NWT-BNT4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. NWT-BNT4 138.0 KV 508070 TO BANN 4 138.0 KV 508054 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-003 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-003 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | OKEENE_4_520536.0 | a. Apply single-phase fault on a.1. OKEENE 4 138.0 KV 521016 TO WATNGSW4 138.0 KV 520536 CKT 1 b. with stuck breaker near OKEENE 4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. OKEENE 4 138.0 KV 521016 TO DOVERSW4 138.0 KV 520882 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | PATTERS4_504124.0 | a. Apply single-phase fault on a.1. PATTERS4 138.0 KV 507431 TO ASHDWN_W 4 138.0 KV 504124 CKT 1 a.2. LOAD A1 504124 a.3. ASHDWN_W 4 138.0 KV 504124 TO CRAIGJT4 138.0 KV 510890 CKT 1 b. with stuck breaker near PATTERS4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. PATTERS4 138.0 KV 507431 TO SNASHVL4 138.0 KV 507434 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | PECANCK5_515230 | a. Apply single-phase fault on a.1. PECANCK5 161.0 KV 515234 TO AGENCY 5 161.0 KV 515230 CKT 1 b. with stuck breaker near PECANCK5161 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. PECANCK5 161.0 KV 515234 TO 5TRIBES5 161.0 KV 515228 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | PECANCK7_509782 | a. Apply single-phase fault on a.1. PECANCK7 345.0 KV 515235 TO R.S.S.-7 345.0 KV 509782 CKT 1 b. with stuck breaker near PECANCK7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. PECANCK7 345.0 KV 515235 TO MUSKOGE7 345.0 KV 515224 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | RENO_4_514941 | a. Apply single-phase fault on a.1. RENO 4 138.0 KV 514973 TO DUNJEE 4 138.0 KV 514884 CKT 1 a.2. LOAD 1 514884 a.3. DUNJEE 4 138.0 KV 514884 TO HSL 4 138.0 KV 514941 CKT 1 b. with stuck breaker near RENO 4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. RENO 4 138.0 KV 514973 TO NE10TH 4 138.0 KV 514964 CKT 1 c.2. LOAD 1 514964 c.3. NE10TH 4 138.0 KV 514964 TO MIDWAY 4 138.0 KV 514966 CKT 1 c.4. LOAD 1 514966 c.5. MIDWAY 4 138.0 KV 514966 TO HSL 4 138.0 KV 514941 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | SAPLPRD4_509896 | a. Apply single-phase fault on a.1. SAPLPRD4 138.0 KV 509871 TO DENV_WTAP4 138.0 KV 509896 CKT 1 b. with stuck breaker near SAPLPRD4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. SAPLPRD4 138.0 KV 509871 TO OAKSWTP4 138.0 KV 509848 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | SE15TH_4_514941 | a. Apply single-phase fault on a.1. SE15TH 4 138.0 KV 514993 TO HSL 4 138.0 KV 514941 CKT 1 b. with stuck breaker near SE15TH 4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. SE15TH 4 138.0 KV 514993 TO GLENDAL4 138.0 KV 514986 CKT 1 c.2. LOAD 1 514986 c.3. GLENDAL4 138.0 KV 514986 TO TINKER74 138.0 KV 515959 CKT 1 c.4. LOAD 1 515959 c.5. TINKER74 138.0 KV 515959 TO TINKER64 138.0 KV 515806 CKT 1 c.6. LOAD 1 515806 c.7. TINKER64 138.0 KV 515806 TO TINKER54 138.0 KV 514994 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | SEMINOL7_510907 | a. Apply single-phase fault on a.1. SEMINOL7 345.0 KV 515045 TO PITTSB-7 345.0 KV 510907 CKT 1 b. with stuck breaker near SEMINOL7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. SEMINOL7 345.0 KV 515045 TO ARCADIA7 345.0 KV 514908 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | SKYLINE4_514851 | a. Apply single-phase fault on a.1. SKYLINE4 138.0 KV 514850 TO QUAILCK4 138.0 KV 514851 CKT 1 b. with stuck breaker near SKYLINE4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. SKYLINE4 138.0 KV 514850 TO MEMRIAL4 138.0 KV 514835 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | SUGARHL4_507454 | a. Apply single-phase fault on a.1. SUGARHL4 138.0 KV 508080 TO TURK 4 138.0 KV 507454 CKT 1 b. with stuck breaker near SUGARHL4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. SUGARHL4 138.0 KV 508080 TO NWTXARK4 138.0 KV 508071 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | SUNNYSD7_511568 | a. Apply single-phase fault on a.1. SUNNYSD7 345.0 KV 515136 TO TERRYRD7 345.0 KV 511568 CKT 1 b. with stuck breaker near SUNNYSD7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. SUNNYSD7 345.0 KV 515136 TO G17-075-TAP 345.0 KV 560088 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | SW_5TH_4_514922 | a. Apply single-phase fault on a.1. SW 5TH 4 138.0 KV 514920 TO CLASSEN4 138.0 KV 514922 CKT 1 b. with stuck breaker near SW 5TH 4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. SW 5TH 4 138.0 KV 514920 TO MUSTANG4 138.0 KV 514861 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | SW_SHV_7_508809 | a. Apply single-phase fault on a.1. SW SHV 7 345.0 KV 507760 TO LONGWD 7 345.0 KV 508809 CKT 1 b. with stuck breaker near SW SHV 7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. SW SHV 7 345.0 KV 507760 TO DOLHILL7 345.0 KV 500250 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | TNO4_509895 | a. Apply single-phase fault on a.1. T.NO.--4 138.0 KV 509817 TO T.NO.2-4 138.0 KV 509895 CKT 1 b. with stuck breaker near T.NO.--4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. T.NO.--4 138.0 KV 509817 TO CDC-WT 4 138.0 KV 509842 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | TPS4_509800 | a. Apply single-phase fault on a.1. T.P.S.-4 138.0 KV 509788 TO 36LEWIS4 138.0 KV 509800 CKT 1 a.2. LOAD 1 509800 a.3. 36LEWIS4 138.0 KV 509800 TO 52DELTP4 138.0 KV 509776 CKT 1 b. with stuck breaker near T.P.S.-4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. T.P.S.-4 138.0 KV 509788 TO 36&OLY-4 138.0 KV 509724 CKT 1 c.2. LOAD 1 509724 c.3. 36&OLY-4 138.0 KV 509724 TO CARSN-T4 138.0 KV 509739 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for 2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | TSE4_509828 | a. Apply single-phase fault on a.1. T.S.E.-4 138.0 KV 509811 TO 21STTAP4 138.0 KV 509828 CKT 1 b. with stuck breaker near T.S.E.-4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. T.S.E.-4 138.0 KV 509811 TO 52DELTP4 138.0 KV 509776 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | TWNLKSW4_520847 | a. Apply single-phase fault on a.1. TWNLKSW4 138.0 KV 521073 TO TWNLKJT4 138.0 KV 520847 CKT 1 b. with stuck breaker near TWNLKSW4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. DOVERSW4 138.0 KV 520882 TO DOVER 4 138.0 KV 520879 CKT 1 c.2. LOAD 1 520879 c.3. DOVER 4 138.0 KV 520879 TO TWNLAKE4 138.0 KV 520540 CKT 1 c.4. LOAD 1 520540 c.5. TWNLAKE4 138.0 KV 520540 TO TWNLKSW4 138.0 KV 521073 CKT Z1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | WESTERN4_514870 | a. Apply single-phase fault on a.1. WESTERN4 138.0 KV 514869 TO STNWAL 4 138.0 KV 514870 CKT 1 b. with stuck breaker near WESTERN4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. WESTERN4 138.0 KV 514869 TO DOUGLTP4 138.0 KV 514868 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | WILKES_7_508809 | a. Apply single-phase fault on a.1. WILKES 7 345.0 KV 508841 TO LONGWD 7 345.0 KV 508809 CKT 1 b. with stuck breaker near WILKES 7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. WILKES 7 345.0 KV 508841 TO WELSH 7 345.0 KV 508359 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | WWRDEHV7_515852 | a. Apply single-phase fault on a.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 1 b. with stuck breaker near WWRDEHV7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_100_P5_Washita | Single phase fault with stuck relay near WASHITA4 (521089) 138 kV Bus a. Apply Fault at theWASHITA4 (521089) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 521089 TO 511477 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_101_P5_LES | Single phase fault with stuck relay near L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at theL.E.S.-4 (511467) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 511467 TO 511437 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_102_P5_LES | Single phase fault with stuck relay near L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at theL.E.S.-4 (511467) 138 kV Bus b. Clear fault after 72 cycles and trip the faulted elements: b.1. LINE 511467 TO 511494 CKT 1 b.2. LINE 511494 TO 511437 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2015-013 trips on voltage protection settings | Disabling voltage protection settings for GEN-2015-013 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_103_P5_LES | Single phase fault with stuck relay near L.E.S.-2 (511466) 69 kV Bus a. Apply Fault at theL.E.S.-2 (511466) 69 kV Bus b. Clear fault after 41 cycles and trip the faulted elements: b.1. LINE 511466 TO 511436 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCV WTG trips on voltage protection settings | Disabling voltage protection settings for BCV WTG prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_104_P5_SouthHudson | Single phase fault with stuck relay near S.HUD.-4 (509833) 138 kV Bus a. Apply Fault at theS.HUD.-4 (509833) 138 kV Bus b. Clear fault after 55 cycles and trip the faulted elements: b.1. LINE 509833 TO 509764 CKT 1 b.2. LINE 509764 TO 509809 CKT 1 b.3. LINE 509809 TO 509813 CKT 1 b.4. LINE 509813 TO 509853 CKT 1 b.5. LINE 509853 TO 509783 CKT 1 b.6. LOAD 1 509729 b.7. LOAD 1 509730 b.8. LOAD 1 509731 b.9. LOAD 1 509732 b.10. DISCONNECT 509729 b.11. DISCONNECT 509730 b.12. DISCONNECT 509731 b.13. DISCONNECT 509732 b.14. DISCONNECT 509764 b.15. DISCONNECT 509809 b.16. DISCONNECT 509813 b.17. DISCONNECT 509853 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_105_P5_96th&Yale | Single phase fault with stuck relay near 96YALE-4 (509847) 138 kV Bus a. Apply Fault at the96YALE-4 (509847) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509847 TO 509858 CKT 1 b.2. LINE 509858 TO 509849 CKT 1 b.3. LINE 509849 TO 509783 CKT 1 b.4. LOAD 1 509738 b.5. LOAD 1 509810 b.6. LOAD 1 509857 b.7. DISCONNECT 509738 b.8. DISCONNECT 509810 b.9. DISCONNECT 509849 b.10. DISCONNECT 509857 b.11. DISCONNECT 509858 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_106_P5_KimberlyClark.id | Single phase fault with stuck relay near KIMCLRK4 (509845) 138 kV Bus a. Apply Fault at theKIMCLRK4 (509845) 138 kV Bus b. Clear fault after 35 cycles and trip the faulted elements: b.1. LINE 509845 TO 509775 CKT 1 b.2. LOAD 1 509775 b.3. DISCONNECT 509775 b.4. LINE 509775 TO 509783 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_107_P5_OG&Ebee | Single phase fault with stuck relay near BEELINE4 (515247) 138 kV Bus a. Apply Fault at theBEELINE4 (515247) 138 kV Bus b. Clear fault after 26 cycles and trip the faulted elements: b.1. LINE 515247 TO 515473 CKT 1 b.2. LOAD 1 515248 b.3. DISCONNECT 515248 b.4. DISCONNECT 515473 b.5. LINE 515473 TO 509783 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_108_P5_SapulpaRoad | Single phase fault with stuck relay near SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at theSAPLPRD4 (509871) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509871 TO 509759 CKT 1 b.2. LINE 509759 TO 509753 CKT 1 b.3. LOAD 1 509753 b.4. LOAD 1 509759 b.5. DISCONNECT 509753 b.6. DISCONNECT 509759 b.7. LINE 509753 TO 509783 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_109_P5_WeleetkaSWPA | Single phase fault with stuck relay near WELEETK4 (505592) 138 kV Bus a. Apply Fault at theWELEETK4 (505592) 138 kV Bus b. Clear fault after 33 cycles and trip the faulted elements: b.1. LINE 505592 TO 510902 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_110_P5_Henryetta138kV | Single phase fault with stuck relay near HENRYET4 (510892) 138 kV Bus a. Apply Fault at theHENRYET4 (510892) 138 kV Bus b. Clear fault after 33 cycles and trip the faulted elements: b.1. LINE 510892 TO 510902 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_12_P5_Linwood | Single phase fault with stuck relay near LINWOOD4 (507738) 138 kV Bus a. Apply Fault at theLINWOOD4 (507738) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 507742 TO 507711 CKT 1 b.2. LINE 507771 TO 507755 CKT 1 b.3. LOAD 1 507738 b.4. LOAD 1 507742 b.5. LOAD 1 507748 b.6. DISCONNECT 507738 b.7. DISCONNECT 507742 b.8. DISCONNECT 507748 b.9. DISCONNECT 507771 b.10. LINE 507748 TO 507759 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_15_P5_ChambersSpring | Single phase fault with stuck relay near CHAMSPR5 (506944) 161 kV Bus a. Apply Fault at theCHAMSPR5 (506944) 161 kV Bus b. Clear fault after 25 cycles and trip the faulted elements: b.1. LINE 506944 TO 504202 CKT 1 b.2. LOAD A1 504202 b.3. DISCONNECT 504202 b.4. LINE 504202 TO 506934 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_16_P5_Siloam | Single phase fault with stuck relay near SILOAM 5 (506948) 161 kV Bus a. Apply Fault at theSILOAM 5 (506948) 161 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 506948 TO 506934 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_17_P5_Tontitown | Single phase fault with stuck relay near TONTITN5 (506957) 161 kV Bus a. Apply Fault at theTONTITN5 (506957) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506957 TO 506934 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-141 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-141 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_18_P5_Decatur | Single phase fault with stuck relay near DEC392 5 (547484) 161 kV Bus a. Apply Fault at theDEC392 5 (547484) 161 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 547484 TO 506934 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-141 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-141 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_19_P5_Dyess | Single phase fault with stuck relay near DYESS 5 (506927) 161 kV Bus a. Apply Fault at theDYESS 5 (506927) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506927 TO 506957 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_20_P5_Dyess | Single phase fault with stuck relay near DYESS 5 (506927) 161 kV Bus a. Apply Fault at theDYESS 5 (506927) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506927 TO 504010 CKT 1 b.2. LOAD A1 504010 b.3. DISCONNECT 504010 b.4. DISCONNECT 504011 b.5. DISCONNECT 504012 b.6. DISCONNECT 504013 b.7. DISCONNECT 504014 b.8. LINE 504010 TO 506957 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_21_P5_ChamberSprings | Single phase fault with stuck relay near CHAMSPR5 (506944) 161 kV Bus a. Apply Fault at theCHAMSPR5 (506944) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506944 TO 506957 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_22_P5_Lowell | Single phase fault with stuck relay near LOWELL 5 (506938) 161 kV Bus a. Apply Fault at theLOWELL 5 (506938) 161 kV Bus b. Clear fault after 21 cycles and trip the faulted elements: b.1. LINE 506938 TO 506991 CKT 1 b.2. LOAD 1 506991 b.3. DISCONNECT 506991 b.4. LINE 506991 TO 506957 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_23_P5_FlintCreek | Single phase fault with stuck relay near FLINTCR5 (506934) 161 kV Bus a. Apply Fault at theFLINTCR5 (506934) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506934 TO 506957 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_24_P5_Longwood | Single phase fault with stuck relay near LONGWD 4 (508808) 138 kV Bus a. Apply Fault at theLONGWD 4 (508808) 138 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 508808 TO 507774 CKT 1 b.2. LINE 507774 TO 507749 CKT 1 b.3. LOAD 1 507749 b.4. LOAD 1 507774 b.5. DISCONNECT 507749 b.6. DISCONNECT 507774 b.7. LINE 507749 TO 507711 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_25_P5_Linwood | Single phase fault with stuck relay near LINWOOD4 (507738) 138 kV Bus a. Apply Fault at theLINWOOD4 (507738) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 507738 TO 507742 CKT 1 b.2. LOAD 1 507742 b.3. DISCONNECT 507742 b.4. LINE 507742 TO 507711 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_26_P5_Whitney | Single phase fault with stuck relay near WHITNEY4 (508575) 138 kV Bus a. Apply Fault at theWHITNEY4 (508575) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508575 TO 508582 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_27_P5_Harrison | Single phase fault with stuck relay near HARRISN4 (508544) 138 kV Bus a. Apply Fault at theHARRISN4 (508544) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508544 TO 508582 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_28_P5_STXEastman | Single phase fault with stuck relay near SOTXEST4 (508570) 138 kV Bus a. Apply Fault at theSOTXEST4 (508570) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508570 TO 508582 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_29_P5_Marshall | Single phase fault with stuck relay near MARSHL-4 (508557) 138 kV Bus a. Apply Fault at theMARSHL-4 (508557) 138 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 508557 TO 508562 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_30_P5_Scottsville | Single phase fault with stuck relay near SCOTTSV4 (508567) 138 kV Bus a. Apply Fault at theSCOTTSV4 (508567) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508567 TO 508569 CKT 1 b.2. LINE 508569 TO 508566 CKT 1 b.3. LOAD 1 508569 b.4. LOAD 1 508577 b.5. LOAD 2 508577 b.6. DISCONNECT 508566 b.7. DISCONNECT 508569 b.8. DISCONNECT 508577 b.9. LINE 508566 TO 508562 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_31_P5_KnoxLee | Single phase fault with stuck relay near KNOXLEE4 (508548) 138 kV Bus a. Apply Fault at theKNOXLEE4 (508548) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 508548 TO 508596 CKT 1 b.2. LINE 508596 TO 509092 CKT 1 b.3. LOAD 1 509092 b.4. LOAD 1 509605 b.5. DISCONNECT 508596 b.6. DISCONNECT 509092 b.7. DISCONNECT 509605 b.8. LINE 509092 TO 508562 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_32_P5_Whitney | Single phase fault with stuck relay near WHITNEY4 (508575) 138 kV Bus a. Apply Fault at theWHITNEY4 (508575) 138 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 508575 TO 508595 CKT 1 b.2. LOAD 1 508595 b.3. DISCONNECT 508595 b.4. LINE 508595 TO 508562 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_33_P5_Pirkey | Single phase fault with stuck relay near PIRKEY 4 (508562) 138 kV Bus a. Apply Fault at thePIRKEY 4 (508562) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 508562 TO 509092 CKT 1 b.2. LINE 509092 TO 508596 CKT 1 b.3. LOAD 1 509092 b.4. LOAD 1 509605 b.5. DISCONNECT 508596 b.6. DISCONNECT 509092 b.7. DISCONNECT 509605 b.8. LINE 508596 TO 508548 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_34_P5_RockHill | Single phase fault with stuck relay near ROKHILL4 (509083) 138 kV Bus a. Apply Fault at theROKHILL4 (509083) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509083 TO 509087 CKT 1 b.2. LINE 509087 TO 509059 CKT 1 b.3. LOAD 1 509059 b.4. LOAD 1 509087 b.5. LOAD 2 509087 b.6. DISCONNECT 509059 b.7. DISCONNECT 509087 b.8. LINE 509059 TO 508548 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_35_P5_STXEastman | Single phase fault with stuck relay near SOTXEST4 (508570) 138 kV Bus a. Apply Fault at theSOTXEST4 (508570) 138 kV Bus b. Clear fault after 36 cycles and trip the faulted elements: b.1. LINE 508570 TO 508548 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_36_P5_Harrison | Single phase fault with stuck relay near HARRISN4 (508544) 138 kV Bus a. Apply Fault at theHARRISN4 (508544) 138 kV Bus b. Clear fault after 24 cycles and trip the faulted elements: b.1. LINE 508544 TO 508548 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_37_P5_NWHenderson | Single phase fault with stuck relay near NWHENDR4 (509076) 138 kV Bus a. Apply Fault at theNWHENDR4 (509076) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509076 TO 509077 CKT 1 b.2. LINE 509077 TO 509078 CKT 1 b.3. LOAD 1 509077 b.4. LOAD 1 509078 b.5. DISCONNECT 509077 b.6. DISCONNECT 509078 b.7. LINE 509078 TO 508548 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_92_P5_36th&Lewis | Single phase fault with stuck relay near 36LEWIS4 (509800) 138 kV Bus a. Apply Fault at the36LEWIS4 (509800) 138 kV Bus b. Clear fault after 65 cycles and trip the faulted elements: b.1. LINE 509800 TO 509788 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_93_P5_Riverside | Single phase fault with stuck relay near R.S.S.-4 (509783) 138 kV Bus a. Apply Fault at theR.S.S.-4 (509783) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 509783 TO 509814 CKT 1 b.2. LOAD 1 509856 b.3. LOAD 1 509859 b.4. DISCONNECT 509814 b.5. DISCONNECT 509856 b.6. DISCONNECT 509859 b.7. LINE 509814 TO 509788 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_94_P5_72nd&Elwood | Single phase fault with stuck relay near 72ELWOD4 (509888) 138 kV Bus a. Apply Fault at the72ELWOD4 (509888) 138 kV Bus b. Clear fault after 45 cycles and trip the faulted elements: b.1. LINE 509888 TO 509788 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_95_P5_Carson | Single phase fault with stuck relay near CARSN-S4 (509756) 138 kV Bus a. Apply Fault at theCARSN-S4 (509756) 138 kV Bus b. Clear fault after 4 cycles and trip the faulted elements: b.1. LINE 509756 TO 509788 CKT 1 b.2. LOAD 1 509742 b.3. LOAD 1 509756 b.4. LOAD 1 509777 b.5. DISCONNECT 509742 b.6. DISCONNECT 509756 b.7. DISCONNECT 509777 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_96_P5_SapulpaRd | Single phase fault with stuck relay near SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at theSAPLPRD4 (509871) 138 kV Bus b. Clear fault after 33 cycles and trip the faulted elements: b.1. LINE 509871 TO 509848 CKT 1 b.2. LOAD 1 509727 b.3. DISCONNECT 509727 b.4. DISCONNECT 509848 b.5. LINE 509848 TO 509788 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_97_P5_36th&Olympia | Single phase fault with stuck relay near 36&OLY-4 (509724) 138 kV Bus a. Apply Fault at the36&OLY-4 (509724) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509724 TO 509788 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_98_P5_Claremore | Single phase fault with stuck relay near CLARMR 4 (512707) 138 kV Bus a. Apply Fault at theCLARMR 4 (512707) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 513124 TO 512707 CKT 1 b.2. DISCONNECT 513124 b.3. LINE 510396 TO 513124 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT_AEPW_2022_99_P5_Anadarko | Single phase fault with stuck relay near ANADARK4 (520814) 138 kV Bus a. Apply Fault at theANADARK4 (520814) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 520814 TO 511477 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT__AEPW-2022-90-P5-TulsaNorth | Sngle phase fault with stuck relay near Tulsa North (509817) 138 kV Bus a. Apply Fault at the Tulsa North (509817) 138 kV Bus b. Run fault for 23 cycles and trip faulted elements b.1. LINE FROM BUS 509842 TO BUS 509784 CKT 1 c. Run fault for 4 cycles and trip faulted elements c.1. LINE FROM BUS 509863 TO BUS 509801 CKT 1 c.2. LINE FROM BUS 509844 TO BUS 509860 CKT 1 c.3. DISCONNECT BUS 509894 d. Run fault for 5 cycles and trip faulted elements d.1. LINE FROM BUS 509839 TO BUS 509887 CKT 1 e. Run fault for 4 cycles and trip faulted elements e.1. LINE FROM BUS 509851 TO BUS 509757 CKT 1 f. Run fault for 1 cycles and trip faulted elements f.1. LINE FROM BUS 509817 TO BUS 510396 CKT 1 g. Clear fault after 11 cycles and trip the faulted elements g.1. LINE FROM BUS 509884 TO BUS 510388 CKT 1 g.2. LOAD 1 BUS 509714 g.3.LOAD 1 BUS 509715 g.4. LOAD 1 BUS 509726 g.5. LOAD 1 BUS 509743 g.6. LOAD 1 BUS 509805 g.7. LOAD 1 BUS 509817 g.8. LOAD 1 BUS 509818 g.9. LOAD 1 BUS 509822 g.10. LOAD 1 BUS 509825 g.11. LOAD 1 BUS 509837 g.12. LOAD 1 BUS 509840 g.13. LOAD 1 BUS 509884 g.14. DISCONNECT BUS 509714 g.15. DISCONNECT BUS 509715 g.16 DISCONNECT BUS 509726 g.17. DISCONNECT BUS 509743 g.18. DISCONNECT BUS 509746 g.19. DISCONNECT BUS 509805 g.20. DISCONNECT BUS 509817 g.21. DISCONNECT BUS 509818 g.22. DISCONNECT BUS 509822 g.23. DISCONNECT BUS 509825 g.24. DISCONNECT BUS 509837 g.25. DISCONNECT BUS 509839 g.26. DISCONNECT BUS 509840 g.27. DISCONNECT BUS 509842 g.28. DISCONNECT BUS 509844 g.29. DISCONNECT BUS 509851 g.30. DISCONNECT BUS 509862 g.31. DISCONNECT BUS 509863 g.32. DISCONNECT BUS 509884 g.33. DISCONNECT BUS 509900 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-028 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-028 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT__AEPW-2022-91-P5-TulsaSoutheast | Sngle phase fault with stuck relay near Tulsa SouthEast (509811) 138 kV Bus a. Apply Fault at the Tulsa SouthEast (509811) 138 kV Bus b. Run fault for 27 cycles and trip faulted elements b.1. LINE FROM BUS 509811 TO BUS 509831 CKT 1 b.2. LINE FROM BUS 509811 TO BUS 509833 CKT 1 c. Run fault for 3 cycles and trip faulted elements c.1. LINE FROM BUS 509781 TO BUS 509718 CKT 1 d. Run fault for 4 cycles and trip faulted elements d.1. LINE FROM BUS 509763 TO BUS 509772 CKT 1 e. Run fault for 4 cycles and trip faulted elements e.1. LINE FROM BUS 509765 TO BUS 509855 CKT 1 f. Run fault for 4 cycles and trip faulted elements f.1. LINE FROM BUS 509785 TO BUS 509891 CKT 1 g. Clear fault after 9 cycles and trip the faulted elements g.1. LINE FROM BUS 509776 TO BUS 509800 CKT 1 g.2. LOAD 1 BUS 509716 g.3. LOAD 1 BUS 509717 g.4. LOAD 1 BUS 509728 g.5. LOAD 1 BUS 509733 g.6. LOAD 1 BUS 509734 g.7. LOAD 1 BUS 509735 g.8. LOAD 1 BUS 509744 g.9. LOAD 1 BUS 509760 g.10. LOAD 1 BUS 509761 g.11. LOAD 1 BUS 509774 g.12. LOAD 1 BUS 509779 g.13. LOAD 1 BUS 509780 g.14. LOAD 1 BUS 509797 g.15. LOAD 1 BUS 509808 g.16. LOAD 1 BUS 509811 g.17. LOAD 1 BUS 509824 g.18. LOAD 1 BUS 509826 g.19. LOAD 1 BUS 509827 g.20. LOAD 1 BUS 509829 g.21. LOAD 1 BUS 509861 g.22. LOAD 1 BUS 509886 g.23. DISCONNECT BUS 509716 g.24. DISCONNECT BUS 509717 g.25. DISCONNECT BUS 509718 g.26. DISCONNECT BUS 509728 g.27. DISCONNECT BUS 509733 g.28. DISCONNECT BUS 509734 g.29. DISCONNECT BUS 509735 g.30. DISCONNECT BUS 509744 g.31. DISCONNECT BUS 509760 g.32. DISCONNECT BUS 509761 g.33. DISCONNECT BUS 509762 g.34. DISCONNECT BUS 509763 g.35. DISCONNECT BUS 509765 g.36. DISCONNECT BUS 509771 g.37. DISCONNECT BUS 509774 g.38. DISCONNECT BUS 509776 g.39. DISCONNECT BUS 509779 g.40. DISCONNECT BUS 509780 g.41. DISCONNECT BUS 509785 g.42. DISCONNECT BUS 509797 g.43. DISCONNECT BUS 509808 g.44. DISCONNECT BUS 509811 g.45. DISCONNECT BUS 509820 g.46. DISCONNECT BUS 509824 g.47. DISCONNECT BUS 509826 g.48. DISCONNECT BUS 509827 g.49. DISCONNECT BUS 509828 g.50. DISCONNECT BUS 509829 g.51. DISCONNECT BUS 509830 g.52. DISCONNECT BUS 509861 g.53. DISCONNECT BUS 509873 g.54. DISCONNECT BUS 509886 g.55. LINE FROM BUS 509771 TO BUS 509790 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-048, GEN-2018-027 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-048, GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT__OKGE-All-36-P5_1-INGLEWD4 | Sngle phase fault with stuck relay near INGLEWD (515060) 138 kV Bus a. Apply Fault at the INGLEWD (515060) 138 kV Bus b. Run fault for 37.98 cycles and trip faulted elements b.1. LINE FROM BUS 515060 TO BUS 515059 CKT 1 c. Run fault for 19.98 cycles and trip faulted elements c.1. LINE FROM BUS 515060 TO BUS 515059 CKT 1 d. Run fault for 37.98 cycles and trip faulted elements d.1. LINE FROM BUS 515060 TO BUS 515059 CKT 1 e. Run fault for 56.46 cycles and trip faulted elements e.1. LINE FROM BUS 514941 TO BUS 515480 CKT 1 f. Run fault for 19.98 cycles and trip faulted elements f.1. LINE FROM BUS 514941 TO BUS 515480 CKT 1 g. Run fault for 97.80 cycles g.1. CLOSE LINE FROM BUS 515442 TO BUS 515046 CKT 1 h. Run fault for 16.62 cycles and trip faulted elements h.1. LINE FROM BUS 514941 TO BUS 515480 CKT 1 i. Run fault for 27.60 cycles and trip faulted elements i.1. LINE FROM BUS 514973 TO BUS 514884 CKT 1 j. Run fault for 6.60 cycles and trip faulted elements j.1. LINE FROM BUS 514973 TO BUS 514964 CKT 1 k. Run fault for 6.00 cycles and trip faulted elements k.1. LINE FROM BUS 514993 TO BUS 514941 CKT 1 l. Run fault for 7.38 cycles and trip faulted elements l.1. LINE FROM BUS 514973 TO BUS 514884 CKT 1 m. Run fault for 6.60 cycles m.1. CLOSE LINE FROM BUS 514973 TO BUS 514964 CKT 1 n. Run fault for 6.00 cycles n.1. CLOSE LINE FROM BUS 514993 TO BUS 514941 CKT 1 o. Run fault for 21.00 cycles and trip faulted elements o.1. LINE FROM BUS 515442 TO BUS 515046 CKT 1 p. Run fault for 30.6 cycles and trip faulted elements p.1. LINE FROM BUS 514973 TO BUS 514884 CKT 1 q. Run fault for 13.20 cycles and trip faulted elements q.1. LINE FROM BUS 514973 TO BUS 514964 CKT 1 r. Run fault for 12.00 cycles and trip faulted elements r.1. LINE FROM BUS 514993 TO BUS 514941 CKT 1 s. Run fault for 20.82 cycles and trip faulted elements s.1. LINE FROM BUS 514941 TO BUS 514906 CKT 1 t. Run fault for 19.98 cycles t.1. CLOSE LINE FROM BUS 514941 TO BUS 514906 CKT 1 u. Run fault for 57.42 cycles and trip faulted elements u.1. LINE FROM BUS 514927 TO BUS 514937 CKT 1 v. Clear fault after 60.00 cycles and trip the faulted elements v.1. LINE FROM BUS 514941 TO BUS 514906 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT__OKGE-All-37-P5_2-TARBY5 | Sngle phase fault with stuck relay near TARBY5 (515264) 161 kV Bus a. Apply Fault at the TARBY5 (515264) 161 kV Bus b. Run fault for 24 cycles and trip faulted elements b.1. LINE FROM BUS 515259 TO BUS 515275 CKT 1 b.2. LINE FROM BUS 515259 TO BUS 515260 CKT 1 c. Run fault for 34 cycles and trip faulted elements c.1. LINE FROM BUS 515262 TO BUS 515264 CKT 1 d. Run fault for 34 cycles and d.1. CLOSE LINE FROM BUS 515259 TO BUS 515275 CKT 1 d.2. CLOSE LINE FROM BUS 515259 TO BUS 515260 CKT 1 e. Run fault for 59 cycles and trip faulted elements e.1. LINE FROM BUS 515259 TO BUS 515275 CKT 1 e.2. LINE FROM BUS 515259 TO BUS 515260 CKT 1 f. Run fault for 80 cycles and trip faulted elements f.1. LINE FROM BUS 515282 TO BUS 515276 CKT 1 g. Run fault for 90 cycles and g.1. CLOSE LINE FROM BUS 515282 TO BUS 515276 CKT 1 h. Run fault for 126 cycles and trip faulted elements h.1. LINE FROM BUS 515263 TO BUS 515272 CKT 1 i. Run fault for 136 cycles and i.1. CLOSE LINE FROM BUS 515263 TO BUS 515272 CKT 1 j. Run fault for 170 cycles and trip faulted elements j.1. LINE FROM BUS 515282 TO BUS 515276 CKT 1 k. Run fault for 185 cycles and trip faulted elements k.1. LINE FROM BUS 515264 TO BUS 515265 CKT 1 l. Run fault for 195 cycles and l.1. CLOSE LINE FROM BUS 515264 TO BUS 515265 CKT 1 m. Run fault for 262 cycles and trip faulted elements m.1. LINE FROM BUS 515263 TO BUS 515272 CKT 1 n. Clear fault after 380 cycles and trip faulted elements n.1. LINE FROM BUS 515264 TO BUS 515265 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT__OKGE-All-38-P5_2-WINDFRM4 | Sngle phase fault with stuck relay near WINDFRM4 (515785) 138 kV Bus a. Apply Fault at the WINDFRM4 (515785) 138 kV Bus b. Run fault for 27 cycles and trip faulted elements b.1. LINE FROM BUS 515785 TO BUS 515786 CKT 1 b.2. LINE FROM BUS 514785 TO BUS 515785 CKT 1 b.3. LINE FROM BUS 515785 TO BUS 520999 CKT 1 c. Run fault for 37.02 cycles and c.1. CLOSE LINE FROM BUS 515785 TO BUS 515786 CKT 1 c.2. CLOSE LINE FROM BUS 514785 TO BUS 515785 CKT 1 c.3. CLOSE LINE FROM BUS 515785 TO BUS 520999 CKT 1 d. Clear fault after 64.02 cycles and trip faulted elements d.1. LINE FROM BUS 515785 TO BUS 515786 CKT 1 d.2. LINE FROM BUS 514785 TO BUS 515785 CKT 1 d.3. LINE FROM BUS 515785 TO BUS 520999 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT__AEPW-2022-11-P5-Lieberman | Sngle phase fault with stuck relay near Lieberman (508806) 138 kV Bus a. Apply Fault at the Lieberman (508806) 138 kV Bus b. Run fault for 23 cycles and trip faulted elements b.1. LINE FROM BUS 508806 TO BUS 507711 CKT 1 c. Run fault for 4 cycles and trip faulted elements c.1. LINE FROM BUS 508833 TO BUS 508835 CKT 1 c.2. LINE FROM BUS 507772 TO BUS 507751 CKT 1 d. Run fault for 3 cycles and trip faulted elements d.1. LINE FROM BUS 508806 TO BUS 508833 CKT 1 e. Run fault for 4 cycles and trip faulted elements e.1. LINE FROM BUS 508806 TO BUS 508808 CKT 1 f. Run fault for 26 cycles and trip faulted elements f.1. LINE FROM BUS 508812 TO BUS 508815 CKT 1 g. Clear fault after 67 cycles and trip faulted elements f.1. LINE FROM BUS 508805 TO BUS 508801 CKT 1 f.2. DROP GENERATOR 1 BUS 509401 f.3. DROP GENERATOR 1 BUS 509402 f.4. DROP LOAD 1 BUS 508805 f.5. DROP LOAD 1 BUS 508812 f.6. DROP LOAD 1 BUS 508833 f.7. DROP LOAD S1 BUS 509401 f.8. DROP LOAD S1 BUS 509402 f.9. DISCONNECT BUS 508805 f.10. DISCONNECT BUS 508806 f.11. DISCONNECT BUS 508812 f.12. DISCONNECT BUS 508820 f.13. DISCONNECT BUS 508821 f.14. DISCONNECT BUS 508822 f.15. DISCONNECT BUS 508833 f.16. DISCONNECT BUS 509401 f.17. DISCONNECT BUS 509402 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT__AEPW-2022-13-P5-SugarHill | Sngle phase fault with stuck relay near SugarHill (508080) 138 kV Bus a. Apply Fault at the SugarHill (508080) 138 kV Bus b. Run fault for 23 cycles and trip faulted elements b.1. LINE FROM BUS 508080 TO BUS 507454 CKT 1 c. Run fault for 3 cycles and trip faulted elements c.1. LINE FROM BUS 508082 TO BUS 508085 CKT 1 d. Run fault for 7 cycles and trip faulted elements d.1. LINE FROM BUS 508080 TO BUS 508071 CKT 1 e. Run fault for 55 cycles and trip faulted elements e.1. LINE FROM BUS 508073 TO BUS 508053 CKT 1 f. Run fault for 18 cycles and trip faulted elements f.1. LINE FROM BUS 508081 TO BUS 508084 CKT 1 g. Clear fault after 56 cycles and trip faulted elements f.1. LINE FROM BUS 508051 TO BUS 507429 CKT 1 f.2. DROP LOAD A1 BUS 504109 f.3. DROP LOAD 1 BUS 508051 f.4. DROP LOAD 1 BUS 508073 f.5. DROP LOAD 1 BUS 508076 f.6. DROP LOAD 1 BUS 508080 f.7. DROP LOAD 1 BUS 508094 f.8. DISCONNECT BUS 504109 f.9. DISCONNECT BUS 508051 f.10. DISCONNECT BUS 508066 f.11. DISCONNECT BUS 508073 f.12. DISCONNECT BUS 508076 f.13. DISCONNECT BUS 508079 f.14. DISCONNECT BUS 508080 f.15. DISCONNECT BUS 508081 f.16. DISCONNECT BUS 508082 f.17. DISCONNECT BUS 508094 f.18 DISCONNECT BUS 508103 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT__AEPW-2022-14-P5-FtHumbug | Sngle phase fault with stuck relay near FtHumbug (507731) 138 kV Bus a. Apply Fault at the FtHumbug (507731) 138 kV Bus b. Run fault for 21 cycles and trip faulted elements b.1. LINE FROM BUS 507731 TO BUS 507711 CKT 1 c. Run fault for 3 cycles and trip faulted elements c.1. LINE FROM BUS 507731 TO BUS 507763 CKT 1 d. Run fault for 33 cycles and trip faulted elements d.1. LINE FROM BUS 507730 TO BUS 507716 CKT 1 e. Run fault for 1 cycles and trip faulted elements e.1. LINE FROM BUS 507735 TO BUS 507755 CKT 1 f. Clear fault after 2 cycles and trip faulted elements f.1. LINE FROM BUS 507722 TO BUS 507717 CKT 1 f.2. DROP LOAD 1 BUS 507722 f.3. DROP LOAD 1 BUS 507730 f.4. DROP LOAD 1 BUS 507735 f.5. DROP LOAD 1 BUS 507746 f.6. DISCONNECT BUS 507722 f.7. DISCONNECT BUS 507730 f.8. DISCONNECT BUS 507731 f.9. DISCONNECT BUS 507735 f.10. DISCONNECT BUS 507746 f.11. DISCONNECT BUS 507753 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT__AEPW-2022-85-P5-LES | Sngle phase fault with stuck relay near LES (511467) 138 kV Bus a. Apply Fault at the FtHumbug (507731) 138 kV Bus b. Run fault for 27 cycles and trip faulted elements b.1. LINE FROM BUS 511437 TO BUS 511494 CKT 1 b.2. LINE FROM BUS 511512 TO BUS 511439 CKT 1 b.3. LINE FROM BUS 511477 TO BUS 511563 CKT 1 c. Run fault for 12 cycles and trip faulted elements c.1. LINE FROM BUS 529304 TO BUS 511494 CKT 1 d. Run fault for 15 cycles and trip faulted elements d.1. DISCONNECT BUS 511415 e. Run fault for 1 cycles and trip faulted elements e.1. DISCONNECT BUS 511416 f. Run fault for 2 cycles and trip faulted elements f.1. LINE FROM BUS 511474 TO BUS 511467 CKT 1 g. Run fault for 6 cycles and trip faulted elements g.1. DISCONNECT BUS 511411 h. Run fault for 2 cycles and trip faulted elements h.1. LINE FROM BUS 511437 TO BUS 511467 CKT 1 i. Run fault for 7 cycles and trip faulted elements i.1. DISCONNECT BUS 511414 j. Run fault for 24 cycles and trip faulted elements j.1. INE FROM BUS 511467 TO BUS 511486 CKT 1 k. Clear fault after 15 cycles and trip faulted elements k.1. LINE FROM BUS 511477 TO BUS 511421 CKT 1 k.2. DROP LOAD 1 BUS 511422 k.3. DROP LOAD 1 BUS 511431 k.4. DROP LOAD 1 BUS 511467 k.5. DISCONNECT BUS 511422 k.6. DISCONNECT BUS 511423 k.7. DISCONNECT BUS 511431 k.8. DISCONNECT BUS 511439 k.9. DISCONNECT BUS 511494 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2015-013 trips on voltage protection settings | Disabling voltage protection settings for GEN-2015-013 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT__AEPW-2022-86-P5-Oneta | Sngle phase fault with stuck relay near Oneta (509807) 345 kV Bus a. Apply Fault at the Oneta (509807) 345 kV Bus b. Run fault for 26 cycles and trip faulted elements b.1. LINE FROM BUS 509807 TO BUS 509836 CKT 1 b.2. LINE FROM BUS 509807 TO BUS 509836 CKT 2 b.3. INE FROM BUS 509807 TO BUS 509782 CKT 1 c. Run fault for 18 cycles and trip faulted elements c.1. LINE FROM BUS 509807 TO BUS 509745 CKT 1 d. Run fault for 1 cycles and trip faulted elements d.1. LINE FROM BUS 509807 TO BUS 510406 CKT 1 e. Clear fault after 35 cycles and trip faulted elements e.1. LINE FROM BUS 509806 TO BUS 509891 CKT 1 e.2. LINE FROM BUS 509806 TO BUS 509869 CKT 1 e.3. LINE FROM BUS 509806 TO BUS 509769 CKT 1 e.4. LINE FROM BUS 509806 TO BUS 509786 CKT 1 e.5. LINE FROM BUS 509806 TO BUS 509768 CKT 1 e.6. DROP GENERATOR 1 BUS 511938 e.7. DROP GENERATOR 1 BUS 511939 e.8. DROP GENERATOR 1 BUS 511940 e.9. DROP GENERATOR 1 BUS 511941 e.10. DROP GENERATOR 1 BUS 511942 e.11. DROP GENERATOR 1 BUS 511943 e.12. DROP LOAD 1 BUS 509806 e.13. DROP LOAD S1 BUS 511940 e.14. DROP LOAD S1 BUS 511943 e.15. DISCONNECT BUS 509806 e.16. DISCONNECT BUS 509807 e.17. DISCONNECT BUS 509836 e.18. DISCONNECT BUS 509868 e.19. DISCONNECT BUS 509874 e.20. DISCONNECT BUS 509881 e.21. DISCONNECT BUS 511938 e.22. DISCONNECT BUS 511939 e.23. DISCONNECT BUS 511940 e.24. DISCONNECT BUS 511941 e.25. DISCONNECT BUS 511942 e.26. DISCONNECT BUS 511943 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027, GEN-2018-028, GEN-2017-141 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-027, GEN-2018-028, GEN-2017-141 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT__AEPW-2022-88-P5-TPS | Sngle phase fault with stuck relay near TPS (509788) 138 kV Bus a. Apply Fault at the TPS (509788) 138 kV Bus b. Run fault for 16 cycles and trip faulted elements b.1. LINE FROM BUS 509788 TO BUS 509724 CKT 1 c. Run fault for 15 cycles and trip faulted elements c.1. LINE FROM BUS 509788 TO BUS 509800 CKT 1 d. Run fault for 2 cycles and trip faulted elements d.1. LINE FROM BUS 509850 TO BUS 509783 CKT 1 d.2. LINE FROM BUS 509848 TO BUS 509871 CKT 1 e. Run fault for 2 cycles and trip faulted elements e.1. LINE FROM BUS 509788 TO BUS 509888 CKT 1 f. Run fault for 18 cycles and trip faulted elements f.1. LINE FROM BUS 509814 TO BUS 509783 CKT 1 g. Clear fault after 195 cycles and trip faulted elements g.1. DISCONNECT BUS 509880 g.2. DROP GENERATOR 1 BUS 509890 g.3. DROP GENERATOR 1 BUS 511854 g.4. DROP GENERATOR 1 BUS 511858 g.5. DROP LOAD 1 BUS 509727 g.6. DROP LOAD 1 BUS 509742 g.7. DROP LOAD 1 BUS 509750 g.8. DROP LOAD 1 BUS 509751 g.9. DROP LOAD 1 BUS 509756 g.10. DROP LOAD 1 BUS 509777 g.11. DROP LOAD 1 BUS 509788 g.12. DROP LOAD 1 BUS 509789 g.13. DROP LOAD 1 BUS 509795 g.14. DROP LOAD 1 BUS 509846 g.15. DROP LOAD 1 BUS 509856 g.16. DROP LOAD 1 BUS 509859 g.17. DROP LOAD S1 BUS 511854 g.18. DROP LOAD S1 BUS 511858 g.19. DISCONNECT BUS 509727 g.20. DISCONNECT BUS 509742 g.21. DISCONNECT BUS 509750 g.22. DISCONNECT BUS 509751 g.23. DISCONNECT BUS 509756 g.24. DISCONNECT BUS 509777 g.25. DISCONNECT BUS 509795 g.26. DISCONNECT BUS 509814 g.27. DISCONNECT BUS 509846 g.28. DISCONNECT BUS 509848 g.29. DISCONNECT BUS 509850 g.30. DISCONNECT BUS 509856 g.31. DISCONNECT BUS 509859 g.32. DISCONNECT BUS 509890 g.33. DISCONNECT BUS 511854 g.34. DISCONNECT BUS 511858 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25S | Transfer | FAULT__AEPW-2022-89-P5-Weleetka | Sngle phase fault with stuck relay near Weleetka (510902) 138 kV Bus a. Apply Fault at the Weleetka (510902) 138 kV Bus b. Run fault for 18 cycles and trip faulted elements b.1. LINE FROM BUS 510921 TO BUS 510908 CKT 1 c. Run fault for 6 cycles and trip faulted elements c.1. LINE FROM BUS 510877 TO BUS 510948 CKT 1 d. Run fault for 3 cycles and trip faulted elements d.1. LINE FROM BUS 510902 TO BUS 505592 CKT 1 e. Run fault for 6 cycles and trip faulted elements e.1. LINE FROM BUS 510902 TO BUS 510892 CKT 1 f. Run fault for 24 cycles and trip faulted elements f.1. LINE FROM BUS 515078 TO BUS 510877 CKT 1 g. Clear fault after 5 cycles and trip faulted elements g.1. LINE FROM BUS 510923 TO BUS 510898 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_100_P5_Washita | Single phase fault with stuck relay near WASHITA4 (521089) 138 kV Bus a. Apply Fault at theWASHITA4 (521089) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 521089 TO 511477 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_101_P5_LES | Single phase fault with stuck relay near L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at theL.E.S.-4 (511467) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 511467 TO 511437 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_102_P5_LES | Single phase fault with stuck relay near L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at theL.E.S.-4 (511467) 138 kV Bus b. Clear fault after 72 cycles and trip the faulted elements: b.1. LINE 511467 TO 511494 CKT 1 b.2. LINE 511494 TO 511437 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_103_P5_LES | Single phase fault with stuck relay near L.E.S.-2 (511466) 69 kV Bus a. Apply Fault at theL.E.S.-2 (511466) 69 kV Bus b. Clear fault after 41 cycles and trip the faulted elements: b.1. LINE 511466 TO 511436 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_104_P5_SouthHudson | Single phase fault with stuck relay near S.HUD.-4 (509833) 138 kV Bus a. Apply Fault at theS.HUD.-4 (509833) 138 kV Bus b. Clear fault after 55 cycles and trip the faulted elements: b.1. LINE 509833 TO 509764 CKT 1 b.2. LINE 509764 TO 509809 CKT 1 b.3. LINE 509809 TO 509813 CKT 1 b.4. LINE 509813 TO 509853 CKT 1 b.5. LINE 509853 TO 509783 CKT 1 b.6. LOAD 1 509729 b.7. LOAD 1 509730 b.8. LOAD 1 509731 b.9. LOAD 1 509732 b.10. DISCONNECT 509729 b.11. DISCONNECT 509730 b.12. DISCONNECT 509731 b.13. DISCONNECT 509732 b.14. DISCONNECT 509764 b.15. DISCONNECT 509809 b.16. DISCONNECT 509813 b.17. DISCONNECT 509853 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_105_P5_96th&Yale | Single phase fault with stuck relay near 96YALE-4 (509847) 138 kV Bus a. Apply Fault at the96YALE-4 (509847) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509847 TO 509858 CKT 1 b.2. LINE 509858 TO 509849 CKT 1 b.3. LINE 509849 TO 509783 CKT 1 b.4. LOAD 1 509738 b.5. LOAD 1 509810 b.6. LOAD 1 509857 b.7. DISCONNECT 509738 b.8. DISCONNECT 509810 b.9. DISCONNECT 509849 b.10. DISCONNECT 509857 b.11. DISCONNECT 509858 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_106_P5_KimberlyClark.id | Single phase fault with stuck relay near KIMCLRK4 (509845) 138 kV Bus a. Apply Fault at theKIMCLRK4 (509845) 138 kV Bus b. Clear fault after 35 cycles and trip the faulted elements: b.1. LINE 509845 TO 509775 CKT 1 b.2. LOAD 1 509775 b.3. DISCONNECT 509775 b.4. LINE 509775 TO 509783 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_107_P5_OG&Ebee | Single phase fault with stuck relay near BEELINE4 (515247) 138 kV Bus a. Apply Fault at theBEELINE4 (515247) 138 kV Bus b. Clear fault after 26 cycles and trip the faulted elements: b.1. LINE 515247 TO 515473 CKT 1 b.2. LOAD 1 515248 b.3. DISCONNECT 515248 b.4. DISCONNECT 515473 b.5. LINE 515473 TO 509783 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_108_P5_SapulpaRoad | Single phase fault with stuck relay near SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at theSAPLPRD4 (509871) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509871 TO 509759 CKT 1 b.2. LINE 509759 TO 509753 CKT 1 b.3. LOAD 1 509753 b.4. LOAD 1 509759 b.5. DISCONNECT 509753 b.6. DISCONNECT 509759 b.7. LINE 509753 TO 509783 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_109_P5_WeleetkaSWPA | Single phase fault with stuck relay near WELEETK4 (505592) 138 kV Bus a. Apply Fault at theWELEETK4 (505592) 138 kV Bus b. Clear fault after 33 cycles and trip the faulted elements: b.1. LINE 505592 TO 510902 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_110_P5_Henryetta138kV | Single phase fault with stuck relay near HENRYET4 (510892) 138 kV Bus a. Apply Fault at theHENRYET4 (510892) 138 kV Bus b. Clear fault after 33 cycles and trip the faulted elements: b.1. LINE 510892 TO 510902 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_12_P5_Linwood | Single phase fault with stuck relay near LINWOOD4 (507738) 138 kV Bus a. Apply Fault at theLINWOOD4 (507738) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 507742 TO 507711 CKT 1 b.2. LINE 507771 TO 507755 CKT 1 b.3. LOAD 1 507738 b.4. LOAD 1 507742 b.5. LOAD 1 507748 b.6. DISCONNECT 507738 b.7. DISCONNECT 507742 b.8. DISCONNECT 507748 b.9. DISCONNECT 507771 b.10. LINE 507748 TO 507759 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_15_P5_ChambersSpring | Single phase fault with stuck relay near CHAMSPR5 (506944) 161 kV Bus a. Apply Fault at theCHAMSPR5 (506944) 161 kV Bus b. Clear fault after 25 cycles and trip the faulted elements: b.1. LINE 506944 TO 504202 CKT 1 b.2. LOAD A1 504202 b.3. DISCONNECT 504202 b.4. LINE 504202 TO 506934 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_16_P5_Siloam | Single phase fault with stuck relay near SILOAM 5 (506948) 161 kV Bus a. Apply Fault at theSILOAM 5 (506948) 161 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 506948 TO 506934 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_17_P5_Tontitown | Single phase fault with stuck relay near TONTITN5 (506957) 161 kV Bus a. Apply Fault at theTONTITN5 (506957) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506957 TO 506934 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_18_P5_Decatur | Single phase fault with stuck relay near DEC392 5 (547484) 161 kV Bus a. Apply Fault at theDEC392 5 (547484) 161 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 547484 TO 506934 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_19_P5_Dyess | Single phase fault with stuck relay near DYESS 5 (506927) 161 kV Bus a. Apply Fault at theDYESS 5 (506927) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506927 TO 506957 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_20_P5_Dyess | Single phase fault with stuck relay near DYESS 5 (506927) 161 kV Bus a. Apply Fault at theDYESS 5 (506927) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506927 TO 504010 CKT 1 b.2. LOAD A1 504010 b.3. DISCONNECT 504010 b.4. DISCONNECT 504011 b.5. DISCONNECT 504012 b.6. DISCONNECT 504013 b.7. DISCONNECT 504014 b.8. LINE 504010 TO 506957 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_21_P5_ChamberSprings | Single phase fault with stuck relay near CHAMSPR5 (506944) 161 kV Bus a. Apply Fault at theCHAMSPR5 (506944) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506944 TO 506957 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_22_P5_Lowell | Single phase fault with stuck relay near LOWELL 5 (506938) 161 kV Bus a. Apply Fault at theLOWELL 5 (506938) 161 kV Bus b. Clear fault after 21 cycles and trip the faulted elements: b.1. LINE 506938 TO 506991 CKT 1 b.2. LOAD 1 506991 b.3. DISCONNECT 506991 b.4. LINE 506991 TO 506957 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_23_P5_FlintCreek | Single phase fault with stuck relay near FLINTCR5 (506934) 161 kV Bus a. Apply Fault at theFLINTCR5 (506934) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506934 TO 506957 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_24_P5_Longwood | Single phase fault with stuck relay near LONGWD 4 (508808) 138 kV Bus a. Apply Fault at theLONGWD 4 (508808) 138 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 508808 TO 507774 CKT 1 b.2. LINE 507774 TO 507749 CKT 1 b.3. LOAD 1 507749 b.4. LOAD 1 507774 b.5. DISCONNECT 507749 b.6. DISCONNECT 507774 b.7. LINE 507749 TO 507711 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-050 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-050 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_25_P5_Linwood | Single phase fault with stuck relay near LINWOOD4 (507738) 138 kV Bus a. Apply Fault at theLINWOOD4 (507738) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 507738 TO 507742 CKT 1 b.2. LOAD 1 507742 b.3. DISCONNECT 507742 b.4. LINE 507742 TO 507711 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_26_P5_Whitney | Single phase fault with stuck relay near WHITNEY4 (508575) 138 kV Bus a. Apply Fault at theWHITNEY4 (508575) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508575 TO 508582 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_27_P5_Harrison | Single phase fault with stuck relay near HARRISN4 (508544) 138 kV Bus a. Apply Fault at theHARRISN4 (508544) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508544 TO 508582 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_28_P5_STXEastman | Single phase fault with stuck relay near SOTXEST4 (508570) 138 kV Bus a. Apply Fault at theSOTXEST4 (508570) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508570 TO 508582 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_29_P5_Marshall | Single phase fault with stuck relay near MARSHL-4 (508557) 138 kV Bus a. Apply Fault at theMARSHL-4 (508557) 138 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 508557 TO 508562 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_30_P5_Scottsville | Single phase fault with stuck relay near SCOTTSV4 (508567) 138 kV Bus a. Apply Fault at theSCOTTSV4 (508567) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508567 TO 508569 CKT 1 b.2. LINE 508569 TO 508566 CKT 1 b.3. LOAD 1 508569 b.4. LOAD 1 508577 b.5. LOAD 2 508577 b.6. DISCONNECT 508566 b.7. DISCONNECT 508569 b.8. DISCONNECT 508577 b.9. LINE 508566 TO 508562 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_31_P5_KnoxLee | Single phase fault with stuck relay near KNOXLEE4 (508548) 138 kV Bus a. Apply Fault at theKNOXLEE4 (508548) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 508548 TO 508596 CKT 1 b.2. LINE 508596 TO 509092 CKT 1 b.3. LOAD 1 509092 b.4. LOAD 1 509605 b.5. DISCONNECT 508596 b.6. DISCONNECT 509092 b.7. DISCONNECT 509605 b.8. LINE 509092 TO 508562 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_32_P5_Whitney | Single phase fault with stuck relay near WHITNEY4 (508575) 138 kV Bus a. Apply Fault at theWHITNEY4 (508575) 138 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 508575 TO 508595 CKT 1 b.2. LOAD 1 508595 b.3. DISCONNECT 508595 b.4. LINE 508595 TO 508562 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_33_P5_Pirkey | Single phase fault with stuck relay near PIRKEY 4 (508562) 138 kV Bus a. Apply Fault at thePIRKEY 4 (508562) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 508562 TO 509092 CKT 1 b.2. LINE 509092 TO 508596 CKT 1 b.3. LOAD 1 509092 b.4. LOAD 1 509605 b.5. DISCONNECT 508596 b.6. DISCONNECT 509092 b.7. DISCONNECT 509605 b.8. LINE 508596 TO 508548 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_34_P5_RockHill | Single phase fault with stuck relay near ROKHILL4 (509083) 138 kV Bus a. Apply Fault at theROKHILL4 (509083) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509083 TO 509087 CKT 1 b.2. LINE 509087 TO 509059 CKT 1 b.3. LOAD 1 509059 b.4. LOAD 1 509087 b.5. LOAD 2 509087 b.6. DISCONNECT 509059 b.7. DISCONNECT 509087 b.8. LINE 509059 TO 508548 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_35_P5_STXEastman | Single phase fault with stuck relay near SOTXEST4 (508570) 138 kV Bus a. Apply Fault at theSOTXEST4 (508570) 138 kV Bus b. Clear fault after 36 cycles and trip the faulted elements: b.1. LINE 508570 TO 508548 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_36_P5_Harrison | Single phase fault with stuck relay near HARRISN4 (508544) 138 kV Bus a. Apply Fault at theHARRISN4 (508544) 138 kV Bus b. Clear fault after 24 cycles and trip the faulted elements: b.1. LINE 508544 TO 508548 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_37_P5_NWHenderson | Single phase fault with stuck relay near NWHENDR4 (509076) 138 kV Bus a. Apply Fault at theNWHENDR4 (509076) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509076 TO 509077 CKT 1 b.2. LINE 509077 TO 509078 CKT 1 b.3. LOAD 1 509077 b.4. LOAD 1 509078 b.5. DISCONNECT 509077 b.6. DISCONNECT 509078 b.7. LINE 509078 TO 508548 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_92_P5_36th&Lewis | Single phase fault with stuck relay near 36LEWIS4 (509800) 138 kV Bus a. Apply Fault at the36LEWIS4 (509800) 138 kV Bus b. Clear fault after 65 cycles and trip the faulted elements: b.1. LINE 509800 TO 509788 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_93_P5_Riverside | Single phase fault with stuck relay near R.S.S.-4 (509783) 138 kV Bus a. Apply Fault at theR.S.S.-4 (509783) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 509783 TO 509814 CKT 1 b.2. LOAD 1 509856 b.3. LOAD 1 509859 b.4. DISCONNECT 509814 b.5. DISCONNECT 509856 b.6. DISCONNECT 509859 b.7. LINE 509814 TO 509788 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_94_P5_72nd&Elwood | Single phase fault with stuck relay near 72ELWOD4 (509888) 138 kV Bus a. Apply Fault at the72ELWOD4 (509888) 138 kV Bus b. Clear fault after 45 cycles and trip the faulted elements: b.1. LINE 509888 TO 509788 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_95_P5_Carson | Single phase fault with stuck relay near CARSN-S4 (509756) 138 kV Bus a. Apply Fault at theCARSN-S4 (509756) 138 kV Bus b. Clear fault after 4 cycles and trip the faulted elements: b.1. LINE 509756 TO 509788 CKT 1 b.2. LOAD 1 509742 b.3. LOAD 1 509756 b.4. LOAD 1 509777 b.5. DISCONNECT 509742 b.6. DISCONNECT 509756 b.7. DISCONNECT 509777 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_96_P5_SapulpaRd | Single phase fault with stuck relay near SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at theSAPLPRD4 (509871) 138 kV Bus b. Clear fault after 33 cycles and trip the faulted elements: b.1. LINE 509871 TO 509848 CKT 1 b.2. LOAD 1 509727 b.3. DISCONNECT 509727 b.4. DISCONNECT 509848 b.5. LINE 509848 TO 509788 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_97_P5_36th&Olympia | Single phase fault with stuck relay near 36&OLY-4 (509724) 138 kV Bus a. Apply Fault at the36&OLY-4 (509724) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509724 TO 509788 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_98_P5_Claremore | Single phase fault with stuck relay near CLARMR 4 (512707) 138 kV Bus a. Apply Fault at theCLARMR 4 (512707) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 513124 TO 512707 CKT 1 b.2. DISCONNECT 513124 b.3. LINE 510396 TO 513124 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT_AEPW_2022_99_P5_Anadarko | Single phase fault with stuck relay near ANADARK4 (520814) 138 kV Bus a. Apply Fault at theANADARK4 (520814) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 520814 TO 511477 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT__AEPW-2022-90-P5-TulsaNorth | Sngle phase fault with stuck relay near Tulsa North (509817) 138 kV Bus a. Apply Fault at the Tulsa North (509817) 138 kV Bus b. Run fault for 23 cycles and trip faulted elements b.1. LINE FROM BUS 509842 TO BUS 509784 CKT 1 c. Run fault for 4 cycles and trip faulted elements c.1. LINE FROM BUS 509863 TO BUS 509801 CKT 1 c.2. LINE FROM BUS 509844 TO BUS 509860 CKT 1 c.3. DISCONNECT BUS 509894 d. Run fault for 5 cycles and trip faulted elements d.1. LINE FROM BUS 509839 TO BUS 509887 CKT 1 e. Run fault for 4 cycles and trip faulted elements e.1. LINE FROM BUS 509851 TO BUS 509757 CKT 1 f. Run fault for 1 cycles and trip faulted elements f.1. LINE FROM BUS 509817 TO BUS 510396 CKT 1 g. Clear fault after 11 cycles and trip the faulted elements g.1. LINE FROM BUS 509884 TO BUS 510388 CKT 1 g.2. LOAD 1 BUS 509714 g.3.LOAD 1 BUS 509715 g.4. LOAD 1 BUS 509726 g.5. LOAD 1 BUS 509743 g.6. LOAD 1 BUS 509805 g.7. LOAD 1 BUS 509817 g.8. LOAD 1 BUS 509818 g.9. LOAD 1 BUS 509822 g.10. LOAD 1 BUS 509825 g.11. LOAD 1 BUS 509837 g.12. LOAD 1 BUS 509840 g.13. LOAD 1 BUS 509884 g.14. DISCONNECT BUS 509714 g.15. DISCONNECT BUS 509715 g.16 DISCONNECT BUS 509726 g.17. DISCONNECT BUS 509743 g.18. DISCONNECT BUS 509746 g.19. DISCONNECT BUS 509805 g.20. DISCONNECT BUS 509817 g.21. DISCONNECT BUS 509818 g.22. DISCONNECT BUS 509822 g.23. DISCONNECT BUS 509825 g.24. DISCONNECT BUS 509837 g.25. DISCONNECT BUS 509839 g.26. DISCONNECT BUS 509840 g.27. DISCONNECT BUS 509842 g.28. DISCONNECT BUS 509844 g.29. DISCONNECT BUS 509851 g.30. DISCONNECT BUS 509862 g.31. DISCONNECT BUS 509863 g.32. DISCONNECT BUS 509884 g.33. DISCONNECT BUS 509900 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-028 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-028 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT__AEPW-2022-91-P5-TulsaSoutheast | Sngle phase fault with stuck relay near Tulsa SouthEast (509811) 138 kV Bus a. Apply Fault at the Tulsa SouthEast (509811) 138 kV Bus b. Run fault for 27 cycles and trip faulted elements b.1. LINE FROM BUS 509811 TO BUS 509831 CKT 1 b.2. LINE FROM BUS 509811 TO BUS 509833 CKT 1 c. Run fault for 3 cycles and trip faulted elements c.1. LINE FROM BUS 509781 TO BUS 509718 CKT 1 d. Run fault for 4 cycles and trip faulted elements d.1. LINE FROM BUS 509763 TO BUS 509772 CKT 1 e. Run fault for 4 cycles and trip faulted elements e.1. LINE FROM BUS 509765 TO BUS 509855 CKT 1 f. Run fault for 4 cycles and trip faulted elements f.1. LINE FROM BUS 509785 TO BUS 509891 CKT 1 g. Clear fault after 9 cycles and trip the faulted elements g.1. LINE FROM BUS 509776 TO BUS 509800 CKT 1 g.2. LOAD 1 BUS 509716 g.3. LOAD 1 BUS 509717 g.4. LOAD 1 BUS 509728 g.5. LOAD 1 BUS 509733 g.6. LOAD 1 BUS 509734 g.7. LOAD 1 BUS 509735 g.8. LOAD 1 BUS 509744 g.9. LOAD 1 BUS 509760 g.10. LOAD 1 BUS 509761 g.11. LOAD 1 BUS 509774 g.12. LOAD 1 BUS 509779 g.13. LOAD 1 BUS 509780 g.14. LOAD 1 BUS 509797 g.15. LOAD 1 BUS 509808 g.16. LOAD 1 BUS 509811 g.17. LOAD 1 BUS 509824 g.18. LOAD 1 BUS 509826 g.19. LOAD 1 BUS 509827 g.20. LOAD 1 BUS 509829 g.21. LOAD 1 BUS 509861 g.22. LOAD 1 BUS 509886 g.23. DISCONNECT BUS 509716 g.24. DISCONNECT BUS 509717 g.25. DISCONNECT BUS 509718 g.26. DISCONNECT BUS 509728 g.27. DISCONNECT BUS 509733 g.28. DISCONNECT BUS 509734 g.29. DISCONNECT BUS 509735 g.30. DISCONNECT BUS 509744 g.31. DISCONNECT BUS 509760 g.32. DISCONNECT BUS 509761 g.33. DISCONNECT BUS 509762 g.34. DISCONNECT BUS 509763 g.35. DISCONNECT BUS 509765 g.36. DISCONNECT BUS 509771 g.37. DISCONNECT BUS 509774 g.38. DISCONNECT BUS 509776 g.39. DISCONNECT BUS 509779 g.40. DISCONNECT BUS 509780 g.41. DISCONNECT BUS 509785 g.42. DISCONNECT BUS 509797 g.43. DISCONNECT BUS 509808 g.44. DISCONNECT BUS 509811 g.45. DISCONNECT BUS 509820 g.46. DISCONNECT BUS 509824 g.47. DISCONNECT BUS 509826 g.48. DISCONNECT BUS 509827 g.49. DISCONNECT BUS 509828 g.50. DISCONNECT BUS 509829 g.51. DISCONNECT BUS 509830 g.52. DISCONNECT BUS 509861 g.53. DISCONNECT BUS 509873 g.54. DISCONNECT BUS 509886 g.55. LINE FROM BUS 509771 TO BUS 509790 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT__OKGE-All-36-P5_1-INGLEWD4 | Sngle phase fault with stuck relay near INGLEWD (515060) 138 kV Bus a. Apply Fault at the INGLEWD (515060) 138 kV Bus b. Run fault for 37.98 cycles and trip faulted elements b.1. LINE FROM BUS 515060 TO BUS 515059 CKT 1 c. Run fault for 19.98 cycles and trip faulted elements c.1. LINE FROM BUS 515060 TO BUS 515059 CKT 1 d. Run fault for 37.98 cycles and trip faulted elements d.1. LINE FROM BUS 515060 TO BUS 515059 CKT 1 e. Run fault for 56.46 cycles and trip faulted elements e.1. LINE FROM BUS 514941 TO BUS 515480 CKT 1 f. Run fault for 19.98 cycles and trip faulted elements f.1. LINE FROM BUS 514941 TO BUS 515480 CKT 1 g. Run fault for 97.80 cycles g.1. CLOSE LINE FROM BUS 515442 TO BUS 515046 CKT 1 h. Run fault for 16.62 cycles and trip faulted elements h.1. LINE FROM BUS 514941 TO BUS 515480 CKT 1 i. Run fault for 27.60 cycles and trip faulted elements i.1. LINE FROM BUS 514973 TO BUS 514884 CKT 1 j. Run fault for 6.60 cycles and trip faulted elements j.1. LINE FROM BUS 514973 TO BUS 514964 CKT 1 k. Run fault for 6.00 cycles and trip faulted elements k.1. LINE FROM BUS 514993 TO BUS 514941 CKT 1 l. Run fault for 7.38 cycles and trip faulted elements l.1. LINE FROM BUS 514973 TO BUS 514884 CKT 1 m. Run fault for 6.60 cycles m.1. CLOSE LINE FROM BUS 514973 TO BUS 514964 CKT 1 n. Run fault for 6.00 cycles n.1. CLOSE LINE FROM BUS 514993 TO BUS 514941 CKT 1 o. Run fault for 21.00 cycles and trip faulted elements o.1. LINE FROM BUS 515442 TO BUS 515046 CKT 1 p. Run fault for 30.6 cycles and trip faulted elements p.1. LINE FROM BUS 514973 TO BUS 514884 CKT 1 q. Run fault for 13.20 cycles and trip faulted elements q.1. LINE FROM BUS 514973 TO BUS 514964 CKT 1 r. Run fault for 12.00 cycles and trip faulted elements r.1. LINE FROM BUS 514993 TO BUS 514941 CKT 1 s. Run fault for 20.82 cycles and trip faulted elements s.1. LINE FROM BUS 514941 TO BUS 514906 CKT 1 t. Run fault for 19.98 cycles t.1. CLOSE LINE FROM BUS 514941 TO BUS 514906 CKT 1 u. Run fault for 57.42 cycles and trip faulted elements u.1. LINE FROM BUS 514927 TO BUS 514937 CKT 1 v. Clear fault after 60.00 cycles and trip the faulted elements v.1. LINE FROM BUS 514941 TO BUS 514906 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-029 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-029 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT__OKGE-All-37-P5_2-TARBY5 | Sngle phase fault with stuck relay near TARBY5 (515264) 161 kV Bus a. Apply Fault at the TARBY5 (515264) 161 kV Bus b. Run fault for 24 cycles and trip faulted elements b.1. LINE FROM BUS 515259 TO BUS 515275 CKT 1 b.2. LINE FROM BUS 515259 TO BUS 515260 CKT 1 c. Run fault for 34 cycles and trip faulted elements c.1. LINE FROM BUS 515262 TO BUS 515264 CKT 1 d. Run fault for 34 cycles and d.1. CLOSE LINE FROM BUS 515259 TO BUS 515275 CKT 1 d.2. CLOSE LINE FROM BUS 515259 TO BUS 515260 CKT 1 e. Run fault for 59 cycles and trip faulted elements e.1. LINE FROM BUS 515259 TO BUS 515275 CKT 1 e.2. LINE FROM BUS 515259 TO BUS 515260 CKT 1 f. Run fault for 80 cycles and trip faulted elements f.1. LINE FROM BUS 515282 TO BUS 515276 CKT 1 g. Run fault for 90 cycles and g.1. CLOSE LINE FROM BUS 515282 TO BUS 515276 CKT 1 h. Run fault for 126 cycles and trip faulted elements h.1. LINE FROM BUS 515263 TO BUS 515272 CKT 1 i. Run fault for 136 cycles and i.1. CLOSE LINE FROM BUS 515263 TO BUS 515272 CKT 1 j. Run fault for 170 cycles and trip faulted elements j.1. LINE FROM BUS 515282 TO BUS 515276 CKT 1 k. Run fault for 185 cycles and trip faulted elements k.1. LINE FROM BUS 515264 TO BUS 515265 CKT 1 l. Run fault for 195 cycles and l.1. CLOSE LINE FROM BUS 515264 TO BUS 515265 CKT 1 m. Run fault for 262 cycles and trip faulted elements m.1. LINE FROM BUS 515263 TO BUS 515272 CKT 1 n. Clear fault after 380 cycles and trip faulted elements n.1. LINE FROM BUS 515264 TO BUS 515265 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT__OKGE-All-38-P5_2-WINDFRM4 | Sngle phase fault with stuck relay near WINDFRM4 (515785) 138 kV Bus a. Apply Fault at the WINDFRM4 (515785) 138 kV Bus b. Run fault for 27 cycles and trip faulted elements b.1. LINE FROM BUS 515785 TO BUS 515786 CKT 1 b.2. LINE FROM BUS 514785 TO BUS 515785 CKT 1 b.3. LINE FROM BUS 515785 TO BUS 520999 CKT 1 c. Run fault for 37.02 cycles and c.1. CLOSE LINE FROM BUS 515785 TO BUS 515786 CKT 1 c.2. CLOSE LINE FROM BUS 514785 TO BUS 515785 CKT 1 c.3. CLOSE LINE FROM BUS 515785 TO BUS 520999 CKT 1 d. Clear fault after 64.02 cycles and trip faulted elements d.1. LINE FROM BUS 515785 TO BUS 515786 CKT 1 d.2. LINE FROM BUS 514785 TO BUS 515785 CKT 1 d.3. LINE FROM BUS 515785 TO BUS 520999 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT__AEPW-2022-11-P5-Lieberman | Sngle phase fault with stuck relay near Lieberman (508806) 138 kV Bus a. Apply Fault at the Lieberman (508806) 138 kV Bus b. Run fault for 23 cycles and trip faulted elements b.1. LINE FROM BUS 508806 TO BUS 507711 CKT 1 c. Run fault for 4 cycles and trip faulted elements c.1. LINE FROM BUS 508833 TO BUS 508835 CKT 1 c.2. LINE FROM BUS 507772 TO BUS 507751 CKT 1 d. Run fault for 3 cycles and trip faulted elements d.1. LINE FROM BUS 508806 TO BUS 508833 CKT 1 e. Run fault for 4 cycles and trip faulted elements e.1. LINE FROM BUS 508806 TO BUS 508808 CKT 1 f. Run fault for 26 cycles and trip faulted elements f.1. LINE FROM BUS 508812 TO BUS 508815 CKT 1 g. Clear fault after 67 cycles and trip faulted elements f.1. LINE FROM BUS 508805 TO BUS 508801 CKT 1 f.2. DROP GENERATOR 1 BUS 509401 f.3. DROP GENERATOR 1 BUS 509402 f.4. DROP LOAD 1 BUS 508805 f.5. DROP LOAD 1 BUS 508812 f.6. DROP LOAD 1 BUS 508833 f.7. DROP LOAD S1 BUS 509401 f.8. DROP LOAD S1 BUS 509402 f.9. DISCONNECT BUS 508805 f.10. DISCONNECT BUS 508806 f.11. DISCONNECT BUS 508812 f.12. DISCONNECT BUS 508820 f.13. DISCONNECT BUS 508821 f.14. DISCONNECT BUS 508822 f.15. DISCONNECT BUS 508833 f.16. DISCONNECT BUS 509401 f.17. DISCONNECT BUS 509402 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT__AEPW-2022-13-P5-SugarHill | Sngle phase fault with stuck relay near SugarHill (508080) 138 kV Bus a. Apply Fault at the SugarHill (508080) 138 kV Bus b. Run fault for 23 cycles and trip faulted elements b.1. LINE FROM BUS 508080 TO BUS 507454 CKT 1 c. Run fault for 3 cycles and trip faulted elements c.1. LINE FROM BUS 508082 TO BUS 508085 CKT 1 d. Run fault for 7 cycles and trip faulted elements d.1. LINE FROM BUS 508080 TO BUS 508071 CKT 1 e. Run fault for 55 cycles and trip faulted elements e.1. LINE FROM BUS 508073 TO BUS 508053 CKT 1 f. Run fault for 18 cycles and trip faulted elements f.1. LINE FROM BUS 508081 TO BUS 508084 CKT 1 g. Clear fault after 56 cycles and trip faulted elements f.1. LINE FROM BUS 508051 TO BUS 507429 CKT 1 f.2. DROP LOAD A1 BUS 504109 f.3. DROP LOAD 1 BUS 508051 f.4. DROP LOAD 1 BUS 508073 f.5. DROP LOAD 1 BUS 508076 f.6. DROP LOAD 1 BUS 508080 f.7. DROP LOAD 1 BUS 508094 f.8. DISCONNECT BUS 504109 f.9. DISCONNECT BUS 508051 f.10. DISCONNECT BUS 508066 f.11. DISCONNECT BUS 508073 f.12. DISCONNECT BUS 508076 f.13. DISCONNECT BUS 508079 f.14. DISCONNECT BUS 508080 f.15. DISCONNECT BUS 508081 f.16. DISCONNECT BUS 508082 f.17. DISCONNECT BUS 508094 f.18 DISCONNECT BUS 508103 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT__AEPW-2022-14-P5-FtHumbug | Sngle phase fault with stuck relay near FtHumbug (507731) 138 kV Bus a. Apply Fault at the FtHumbug (507731) 138 kV Bus b. Run fault for 21 cycles and trip faulted elements b.1. LINE FROM BUS 507731 TO BUS 507711 CKT 1 c. Run fault for 3 cycles and trip faulted elements c.1. LINE FROM BUS 507731 TO BUS 507763 CKT 1 d. Run fault for 33 cycles and trip faulted elements d.1. LINE FROM BUS 507730 TO BUS 507716 CKT 1 e. Run fault for 1 cycles and trip faulted elements e.1. LINE FROM BUS 507735 TO BUS 507755 CKT 1 f. Clear fault after 2 cycles and trip faulted elements f.1. LINE FROM BUS 507722 TO BUS 507717 CKT 1 f.2. DROP LOAD 1 BUS 507722 f.3. DROP LOAD 1 BUS 507730 f.4. DROP LOAD 1 BUS 507735 f.5. DROP LOAD 1 BUS 507746 f.6. DISCONNECT BUS 507722 f.7. DISCONNECT BUS 507730 f.8. DISCONNECT BUS 507731 f.9. DISCONNECT BUS 507735 f.10. DISCONNECT BUS 507746 f.11. DISCONNECT BUS 507753 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT__AEPW-2022-85-P5-LES | Sngle phase fault with stuck relay near LES (511467) 138 kV Bus a. Apply Fault at the FtHumbug (507731) 138 kV Bus b. Run fault for 27 cycles and trip faulted elements b.1. LINE FROM BUS 511437 TO BUS 511494 CKT 1 b.2. LINE FROM BUS 511512 TO BUS 511439 CKT 1 b.3. LINE FROM BUS 511477 TO BUS 511563 CKT 1 c. Run fault for 12 cycles and trip faulted elements c.1. LINE FROM BUS 529304 TO BUS 511494 CKT 1 d. Run fault for 15 cycles and trip faulted elements d.1. DISCONNECT BUS 511415 e. Run fault for 1 cycles and trip faulted elements e.1. DISCONNECT BUS 511416 f. Run fault for 2 cycles and trip faulted elements f.1. LINE FROM BUS 511474 TO BUS 511467 CKT 1 g. Run fault for 6 cycles and trip faulted elements g.1. DISCONNECT BUS 511411 h. Run fault for 2 cycles and trip faulted elements h.1. LINE FROM BUS 511437 TO BUS 511467 CKT 1 i. Run fault for 7 cycles and trip faulted elements i.1. DISCONNECT BUS 511414 j. Run fault for 24 cycles and trip faulted elements j.1. INE FROM BUS 511467 TO BUS 511486 CKT 1 k. Clear fault after 15 cycles and trip faulted elements k.1. LINE FROM BUS 511477 TO BUS 511421 CKT 1 k.2. DROP LOAD 1 BUS 511422 k.3. DROP LOAD 1 BUS 511431 k.4. DROP LOAD 1 BUS 511467 k.5. DISCONNECT BUS 511422 k.6. DISCONNECT BUS 511423 k.7. DISCONNECT BUS 511431 k.8. DISCONNECT BUS 511439 k.9. DISCONNECT BUS 511494 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-097 trips on voltage protection settings | Disabling voltage protection settings for GEN-2016-097 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT__AEPW-2022-86-P5-Oneta | Sngle phase fault with stuck relay near Oneta (509807) 345 kV Bus a. Apply Fault at the Oneta (509807) 345 kV Bus b. Run fault for 26 cycles and trip faulted elements b.1. LINE FROM BUS 509807 TO BUS 509836 CKT 1 b.2. LINE FROM BUS 509807 TO BUS 509836 CKT 2 b.3. INE FROM BUS 509807 TO BUS 509782 CKT 1 c. Run fault for 18 cycles and trip faulted elements c.1. LINE FROM BUS 509807 TO BUS 509745 CKT 1 d. Run fault for 1 cycles and trip faulted elements d.1. LINE FROM BUS 509807 TO BUS 510406 CKT 1 e. Clear fault after 35 cycles and trip faulted elements e.1. LINE FROM BUS 509806 TO BUS 509891 CKT 1 e.2. LINE FROM BUS 509806 TO BUS 509869 CKT 1 e.3. LINE FROM BUS 509806 TO BUS 509769 CKT 1 e.4. LINE FROM BUS 509806 TO BUS 509786 CKT 1 e.5. LINE FROM BUS 509806 TO BUS 509768 CKT 1 e.6. DROP GENERATOR 1 BUS 511938 e.7. DROP GENERATOR 1 BUS 511939 e.8. DROP GENERATOR 1 BUS 511940 e.9. DROP GENERATOR 1 BUS 511941 e.10. DROP GENERATOR 1 BUS 511942 e.11. DROP GENERATOR 1 BUS 511943 e.12. DROP LOAD 1 BUS 509806 e.13. DROP LOAD S1 BUS 511940 e.14. DROP LOAD S1 BUS 511943 e.15. DISCONNECT BUS 509806 e.16. DISCONNECT BUS 509807 e.17. DISCONNECT BUS 509836 e.18. DISCONNECT BUS 509868 e.19. DISCONNECT BUS 509874 e.20. DISCONNECT BUS 509881 e.21. DISCONNECT BUS 511938 e.22. DISCONNECT BUS 511939 e.23. DISCONNECT BUS 511940 e.24. DISCONNECT BUS 511941 e.25. DISCONNECT BUS 511942 e.26. DISCONNECT BUS 511943 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-024, GEN-2018-027, GEN-2018-028 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-024, GEN-2018-027, GEN-2018-028 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT__AEPW-2022-88-P5-TPS | Sngle phase fault with stuck relay near TPS (509788) 138 kV Bus a. Apply Fault at the TPS (509788) 138 kV Bus b. Run fault for 16 cycles and trip faulted elements b.1. LINE FROM BUS 509788 TO BUS 509724 CKT 1 c. Run fault for 15 cycles and trip faulted elements c.1. LINE FROM BUS 509788 TO BUS 509800 CKT 1 d. Run fault for 2 cycles and trip faulted elements d.1. LINE FROM BUS 509850 TO BUS 509783 CKT 1 d.2. LINE FROM BUS 509848 TO BUS 509871 CKT 1 e. Run fault for 2 cycles and trip faulted elements e.1. LINE FROM BUS 509788 TO BUS 509888 CKT 1 f. Run fault for 18 cycles and trip faulted elements f.1. LINE FROM BUS 509814 TO BUS 509783 CKT 1 g. Clear fault after 195 cycles and trip faulted elements g.1. DISCONNECT BUS 509880 g.2. DROP GENERATOR 1 BUS 509890 g.3. DROP GENERATOR 1 BUS 511854 g.4. DROP GENERATOR 1 BUS 511858 g.5. DROP LOAD 1 BUS 509727 g.6. DROP LOAD 1 BUS 509742 g.7. DROP LOAD 1 BUS 509750 g.8. DROP LOAD 1 BUS 509751 g.9. DROP LOAD 1 BUS 509756 g.10. DROP LOAD 1 BUS 509777 g.11. DROP LOAD 1 BUS 509788 g.12. DROP LOAD 1 BUS 509789 g.13. DROP LOAD 1 BUS 509795 g.14. DROP LOAD 1 BUS 509846 g.15. DROP LOAD 1 BUS 509856 g.16. DROP LOAD 1 BUS 509859 g.17. DROP LOAD S1 BUS 511854 g.18. DROP LOAD S1 BUS 511858 g.19. DISCONNECT BUS 509727 g.20. DISCONNECT BUS 509742 g.21. DISCONNECT BUS 509750 g.22. DISCONNECT BUS 509751 g.23. DISCONNECT BUS 509756 g.24. DISCONNECT BUS 509777 g.25. DISCONNECT BUS 509795 g.26. DISCONNECT BUS 509814 g.27. DISCONNECT BUS 509846 g.28. DISCONNECT BUS 509848 g.29. DISCONNECT BUS 509850 g.30. DISCONNECT BUS 509856 g.31. DISCONNECT BUS 509859 g.32. DISCONNECT BUS 509890 g.33. DISCONNECT BUS 511854 g.34. DISCONNECT BUS 511858 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on voltage protection settings | Disabling voltage protection settings for GEN-2018-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted
04 SOUTHEAST | DISIS-2018-001 | 25W | Transfer | FAULT__AEPW-2022-89-P5-Weleetka | Sngle phase fault with stuck relay near Weleetka (510902) 138 kV Bus a. Apply Fault at the Weleetka (510902) 138 kV Bus b. Run fault for 18 cycles and trip faulted elements b.1. LINE FROM BUS 510921 TO BUS 510908 CKT 1 c. Run fault for 6 cycles and trip faulted elements c.1. LINE FROM BUS 510877 TO BUS 510948 CKT 1 d. Run fault for 3 cycles and trip faulted elements d.1. LINE FROM BUS 510902 TO BUS 505592 CKT 1 e. Run fault for 6 cycles and trip faulted elements e.1. LINE FROM BUS 510902 TO BUS 510892 CKT 1 f. Run fault for 24 cycles and trip faulted elements f.1. LINE FROM BUS 515078 TO BUS 510877 CKT 1 g. Clear fault after 5 cycles and trip faulted elements g.1. LINE FROM BUS 510923 TO BUS 510898 CKT 1 | P5_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_112GORE4__LAIRGST4 | 3 Phase fault 112GORE4 (511488) 138 kV Bus a. Apply fault at the 112GORE4 (511488) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 138 KV 511488 TO LAIRGST4 138 KV 511510 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_112GORE4__RPPAPER4 | 3 Phase fault 112GORE4 (511488) 138 kV Bus a. Apply fault at the 112GORE4 (511488) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 138 KV 511488 TO RPPAPER4 138 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_2CARNEY__2LUTHER | 3 Phase fault 2CARNEY (300834) 69 kV Bus a. Apply fault at the 2CARNEY (300834) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CARNEY 69 KV 300834 TO 2LUTHER 69 KV 300856 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_2COLINS__COLNSGR2 | 3 Phase fault 2COLINS (300992) 69 kV Bus a. Apply fault at the 2COLINS (300992) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2COLINS 69 KV 300992 TO COLNSGR2 69 KV 512870 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_2MERIDAN__2LUTHER | 3 Phase fault 2MERIDAN (300839) 69 kV Bus a. Apply fault at the 2MERIDAN (300839) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MERIDAN 69 KV 300839 TO 2LUTHER 69 KV 300856 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_2OWASSO__COLNSGR2 | 3 Phase fault 2OWASSO (300998) 69 kV Bus a. Apply fault at the 2OWASSO (300998) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2OWASSO 69 KV 300998 TO COLNSGR2 69 KV 512870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_2OWASSO__DAWSON | 3 Phase fault 2OWASSO (300998) 69 kV Bus a. Apply fault at the 2OWASSO (300998) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2OWASSO 69 KV 300998 TO DAWSON-2 69 KV 509791 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_2VERA__COLNSGR2 | 3 Phase fault 2VERA (301006) 69 kV Bus a. Apply fault at the 2VERA (301006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2VERA 69 KV 301006 TO COLNSGR2 69 KV 512870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_36&MER_4__HOBBYLO4 | 3 Phase fault 36&MER 4 (514888) 138 kV Bus a. Apply fault at the 36&MER 4 (514888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 36&MER 4 138 KV 514888 TO HOBBYLO4 138 KV 515338 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_36&MER_4__SW_5TH_4 | 3 Phase fault 36&MER 4 (514888) 138 kV Bus a. Apply fault at the 36&MER 4 (514888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 36&MER 4 138 KV 514888 TO SW 5TH 4 138 KV 514920 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_38TH_ST2__BETHANY2 | 3 Phase fault 38TH ST2 (514845) 69 kV Bus a. Apply fault at the 38TH ST2 (514845) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 38TH ST2 69 KV 514845 TO BETHANY2 69 KV 514914 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_38TH_ST4__HEFNER_4 | 3 Phase fault 38TH ST4 (514846) 138 kV Bus a. Apply fault at the 38TH ST4 (514846) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TULSA 4 138 KV 514847 TO HEFNER 4 138 KV 514848 CKT 1 b.2. 38TH ST4 138 KV 514846 TO TULSA 4 138 KV 514847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_38TH_ST4__TULSA__4 | 3 Phase fault 38TH ST4 (514846) 138 kV Bus a. Apply fault at the 38TH ST4 (514846) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 38TH ST4 138 KV 514846 TO TULSA 4 138 KV 514847 CKT 1 b.2. LOAD 1 514847 b.3. TULSA 4 138 KV 514847 TO HEFNER 4 138 KV 514848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_3ADA_LA__3MINDEN_LA! | 3 Phase fault 3ADA_LA (337360) 115 kV Bus a. Apply fault at the 3ADA_LA (337360) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3ADA_LA 115 KV 337360 TO 3MINDEN_LA! 115 KV 337361 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_3EL_DORADO!__3ELDORADO.E! | 3 Phase fault 3EL DORADO! (337539) 115 kV Bus a. Apply fault at the 3EL DORADO! (337539) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3EL DORADO! 115 KV 337539 TO 3ELDORADO.E! 115 KV 337553 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_3EL_DORADO!__3ELD_DONAN | 3 Phase fault 3EL DORADO! (337539) 115 kV Bus a. Apply fault at the 3EL DORADO! (337539) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3EL DORADO! 115 KV 337539 TO 3ELD DONAN 115 KV 337540 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_3EL_DORADO!__3ELD_QUINN | 3 Phase fault 3EL DORADO! (337539) 115 kV Bus a. Apply fault at the 3EL DORADO! (337539) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3EL DORADO! 115 KV 337539 TO 3ELD QUINN 115 KV 337560 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_3KERLIN+__3EMERSON! | 3 Phase fault 3KERLIN+ (337524) 115 kV Bus a. Apply fault at the 3KERLIN+ (337524) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3KERLIN+ 115 KV 337524 TO 3EMERSON! 115 KV 337526 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_3MINDEN_LA!__3LA_ORD_PLNT | 3 Phase fault 3MINDEN_LA! (337361) 115 kV Bus a. Apply fault at the 3MINDEN_LA! (337361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MINDEN_LA! 115 KV 337361 TO 3LA_ORD_PLNT 115 KV 337362 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_3MINDEN_LA!__3SAREPTA! | 3 Phase fault 3MINDEN_LA! (337361) 115 kV Bus a. Apply fault at the 3MINDEN_LA! (337361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MINDEN_LA! 115 KV 337361 TO 3SAREPTA! 115 KV 337363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_3MINDEN_LA!__MINDEN | 3 Phase fault 3MINDEN_LA! (337361) 115 kV Bus a. Apply fault at the 3MINDEN_LA! (337361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MINDEN_LA! 115 KV 337361 TO MINDEN-3 115 KV 507788 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_3MINDEN_LG__3MINDEN_LA! | 3 Phase fault 3MINDEN_LG (303302) 115 kV Bus a. Apply fault at the 3MINDEN_LG (303302) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MINDEN_LG 115 KV 303302 TO 3MINDEN_LA! 115 KV 337361 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_3SAREPTA!__3CULLEN | 3 Phase fault 3SAREPTA! (337363) 115 kV Bus a. Apply fault at the 3SAREPTA! (337363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115 KV 337363 TO 3CULLEN 115 KV 337364 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_3SAREPTA!__3EMERSON! | 3 Phase fault 3SAREPTA! (337363) 115 kV Bus a. Apply fault at the 3SAREPTA! (337363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115 KV 337363 TO 3HAYNESVILLE 115 KV 337366 CKT 1 b.2. LOAD 1 337366 b.3. LOAD LG 337366 b.4. 3HAYNESVILLE 115 KV 337366 TO 3EMERSON! 115 KV 337526 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_3SAREPTA!__3SPRINGHILL | 3 Phase fault 3SAREPTA! (337363) 115 kV Bus a. Apply fault at the 3SAREPTA! (337363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115 KV 337363 TO 3SPRINGHILL 115 KV 337365 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_3SMACKOVER+__3EL_DORADO! | 3 Phase fault 3SMACKOVER+ (337537) 115 kV Bus a. Apply fault at the 3SMACKOVER+ (337537) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SMACKOVER+ 115 KV 337537 TO 3EL DORADO! 115 KV 337539 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_3SPRINGHILL__3TAYLOR | 3 Phase fault 3SPRINGHILL (337365) 115 kV Bus a. Apply fault at the 3SPRINGHILL (337365) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SPRINGHILL 115 KV 337365 TO 3TAYLOR 115 KV 337500 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_44&SUNL2__ELMCRK_2 | 3 Phase fault 44&SUNL2 (514979) 69 kV Bus a. Apply fault at the 44&SUNL2 (514979) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 44&SUNL2 69 KV 514979 TO ELMCRK 2 69 KV 514982 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_44&SUNL2__SUNNYLN2 | 3 Phase fault 44&SUNL2 (514979) 69 kV Bus a. Apply fault at the 44&SUNL2 (514979) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 44&SUNL2 69 KV 514979 TO SUNNYLN2 69 KV 514980 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_46ST | 3 Phase fault 46ST--E4 (509837) 138 kV Bus a. Apply fault at the 46ST--E4 (509837) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 46ST--E4 138 KV 509837 TO 46ST-TP-4 138 KV 509900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_4BRISTOW__4SILVCTY | 3 Phase fault 4BRISTOW (300137) 138 kV Bus a. Apply fault at the 4BRISTOW (300137) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4BRISTOW 138 KV 300137 TO 4SILVCTY 138 KV 300140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_4CLEVLND__4SFORKKTP | 3 Phase fault 4CLEVLND (300138) 138 kV Bus a. Apply fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138 KV 300138 TO 4JAVINE 138 KV 300996 CKT 1 b.2. LOAD 1 300996 b.3. LOAD 2 300996 b.4. 4JAVINE 138 KV 300996 TO 4SFORKKTP 138 KV 301339 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_4CLEVLND__4SILVCTY | 3 Phase fault 4CLEVLND (300138) 138 kV Bus a. Apply fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138 KV 300138 TO 4SILVCTY 138 KV 300140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_4CLEVLND__CLEVLND_4 | 3 Phase fault 4CLEVLND (300138) 138 kV Bus a. Apply fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138 KV 300138 TO CLEVLND 4 138 KV 512729 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_4CLEVLND__PAWNSW4 | 3 Phase fault 4CLEVLND (300138) 138 kV Bus a. Apply fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138 KV 300138 TO PAWNSW4 138 KV 512749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_4FAIRFAX__PAWNSW4 | 3 Phase fault 4FAIRFAX (300139) 138 kV Bus a. Apply fault at the 4FAIRFAX (300139) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FAIRFAX 138 KV 300139 TO PAWNSW4 138 KV 512749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_4FISHERTP__4SILVCTY | 3 Phase fault 4FISHERTP (300131) 138 kV Bus a. Apply fault at the 4FISHERTP (300131) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FISHERTP 138 KV 300131 TO 4SILVCTY 138 KV 300140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_4LUTHER__4MEMORALT | 3 Phase fault 4LUTHER (300135) 138 kV Bus a. Apply fault at the 4LUTHER (300135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4LUTHER 138 KV 300135 TO 4MEMORALT 138 KV 300136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_4LUTHER__4STROUD138 | 3 Phase fault 4LUTHER (300135) 138 kV Bus a. Apply fault at the 4LUTHER (300135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4LUTHER 138 KV 300135 TO 4LUTHERD 138 KV 301372 CKT 1 b.2. LOAD 1 301372 b.3. 4WARWICK 138 KV 300915 TO 4LUTHERD 138 KV 301372 CKT 1 b.4. LOAD 1 301372 b.5. 4STROUD138 138 KV 300914 TO 4WARWICK 138 KV 300915 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_4MEMORALT__4MEMORAL | 3 Phase fault 4MEMORALT (300136) 138 kV Bus a. Apply fault at the 4MEMORALT (300136) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MEMORALT 138 KV 300136 TO 4MEMORAL 138 KV 301541 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_4MEMORALT__JNSKAMO4 | 3 Phase fault 4MEMORALT (300136) 138 kV Bus a. Apply fault at the 4MEMORALT (300136) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MEMORALT 138 KV 300136 TO JNSKAMO4 138 KV 514906 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_4MURFBORO__SNASHVL4 | 3 Phase fault 4MURFBORO (337672) 138 kV Bus a. Apply fault at the 4MURFBORO (337672) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MURFBORO 138 KV 337672 TO SNASHVL4 138 KV 507434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_4SFORKK__4SFORKKTP | 3 Phase fault 4SFORKK (300165) 138 kV Bus a. Apply fault at the 4SFORKK (300165) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SFORKK 138 KV 300165 TO 4SFORKKTP 138 KV 301339 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_4SILVCTY__4STILWTR | 3 Phase fault 4SILVCTY (300140) 138 kV Bus a. Apply fault at the 4SILVCTY (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY 138 KV 300140 TO 4STILWTR 138 KV 300141 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_4SILVCTY__SILVCTYGR4 | 3 Phase fault 4SILVCTY (300140) 138 kV Bus a. Apply fault at the 4SILVCTY (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY 138 KV 300140 TO SILVCTYGR4 138 KV 512726 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_4SKIAETP__4SFORKKTP | 3 Phase fault 4SKIAETP (300146) 138 kV Bus a. Apply fault at the 4SKIAETP (300146) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SKIAETP 138 KV 300146 TO 4SFORKKTP 138 KV 301339 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_4SKIAETP__COLLINS4 | 3 Phase fault 4SKIAETP (300146) 138 kV Bus a. Apply fault at the 4SKIAETP (300146) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SKIAETP 138 KV 300146 TO COLLINS4 138 KV 512705 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_4STROUDDIST__4STROUD138 | 3 Phase fault 4STROUDDIST (300838) 138 kV Bus a. Apply fault at the 4STROUDDIST (300838) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STROUDDIST 138 KV 300838 TO 4STROUD138 138 KV 300914 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_52DEL | 3 Phase fault 52DEL-W4 (509856) 138 kV Bus a. Apply fault at the 52DEL-W4 (509856) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 52DEL-W4 138 KV 509856 TO S HILLW4 138 KV 509859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_52DELTP4__T.P.S. | 3 Phase fault 52DELTP4 (509776) 138 kV Bus a. Apply fault at the 52DELTP4 (509776) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 52DELTP4 138 KV 509776 TO 36LEWIS4 138 KV 509800 CKT 1 b.2. LOAD 1 509800 b.3. T.P.S.-4 138 KV 509788 TO 36LEWIS4 138 KV 509800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_52DELTP4__T.S.E. | 3 Phase fault 52DELTP4 (509776) 138 kV Bus a. Apply fault at the 52DELTP4 (509776) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 52DELTP4 138 KV 509776 TO T.S.E.-4 138 KV 509811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_52DELTP4__ZUNIS | 3 Phase fault 52DELTP4 (509776) 138 kV Bus a. Apply fault at the 52DELTP4 (509776) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 52DELTP4 138 KV 509776 TO ZUNIS-S4 138 KV 509826 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_52DELWT4__S_HILLW4 | 3 Phase fault 52DELWT4 (509814) 138 kV Bus a. Apply fault at the 52DELWT4 (509814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 52DELWT4 138 KV 509814 TO S HILLW4 138 KV 509859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_53CACHE4__ARTVLTP4 | 3 Phase fault 53CACHE4 (511509) 138 kV Bus a. Apply fault at the 53CACHE4 (511509) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53CACHE4 138 KV 511509 TO ARTVLTP4 138 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_53GARNT4__77MEMTP4 | 3 Phase fault 53GARNT4 (509762) 138 kV Bus a. Apply fault at the 53GARNT4 (509762) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARNT4 138 KV 509762 TO 77MEMTP4 138 KV 509765 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_53GARNT4__T.S.E. | 3 Phase fault 53GARNT4 (509762) 138 kV Bus a. Apply fault at the 53GARNT4 (509762) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARNT4 138 KV 509762 TO T.S.E.-4 138 KV 509811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_53GARN_4__53GARNT4 | 3 Phase fault 53GARN 4 (509734) 138 kV Bus a. Apply fault at the 53GARN 4 (509734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARN 4 138 KV 509734 TO 53GARNT4 138 KV 509762 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_53GARST4__53GARNS4 | 3 Phase fault 53GARST4 (509763) 138 kV Bus a. Apply fault at the 53GARST4 (509763) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARST4 138 KV 509763 TO 53GARNS4 138 KV 509774 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_53GARST4__FORD | 3 Phase fault 53GARST4 (509763) 138 kV Bus a. Apply fault at the 53GARST4 (509763) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARST4 138 KV 509763 TO FORD---4 138 KV 509772 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_53GARST4__T.S.E. | 3 Phase fault 53GARST4 (509763) 138 kV Bus a. Apply fault at the 53GARST4 (509763) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARST4 138 KV 509763 TO T.S.E.-4 138 KV 509811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_5CDRCRST__TAHLQH_5 | 3 Phase fault 5CDRCRST (301344) 161 kV Bus a. Apply fault at the 5CDRCRST (301344) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CDRCRST 161 KV 301344 TO TAHLQH 5 161 KV 512655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_5CHOTEAU1__5CHOTEAU2 | 3 Phase fault 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 161 KV 300069 TO 5CHOTEAU2 161 KV 301348 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_5CHOTEAU1__MAID___5 | 3 Phase fault 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 161 KV 300069 TO MAID 5 161 KV 512648 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_5ELMCRK__CATSAGR5 | 3 Phase fault 5ELMCRK (300993) 161 kV Bus a. Apply fault at the 5ELMCRK (300993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ELMCRK 161 KV 300993 TO CATSAGR5 161 KV 512638 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_5PARK__TAHLQH_5 | 3 Phase fault 5PARK (301307) 161 kV Bus a. Apply fault at the 5PARK (301307) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PARK 161 KV 301307 TO TAHLQH 5 161 KV 512655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_5TRIBES2__AGENCY_2 | 3 Phase fault 5TRIBES2 (515227) 69 kV Bus a. Apply fault at the 5TRIBES2 (515227) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TENYSON2 69 KV 515217 TO 5TRIBES2 69 KV 515227 CKT 1 b.2. HONORHT2 69 KV 515216 TO TENYSON2 69 KV 515217 CKT 1 b.3. LOAD 1 515217 b.4. HONORHT2 69 KV 515216 TO AGENCY 2 69 KV 515229 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_5TRIBES2__WELLSPA2 | 3 Phase fault 5TRIBES2 (515227) 69 kV Bus a. Apply fault at the 5TRIBES2 (515227) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHECOTA2 69 KV 515201 TO WELLS 2 69 KV 515202 CKT 1 b.2. LOAD 1 515202 b.3. CHECOTA2 69 KV 515201 TO 5TRIBES2 69 KV 515227 CKT 1 b.4. WELLS 2 69 KV 515202 TO WELLSPA2 69 KV 515215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_5TRIBES5__MUSKOGE5 | 3 Phase fault 5TRIBES5 (515228) 161 kV Bus a. Apply fault at the 5TRIBES5 (515228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TRIBES5 161 KV 515228 TO HANCOK-5 161 KV 515250 CKT 1 b.2. LOAD 1 515250 b.3. HANCOK-5 161 KV 515250 TO THRERVR5 161 KV 515640 CKT 1 b.4. LOAD 1 515640 b.5. MUSKOGE5 161 KV 515222 TO THRERVR5 161 KV 515640 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_5TRIBES5__PECANCK5 | 3 Phase fault 5TRIBES5 (515228) 161 kV Bus a. Apply fault at the 5TRIBES5 (515228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TRIBES5 161 KV 515228 TO PECANCK5 161 KV 515234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_77MEM | 3 Phase fault 77MEM-E4 (509735) 138 kV Bus a. Apply fault at the 77MEM-E4 (509735) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 77MEM-E4 138 KV 509735 TO 77MEMTP4 138 KV 509765 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_77MEM | 3 Phase fault 77MEM-W4 (509766) 138 kV Bus a. Apply fault at the 77MEM-W4 (509766) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 77MEM-W4 138 KV 509766 TO E.61ST-4 138 KV 509831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_77MEMTP4__81GARN | 3 Phase fault 77MEMTP4 (509765) 138 kV Bus a. Apply fault at the 77MEMTP4 (509765) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 77MEMTP4 138 KV 509765 TO 81GARN-4 138 KV 509855 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_7BLACKBERRY__NEOSHO_7 | 3 Phase fault 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY 345 KV 300739 TO NEOSHO 7 345 KV 532793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_7SAREPTA%__7EL_DORADO | 3 Phase fault 7SAREPTA% (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345 KV 337376 TO 7EL DORADO 345 KV 337562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_7SAREPTA%__LONGWD_7 | 3 Phase fault 7SAREPTA% (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345 KV 337376 TO LONGWD 7 345 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_7SPORTSMAN__GRDA1__7 | 3 Phase fault 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN 345 KV 300740 TO GRDA1 7 345 KV 512650 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_81GARN | 3 Phase fault 81GARN-4 (509855) 138 kV Bus a. Apply fault at the 81GARN-4 (509855) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81GARN-4 138 KV 509855 TO E_121ST4 138 KV 509889 CKT 1 b.2. LOAD 1 509889 b.3. 121LYNN4 138 KV 509869 TO E_121ST4 138 KV 509889 CKT 1 b.4. LOAD 1 509889 b.5. ONETA--4 138 KV 509806 TO 121LYNN4 138 KV 509869 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_81YALEN4__81YALTP4 | 3 Phase fault 81YALEN4 (509730) 138 kV Bus a. Apply fault at the 81YALEN4 (509730) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81YALEN4 138 KV 509730 TO 81YALTP4 138 KV 509809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_81YALES4__WARNTAP4 | 3 Phase fault 81YALES4 (509810) 138 kV Bus a. Apply fault at the 81YALES4 (509810) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81YALES4 138 KV 509810 TO WARNTAP4 138 KV 509858 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_81YALTP4__SHILETP4 | 3 Phase fault 81YALTP4 (509809) 138 kV Bus a. Apply fault at the 81YALTP4 (509809) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81YALTP4 138 KV 509809 TO SHILETP4 138 KV 509813 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_8ANO%__8P.HILL% | 3 Phase fault 8ANO% (337909) 500 kV Bus a. Apply fault at the 8ANO% (337909) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500 KV 337909 TO 8P.HILL% 500 KV 337922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_8ANO%__FTSMITH8 | 3 Phase fault 8ANO% (337909) 500 kV Bus a. Apply fault at the 8ANO% (337909) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500 KV 337909 TO FTSMITH8 500 KV 515305 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_8EL_DORADO%__8PANDA% | 3 Phase fault 8EL DORADO% (337561) 500 kV Bus a. Apply fault at the 8EL DORADO% (337561) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 500 KV 337561 TO 8PANDA% 500 KV 338440 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_8EL_DORADO%__8SHERIDAN% | 3 Phase fault 8EL DORADO% (337561) 500 kV Bus a. Apply fault at the 8EL DORADO% (337561) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 500 KV 337561 TO 8SHERIDAN% 500 KV 337643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_8HAPPYVALY%__8ANO% | 3 Phase fault 8HAPPYVALY% (337811) 500 kV Bus a. Apply fault at the 8HAPPYVALY% (337811) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8HAPPYVALY% 500 KV 337811 TO 8ANO% 500 KV 337909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_8MCNEIL%__8EL_DORADO% | 3 Phase fault 8MCNEIL% (337515) 500 kV Bus a. Apply fault at the 8MCNEIL% (337515) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MCNEIL% 500 KV 337515 TO 8EL DORADO% 500 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_8MCNEIL%__8ETTA% | 3 Phase fault 8MCNEIL% (337515) 500 kV Bus a. Apply fault at the 8MCNEIL% (337515) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MCNEIL% 500 KV 337515 TO 8ETTA% 500 KV 337754 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_8MT_OLIVE%__8EL_DORADO% | 3 Phase fault 8MT_OLIVE% (337368) 500 kV Bus a. Apply fault at the 8MT_OLIVE% (337368) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MT_OLIVE% 500 KV 337368 TO 8EL DORADO% 500 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_8MT_OLIVE%__LAYFLD8 | 3 Phase fault 8MT_OLIVE% (337368) 500 kV Bus a. Apply fault at the 8MT_OLIVE% (337368) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MT_OLIVE% 500 KV 337368 TO LAYFLD8 500 KV 509366 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_8SHERIDAN%__8MABELVALE% | 3 Phase fault 8SHERIDAN% (337643) 500 kV Bus a. Apply fault at the 8SHERIDAN% (337643) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHERIDAN% 500 KV 337643 TO 8MABELVALE% 500 KV 337808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_8SHERIDAN%__8MAGNETCOVE% | 3 Phase fault 8SHERIDAN% (337643) 500 kV Bus a. Apply fault at the 8SHERIDAN% (337643) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHERIDAN% 500 KV 337643 TO 8MAGNETCOVE% 500 KV 337763 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_8SHERIDAN%__8WHT_BLUFF% | 3 Phase fault 8SHERIDAN% (337643) 500 kV Bus a. Apply fault at the 8SHERIDAN% (337643) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHERIDAN% 500 KV 337643 TO 8WHT BLUFF% 500 KV 337651 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_8STERLING%__8EL_DORADO% | 3 Phase fault 8STERLING% (337420) 500 kV Bus a. Apply fault at the 8STERLING% (337420) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8STERLING% 500 KV 337420 TO 8EL DORADO% 500 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_8STERLING%__8PERRYVILLE% | 3 Phase fault 8STERLING% (337420) 500 kV Bus a. Apply fault at the 8STERLING% (337420) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8STERLING% 500 KV 337420 TO 8PERRYVILLE% 500 KV 337427 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_8STERLING2%__8STERLING% | 3 Phase fault 8STERLING2% (337413) 500 kV Bus a. Apply fault at the 8STERLING2% (337413) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8STERLING2% 500 KV 337413 TO 8STERLING% 500 KV 337420 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_A.A. | 3 Phase fault A.A.---4 (509784) 138 kV Bus a. Apply fault at the A.A.---4 (509784) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. A.A.---4 138 KV 509784 TO CDC-WT 4 138 KV 509842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_A.A. | 3 Phase fault A.A.---4 (509784) 138 kV Bus a. Apply fault at the A.A.---4 (509784) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. A.A.---4 138 KV 509784 TO MINGORD4 138 KV 509802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_A.A. | 3 Phase fault A.A.---4 (509784) 138 kV Bus a. Apply fault at the A.A.---4 (509784) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOHAWK 4 138 KV 509801 TO PPTAP 4 138 KV 509863 CKT 1 b.2. A.A.---4 138 KV 509784 TO MOHAWK 4 138 KV 509801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_AGENCY_2__JAMESVL2 | 3 Phase fault AGENCY 2 (515229) 69 kV Bus a. Apply fault at the AGENCY 2 (515229) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AGENCY 2 69 KV 515229 TO JAMESVL2 69 KV 515240 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_AGENCY_5__EUCLID_5 | 3 Phase fault AGENCY 5 (515230) 161 kV Bus a. Apply fault at the AGENCY 5 (515230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AGENCY 5 161 KV 515230 TO EUCLID 5 161 KV 515251 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_AGENCY_5__PECANCK5 | 3 Phase fault AGENCY 5 (515230) 161 kV Bus a. Apply fault at the AGENCY 5 (515230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AGENCY 5 161 KV 515230 TO PECANCK5 161 KV 515234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ALWUETP4__ALLUWE_4 | 3 Phase fault ALWUETP4 (510429) 138 kV Bus a. Apply fault at the ALWUETP4 (510429) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALWUETP4 138 KV 510429 TO ALLUWE 4 138 KV 510430 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ANADARK2__CADDO__2 | 3 Phase fault ANADARK2 (520810) 69 kV Bus a. Apply fault at the ANADARK2 (520810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK2 69 KV 520810 TO CADDO 2 69 KV 520838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ANADARK4__CHERRYRD_4 | 3 Phase fault ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138 KV 520814 TO CHERRYRD 4 138 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ANADARK4__FLETCH | 3 Phase fault ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138 KV 520814 TO GEORGIA4 138 KV 520923 CKT 1 b.2. LOAD 1 520923 b.3. FLETCH-4 138 KV 520912 TO GEORGIA4 138 KV 520923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ANADARK4__TUTLETP4 | 3 Phase fault ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138 KV 520814 TO POCASET4 138 KV 521031 CKT 1 b.2. LOAD 1 521031 b.3. POCASET4 138 KV 521031 TO TUTLETP4 138 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ANDRCKT2__MAUDT__2 | 3 Phase fault ANDRCKT2 (509658) 69 kV Bus a. Apply fault at the ANDRCKT2 (509658) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUDT 2 69 KV 509653 TO MAUD 2 69 KV 509657 CKT 1 b.2. LOAD 1 509657 b.3. MAUD 2 69 KV 509657 TO ANDRCKT2 69 KV 509658 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ANDRCKT2__SPRNGHL2 | 3 Phase fault ANDRCKT2 (509658) 69 kV Bus a. Apply fault at the ANDRCKT2 (509658) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDRCKT2 69 KV 509658 TO SIMMS 2 69 KV 509659 CKT 1 b.2. LOAD 1 509659 b.3. SIMMS 2 69 KV 509659 TO SDEKALB2 69 KV 509660 CKT 1 b.4. LOAD 1 509660 b.5. SDEKALB2 69 KV 509660 TO WDEKALB2 69 KV 509661 CKT 1 b.6. LOAD 1 509661 b.7. WDEKALB2 69 KV 509661 TO SPRNGHL2 69 KV 509662 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ANDRSNC4__MUNZCTY4 | 3 Phase fault ANDRSNC4 (508050) 138 kV Bus a. Apply fault at the ANDRSNC4 (508050) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDRSNC4 138 KV 508050 TO BRYANML4 138 KV 508056 CKT 1 b.2. LOAD 1 508056 b.3. BRYANML4 138 KV 508056 TO MUNZCTY4 138 KV 508064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ARAPAHO2__HM | 3 Phase fault ARAPAHO2 (520815) 69 kV Bus a. Apply fault at the ARAPAHO2 (520815) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARAPAHO2 69 KV 520815 TO HM-BTTP2 69 KV 520942 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ARBUCKL4__VANOSTP4 | 3 Phase fault ARBUCKL4 (515117) 138 kV Bus a. Apply fault at the ARBUCKL4 (515117) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARBUCKL4 138 KV 515117 TO VANOSTP4 138 KV 515531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ARCADIA4__DANFRTH4 | 3 Phase fault ARCADIA4 (514907) 138 kV Bus a. Apply fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 138 KV 514907 TO RNDBARN4 138 KV 515461 CKT 1 b.2. LOAD 1 515461 b.3. BURGETT4 138 KV 514510 TO RNDBARN4 138 KV 515461 CKT 1 b.4. LOAD 1 515461 b.5. BURGETT4 138 KV 514510 TO DANFRTH4 138 KV 514833 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ARCADIA4__LGARBER4 | 3 Phase fault ARCADIA4 (514907) 138 kV Bus a. Apply fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 138 KV 514907 TO LGARBER4 138 KV 515465 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ARCADIA7__GEN | 3 Phase fault ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345 KV 514908 TO GEN-2017-133 345 KV 760032 CKT 4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ARCADIA7__REDBUD_7 | 3 Phase fault ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345 KV 514908 TO REDBUD 7 345 KV 514909 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ARCADIA7__SEMINOL7 | 3 Phase fault ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345 KV 514908 TO SEMINOL7 345 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ARSHILL4__FTHUMBG4 | 3 Phase fault ARSHILL4 (507711) 138 kV Bus a. Apply fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138 KV 507711 TO FTHUMBG4 138 KV 507731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ARSHILL4__LIEBERM4 | 3 Phase fault ARSHILL4 (507711) 138 kV Bus a. Apply fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138 KV 507711 TO LIEBERM4 138 KV 508806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ARSHILL4__MCWILLI4 | 3 Phase fault ARSHILL4 (507711) 138 kV Bus a. Apply fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138 KV 507711 TO MCWILLI4 138 KV 507742 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ARSHILL4__RAINES_4 | 3 Phase fault ARSHILL4 (507711) 138 kV Bus a. Apply fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138 KV 507711 TO RAINES 4 138 KV 507749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ARSHILL4__STLGENS4 | 3 Phase fault ARSHILL4 (507711) 138 kV Bus a. Apply fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138 KV 507711 TO STLGENS4 138 KV 507789 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ARTVLTP4__ARTVILL4 | 3 Phase fault ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTVLTP4 138 KV 511537 TO ARTVILL4 138 KV 511538 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ASPEN__4__MOORLND4 | 3 Phase fault ASPEN 4 (520462) 138 kV Bus a. Apply fault at the ASPEN 4 (520462) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASPEN 4 138 KV 520462 TO MOORLND4 138 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_B.BOWTP4__CRAIGJT4 | 3 Phase fault B.BOWTP4 (510888) 138 kV Bus a. Apply fault at the B.BOWTP4 (510888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B.BOWTP4 138 KV 510888 TO CRAIGJT4 138 KV 510890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_B.BOW__4__B.BOWTP4 | 3 Phase fault B.BOW 4 (510864) 138 kV Bus a. Apply fault at the B.BOW 4 (510864) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B.BOW 4 138 KV 510864 TO B.BOWTP4 138 KV 510888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_B111 | 3 Phase fault B111---4 (509767) 138 kV Bus a. Apply fault at the B111---4 (509767) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B111---4 138 KV 509767 TO BA101ST4 138 KV 509768 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BA.N | 3 Phase fault BA.N-ST4 (509786) 138 kV Bus a. Apply fault at the BA.N-ST4 (509786) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.N-ST4 138 KV 509786 TO LLANETP4 138 KV 509804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BA.N | 3 Phase fault BA.N-ST4 (509786) 138 kV Bus a. Apply fault at the BA.N-ST4 (509786) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.N-ST4 138 KV 509786 TO ONETA--4 138 KV 509806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BA.NO | 3 Phase fault BA.NO-S4 (509721) 138 kV Bus a. Apply fault at the BA.NO-S4 (509721) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.NO-S4 138 KV 509721 TO BA.N-ST4 138 KV 509786 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BA101ST4__ONETA | 3 Phase fault BA101ST4 (509768) 138 kV Bus a. Apply fault at the BA101ST4 (509768) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101ST4 138 KV 509768 TO ONETA--4 138 KV 509806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BA101_S4__BA101ST4 | 3 Phase fault BA101 S4 (509737) 138 kV Bus a. Apply fault at the BA101 S4 (509737) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101 S4 138 KV 509737 TO BA101ST4 138 KV 509768 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BA81 | 3 Phase fault BA81---4 (509747) 138 kV Bus a. Apply fault at the BA81---4 (509747) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA81---4 138 KV 509747 TO BA101-N4 138 KV 509769 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BA81 | 3 Phase fault BA81---4 (509747) 138 kV Bus a. Apply fault at the BA81---4 (509747) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA81---4 138 KV 509747 TO FORD---4 138 KV 509772 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BADGER_7__BLUWND_7 | 3 Phase fault BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345 KV 515677 TO BLUWND 7 345 KV 515686 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BADGER_7__G16 | 3 Phase fault BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345 KV 515677 TO G16-003-TAP 345 KV 560071 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BADGER_7__GEN | 3 Phase fault BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345 KV 515677 TO GEN-2015-082 345 KV 585190 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BANNTAP4__E41ST_E4 | 3 Phase fault BANNTAP4 (509785) 138 kV Bus a. Apply fault at the BANNTAP4 (509785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANNTAP4 138 KV 509785 TO E41ST_E4 138 KV 509861 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BANN___2__LSORDTP2 | 3 Phase fault BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69 KV 508053 TO LSORDTP2 69 KV 508063 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BANN___2__SUGHLWT2 | 3 Phase fault BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69 KV 508053 TO REDLICK2 69 KV 508073 CKT 1 b.2. LOAD 1 508073 b.3. REDLICK2 69 KV 508073 TO RICHMND2 69 KV 508076 CKT 1 b.4. LOAD 1 508076 b.5. NW_TEXAR 2 69 KV 504109 TO RICHMND2 69 KV 508076 CKT 1 b.6. LOAD 1 508076 b.7. NW_TEXAR 2 69 KV 504109 TO SUGHLWT2 69 KV 508082 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BANN___2__TAYLOR_2 | 3 Phase fault BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69 KV 508053 TO KINGHWY2 69 KV 508061 CKT 1 b.2. LOAD 1 508061 b.3. KINGHWY2 69 KV 508061 TO TEXOPER2 69 KV 508087 CKT 1 b.4. LOAD 1 508087 b.5. TAYLOR 2 69 KV 508083 TO TEXOPER2 69 KV 508087 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BANN___4__NWT | 3 Phase fault BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138 KV 508054 TO NWT-BNT4 138 KV 508070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BANN___4__REDSPRG4 | 3 Phase fault BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138 KV 508054 TO REDSPRG4 138 KV 508075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BANN___4__SETEXAR4 | 3 Phase fault BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138 KV 508054 TO SETEXAR4 138 KV 508078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BARITE | 3 Phase fault BARITE-RD 4 (504379) 138 kV Bus a. Apply fault at the BARITE-RD 4 (504379) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARITE-RD 4 138 KV 504379 TO BARITERDTP 4 138 KV 507463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BARNSAL4__MOUNDRD4 | 3 Phase fault BARNSAL4 (510388) 138 kV Bus a. Apply fault at the BARNSAL4 (510388) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARNSAL4 138 KV 510388 TO BARNPMP4 138 KV 510433 CKT 1 b.2. LOAD 1 510433 b.3. MOUNDRD4 138 KV 510395 TO BARNPMP4 138 KV 510433 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BAWATAP2__COWETAP2 | 3 Phase fault BAWATAP2 (509718) 69 kV Bus a. Apply fault at the BAWATAP2 (509718) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAWATAP2 69 KV 509718 TO COWETAP2 69 KV 509781 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BAWATAP2__T.S.E. | 3 Phase fault BAWATAP2 (509718) 69 kV Bus a. Apply fault at the BAWATAP2 (509718) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAWATAP2 69 KV 509718 TO T.S.E.-2 69 KV 509820 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BAWATER2__BAWATAP2 | 3 Phase fault BAWATER2 (509717) 69 kV Bus a. Apply fault at the BAWATER2 (509717) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAWATER2 69 KV 509717 TO BAWATAP2 69 KV 509718 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BCVI_HVB__SLKHILLS_4 | 3 Phase fault BCVI_HVB (520514) 138 kV Bus a. Apply fault at the BCVI_HVB (520514) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BCVI_HVB 138 KV 520514 TO SLKHILLS 4 138 KV 521103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BCV_SW_4__CHERRYRD_4 | 3 Phase fault BCV SW 4 (520513) 138 kV Bus a. Apply fault at the BCV SW 4 (520513) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BCV SW 4 138 KV 520513 TO CHERRYRD 4 138 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BC_SW__4__SLKHILLS_4 | 3 Phase fault BC SW 4 (520512) 138 kV Bus a. Apply fault at the BC SW 4 (520512) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BC SW 4 138 KV 520512 TO SLKHILLS 4 138 KV 521103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BEELINE4__BLUEBEL4 | 3 Phase fault BEELINE4 (515247) 138 kV Bus a. Apply fault at the BEELINE4 (515247) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONESTR4 138 KV 515245 TO BEELINE4 138 KV 515247 CKT 1 b.2. LOAD 1 515247 b.3. KELLYVL4 138 KV 515200 TO LONESTR4 138 KV 515245 CKT 1 b.4. LOAD 1 515245 b.5. KELLYVL4 138 KV 515200 TO BLUEBEL4 138 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BEELINE4__EXPGLNT4 | 3 Phase fault BEELINE4 (515247) 138 kV Bus a. Apply fault at the BEELINE4 (515247) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEELINE4 138 KV 515247 TO EXPGLNT4 138 KV 515473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BEELINE4__POLECTP4 | 3 Phase fault BEELINE4 (515247) 138 kV Bus a. Apply fault at the BEELINE4 (515247) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIBBENS4 138 KV 515237 TO BEELINE4 138 KV 515247 CKT 1 b.2. LOAD 1 515247 b.3. POLECTP4 138 KV 515218 TO TIBBENS4 138 KV 515237 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BELISLE4__38TH_ST4 | 3 Phase fault BELISLE4 (514844) 138 kV Bus a. Apply fault at the BELISLE4 (514844) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELISLE4 138 KV 514844 TO 38TH ST4 138 KV 514846 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BELISLE4__WESTERN4 | 3 Phase fault BELISLE4 (514844) 138 kV Bus a. Apply fault at the BELISLE4 (514844) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELISLE4 138 KV 514844 TO WESTERN4 138 KV 514869 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BEVYTAP5__FTSMTHE5 | 3 Phase fault BEVYTAP5 (515299) 161 kV Bus a. Apply fault at the BEVYTAP5 (515299) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVYTAP5 161 KV 515299 TO FTSMTHE5 161 KV 515300 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BING | 3 Phase fault BING-TP2 (511443) 69 kV Bus a. Apply fault at the BING-TP2 (511443) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BING-TP2 69 KV 511443 TO S.W.S.-2 69 KV 511476 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BINGERJ4__NIJECT_4 | 3 Phase fault BINGERJ4 (520827) 138 kV Bus a. Apply fault at the BINGERJ4 (520827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BINGERJ4 138 KV 520827 TO NIJECT 4 138 KV 521010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BINGERJ4__SICKLES4 | 3 Phase fault BINGERJ4 (520827) 138 kV Bus a. Apply fault at the BINGERJ4 (520827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BINGERJ4 138 KV 520827 TO SICKLES4 138 KV 521050 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BLANCH | 3 Phase fault BLANCH-2 (508801) 69 kV Bus a. Apply fault at the BLANCH-2 (508801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCH-2 69 KV 508801 TO LIEBERM2 69 KV 508805 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BLANCHD4__OU_SW_4 | 3 Phase fault BLANCHD4 (520828) 138 kV Bus a. Apply fault at the BLANCHD4 (520828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCHD4 138 KV 520828 TO OU SW 4 138 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BLOOMBG2__IPC_TAP2 | 3 Phase fault BLOOMBG2 (508055) 69 kV Bus a. Apply fault at the BLOOMBG2 (508055) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLOOMBG2 69 KV 508055 TO IPC TAP2 69 KV 508058 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BLUEBEL4__BOWDEN_4 | 3 Phase fault BLUEBEL4 (515242) 138 kV Bus a. Apply fault at the BLUEBEL4 (515242) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBEL4 138 KV 515242 TO BOWDEN 4 138 KV 515243 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BLUERIV4__PARKLN_4 | 3 Phase fault BLUERIV4 (515133) 138 kV Bus a. Apply fault at the BLUERIV4 (515133) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUERIV4 138 KV 515133 TO PARKLN 4 138 KV 515178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BORDER_____7__BECKHAM7 | 3 Phase fault BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345 KV 515458 TO BECKHAM7 345 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BORDER_____7__TUCO_INT___7 | 3 Phase fault BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345 KV 515458 TO TUCO_INT 7 345 KV 525832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BOWMAN_2__KNGINDT2 | 3 Phase fault BOWMAN 2 (514813) 69 kV Bus a. Apply fault at the BOWMAN 2 (514813) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOWMAN 2 69 KV 514813 TO KNGINDT2 69 KV 515625 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BOWMAN_2__OMKINGF2 | 3 Phase fault BOWMAN 2 (514813) 69 kV Bus a. Apply fault at the BOWMAN 2 (514813) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOWMAN 2 69 KV 514813 TO OMKINGF2 69 KV 529280 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BOWMAN_2__TURCRKT2 | 3 Phase fault BOWMAN 2 (514813) 69 kV Bus a. Apply fault at the BOWMAN 2 (514813) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOWMAN 2 69 KV 514813 TO TURCRKT2 69 KV 515517 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BRANDYBR__PIRKEY_4 | 3 Phase fault BRANDYBR (508596) 138 kV Bus a. Apply fault at the BRANDYBR (508596) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRANDYBR 138 KV 508596 TO EASTON 4 138 KV 509092 CKT 1 b.2. LOAD 1 509092 b.3. PIRKEY 4 138 KV 508562 TO EASTON 4 138 KV 509092 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BRCKWND4__BRECKNR4 | 3 Phase fault BRCKWND4 (514642) 138 kV Bus a. Apply fault at the BRCKWND4 (514642) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRCKWND4 138 KV 514642 TO BRECKNR4 138 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BRECKNR4__ENIDINT4 | 3 Phase fault BRECKNR4 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 138 KV 514815 TO ENIDINT4 138 KV 515383 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BRECKNR4__PLNSMEN4 | 3 Phase fault BRECKNR4 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 138 KV 514815 TO PLNSMEN4 138 KV 515641 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BRIDGCR4__SUNSHIN4 | 3 Phase fault BRIDGCR4 (520501) 138 kV Bus a. Apply fault at the BRIDGCR4 (520501) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRIDGCR4 138 KV 520501 TO SUNSHIN4 138 KV 521059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BRIDGCR4__TUTLETP4 | 3 Phase fault BRIDGCR4 (520501) 138 kV Bus a. Apply fault at the BRIDGCR4 (520501) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRIDGCR4 138 KV 520501 TO TUTLETP4 138 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BRISTOW4__BLUEBEL4 | 3 Phase fault BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 138 KV 515035 TO BLUEBEL4 138 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BRISTOW4__GRNWOOD4 | 3 Phase fault BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 138 KV 515035 TO GRNWOOD4 138 KV 515417 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BRISTOW4__KEYWEST4 | 3 Phase fault BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 138 KV 515035 TO KEYWEST4 138 KV 515048 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BRKN_BW4__BETHEL_4 | 3 Phase fault BRKN BW4 (505614) 138 kV Bus a. Apply fault at the BRKN BW4 (505614) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRKN BW4 138 KV 505614 TO BETHEL 4 138 KV 510928 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BRKN_BW4__CRAIGJT4 | 3 Phase fault BRKN BW4 (505614) 138 kV Bus a. Apply fault at the BRKN BW4 (505614) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRKN BW4 138 KV 505614 TO CRAIGJT4 138 KV 510890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BRKN_BW4__HOCHTWN4 | 3 Phase fault BRKN BW4 (505614) 138 kV Bus a. Apply fault at the BRKN BW4 (505614) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRKN BW4 138 KV 505614 TO HOCHTWN4 138 KV 520943 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BRYANML4__MUNZCTY4 | 3 Phase fault BRYANML4 (508056) 138 kV Bus a. Apply fault at the BRYANML4 (508056) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRYANML4 138 KV 508056 TO MUNZCTY4 138 KV 508064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BTLRJCT2__HM | 3 Phase fault BTLRJCT2 (520457) 69 kV Bus a. Apply fault at the BTLRJCT2 (520457) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BTLRJCT2 69 KV 520457 TO HM-BTTP2 69 KV 520942 CKT NO c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BUFFALO7__THISTLE7 | 3 Phase fault BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345 KV 532782 TO THISTLE7 345 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BUFORDR2__COOKVTP2 | 3 Phase fault BUFORDR2 (508287) 69 kV Bus a. Apply fault at the BUFORDR2 (508287) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFORDR2 69 KV 508287 TO COOKVTP2 69 KV 508338 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BUFORDR2__DEKALB_2 | 3 Phase fault BUFORDR2 (508287) 69 kV Bus a. Apply fault at the BUFORDR2 (508287) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFORDR2 69 KV 508287 TO DEKALB 2 69 KV 508289 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BUFORDR2__NAPLES_2 | 3 Phase fault BUFORDR2 (508287) 69 kV Bus a. Apply fault at the BUFORDR2 (508287) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFORDR2 69 KV 508287 TO NAPLES 2 69 KV 508307 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BULFOOT4__BULFTTP4 | 3 Phase fault BULFOOT4 (515960) 138 kV Bus a. Apply fault at the BULFOOT4 (515960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFOOT4 138 KV 515960 TO BULFTTP4 138 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BULFTTP4__DOVERSW4 | 3 Phase fault BULFTTP4 (520535) 138 kV Bus a. Apply fault at the BULFTTP4 (520535) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFTTP4 138 KV 520535 TO DOVERSW4 138 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BUNCHCK4__BRECKNR4 | 3 Phase fault BUNCHCK4 (514701) 138 kV Bus a. Apply fault at the BUNCHCK4 (514701) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 138 KV 514701 TO BRECKNR4 138 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BV | 3 Phase fault BV-COM-4 (510390) 138 kV Bus a. Apply fault at the BV-COM-4 (510390) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BV-COM-4 138 KV 510390 TO BV-SE--4 138 KV 510391 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BV | 3 Phase fault BV-COM-4 (510390) 138 kV Bus a. Apply fault at the BV-COM-4 (510390) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BV-COM-4 138 KV 510390 TO MOUNDRD4 138 KV 510395 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BV | 3 Phase fault BV-SE--4 (510391) 138 kV Bus a. Apply fault at the BV-SE--4 (510391) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BV-SE--4 138 KV 510391 TO BLUESTM4 138 KV 510394 CKT 1 b.2. LOAD 1 510394 b.3. BV-COM-4 138 KV 510390 TO BLUESTM4 138 KV 510394 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BV | 3 Phase fault BV-SE--4 (510391) 138 kV Bus a. Apply fault at the BV-SE--4 (510391) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NBVILLE4 138 KV 510386 TO BV-SE--4 138 KV 510391 CKT 1 b.2. LOAD 1 510391 b.3. NBVILLE4 138 KV 510386 TO COFFEYT4 138 KV 510422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BVRCNTY7__BADGER_7 | 3 Phase fault BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345 KV 515554 TO BADGER 7 345 KV 515677 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_C | 3 Phase fault C-RIVER4 (510946) 138 kV Bus a. Apply fault at the C-RIVER4 (510946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C-RIVER4 138 KV 510946 TO TALAWANDA 4 138 KV 510951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_C | 3 Phase fault C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 345 KV 515422 TO FIREWHL-TAP 345 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CADDO__2__WASHITA2 | 3 Phase fault CADDO 2 (520838) 69 kV Bus a. Apply fault at the CADDO 2 (520838) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CADDO 2 69 KV 520838 TO WASHITA2 69 KV 521088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CALRYTP2__MUSKOGE2 | 3 Phase fault CALRYTP2 (515211) 69 kV Bus a. Apply fault at the CALRYTP2 (515211) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALRYTP2 69 KV 515211 TO MUSKOGE2 69 KV 515221 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CANADN | 3 Phase fault CANADN-4 (514947) 138 kV Bus a. Apply fault at the CANADN-4 (514947) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADN-4 138 KV 514947 TO CANADNS4 138 KV 520842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CANADN7__FSHRTAP7 | 3 Phase fault CANADN7 (515605) 345 kV Bus a. Apply fault at the CANADN7 (515605) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANADN7 345 KV 515605 TO FSHRTAP7 345 KV 515610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CANADNS4__GOLDSBY4 | 3 Phase fault CANADNS4 (520842) 138 kV Bus a. Apply fault at the CANADNS4 (520842) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 138 KV 520842 TO GOLDSBY4 138 KV 520924 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CANA___4__CALUMET4 | 3 Phase fault CANA 4 (520502) 138 kV Bus a. Apply fault at the CANA 4 (520502) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANA 4 138 KV 520502 TO CALUMET4 138 KV 520839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CAN_GAS4__JENSEN_4 | 3 Phase fault CAN_GAS4 (511540) 138 kV Bus a. Apply fault at the CAN_GAS4 (511540) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 138 KV 511540 TO JENSEN 4 138 KV 514821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CARROLL6__DOLHILL6 | 3 Phase fault CARROLL6 (500140) 230 kV Bus a. Apply fault at the CARROLL6 (500140) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARROLL6 230 KV 500140 TO DOLHILL6 230 KV 500260 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CARSN | 3 Phase fault CARSN-N4 (509741) 138 kV Bus a. Apply fault at the CARSN-N4 (509741) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-N4 138 KV 509741 TO CARSONT4 138 KV 509865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CARSN | 3 Phase fault CARSN-S4 (509756) 138 kV Bus a. Apply fault at the CARSN-S4 (509756) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-S4 138 KV 509756 TO KENSH-W4 138 KV 509777 CKT 1 b.2. LOAD 1 509777 b.3. DENVR-C4 138 KV 509742 TO KENSH-W4 138 KV 509777 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CARSN | 3 Phase fault CARSN-S4 (509756) 138 kV Bus a. Apply fault at the CARSN-S4 (509756) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-S4 138 KV 509756 TO T.P.S.-4 138 KV 509788 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CARSN | 3 Phase fault CARSN-T4 (509739) 138 kV Bus a. Apply fault at the CARSN-T4 (509739) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-T4 138 KV 509739 TO UNIONAV4 138 KV 509740 CKT 1 b.2. LOAD 1 509740 b.3. UNIONAV4 138 KV 509740 TO CARSN-C4 138 KV 509749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CARSN | 3 Phase fault CARSN-T4 (509739) 138 kV Bus a. Apply fault at the CARSN-T4 (509739) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-T4 138 KV 509739 TO S.S.---4 138 KV 509815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CARTER_4__CHIKSAW4 | 3 Phase fault CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138 KV 515138 TO CHIKSAW4 138 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CARTER_4__HONEYCK4 | 3 Phase fault CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138 KV 515138 TO HONEYCK4 138 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CARTHGT4__LOGANSP4 | 3 Phase fault CARTHGT4 (509060) 138 kV Bus a. Apply fault at the CARTHGT4 (509060) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHGT4 138 KV 509060 TO LOGANSP4 138 KV 509071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CARTRCO4__GEN | 3 Phase fault CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138 KV 515561 TO GEN-2017-027 138 KV 588710 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CARTRCO4__ORIGINW4 | 3 Phase fault CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138 KV 515561 TO ORIGINW4 138 KV 515563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CASHION4__TWNLKJT4 | 3 Phase fault CASHION4 (520479) 138 kV Bus a. Apply fault at the CASHION4 (520479) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASHION4 138 KV 520479 TO TWNLKJT4 138 KV 520847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CATOOSA2__DAWSON | 3 Phase fault CATOOSA2 (509799) 69 kV Bus a. Apply fault at the CATOOSA2 (509799) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BCIRCLE2 69 KV 509794 TO CATOOSA2 69 KV 509799 CKT 1 b.2. DAWSON-2 69 KV 509791 TO BCIRCLE2 69 KV 509794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CATOOSA4__CDC | 3 Phase fault CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138 KV 509790 TO OWAS88_4 138 KV 509887 CKT 1 b.2. LOAD 1 509887 b.3. CDC-ET 4 138 KV 509839 TO OWAS88_4 138 KV 509887 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CATOOSA4__LLANETP4 | 3 Phase fault CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138 KV 509790 TO LLANETP4 138 KV 509804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CATOOSA4__PCATSAT4 | 3 Phase fault CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138 KV 509790 TO PCATSAT4 138 KV 509841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CATOOSA4__TERNITP4 | 3 Phase fault CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138 KV 509790 TO TERNITP4 138 KV 509835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CATSAGR5__COLINS_5 | 3 Phase fault CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ELMCRK 161 KV 300993 TO CATSAGR5 161 KV 512638 CKT 1 b.2. 5ELMCRK 161 KV 300993 TO COLINS 5 161 KV 512627 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CATSAGR5__MAID___5 | 3 Phase fault CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 161 KV 512638 TO MAID 5 161 KV 512648 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CDC | 3 Phase fault CDC-ET 4 (509839) 138 kV Bus a. Apply fault at the CDC-ET 4 (509839) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CDC-ET 4 138 KV 509839 TO OWAS88_4 138 KV 509887 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CDRDLTP4__OKEENE_4 | 3 Phase fault CDRDLTP4 (520848) 138 kV Bus a. Apply fault at the CDRDLTP4 (520848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CDRDLTP4 138 KV 520848 TO OKEENE 4 138 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CEDARLN4__SOONRTP4 | 3 Phase fault CEDARLN4 (514948) 138 kV Bus a. Apply fault at the CEDARLN4 (514948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARLN4 138 KV 514948 TO SOONRTP4 138 KV 514949 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CEDRDAL4__CDRDLTP4 | 3 Phase fault CEDRDAL4 (520507) 138 kV Bus a. Apply fault at the CEDRDAL4 (520507) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDRDAL4 138 KV 520507 TO CDRDLTP4 138 KV 520848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CEMRD_TP4__CMTRYRD4 | 3 Phase fault CEMRD_TP4 (511576) 138 kV Bus a. Apply fault at the CEMRD_TP4 (511576) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEMRD_TP4 138 KV 511576 TO CMTRYRD4 138 KV 515864 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CHAMSPR7__CLARKSV7 | 3 Phase fault CHAMSPR7 (506945) 345 kV Bus a. Apply fault at the CHAMSPR7 (506945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAMSPR7 345 KV 506945 TO CLARKSV7 345 KV 509745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CHAMSPR7__TONTITN7 | 3 Phase fault CHAMSPR7 (506945) 345 kV Bus a. Apply fault at the CHAMSPR7 (506945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAMSPR7 345 KV 506945 TO TONTITN7 345 KV 506959 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CHAPELH4__CHAPLHL4 | 3 Phase fault CHAPELH4 (508337) 138 kV Bus a. Apply fault at the CHAPELH4 (508337) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPELH4 138 KV 508337 TO CHAPLHL4 138 KV 509664 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CHCKSHA4__CKSHATP4 | 3 Phase fault CHCKSHA4 (520472) 138 kV Bus a. Apply fault at the CHCKSHA4 (520472) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHCKSHA4 138 KV 520472 TO CKSHATP4 138 KV 520473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CHEEKTP4__CHEEK_4 | 3 Phase fault CHEEKTP4 (515415) 138 kV Bus a. Apply fault at the CHEEKTP4 (515415) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHEEKTP4 138 KV 515415 TO CHEEK_4 138 KV 521125 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CHERYCK4__NORMHLL4 | 3 Phase fault CHERYCK4 (514957) 138 kV Bus a. Apply fault at the CHERYCK4 (514957) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERYCK4 138 KV 514957 TO NORMHLL4 138 KV 516097 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CHISHOLM7__BECKHAM7 | 3 Phase fault CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345 KV 511553 TO BECKHAM7 345 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CHISHOLM7__G16 | 3 Phase fault CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345 KV 511553 TO G16-037-TAP 345 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CHISHOM4__FAIRFLD4 | 3 Phase fault CHISHOM4 (515374) 138 kV Bus a. Apply fault at the CHISHOM4 (515374) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOM4 138 KV 515374 TO FAIRFLD4 138 KV 515468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CHOUTEAUCRK5__GEN | 3 Phase fault CHOUTEAUCRK5 (513570) 161 kV Bus a. Apply fault at the CHOUTEAUCRK5 (513570) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHOUTEAUCRK5 161 KV 513570 TO GEN-2017-061 161 KV 588990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CIMARON4__DVISION4 | 3 Phase fault CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYMAKR4 138 KV 514863 TO CIMARON4 138 KV 514898 CKT 1 b.2. DVISION4 138 KV 514853 TO HAYMAKR4 138 KV 514863 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CIMARON4__MCCLAIN4 | 3 Phase fault CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA 4 138 KV 514895 TO CIMARON4 138 KV 514898 CKT 1 b.2. SARA 4 138 KV 514895 TO MCCLAIN4 138 KV 514902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CIMARON4__MUSTANG4 | 3 Phase fault CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CZECHAL4 138 KV 514894 TO CIMARON4 138 KV 514898 CKT 1 b.2. XEROX 4 138 KV 514893 TO CZECHAL4 138 KV 514894 CKT 1 b.3. LOAD 1 514894 b.4. XEROX 4 138 KV 514893 TO MORGAN 4 138 KV 514896 CKT 1 b.5. LOAD 1 514896 b.6. MUSTANG4 138 KV 514861 TO MORGAN 4 138 KV 514896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CIMARON7__FSHRTAP7 | 3 Phase fault CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345 KV 514901 TO FSHRTAP7 345 KV 515610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CIMARON7__MATHWSN7 | 3 Phase fault CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345 KV 514901 TO MATHWSN7 345 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CIMARON7__NORMHLL7 | 3 Phase fault CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345 KV 514901 TO NORMHLL7 345 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CIP____4__CDC | 3 Phase fault CIP 4 (509714) 138 kV Bus a. Apply fault at the CIP 4 (509714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIP 4 138 KV 509714 TO CDC-ET 4 138 KV 509839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CIP____4__CDC____4 | 3 Phase fault CIP 4 (509714) 138 kV Bus a. Apply fault at the CIP 4 (509714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIP 4 138 KV 509714 TO CDC 4 138 KV 509715 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CKSHATP4__CORN_TP4 | 3 Phase fault CKSHATP4 (520473) 138 kV Bus a. Apply fault at the CKSHATP4 (520473) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CKSHATP4 138 KV 520473 TO CORN TP4 138 KV 520867 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CL | 3 Phase fault CL-AFTP4 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 138 KV 511446 TO ELKCTY-4 138 KV 511458 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CL | 3 Phase fault CL-AFTP4 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 138 KV 511446 TO HOB-JCT4 138 KV 511463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CLARKCOUNTY7__THISTLE7 | 3 Phase fault CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345 KV 539800 TO THISTLE7 345 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CLARKSV7__GEN | 3 Phase fault CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345 KV 509745 TO GEN-2017-140 345 KV 760389 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CLARKSV7__MUSKOGE7 | 3 Phase fault CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345 KV 509745 TO MUSKOGE7 345 KV 515224 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CLARKSV7__ONETA | 3 Phase fault CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345 KV 509745 TO ONETA--7 345 KV 509807 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CLARMR_5__CHOUTEAUCRK5 | 3 Phase fault CLARMR 5 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 161 KV 512651 TO CHOUTEAUCRK5 161 KV 513570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CLASSEN4__TROSPER4 | 3 Phase fault CLASSEN4 (514922) 138 kV Bus a. Apply fault at the CLASSEN4 (514922) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLASSEN4 138 KV 514922 TO CROSTWN4 138 KV 515851 CKT 1 b.2. LOAD 1 515851 b.3. LIGHTCK4 138 KV 514923 TO CROSTWN4 138 KV 515851 CKT 1 b.4. LOAD 1 515851 b.5. LIGHTCK4 138 KV 514923 TO TROSPER4 138 KV 514963 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CLEOSW_2__RNGWODJ2 | 3 Phase fault CLEOSW 2 (520855) 69 kV Bus a. Apply fault at the CLEOSW 2 (520855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOSW 2 69 KV 520855 TO RNGWODJ2 69 KV 521039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CLEVETP2__SO4TH__2 | 3 Phase fault CLEVETP2 (514722) 69 kV Bus a. Apply fault at the CLEVETP2 (514722) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVETP2 69 KV 514722 TO SO4TH 2 69 KV 514730 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CLEVLND7__G15 | 3 Phase fault CLEVLND7 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 345 KV 512694 TO G15-066T 345 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CLVLDSW4__AMBERTP4 | 3 Phase fault CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138 KV 520508 TO AMBERTP4 138 KV 520530 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CLVLDSW4__ANADARK4 | 3 Phase fault CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138 KV 520508 TO ANADARK4 138 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CLVLDSW4__COGAR__4 | 3 Phase fault CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138 KV 520508 TO COGAR 4 138 KV 520859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CMBLCRK4__CMBLTP_4 | 3 Phase fault CMBLCRK4 (515930) 138 kV Bus a. Apply fault at the CMBLCRK4 (515930) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMBLCRK4 138 KV 515930 TO CMBLTP 4 138 KV 520474 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CMBLTP_4__FOURCTP4 | 3 Phase fault CMBLTP 4 (520474) 138 kV Bus a. Apply fault at the CMBLTP 4 (520474) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMBLTP 4 138 KV 520474 TO FOURCTP4 138 KV 520545 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_COBRN_CREEK3__WHEELER____3 | 3 Phase fault COBRN_CREEK3 (523772) 115 kV Bus a. Apply fault at the COBRN_CREEK3 (523772) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COBRN_CREEK3 115 KV 523772 TO WHEELER 3 115 KV 523776 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_COFFEYT4__DEARING4 | 3 Phase fault COFFEYT4 (510422) 138 kV Bus a. Apply fault at the COFFEYT4 (510422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COFFEYT4 138 KV 510422 TO DEARING4 138 KV 533002 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_COLE___4__OU_SW_4 | 3 Phase fault COLE 4 (520861) 138 kV Bus a. Apply fault at the COLE 4 (520861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLE 4 138 KV 520861 TO OU SW 4 138 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_COLINS_5__CLARMR_5 | 3 Phase fault COLINS 5 (512627) 161 kV Bus a. Apply fault at the COLINS 5 (512627) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5KETONVL 161 KV 300997 TO COLINS 5 161 KV 512627 CKT 1 b.2. 5KETONVL 161 KV 300997 TO CLARMR 5 161 KV 512651 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_COMANC | 3 Phase fault COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69 KV 511436 TO L.E.S.-2 69 KV 511466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_COMANC | 3 Phase fault COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138 KV 511437 TO 112GORE4 138 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_COMANC | 3 Phase fault COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138 KV 511437 TO COMMTAP4 138 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_COMANC | 3 Phase fault COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138 KV 511437 TO L.E.S.-4 138 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_COMMTAP4__OMDUNCN4 | 3 Phase fault COMMTAP4 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMMTAP4 138 KV 511494 TO OMDUNCN4 138 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CORNVIL4__ALEX_BR4 | 3 Phase fault CORNVIL4 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138 KV 511449 TO ALEX BR4 138 KV 511516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CORNVIL4__CORN_TP4 | 3 Phase fault CORNVIL4 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138 KV 511449 TO CORN TP4 138 KV 520867 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CORNVIL4__LEONARD4 | 3 Phase fault CORNVIL4 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138 KV 511449 TO LEONARD4 138 KV 511575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CORNVIL4__MAUD___4 | 3 Phase fault CORNVIL4 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCHD4 138 KV 511508 TO MAUD 4 138 KV 515055 CKT 1 b.2. CORNVIL4 138 KV 511449 TO BLANCHD4 138 KV 511508 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CORNVIL4__N29CHIK4 | 3 Phase fault CORNVIL4 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138 KV 511449 TO N29CHIK4 138 KV 511502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CORNVIL4__NORGE | 3 Phase fault CORNVIL4 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138 KV 511449 TO NORGE--4 138 KV 511483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CORNVIL4__SANTAFE4 | 3 Phase fault CORNVIL4 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138 KV 511449 TO SANTAFE4 138 KV 511492 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CRAIGJT4__HOCHJCT4 | 3 Phase fault CRAIGJT4 (510890) 138 kV Bus a. Apply fault at the CRAIGJT4 (510890) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIGJT4 138 KV 510890 TO MTRIVER4 138 KV 521004 CKT 1 b.2. LOAD 1 521004 b.3. HOCHJCT4 138 KV 520823 TO MTRIVER4 138 KV 521004 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CRAIGJT4__MENA___4 | 3 Phase fault CRAIGJT4 (510890) 138 kV Bus a. Apply fault at the CRAIGJT4 (510890) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENA 4 138 KV 507436 TO GORDON TAP 4 138 KV 507461 CKT 1 b.2. LOAD A1 507461 b.3. GORDON TAP 4 138 KV 507461 TO CRAIGJT4 138 KV 510890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CRESENT4__GEN | 3 Phase fault CRESENT4 (515377) 138 kV Bus a. Apply fault at the CRESENT4 (515377) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESENT4 138 KV 515377 TO GEN-2016-032 138 KV 587210 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CRESENT4__TWNLKSW4 | 3 Phase fault CRESENT4 (515377) 138 kV Bus a. Apply fault at the CRESENT4 (515377) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESENT4 138 KV 515377 TO TWNLKSW4 138 KV 521073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CTNWOOD4__ARCADIA4 | 3 Phase fault CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138 KV 514827 TO ARCADIA4 138 KV 514907 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CTNWOOD4__CRESENT4 | 3 Phase fault CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138 KV 514827 TO CRESENT4 138 KV 515377 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CTNWOOD4__KETCHTP4 | 3 Phase fault CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138 KV 514827 TO LBRTYLK4 138 KV 515373 CKT 1 b.2. LOAD 1 515373 b.3. WATRLOO4 138 KV 514831 TO LBRTYLK4 138 KV 515373 CKT 1 b.4. LOAD 1 515373 b.5. WATRLOO4 138 KV 514831 TO WHITESB4 138 KV 515467 CKT 1 b.6. LOAD 1 515467 b.7. MITCHSB4 138 KV 515466 TO WHITESB4 138 KV 515467 CKT 1 b.8. LOAD 1 515467 b.9. KETCHTP4 138 KV 514828 TO MITCHSB4 138 KV 515466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CTNWOOD4__KINZE__4 | 3 Phase fault CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138 KV 514827 TO PINE ST4 138 KV 514829 CKT 1 b.2. LOAD 1 514829 b.3. LOAD 2 514829 b.4. PINE ST4 138 KV 514829 TO FITZGRD4 138 KV 514830 CKT 1 b.5. LOAD 1 514830 b.6. FITZGRD4 138 KV 514830 TO KINZE 4 138 KV 515008 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CTNWOOD4__LBRTYLK4 | 3 Phase fault CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138 KV 514827 TO LBRTYLK4 138 KV 515373 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CUSTDAY1_5__HERRON_5 | 3 Phase fault CUSTDAY1 5 (513590) 161 kV Bus a. Apply fault at the CUSTDAY1 5 (513590) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTDAY1 5 161 KV 513590 TO HERRON 5 161 KV 513591 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DANFRTH4__KETCH__4 | 3 Phase fault DANFRTH4 (514833) 138 kV Bus a. Apply fault at the DANFRTH4 (514833) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DANFRTH4 138 KV 514833 TO KETCH 4 138 KV 514834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DARENCT2__ALAMANC2 | 3 Phase fault DARENCT2 (509647) 69 kV Bus a. Apply fault at the DARENCT2 (509647) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DARENCT2 69 KV 509647 TO ALAMANC2 69 KV 509649 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DARENCT2__DARENCO2 | 3 Phase fault DARENCT2 (509647) 69 kV Bus a. Apply fault at the DARENCT2 (509647) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DARENCT2 69 KV 509647 TO DARENCO2 69 KV 509648 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DAWSON | 3 Phase fault DAWSON-4 (509792) 138 kV Bus a. Apply fault at the DAWSON-4 (509792) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSON-4 138 KV 509792 TO DAWSONT4 138 KV 509803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DAWSONT4__N21ST | 3 Phase fault DAWSONT4 (509803) 138 kV Bus a. Apply fault at the DAWSONT4 (509803) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONT4 138 KV 509803 TO N21ST--4 138 KV 509866 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DAYTON_4__HOBBYLO4 | 3 Phase fault DAYTON 4 (514892) 138 kV Bus a. Apply fault at the DAYTON 4 (514892) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAYTON 4 138 KV 514892 TO HOBBYLO4 138 KV 515338 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DEEPFKT2__DEEPFRK2 | 3 Phase fault DEEPFKT2 (514970) 69 kV Bus a. Apply fault at the DEEPFKT2 (514970) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEEPFKT2 69 KV 514970 TO DEEPFRK2 69 KV 514974 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DELWARE4__FARML__4 | 3 Phase fault DELWARE4 (510379) 138 kV Bus a. Apply fault at the DELWARE4 (510379) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELWARE4 138 KV 510379 TO FARML 4 138 KV 512734 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DELWARE7__N.E.S. | 3 Phase fault DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 345 KV 510380 TO N.E.S.-7 345 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DELWARE7__NEOSHO_7 | 3 Phase fault DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 345 KV 510380 TO NEOSHO 7 345 KV 532793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DENVR | 3 Phase fault DENVR-E4 (509743) 138 kV Bus a. Apply fault at the DENVR-E4 (509743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVR-E4 138 KV 509743 TO DENVTAP4 138 KV 509746 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DENVR | 3 Phase fault DENVR-W4 (509748) 138 kV Bus a. Apply fault at the DENVR-W4 (509748) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVR-W4 138 KV 509748 TO DENV_WTAP4 138 KV 509896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DENVTAP4__T.NO. | 3 Phase fault DENVTAP4 (509746) 138 kV Bus a. Apply fault at the DENVTAP4 (509746) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVTAP4 138 KV 509746 TO T.NO.--4 138 KV 509817 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DENVTAP4__W.ED. | 3 Phase fault DENVTAP4 (509746) 138 kV Bus a. Apply fault at the DENVTAP4 (509746) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVTAP4 138 KV 509746 TO W.ED.-E4 138 KV 509822 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DEQUEEN2__LOCKESB2 | 3 Phase fault DEQUEEN2 (507418) 69 kV Bus a. Apply fault at the DEQUEEN2 (507418) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEQUEEN2 69 KV 507418 TO LOCKESB2 69 KV 507422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DEQUEEN4__CRAIGJT4 | 3 Phase fault DEQUEEN4 (507419) 138 kV Bus a. Apply fault at the DEQUEEN4 (507419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEQUEEN4 138 KV 507419 TO CRAIGJT4 138 KV 510890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DEWEY__4__CANTNLK4 | 3 Phase fault DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138 KV 514787 TO CANTNLK4 138 KV 515964 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DEWEY__4__REDCLFT4 | 3 Phase fault DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138 KV 514787 TO REDCLFT4 138 KV 515533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DEWEY__4__TALOGA_4 | 3 Phase fault DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138 KV 514787 TO TALOGA 4 138 KV 521065 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DEWEY__4__TLGAWND4 | 3 Phase fault DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138 KV 514787 TO TLGAWND4 138 KV 515390 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DGRASSE4__MOORLND4 | 3 Phase fault DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138 KV 515853 TO MOORLND4 138 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DGRASSE4__ROSEVLY4 | 3 Phase fault DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138 KV 515853 TO ROSEVLY4 138 KV 520436 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DGRASSE7__THISTLE7 | 3 Phase fault DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 345 KV 515852 TO THISTLE7 345 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DIANA__4__DIANASW4 | 3 Phase fault DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 138 KV 508831 TO DIANASW4 138 KV 509639 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DIANA__4__NGPLTAP4 | 3 Phase fault DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 138 KV 508831 TO NGPLTAP4 138 KV 508837 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DILLARD4__WOLFCRK4 | 3 Phase fault DILLARD4 (515142) 138 kV Bus a. Apply fault at the DILLARD4 (515142) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DILLARD4 138 KV 515142 TO WOLFCRK4 138 KV 515143 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DOLHILL7__SW_SHV_7 | 3 Phase fault DOLHILL7 (500250) 345 kV Bus a. Apply fault at the DOLHILL7 (500250) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DOLHILL7 345 KV 500250 TO SW SHV 7 345 KV 507760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DOUGLTP4__CLASSEN4 | 3 Phase fault DOUGLTP4 (514868) 138 kV Bus a. Apply fault at the DOUGLTP4 (514868) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOUGLTP4 138 KV 514868 TO CLASSEN4 138 KV 514922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DOUGLTP4__WESTERN4 | 3 Phase fault DOUGLTP4 (514868) 138 kV Bus a. Apply fault at the DOUGLTP4 (514868) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOUGLTP4 138 KV 514868 TO WESTERN4 138 KV 514869 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DOVERSW2__HENESEY2 | 3 Phase fault DOVERSW2 (520881) 69 kV Bus a. Apply fault at the DOVERSW2 (520881) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW2 69 KV 520881 TO HENESEY2 69 KV 520940 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DOVERSW2__LACEY__2 | 3 Phase fault DOVERSW2 (520881) 69 kV Bus a. Apply fault at the DOVERSW2 (520881) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW2 69 KV 520881 TO LACEY 2 69 KV 520967 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DOVERSW4__GEN | 3 Phase fault DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138 KV 520882 TO GEN-2016-118 138 KV 587940 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DOVERSW4__GEN | 3 Phase fault DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138 KV 520882 TO GEN-2018-011 138 KV 762493 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DOVERSW4__KGFSJCT4 | 3 Phase fault DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKNGFSH4 138 KV 520603 TO DOVERSW4 138 KV 520882 CKT 1 b.2. KGFSJCT4 138 KV 520405 TO NKNGFSH4 138 KV 520603 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DOVERSW4__OKEENE_4 | 3 Phase fault DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138 KV 520882 TO OKEENE 4 138 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DOVERSW4__TWNLKSW4 | 3 Phase fault DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVER 4 138 KV 520879 TO DOVERSW4 138 KV 520882 CKT 1 b.2. TWNLAKE4 138 KV 520540 TO DOVER 4 138 KV 520879 CKT 1 b.3. LOAD 1 520879 b.4. TWNLAKE4 138 KV 520540 TO TWNLKSW4 138 KV 521073 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DOVERTP2__DOVERSW2 | 3 Phase fault DOVERTP2 (514772) 69 kV Bus a. Apply fault at the DOVERTP2 (514772) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERTP2 69 KV 514772 TO DOVERSW2 69 KV 520881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DOVERTP2__REDWING2 | 3 Phase fault DOVERTP2 (514772) 69 kV Bus a. Apply fault at the DOVERTP2 (514772) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERTP2 69 KV 514772 TO REDWING2 69 KV 515976 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DOVERTP2__TURCRKT2 | 3 Phase fault DOVERTP2 (514772) 69 kV Bus a. Apply fault at the DOVERTP2 (514772) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERTP2 69 KV 514772 TO TURCRKT2 69 KV 515517 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DRAPER_4__BARNES_4 | 3 Phase fault DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138 KV 514933 TO BARNES 4 138 KV 515003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DRAPER_4__GM_____4 | 3 Phase fault DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138 KV 514933 TO GM 4 138 KV 514961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DRAPER_4__MIDWEST4 | 3 Phase fault DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138 KV 514933 TO MIDWEST4 138 KV 514946 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DRAPER_4__SOONRTP4 | 3 Phase fault DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138 KV 514933 TO SOONRTP4 138 KV 514949 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DRAPER_7__NORMHLL7 | 3 Phase fault DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345 KV 514934 TO NORMHLL7 345 KV 516096 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DRAPER_7__SEMINOL7 | 3 Phase fault DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345 KV 514934 TO SEMINOL7 345 KV 515045 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DRYGULCH5__GEN | 3 Phase fault DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 161 KV 512629 TO GEN-2017-073 161 KV 589110 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DUGLASV2__DARENCT2 | 3 Phase fault DUGLASV2 (509645) 69 kV Bus a. Apply fault at the DUGLASV2 (509645) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUGLASV2 69 KV 509645 TO BLALOCK2 69 KV 509646 CKT 1 b.2. LOAD 1 509646 b.3. BLALOCK2 69 KV 509646 TO DARENCT2 69 KV 509647 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DUGLASV2__MAUDT__2 | 3 Phase fault DUGLASV2 (509645) 69 kV Bus a. Apply fault at the DUGLASV2 (509645) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUGLASV2 69 KV 509645 TO MAUDT 2 69 KV 509653 CKT NO c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DUGLASV2__ROACH__2 | 3 Phase fault DUGLASV2 (509645) 69 kV Bus a. Apply fault at the DUGLASV2 (509645) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUGLASV2 69 KV 509645 TO NLINDEN2 69 KV 509652 CKT 1 b.2. LOAD 1 509652 b.3. NLINDEN2 69 KV 509652 TO ROACH 2 69 KV 509668 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DUNCAN | 3 Phase fault DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138 KV 511453 TO OMDUNCN4 138 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DVISION4__HAYMAKR4 | 3 Phase fault DVISION4 (514853) 138 kV Bus a. Apply fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 138 KV 514853 TO HAYMAKR4 138 KV 514863 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DVISION4__HEFNER_4 | 3 Phase fault DVISION4 (514853) 138 kV Bus a. Apply fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKESID4 138 KV 514849 TO DVISION4 138 KV 514853 CKT 1 b.2. LOAD 1 514853 b.3. HEFNER 4 138 KV 514848 TO LAKESID4 138 KV 514849 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DVISION4__MUSTANG4 | 3 Phase fault DVISION4 (514853) 138 kV Bus a. Apply fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 138 KV 514853 TO MUSTANG4 138 KV 514861 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DVISION4__NORTWST4 | 3 Phase fault DVISION4 (514853) 138 kV Bus a. Apply fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 138 KV 514853 TO RICHRDS4 138 KV 514862 CKT 1 b.2. LOAD 1 514862 b.3. RICHRDS4 138 KV 514862 TO PIEDMNT4 138 KV 514864 CKT 1 b.4. LOAD 1 514864 b.5. PIEDMNT4 138 KV 514864 TO NORTWST4 138 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DVISION4__RICHRDS4 | 3 Phase fault DVISION4 (514853) 138 kV Bus a. Apply fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 138 KV 514853 TO RICHRDS4 138 KV 514862 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DX | 3 Phase fault DX----W2 (509796) 69 kV Bus a. Apply fault at the DX----W2 (509796) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DX----W2 69 KV 509796 TO S.S.---2 69 KV 509816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_EAGLCHF2__RNGWODJ2 | 3 Phase fault EAGLCHF2 (520890) 69 kV Bus a. Apply fault at the EAGLCHF2 (520890) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLCHF2 69 KV 520890 TO RNGWODJ2 69 KV 521039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_EKNGFSH4__EKFSHTP4 | 3 Phase fault EKNGFSH4 (520484) 138 kV Bus a. Apply fault at the EKNGFSH4 (520484) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EKNGFSH4 138 KV 520484 TO EKFSHTP4 138 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ELRENO_CIMARON | 3 Phase fault EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138 KV 514819 TO CIMARON4 138 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ELRENO_JENSENT | 3 Phase fault EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138 KV 514819 TO JENSENT4 138 KV 514820 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ELRENO_ROMNOSE | 3 Phase fault EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138 KV 514819 TO OMEGA 4 138 KV 515962 CKT 1 b.2. LOAD 1 515962 b.3. ROMNOSE4 138 KV 514823 TO OMEGA 4 138 KV 515962 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ELKCITY6__CHISHOLM6 | 3 Phase fault ELKCITY6 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 230 KV 511490 TO CHISHOLM6 230 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ELKCTY_CLINTJC4 | 3 Phase fault ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 138 KV 511458 TO CLINTJC4 138 KV 511485 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ELKCTY_FALCNRD | 3 Phase fault ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 138 KV 511458 TO FALCNRD4 138 KV 511511 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ELKCTY_REDHLSW | 3 Phase fault ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 138 KV 511458 TO REDHLSW4 138 KV 521116 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_EMPIRE_4__FLETCH | 3 Phase fault EMPIRE 4 (520900) 138 kV Bus a. Apply fault at the EMPIRE 4 (520900) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMPIRE 4 138 KV 520900 TO FLETCH-4 138 KV 520912 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ENID___2__SO4TH__2 | 3 Phase fault ENID 2 (514727) 69 kV Bus a. Apply fault at the ENID 2 (514727) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENID 2 69 KV 514727 TO SO4TH 2 69 KV 514730 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ERLSBOR2__FRSTHIL2 | 3 Phase fault ERLSBOR2 (515073) 69 kV Bus a. Apply fault at the ERLSBOR2 (515073) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ERLSBOR2 69 KV 515073 TO FRSTHIL2 69 KV 515074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_EUFREST2__WELLSPA2 | 3 Phase fault EUFREST2 (515214) 69 kV Bus a. Apply fault at the EUFREST2 (515214) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUFREST2 69 KV 515214 TO WELLSPA2 69 KV 515215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_EXCLART4__EXPCLAR4 | 3 Phase fault EXCLART4 (510401) 138 kV Bus a. Apply fault at the EXCLART4 (510401) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXCLART4 138 KV 510401 TO EXPCLAR4 138 KV 510405 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_EXCLART4__G17 | 3 Phase fault EXCLART4 (510401) 138 kV Bus a. Apply fault at the EXCLART4 (510401) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXCLART4 138 KV 510401 TO G17-077-TAP 138 KV 589154 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_EXPLGLN4__EXPGLNT4 | 3 Phase fault EXPLGLN4 (515248) 138 kV Bus a. Apply fault at the EXPLGLN4 (515248) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXPLGLN4 138 KV 515248 TO EXPGLNT4 138 KV 515473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_EYLAU__4__BUCHANN4 | 3 Phase fault EYLAU 4 (509655) 138 kV Bus a. Apply fault at the EYLAU 4 (509655) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EYLAU 4 138 KV 509655 TO BUCHANN4 138 KV 509656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FAIRVEW2__OKEENE_2 | 3 Phase fault FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69 KV 520909 TO OKEENE 2 69 KV 521015 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FAIRVEW2__OMFAIRV2 | 3 Phase fault FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69 KV 520909 TO OMFAIRV2 69 KV 529343 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FAIRVEW2__RNGWODJ2 | 3 Phase fault FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69 KV 520909 TO RNGWODJ2 69 KV 521039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FIXCT4__FIXICO_4 | 3 Phase fault FIXCT4 (510877) 138 kV Bus a. Apply fault at the FIXCT4 (510877) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIXCT4 138 KV 510877 TO FIXICO 4 138 KV 515078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FIXCT4__WELETK4 | 3 Phase fault FIXCT4 (510877) 138 kV Bus a. Apply fault at the FIXCT4 (510877) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIXCT4 138 KV 510877 TO WELETK4 138 KV 510902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FLETCHR4__FLE_TAP4 | 3 Phase fault FLETCHR4 (511422) 138 kV Bus a. Apply fault at the FLETCHR4 (511422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR4 138 KV 511422 TO FLE TAP4 138 KV 511423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FLE_TAP4__G16 | 3 Phase fault FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138 KV 511423 TO G16-097-TAP 138 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FLE_TAP4__L.E.S. | 3 Phase fault FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138 KV 511423 TO L.E.S.-4 138 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FLOURNY2__PINESRD2 | 3 Phase fault FLOURNY2 (507726) 69 kV Bus a. Apply fault at the FLOURNY2 (507726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 69 KV 507726 TO PINESRD2 69 KV 507747 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FLOURNY2__WASKOM_2 | 3 Phase fault FLOURNY2 (507726) 69 kV Bus a. Apply fault at the FLOURNY2 (507726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 69 KV 507726 TO WASKOM 2 69 KV 508839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FLOURNY2__WOOLWTP2 | 3 Phase fault FLOURNY2 (507726) 69 kV Bus a. Apply fault at the FLOURNY2 (507726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 69 KV 507726 TO WOOLWTP2 69 KV 507770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FOREMAN2__DEQUEEN2 | 3 Phase fault FOREMAN2 (507421) 69 kV Bus a. Apply fault at the FOREMAN2 (507421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORMANR2 69 KV 507407 TO FOREMAN2 69 KV 507421 CKT 1 b.2. LOAD 1 507421 b.3. DEQUEEN 2 69 KV 504120 TO FORMANR2 69 KV 507407 CKT 1 b.4. LOAD A1 507407 b.5. DEQUEEN 2 69 KV 504120 TO DEQUEEN2 69 KV 507418 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FOREMAN2__FOREMAG2 | 3 Phase fault FOREMAN2 (507421) 69 kV Bus a. Apply fault at the FOREMAN2 (507421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOREMAN2 69 KV 507421 TO FOREMAG2 69 KV 507440 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FOREMAN2__PATTERS2 | 3 Phase fault FOREMAN2 (507421) 69 kV Bus a. Apply fault at the FOREMAN2 (507421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOREMAN2 69 KV 507421 TO PATTERS2 69 KV 507429 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FOURCTP4__FOURCNT4 | 3 Phase fault FOURCTP4 (520545) 138 kV Bus a. Apply fault at the FOURCTP4 (520545) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOURCTP4 138 KV 520545 TO FOURCNT4 138 KV 520546 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FOURCTP4__TWNLKJT4 | 3 Phase fault FOURCTP4 (520545) 138 kV Bus a. Apply fault at the FOURCTP4 (520545) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOURCTP4 138 KV 520545 TO TWNLKJT4 138 KV 520847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FRMNTAP4__FAIRMON4 | 3 Phase fault FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138 KV 514709 TO FAIRMON4 138 KV 514712 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FRMNTAP4__SO4TH__4 | 3 Phase fault FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138 KV 514709 TO SO4TH 4 138 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FRMNTAP4__WOODRNG4 | 3 Phase fault FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138 KV 514709 TO WOODRNG4 138 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FRNKLNS4__CANADNS4 | 3 Phase fault FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRNKLNS4 138 KV 520917 TO LIDDELL4 138 KV 520975 CKT 1 b.2. LOAD 1 520975 b.3. NOBLE4 138 KV 520400 TO LIDDELL4 138 KV 520975 CKT 1 b.4. LOAD 1 520975 b.5. NOBLE4 138 KV 520400 TO CANADNS4 138 KV 520842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FRNKLNS4__OU_SW_4 | 3 Phase fault FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ACME 4 138 KV 520802 TO FRNKLNS4 138 KV 520917 CKT 1 b.2. ACME 4 138 KV 520802 TO WNORMAN4 138 KV 521095 CKT 1 b.3. LOAD 1 521095 b.4. LAMAR4 138 KV 520403 TO WNORMAN4 138 KV 521095 CKT 1 b.5. LOAD 1 521095 b.6. LAMAR4 138 KV 520403 TO OU SW 4 138 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FRNKLNS4__PINK_SW4 | 3 Phase fault FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLN4 138 KV 520913 TO FRNKLNS4 138 KV 520917 CKT 1 b.2. FRANKLN4 138 KV 520913 TO PINK SW4 138 KV 521028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FRNKLNS4__SUNSHIN4 | 3 Phase fault FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRNKLNS4 138 KV 520917 TO WMOORE 4 138 KV 521123 CKT 1 b.2. LOAD 1 521123 b.3. BAILEY4 138 KV 520401 TO WMOORE 4 138 KV 521123 CKT 1 b.4. LOAD 1 521123 b.5. BAILEY4 138 KV 520401 TO SUNSHIN4 138 KV 521059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FROGVIL4__HUGO_PP4 | 3 Phase fault FROGVIL4 (520918) 138 kV Bus a. Apply fault at the FROGVIL4 (520918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FROGVIL4 138 KV 520918 TO HUGO PP4 138 KV 520948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FRSTHIL4__STRLGTP4 | 3 Phase fault FRSTHIL4 (515075) 138 kV Bus a. Apply fault at the FRSTHIL4 (515075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRSTHIL4 138 KV 515075 TO STRLGTP4 138 KV 515286 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FTSMTHE5__COLONY_5 | 3 Phase fault FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5 (515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161 KV 515300 TO COLONY 5 161 KV 515345 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FTSMTHE5__FTSMTHW5 | 3 Phase fault FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5 (515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161 KV 515300 TO FTSMTHW5 161 KV 515301 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FTSMTHE5__QUANXTP5 | 3 Phase fault FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5 (515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161 KV 515300 TO QUANXTP5 161 KV 515310 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FTSMTHW5__ARKOMA_5 | 3 Phase fault FTSMTHW5 (515301) 161 kV Bus a. Apply fault at the FTSMTHW5 (515301) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 161 KV 515301 TO ARKOMA 5 161 KV 515306 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FT_GIB_5__OKAYGR_5 | 3 Phase fault FT GIB 5 (505560) 161 kV Bus a. Apply fault at the FT GIB 5 (505560) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FT GIB 5 161 KV 505560 TO OKAYGR 5 161 KV 512640 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FULTONE4__21STTAP4 | 3 Phase fault FULTONE4 (509797) 138 kV Bus a. Apply fault at the FULTONE4 (509797) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FULTONE4 138 KV 509797 TO S21ST--4 138 KV 509808 CKT 1 b.2. LOAD 1 509808 b.3. S21ST--4 138 KV 509808 TO 21STTAP4 138 KV 509828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FULTONW4__KENSH | 3 Phase fault FULTONW4 (509829) 138 kV Bus a. Apply fault at the FULTONW4 (509829) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FULTONW4 138 KV 509829 TO KENSH-E-TP4 138 KV 509830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FULTON____3__HOPE___3 | 3 Phase fault FULTON 3 (503912) 115 kV Bus a. Apply fault at the FULTON 3 (503912) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FULTON 3 115 KV 503912 TO HOPE 3 115 KV 507453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_G07621119 | 3 Phase fault G07621119-20 (515599) 345 kV Bus a. Apply fault at the G07621119-20 (515599) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G07621119-20 345 KV 515599 TO GREAT_WESTRN 345 KV 585410 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_G07621119 | 3 Phase fault G07621119-20 (515599) 345 kV Bus a. Apply fault at the G07621119-20 (515599) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G07621119-20 345 KV 515599 TO PRSIMN_CRK1 345 KV 585430 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_G15 | 3 Phase fault G15-066T (560056) 345 kV Bus a. Apply fault at the G15-066T (560056) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G15-066T 345 KV 560056 TO GEN-2015-066 345 KV 585040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_G16 | 3 Phase fault G16-003-TAP (560071) 345 kV Bus a. Apply fault at the G16-003-TAP (560071) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP 345 KV 560071 TO GEN-2017-011 345 KV 588560 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_G16 | 3 Phase fault G16-037-TAP (560078) 345 kV Bus a. Apply fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345 KV 560078 TO GEN-2016-037 345 KV 587230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_G16 | 3 Phase fault G16-091-TAP (587744) 345 kV Bus a. Apply fault at the G16-091-TAP (587744) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-091-TAP 345 KV 587744 TO GEN-2016-095 345 KV 587770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_G16133G16146__G16133_345GS | 3 Phase fault G16133G16146 (588039) 345 kV Bus a. Apply fault at the G16133G16146 (588039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16133G16146 345 KV 588039 TO G16133_345GS 345 KV 588040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_G17-009_NESHO | 3 Phase fault G17-009-TAP (532777) 345 kV Bus a. Apply fault at the G17-009-TAP (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP 345 KV 532777 TO NEOSHO 7 345 KV 532793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_G17-092_FIREWHLTAP | 3 Phase fault G17-092-SWYD (588838) 345 kV Bus a. Apply fault at the G17-092-SWYD (588838) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-092-SWYD 345 KV 588838 TO FIREWHL-TAP 345 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_G17_151_G18-015 | 3 Phase fault G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345 KV 762216 TO G18-015-TAP 345 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GLASMTN4__MOORLND4 | 3 Phase fault GLASMTN4 (514788) 138 kV Bus a. Apply fault at the GLASMTN4 (514788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLASMTN4 138 KV 514788 TO MOORLND4 138 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GLENWD_4__IMO____4 | 3 Phase fault GLENWD 4 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 138 KV 514734 TO IMO 4 138 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GOLDSBY4__OU_SW_4 | 3 Phase fault GOLDSBY4 (520924) 138 kV Bus a. Apply fault at the GOLDSBY4 (520924) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOLDSBY4 138 KV 520924 TO OU SW 4 138 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GORE___5__EUFAULA5 | 3 Phase fault GORE 5 (505552) 161 kV Bus a. Apply fault at the GORE 5 (505552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161 KV 505552 TO EUFAULA5 161 KV 505570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GORE___5__MUSKTAP5 | 3 Phase fault GORE 5 (505552) 161 kV Bus a. Apply fault at the GORE 5 (505552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161 KV 505552 TO MUSKTAP5 161 KV 505558 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GORE___5__TENKIL_5 | 3 Phase fault GORE 5 (505552) 161 kV Bus a. Apply fault at the GORE 5 (505552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161 KV 505552 TO TENKIL 5 161 KV 505566 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GORE___5__WEBFALL5 | 3 Phase fault GORE 5 (505552) 161 kV Bus a. Apply fault at the GORE 5 (505552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161 KV 505552 TO WEBFALL5 161 KV 505554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GORE___5__WELEETK5 | 3 Phase fault GORE 5 (505552) 161 kV Bus a. Apply fault at the GORE 5 (505552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161 KV 505552 TO WELEETK5 161 KV 505590 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRACMNT4__ANADARK4 | 3 Phase fault GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138 KV 515802 TO ANADARK4 138 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRACMNT4__WASHITA4 | 3 Phase fault GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138 KV 515802 TO WASHITA4 138 KV 521089 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRACMNT7__G16 | 3 Phase fault GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345 KV 515800 TO G16-037-TAP 345 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRACMNT7__G16 | 3 Phase fault GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345 KV 515800 TO G16-091-TAP 345 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRACMNT7__GEN | 3 Phase fault GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345 KV 515800 TO GEN-2015-093 345 KV 563269 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRANNIS___2__DEQUEEN2 | 3 Phase fault GRANNIS 2 (504129) 69 kV Bus a. Apply fault at the GRANNIS 2 (504129) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANNIS 2 69 KV 504129 TO DEQUEEN2 69 KV 507418 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRAPEVINE__6__NICHOLS____6 | 3 Phase fault GRAPEVINE 6 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 230 KV 523771 TO NICHOLS 6 230 KV 524044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRAPEVINE__6__WHEELER____6 | 3 Phase fault GRAPEVINE 6 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 230 KV 523771 TO WHEELER 6 230 KV 523777 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA1__5__CHOUTEAUCRK5 | 3 Phase fault GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 161 KV 512656 TO CHOUTEAUCRK5 161 KV 513570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA1__5__MAID___5 | 3 Phase fault GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 161 KV 512656 TO WMAIN ST5 161 KV 512742 CKT 1 b.2. LOAD 1 512742 b.3. WMAIN ST5 161 KV 512742 TO NWMAID5 161 KV 512757 CKT 1 b.4. LOAD 1 512757 b.5. NWMAID5 161 KV 512757 TO GERALDGAY5 161 KV 512760 CKT 1 b.6. LOAD 1 512760 b.7. MAID 5 161 KV 512648 TO GERALDGAY5 161 KV 512760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA1__5__WAGNOR_5 | 3 Phase fault GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 161 KV 512656 TO WAGNOR 5 161 KV 512700 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA1__7__GREC_TAP5 | 3 Phase fault GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 345 KV 512650 TO GREC TAP5 345 KV 512865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA1__7__TONECE7 | 3 Phase fault GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 345 KV 512650 TO TONECE7 345 KV 512750 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDGVTP4__MEEKRSW4 | 3 Phase fault GRDGVTP4 (520526) 138 kV Bus a. Apply fault at the GRDGVTP4 (520526) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDGVTP4 138 KV 520526 TO MEEKRSW4 138 KV 520994 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GREAT_WESTRN__COWBOY_RIDGE | 3 Phase fault GREAT_WESTRN (585410) 345 kV Bus a. Apply fault at the GREAT_WESTRN (585410) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GREAT_WESTRN 345 KV 585410 TO COWBOY_RIDGE 345 KV 585420 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GREC_TAP5__IGLOOV_7 | 3 Phase fault GREC TAP5 (512865) 345 kV Bus a. Apply fault at the GREC TAP5 (512865) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GREC TAP5 345 KV 512865 TO IGLOOV 7 345 KV 513596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRTWSRN7__GUTHRIE7 | 3 Phase fault GRTWSRN7 (515825) 345 kV Bus a. Apply fault at the GRTWSRN7 (515825) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRTWSRN7 345 KV 515825 TO GUTHRIE7 345 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HAMMTAP4__HAMMETT4 | 3 Phase fault HAMMTAP4 (515046) 138 kV Bus a. Apply fault at the HAMMTAP4 (515046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMMTAP4 138 KV 515046 TO HAMMETT4 138 KV 520951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HAMMTAP4__LINCOLN4 | 3 Phase fault HAMMTAP4 (515046) 138 kV Bus a. Apply fault at the HAMMTAP4 (515046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMMTAP4 138 KV 515046 TO LINCOLN4 138 KV 515442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HARPER2__ANADARK2 | 3 Phase fault HARPER2 (520440) 69 kV Bus a. Apply fault at the HARPER2 (520440) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER2 69 KV 520440 TO ANADARK2 69 KV 520810 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HARRISN4__KNOXLEE4 | 3 Phase fault HARRISN4 (508544) 138 kV Bus a. Apply fault at the HARRISN4 (508544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRISN4 138 KV 508544 TO KNOXLEE4 138 KV 508548 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HARTSIS4__S_SHV__4 | 3 Phase fault HARTSIS4 (507735) 138 kV Bus a. Apply fault at the HARTSIS4 (507735) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARTSIS4 138 KV 507735 TO S SHV 4 138 KV 507755 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HEFNER_4__TENESTP4 | 3 Phase fault HEFNER 4 (514848) 138 kV Bus a. Apply fault at the HEFNER 4 (514848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILSHIR4 138 KV 514836 TO HEFNER 4 138 KV 514848 CKT 1 b.2. WILSHIR4 138 KV 514836 TO TENNESE4 138 KV 514838 CKT 1 b.3. LOAD 1 514838 b.4. TENESTP4 138 KV 514837 TO TENNESE4 138 KV 514838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HENESEY4__BULFTTP4 | 3 Phase fault HENESEY4 (514774) 138 kV Bus a. Apply fault at the HENESEY4 (514774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 138 KV 514774 TO BULFTTP4 138 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HENESEY4__DOVERSW4 | 3 Phase fault HENESEY4 (514774) 138 kV Bus a. Apply fault at the HENESEY4 (514774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 138 KV 514774 TO DOVERSW4 138 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HERRON_5__IGLOOV1_5 | 3 Phase fault HERRON 5 (513591) 161 kV Bus a. Apply fault at the HERRON 5 (513591) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HERRON 5 161 KV 513591 TO IGLOOV1 5 161 KV 513593 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HERRON_5__IGLOOV2_5 | 3 Phase fault HERRON 5 (513591) 161 kV Bus a. Apply fault at the HERRON 5 (513591) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HERRON 5 161 KV 513591 TO IGLOOV2 5 161 KV 513595 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HIGHLND4__PINK_SW4 | 3 Phase fault HIGHLND4 (520941) 138 kV Bus a. Apply fault at the HIGHLND4 (520941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGHLND4 138 KV 520941 TO PINK SW4 138 KV 521028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HLTOPTP__BEELINE2 | 3 Phase fault HLTOPTP (514200) 69 kV Bus a. Apply fault at the HLTOPTP (514200) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLTOPTP 69 KV 514200 TO BEELINE2 69 KV 515246 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HOB | 3 Phase fault HOB-JCT4 (511463) 138 kV Bus a. Apply fault at the HOB-JCT4 (511463) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT4 138 KV 511463 TO MARTHA 4 138 KV 511564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HOB | 3 Phase fault HOB-JCT4 (511463) 138 kV Bus a. Apply fault at the HOB-JCT4 (511463) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT4 138 KV 511463 TO RKY_RDG4 138 KV 511554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HOBBYLO4__CHEMTRN4 | 3 Phase fault HOBBYLO4 (515338) 138 kV Bus a. Apply fault at the HOBBYLO4 (515338) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBYLO4 138 KV 515338 TO CHEMTRN4 138 KV 515367 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HOCHJCT4__DOMINJCT4 | 3 Phase fault HOCHJCT4 (520823) 138 kV Bus a. Apply fault at the HOCHJCT4 (520823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOCHJCT4 138 KV 520823 TO DOMINJCT4 138 KV 521195 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HOCHJCT4__HOCHTWN4 | 3 Phase fault HOCHJCT4 (520823) 138 kV Bus a. Apply fault at the HOCHJCT4 (520823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOCHJCT4 138 KV 520823 TO HOCHTWN4 138 KV 520943 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HOLLYWD4__INDNHIL4 | 3 Phase fault HOLLYWD4 (514953) 138 kV Bus a. Apply fault at the HOLLYWD4 (514953) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLLYWD4 138 KV 514953 TO INDNHIL4 138 KV 514954 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HOOKS__2__LSORDTP2 | 3 Phase fault HOOKS 2 (508057) 69 kV Bus a. Apply fault at the HOOKS 2 (508057) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOKS 2 69 KV 508057 TO LSORDTP2 69 KV 508063 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HOOKS__2__REDRVR | 3 Phase fault HOOKS 2 (508057) 69 kV Bus a. Apply fault at the HOOKS 2 (508057) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOKS 2 69 KV 508057 TO REDRVR-2 69 KV 508074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HOPESWI3__HOPE___3 | 3 Phase fault HOPESWI3 (507452) 115 kV Bus a. Apply fault at the HOPESWI3 (507452) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOPESWI3 115 KV 507452 TO HOPE 3 115 KV 507453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HSLEAST2__DEEPFKT2 | 3 Phase fault HSLEAST2 (514927) 69 kV Bus a. Apply fault at the HSLEAST2 (514927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69 KV 514927 TO GRNPAST2 69 KV 514971 CKT 1 b.2. LOAD 1 514971 b.3. DEEPFKT2 69 KV 514970 TO GRNPAST2 69 KV 514971 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HSLEAST2__HSLWEST2 | 3 Phase fault HSLEAST2 (514927) 69 kV Bus a. Apply fault at the HSLEAST2 (514927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69 KV 514927 TO HSLWEST2 69 KV 514937 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HSLEAST2__MCLOUDT2 | 3 Phase fault HSLEAST2 (514927) 69 kV Bus a. Apply fault at the HSLEAST2 (514927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69 KV 514927 TO MCLOUDT2 69 KV 515504 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HSLEAST2__TXSTELA2 | 3 Phase fault HSLEAST2 (514927) 69 kV Bus a. Apply fault at the HSLEAST2 (514927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69 KV 514927 TO TXSTELA2 69 KV 514985 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HSL____4__GEN | 3 Phase fault HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138 KV 514941 TO GEN-2018-029 138 KV 762647 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HSL____4__HAMMTAP4 | 3 Phase fault HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138 KV 514941 TO HAMMTAP4 138 KV 515046 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HSL____4__JONESSB4 | 3 Phase fault HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138 KV 514941 TO JONESSB4 138 KV 515480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HSL____4__RENO___4 | 3 Phase fault HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138 KV 514941 TO MIDWAY 4 138 KV 514966 CKT 1 b.2. LOAD 1 514966 b.3. NE10TH 4 138 KV 514964 TO MIDWAY 4 138 KV 514966 CKT 1 b.4. LOAD 1 514966 b.5. NE10TH 4 138 KV 514964 TO RENO 4 138 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HSL____4__SE15TH_4 | 3 Phase fault HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138 KV 514941 TO SE15TH 4 138 KV 514993 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HSL____4__SQUIRCK4 | 3 Phase fault HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138 KV 514941 TO DALE 4 138 KV 514987 CKT 1 b.2. LOAD 1 514987 b.3. DALE 4 138 KV 514987 TO SQUIRCK4 138 KV 515059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HUGO | 3 Phase fault HUGO---4 (510901) 138 kV Bus a. Apply fault at the HUGO---4 (510901) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGO---4 138 KV 510901 TO VALIANT4 138 KV 510918 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HUGOITC4__HUGO_PP4 | 3 Phase fault HUGOITC4 (520560) 138 kV Bus a. Apply fault at the HUGOITC4 (520560) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOITC4 138 KV 520560 TO HUGO PP4 138 KV 520948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HUGO_PP4__GEN | 3 Phase fault HUGO PP4 (520948) 138 kV Bus a. Apply fault at the HUGO PP4 (520948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGO PP4 138 KV 520948 TO GEN-2017-023 138 KV 588670 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HUGO_PP4__VALLANT4 | 3 Phase fault HUGO PP4 (520948) 138 kV Bus a. Apply fault at the HUGO PP4 (520948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGO PP4 138 KV 520948 TO VALLANT4 138 KV 521079 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HUGO___7__G17 | 3 Phase fault HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 345 KV 521157 TO G17-075-TAP 345 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HUNTERS7__CHSHLMV7 | 3 Phase fault HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 345 KV 515476 TO CHSHLMV7 345 KV 515477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HUNTERS7__RENFROW7 | 3 Phase fault HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 345 KV 515476 TO RENFROW7 345 KV 515543 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HWY20 | 3 Phase fault HWY20-T4 (509821) 138 kV Bus a. Apply fault at the HWY20-T4 (509821) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HWY20-T4 138 KV 509821 TO WLDCT_HIL4 138 KV 509897 CKT 1 b.2. LOAD 1 509897 b.3. HWY20--4 138 KV 509798 TO WLDCT_HIL4 138 KV 509897 CKT 1 b.4. LOAD 1 509897 b.5. HWY20--4 138 KV 509798 TO OMHOMNY4 138 KV 529306 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_INOLATP4__CATOOSA4 | 3 Phase fault INOLATP4 (509752) 138 kV Bus a. Apply fault at the INOLATP4 (509752) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INOLATP4 138 KV 509752 TO CATOOSA4 138 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_INOLATP4__EXCLART4 | 3 Phase fault INOLATP4 (509752) 138 kV Bus a. Apply fault at the INOLATP4 (509752) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INOLATP4 138 KV 509752 TO ROCKPT-4 138 KV 510437 CKT 1 b.2. LOAD 1 510437 b.3. CHOUTEA4 138 KV 510373 TO ROCKPT-4 138 KV 510437 CKT 1 b.4. LOAD 1 510437 b.5. CHOUTEA4 138 KV 510373 TO EXCLART4 138 KV 510401 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_INOLA__4__INOLATP4 | 3 Phase fault INOLA 4 (509736) 138 kV Bus a. Apply fault at the INOLA 4 (509736) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INOLA 4 138 KV 509736 TO INOLATP4 138 KV 509752 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_IODINE_4__MOORLND4 | 3 Phase fault IODINE 4 (520957) 138 kV Bus a. Apply fault at the IODINE 4 (520957) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IODINE 4 138 KV 520957 TO MOORLND4 138 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_IPC_TAP2__IPC____2 | 3 Phase fault IPC TAP2 (508058) 69 kV Bus a. Apply fault at the IPC TAP2 (508058) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC TAP2 69 KV 508058 TO IPC 2 69 KV 508092 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_IPC_T__4__CASSTP4 | 3 Phase fault IPC T 4 (508059) 138 kV Bus a. Apply fault at the IPC T 4 (508059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138 KV 508059 TO CASSTP4 138 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_IPC_T__4__IPC____4 | 3 Phase fault IPC T 4 (508059) 138 kV Bus a. Apply fault at the IPC T 4 (508059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138 KV 508059 TO IPC 4 138 KV 508095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_JEFFRSN4__LAKEPIN4 | 3 Phase fault JEFFRSN4 (508835) 138 kV Bus a. Apply fault at the JEFFRSN4 (508835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138 KV 508835 TO LAKEPIN4 138 KV 509624 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_JEFFRSN4__WILKES_4 | 3 Phase fault JEFFRSN4 (508835) 138 kV Bus a. Apply fault at the JEFFRSN4 (508835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138 KV 508835 TO WILKES 4 138 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_JENSENT4__CIMARON4 | 3 Phase fault JENSENT4 (514820) 138 kV Bus a. Apply fault at the JENSENT4 (514820) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSENT4 138 KV 514820 TO CIMARON4 138 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_JENSENT4__JENSEN_4 | 3 Phase fault JENSENT4 (514820) 138 kV Bus a. Apply fault at the JENSENT4 (514820) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSENT4 138 KV 514820 TO JENSEN 4 138 KV 514821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_JENSEN_4__EL_RENO4 | 3 Phase fault JENSEN 4 (514821) 138 kV Bus a. Apply fault at the JENSEN 4 (514821) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSEN 4 138 KV 514821 TO EL RENO4 138 KV 520893 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_JNSKAMO4__ARCADIA4 | 3 Phase fault JNSKAMO4 (514906) 138 kV Bus a. Apply fault at the JNSKAMO4 (514906) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 138 KV 514906 TO ARCADIA4 138 KV 514907 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_JNSKAMO4__HSL____4 | 3 Phase fault JNSKAMO4 (514906) 138 kV Bus a. Apply fault at the JNSKAMO4 (514906) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 138 KV 514906 TO HSL 4 138 KV 514941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_JOHNCO_4__CANEYCK4 | 3 Phase fault JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138 KV 514808 TO CANEYCK4 138 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_JOHNCO_4__RUSSET | 3 Phase fault JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138 KV 514808 TO RUSSET-4 138 KV 515120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_JOHNCO_4__SXMLCKT4 | 3 Phase fault JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138 KV 514808 TO SXMLCKT4 138 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_JOHNCO_7__DMNDSPG7 | 3 Phase fault JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345 KV 514809 TO DMNDSPG7 345 KV 516006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_JOHNCO_7__GEN | 3 Phase fault JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345 KV 514809 TO GEN-2017-149 345 KV 760830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_JOHNCO_7__SUNNYSD7 | 3 Phase fault JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345 KV 514809 TO SUNNYSD7 345 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_JONESSB4__LGARBER4 | 3 Phase fault JONESSB4 (515480) 138 kV Bus a. Apply fault at the JONESSB4 (515480) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHTWOOD4 138 KV 514842 TO JONESSB4 138 KV 515480 CKT 1 b.2. CHTWOOD4 138 KV 514842 TO LGARBER4 138 KV 515465 CKT 1 b.3. LOAD 1 515465 b.4. ARCADIA4 138 KV 514907 TO LGARBER4 138 KV 515465 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_KANSATP5__KANSAS_5 | 3 Phase fault KANSATP5 (512714) 161 kV Bus a. Apply fault at the KANSATP5 (512714) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KANSATP5 161 KV 512714 TO KANSAS 5 161 KV 512716 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_KELLYAV4__MEMRIAL4 | 3 Phase fault KELLYAV4 (514501) 138 kV Bus a. Apply fault at the KELLYAV4 (514501) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLYAV4 138 KV 514501 TO MEMRIAL4 138 KV 514835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_KENSH | 3 Phase fault KENSH-E4 (509744) 138 kV Bus a. Apply fault at the KENSH-E4 (509744) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENSH-E4 138 KV 509744 TO ZUNIS-N4 138 KV 509827 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_KENTUKT2__44&SUNL2 | 3 Phase fault KENTUKT2 (514977) 69 kV Bus a. Apply fault at the KENTUKT2 (514977) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENTUKT2 69 KV 514977 TO SAGE 2 69 KV 514978 CKT 1 b.2. LOAD 1 514978 b.3. SAGE 2 69 KV 514978 TO 44&SUNL2 69 KV 514979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_KERR_GR5__KANSATP5 | 3 Phase fault KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161 KV 512635 TO 412SUB 5 161 KV 512637 CKT 1 b.2. LOAD 1 512637 b.3. 412SUB 5 161 KV 512637 TO KANSATP5 161 KV 512714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_KERR_GR5__KERR_BRK1_5 | 3 Phase fault KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161 KV 512635 TO KERR BRK1 5 161 KV 512770 CKT Z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_KERR_GR5__MAID___5 | 3 Phase fault KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161 KV 512635 TO MAID 5 161 KV 512648 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_KERR_GR5__PENSA__5 | 3 Phase fault KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161 KV 512635 TO PENSA 5 161 KV 512654 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_KERR_GR5__SALNCRK5 | 3 Phase fault KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161 KV 512635 TO SALNCRK5 161 KV 512805 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_KETCHTP4__KETCH__4 | 3 Phase fault KETCHTP4 (514828) 138 kV Bus a. Apply fault at the KETCHTP4 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 138 KV 514828 TO KETCH 4 138 KV 514834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_KETCHTP4__NORTWST4 | 3 Phase fault KETCHTP4 (514828) 138 kV Bus a. Apply fault at the KETCHTP4 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 138 KV 514828 TO NORTWST4 138 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_KETCH__4__FAIRFLD4 | 3 Phase fault KETCH 4 (514834) 138 kV Bus a. Apply fault at the KETCH 4 (514834) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCH 4 138 KV 514834 TO FAIRFLD4 138 KV 515468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_KEYSTON4__WEKIWA | 3 Phase fault KEYSTON4 (505610) 138 kV Bus a. Apply fault at the KEYSTON4 (505610) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON4 138 KV 505610 TO WEKIWA-4 138 KV 509757 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_KGFSHSW4__CALUMET4 | 3 Phase fault KGFSHSW4 (520533) 138 kV Bus a. Apply fault at the KGFSHSW4 (520533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSHSW4 138 KV 520533 TO CONCHO 4 138 KV 520865 CKT 1 b.2. LOAD 1 520865 b.3. CALUMET4 138 KV 520839 TO CONCHO 4 138 KV 520865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_KGFSHSW4__CMBLTP_4 | 3 Phase fault KGFSHSW4 (520533) 138 kV Bus a. Apply fault at the KGFSHSW4 (520533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSHSW4 138 KV 520533 TO REEDING4 138 KV 521037 CKT 1 b.2. LOAD 1 521037 b.3. CMBLTP 4 138 KV 520474 TO REEDING4 138 KV 521037 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_KGFSHSW4__EKFSHTP4 | 3 Phase fault KGFSHSW4 (520533) 138 kV Bus a. Apply fault at the KGFSHSW4 (520533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSHSW4 138 KV 520533 TO EKFSHTP4 138 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_KGFSJCT4__EKFSHTP4 | 3 Phase fault KGFSJCT4 (520405) 138 kV Bus a. Apply fault at the KGFSJCT4 (520405) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSJCT4 138 KV 520405 TO EKFSHTP4 138 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_KINZEGR4__KINZE__4 | 3 Phase fault KINZEGR4 (512710) 138 kV Bus a. Apply fault at the KINZEGR4 (512710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZEGR4 138 KV 512710 TO KINZE 4 138 KV 515008 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_KINZE__4__UNVRSTY4 | 3 Phase fault KINZE 4 (515008) 138 kV Bus a. Apply fault at the KINZE 4 (515008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZE 4 138 KV 515008 TO UNVRSTY4 138 KV 515181 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_KIPUMPT2__FTOWSON2 | 3 Phase fault KIPUMPT2 (510876) 69 kV Bus a. Apply fault at the KIPUMPT2 (510876) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KIPUMPT2 69 KV 510876 TO FTOWSON2 69 KV 510917 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_KIPUMPT2__VALIANT2 | 3 Phase fault KIPUMPT2 (510876) 69 kV Bus a. Apply fault at the KIPUMPT2 (510876) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KIPUMPT2 69 KV 510876 TO VALIANT2 69 KV 510910 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_KI_PMPN2__KIPUMPT2 | 3 Phase fault KI PMPN2 (510875) 69 kV Bus a. Apply fault at the KI PMPN2 (510875) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KI PMPN2 69 KV 510875 TO KIPUMPT2 69 KV 510876 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_KNGFSHR7__FSHRTAP7 | 3 Phase fault KNGFSHR7 (515600) 345 kV Bus a. Apply fault at the KNGFSHR7 (515600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KNGFSHR7 345 KV 515600 TO FSHRTAP7 345 KV 515610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_KNOBHIL4__DGRASSE4 | 3 Phase fault KNOBHIL4 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 138 KV 514795 TO DGRASSE4 138 KV 515853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_KNOXLEE4__BRANDYBR | 3 Phase fault KNOXLEE4 (508548) 138 kV Bus a. Apply fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138 KV 508548 TO BRANDYBR 138 KV 508596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_KNOXLEE4__CHEROKE4 | 3 Phase fault KNOXLEE4 (508548) 138 kV Bus a. Apply fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138 KV 508548 TO CHEROKE4 138 KV 509059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_KNOXLEE4__MONROER4 | 3 Phase fault KNOXLEE4 (508548) 138 kV Bus a. Apply fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138 KV 508548 TO MONROER4 138 KV 509073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_KNOXLEE4__OAK2HIL4 | 3 Phase fault KNOXLEE4 (508548) 138 kV Bus a. Apply fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138 KV 508548 TO OAK2HIL4 138 KV 509078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_KNOXLEE4__SOTXEST4 | 3 Phase fault KNOXLEE4 (508548) 138 kV Bus a. Apply fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138 KV 508548 TO SOTXEST4 138 KV 508570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_L.E.S._LGOREN2 | 3 Phase fault L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69 KV 511466 TO LGORE-N2 69 KV 511469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_L.E.S._LGORES2 | 3 Phase fault L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69 KV 511466 TO LGORE-S2 69 KV 511470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_L.E.S._ARTVLTP4 | 3 Phase fault L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138 KV 511467 TO SHERID4 138 KV 511474 CKT 1 b.2. LOAD 1 511474 b.3. SHERID4 138 KV 511474 TO ARTVLTP4 138 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_L.E.S._COMMTAP4 | 3 Phase fault L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138 KV 511467 TO COMMTAP4 138 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_L.E.S._ELGINJT4 | 3 Phase fault L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138 KV 511467 TO ELGINJT4 138 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_L.E.S._SHERID4 | 3 Phase fault L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138 KV 511467 TO SHERID4 138 KV 511474 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_L.E.S._G16-091-TAP | 3 Phase fault L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345 KV 511468 TO G16-091-TAP 345 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_L.E.S._G17-171-TAP | 3 Phase fault L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345 KV 511468 TO G17-171-TAP 345 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LEASIDE_4__LOGANSP4 | 3 Phase fault LEASIDE 4 (507793) 138 kV Bus a. Apply fault at the LEASIDE 4 (507793) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEASIDE 4 138 KV 507793 TO STONWAL4 138 KV 509052 CKT 1 b.2. LOAD 1 509052 b.3. KEATCHI4 138 KV 509050 TO STONWAL4 138 KV 509052 CKT 1 b.4. LOAD 1 509052 b.5. KEATCHI4 138 KV 509050 TO GEORPAC4 138 KV 509064 CKT 1 b.6. GEORPAC4 138 KV 509064 TO LOGANSP4 138 KV 509071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LEONARD4__MLCLMRD4 | 3 Phase fault LEONARD4 (511575) 138 kV Bus a. Apply fault at the LEONARD4 (511575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEONARD4 138 KV 511575 TO MLCLMRD4 138 KV 515933 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LGYEAR_112GORE | 3 Phase fault LG-YEAR4 (511428) 138 kV Bus a. Apply fault at the LG-YEAR4 (511428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-YEAR4 138 KV 511428 TO 112GORE4 138 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LIEBERM2__OILCITY2 | 3 Phase fault LIEBERM2 (508805) 69 kV Bus a. Apply fault at the LIEBERM2 (508805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM2 69 KV 508805 TO OILCITY2 69 KV 508812 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LIEBERM4__G16 | 3 Phase fault LIEBERM4 (508806) 138 kV Bus a. Apply fault at the LIEBERM4 (508806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138 KV 508806 TO G16-167-TAP 138 KV 588404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LIEBERM4__JEFFRSN4 | 3 Phase fault LIEBERM4 (508806) 138 kV Bus a. Apply fault at the LIEBERM4 (508806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138 KV 508806 TO IPCJEFF4 138 KV 508833 CKT 1 b.2. LOAD 1 508833 b.3. IPCJEFF4 138 KV 508833 TO JEFFRSN4 138 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LIEBERM4__LONGWD_4 | 3 Phase fault LIEBERM4 (508806) 138 kV Bus a. Apply fault at the LIEBERM4 (508806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138 KV 508806 TO LONGWD 4 138 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LINCOLN4__MEEKRSW4 | 3 Phase fault LINCOLN4 (515442) 138 kV Bus a. Apply fault at the LINCOLN4 (515442) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINCOLN4 138 KV 515442 TO MEEKER 4 138 KV 520464 CKT 1 b.2. LOAD 1 520464 b.3. MEEKER 4 138 KV 520464 TO MEEKRSW4 138 KV 520994 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LINCOLN4__WOLVRNT4 | 3 Phase fault LINCOLN4 (515442) 138 kV Bus a. Apply fault at the LINCOLN4 (515442) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JACKTWN4 138 KV 515051 TO LINCOLN4 138 KV 515442 CKT 1 b.2. JACKTWN4 138 KV 515051 TO WOLVRNT4 138 KV 515532 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LINTNRD4__NBENTON4 | 3 Phase fault LINTNRD4 (508807) 138 kV Bus a. Apply fault at the LINTNRD4 (508807) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINTNRD4 138 KV 508807 TO NBENTON4 138 KV 508811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LINWOOD4__POWELL_4 | 3 Phase fault LINWOOD4 (507738) 138 kV Bus a. Apply fault at the LINWOOD4 (507738) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINWOOD4 138 KV 507738 TO POWELL 4 138 KV 507748 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LITTLAX2__LITLAXT2 | 3 Phase fault LITTLAX2 (514951) 69 kV Bus a. Apply fault at the LITTLAX2 (514951) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTLAX2 69 KV 514951 TO LITLAXT2 69 KV 515502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LLANE_LLANET | 3 Phase fault LLANE-E4 (509728) 138 kV Bus a. Apply fault at the LLANE-E4 (509728) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LLANE-E4 138 KV 509728 TO LLAN ET4 138 KV 509771 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LLANE_LLANWT | 3 Phase fault LLANE-W4 (509720) 138 kV Bus a. Apply fault at the LLANE-W4 (509720) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LLANE-W4 138 KV 509720 TO LLAN WT4 138 KV 509770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LLAN_ET4__CATOOSA4 | 3 Phase fault LLAN ET4 (509771) 138 kV Bus a. Apply fault at the LLAN ET4 (509771) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LLAN ET4 138 KV 509771 TO CATOOSA4 138 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LLAN_WT4__DAWSONT4 | 3 Phase fault LLAN WT4 (509770) 138 kV Bus a. Apply fault at the LLAN WT4 (509770) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LLAN WT4 138 KV 509770 TO DAWSONT4 138 KV 509803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LLAN_WT4__LLANETP4 | 3 Phase fault LLAN WT4 (509770) 138 kV Bus a. Apply fault at the LLAN WT4 (509770) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LLAN WT4 138 KV 509770 TO LLANETP4 138 KV 509804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LNEOAK_4__NORTWST4 | 3 Phase fault LNEOAK 4 (514873) 138 kV Bus a. Apply fault at the LNEOAK 4 (514873) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNEOAK 4 138 KV 514873 TO NORTWST4 138 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LOCKESB2__NASHVIL2 | 3 Phase fault LOCKESB2 (507422) 69 kV Bus a. Apply fault at the LOCKESB2 (507422) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOCKESB2 69 KV 507422 TO NASHVIL2 69 KV 507426 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LONEGRV4__CHEEKTP4 | 3 Phase fault LONEGRV4 (515144) 138 kV Bus a. Apply fault at the LONEGRV4 (515144) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONEGRV4 138 KV 515144 TO CHEEKTP4 138 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LONGVHT4__WHITNEY4 | 3 Phase fault LONGVHT4 (508554) 138 kV Bus a. Apply fault at the LONGVHT4 (508554) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGVHT4 138 KV 508554 TO WHITNEY4 138 KV 508575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LONGWD_4__FLOURNY4 | 3 Phase fault LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 138 KV 508808 TO OAKPH 4 138 KV 508816 CKT 1 b.2. LOAD 1 508816 b.3. FLOURNY4 138 KV 507727 TO OAKPH 4 138 KV 508816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LONGWD_4__RAINES_4 | 3 Phase fault LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORAM 4 138 KV 507774 TO LONGWD 4 138 KV 508808 CKT 1 b.2. RAINES 4 138 KV 507749 TO NORAM 4 138 KV 507774 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LONGWD_4__SABMINT4 | 3 Phase fault LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SABMINT4 138 KV 508566 TO SEMRSHL4 138 KV 508569 CKT 1 b.2. LOAD 1 508569 b.3. SCOTTSV4 138 KV 508567 TO SEMRSHL4 138 KV 508569 CKT 1 b.4. LOAD 1 508569 b.5. SCOTTSV4 138 KV 508567 TO LONGWD 4 138 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LONGWD_7__GEN | 3 Phase fault LONGWD 7 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345 KV 508809 TO GEN-2018-050 345 KV 762845 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LONGWD_7__WILKES_7 | 3 Phase fault LONGWD 7 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345 KV 508809 TO WILKES 7 345 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LSORDTP2__LSORD__2 | 3 Phase fault LSORDTP2 (508063) 69 kV Bus a. Apply fault at the LSORDTP2 (508063) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSORDTP2 69 KV 508063 TO LSORD 2 69 KV 508093 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LSSOUTH4__DIANA__4 | 3 Phase fault LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138 KV 508297 TO DIANA 4 138 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LSSOUTH4__PITTSB_4 | 3 Phase fault LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138 KV 508297 TO PITTSB_4 138 KV 508313 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LSSOUTH4__WILKES_4 | 3 Phase fault LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138 KV 508297 TO WILKES 4 138 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LTLRLKT2__TXPLSTP2 | 3 Phase fault LTLRLKT2 (514983) 69 kV Bus a. Apply fault at the LTLRLKT2 (514983) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LTLRLKT2 69 KV 514983 TO TXPLSTP2 69 KV 515516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LWS_112GORE | 3 Phase fault LWS-NTP4 (511471) 138 kV Bus a. Apply fault at the LWS-NTP4 (511471) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS-NTP4 138 KV 511471 TO 112GORE4 138 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LWSTAP_4__L.E.S. | 3 Phase fault LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138 KV 511439 TO L.E.S.-4 138 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LWSTAP_4__RPPAPER4 | 3 Phase fault LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138 KV 511439 TO RPPAPER4 138 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LWS___S4__LWSTAP_4 | 3 Phase fault LWS S4 (511431) 138 kV Bus a. Apply fault at the LWS S4 (511431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS S4 138 KV 511431 TO LWSTAP 4 138 KV 511439 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LYDIA__7__VALIANT7 | 3 Phase fault LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345 KV 508298 TO VALIANT7 345 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LYDIA__7__WELSH__7 | 3 Phase fault LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345 KV 508298 TO WELSH 7 345 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MACOCTP2__LITLAXT2 | 3 Phase fault MACOCTP2 (514956) 69 kV Bus a. Apply fault at the MACOCTP2 (514956) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MACOCTP2 69 KV 514956 TO LITLAXT2 69 KV 515502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MAIDTP2__GRDA1_2 | 3 Phase fault MAIDTP2 (512625) 69 kV Bus a. Apply fault at the MAIDTP2 (512625) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIDTP2 69 KV 512625 TO GRDA1 2 69 KV 512727 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MAID___2__AMERCAST_S2 | 3 Phase fault MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 69 KV 512626 TO AMERCAST S2 69 KV 512681 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MAID___2__REDDEN_2 | 3 Phase fault MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 69 KV 512626 TO REDDEN 2 69 KV 512698 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MAID___5__5CDRCRST | 3 Phase fault MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 161 KV 512648 TO LOCSTGVKM 5 161 KV 513050 CKT 1 b.2. LOAD 1 513050 b.3. 5CDRCRST 161 KV 301344 TO LOCSTGVKM 5 161 KV 513050 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MAID___5__GERALDGAY5 | 3 Phase fault MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 161 KV 512648 TO GERALDGAY5 161 KV 512760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MAID___5__GRDA1__5 | 3 Phase fault MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 161 KV 512648 TO GRDA1 5 161 KV 512656 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MAID___5__PENSA__5 | 3 Phase fault MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 161 KV 512629 TO MAID 5 161 KV 512648 CKT 1 b.2. DRYGULCH5 161 KV 512629 TO PENSA 5 161 KV 512654 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MARSHL_JEFFRSN | 3 Phase fault MARSHL-4 (508557) 138 kV Bus a. Apply fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138 KV 508557 TO JEFFRSN4 138 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MARSHL_PIRKEY | 3 Phase fault MARSHL-4 (508557) 138 kV Bus a. Apply fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138 KV 508557 TO PIRKEY 4 138 KV 508562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MARSHL_4__CTNWOOD4 | 3 Phase fault MARSHL 4 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138 KV 514733 TO CTNWOOD4 138 KV 514827 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MARSHL_4__MARSHAL4 | 3 Phase fault MARSHL 4 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138 KV 514733 TO MARSHAL4 138 KV 521006 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MATHWSN7__REDNGTN7 | 3 Phase fault MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345 KV 515497 TO REDNGTN7 345 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MATHWSN7__TRAVERSE3 | 3 Phase fault MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345 KV 515497 TO TRAVERSE3 345 KV 900001 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MAUDT__2__REDWATR2 | 3 Phase fault MAUDT 2 (509653) 69 kV Bus a. Apply fault at the MAUDT 2 (509653) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUDT 2 69 KV 509653 TO REDWATR2 69 KV 509667 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MAUD___2__ERLSBOR2 | 3 Phase fault MAUD 2 (515054) 69 kV Bus a. Apply fault at the MAUD 2 (515054) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 2 69 KV 515054 TO ERLSBOR2 69 KV 515073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MAUD___2__KNAWATP2 | 3 Phase fault MAUD 2 (515054) 69 kV Bus a. Apply fault at the MAUD 2 (515054) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 2 69 KV 515054 TO KNAWATP2 69 KV 515496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MAUD___2__LTRIVRT2 | 3 Phase fault MAUD 2 (515054) 69 kV Bus a. Apply fault at the MAUD 2 (515054) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 2 69 KV 515054 TO LTRIVRT2 69 KV 515503 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MAUD___4__FIXCT4 | 3 Phase fault MAUD 4 (515055) 138 kV Bus a. Apply fault at the MAUD 4 (515055) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EARLSBORO 4 138 KV 510948 TO MAUD 4 138 KV 515055 CKT 1 b.2. FIXCT4 138 KV 510877 TO EARLSBORO 4 138 KV 510948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MAUD___4__FRSTHIL4 | 3 Phase fault MAUD 4 (515055) 138 kV Bus a. Apply fault at the MAUD 4 (515055) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 4 138 KV 515055 TO FRSTHIL4 138 KV 515075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MAYO_LLANET | 3 Phase fault MAYO--N4 (509779) 138 kV Bus a. Apply fault at the MAYO--N4 (509779) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYO--N4 138 KV 509779 TO E41ST_W4 138 KV 509886 CKT 1 b.2. LOAD 1 509886 b.3. LLAN ET4 138 KV 509771 TO E41ST_W4 138 KV 509886 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MAYO_BANNTP4 | 3 Phase fault MAYO--S4 (509780) 138 kV Bus a. Apply fault at the MAYO--S4 (509780) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYO--S4 138 KV 509780 TO BANNTAP4 138 KV 509785 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MCALEST4__TALAWANDA__4 | 3 Phase fault MCALEST4 (510908) 138 kV Bus a. Apply fault at the MCALEST4 (510908) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCALEST4 138 KV 510908 TO TALAWANDA 4 138 KV 510951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MCALESTIND_4__TALAWANDA__4 | 3 Phase fault MCALESTIND 4 (510909) 138 kV Bus a. Apply fault at the MCALESTIND 4 (510909) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCALESTIND 4 138 KV 510909 TO TALAWANDA 4 138 KV 510951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MCCLAIN4__NORMHLL4 | 3 Phase fault MCCLAIN4 (514902) 138 kV Bus a. Apply fault at the MCCLAIN4 (514902) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCLAIN4 138 KV 514902 TO NORMHLL4 138 KV 516097 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MCLOUDT2__SINCPNT2 | 3 Phase fault MCLOUDT2 (515504) 69 kV Bus a. Apply fault at the MCLOUDT2 (515504) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCLOUDT2 69 KV 515504 TO SINCPNT2 69 KV 515642 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MCLOUD_2__MCLOUDT2 | 3 Phase fault MCLOUD 2 (515065) 69 kV Bus a. Apply fault at the MCLOUD 2 (515065) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCLOUD 2 69 KV 515065 TO MCLOUDT2 69 KV 515504 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MEEKRSW4__WREDHIL4 | 3 Phase fault MEEKRSW4 (520994) 138 kV Bus a. Apply fault at the MEEKRSW4 (520994) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEEKRSW4 138 KV 520994 TO WREDHIL4 138 KV 521097 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MEMRIAL4__DANFRTH4 | 3 Phase fault MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTERN4 138 KV 514832 TO MEMRIAL4 138 KV 514835 CKT 1 b.2. LOAD 1 514835 b.3. EASTERN4 138 KV 514832 TO HAFERSB4 138 KV 515469 CKT 1 b.4. LOAD 1 515469 b.5. DANFRTH4 138 KV 514833 TO HAFERSB4 138 KV 515469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MEMRIAL4__JONESSB4 | 3 Phase fault MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138 KV 514835 TO BRYANT 4 138 KV 514839 CKT 1 b.2. LOAD 1 514839 b.3. BRYANT 4 138 KV 514839 TO ACORN 4 138 KV 515459 CKT 1 b.4. LOAD 1 515459 b.5. ACORN 4 138 KV 515459 TO JONESSB4 138 KV 515480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MEMRIAL4__REMPKTP4 | 3 Phase fault MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLYAV4 138 KV 514501 TO MEMRIAL4 138 KV 514835 CKT 1 b.2. LOAD 1 514835 b.3. KELLYAV4 138 KV 514501 TO REMPKTP4 138 KV 514872 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MEMRIAL4__SKYLINE4 | 3 Phase fault MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138 KV 514835 TO SKYLINE4 138 KV 514850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MEMRIAL4__TENESTP4 | 3 Phase fault MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138 KV 514835 TO TENESTP4 138 KV 514837 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MENOTAP4__IMO____4 | 3 Phase fault MENOTAP4 (514789) 138 kV Bus a. Apply fault at the MENOTAP4 (514789) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENOTAP4 138 KV 514789 TO IMO 4 138 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MIDWEST4__FRNKLNS4 | 3 Phase fault MIDWEST4 (514946) 138 kV Bus a. Apply fault at the MIDWEST4 (514946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWEST4 138 KV 514946 TO FRNKLNS4 138 KV 520917 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MIDWEST4__HOLLYWD4 | 3 Phase fault MIDWEST4 (514946) 138 kV Bus a. Apply fault at the MIDWEST4 (514946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWEST4 138 KV 514946 TO HOLLYWD4 138 KV 514953 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MINCO__7__CIMARON7 | 3 Phase fault MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345 KV 514801 TO CIMARON7 345 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MINCO__7__GEN-2017-233 | 3 Phase fault MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345 KV 514801 TO GEN-2017-233 345 KV 761250 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MINCO__7__GRACMNT7 | 3 Phase fault MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345 KV 514801 TO GRACMNT7 345 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MINCO__7__MCNOWND7 | 3 Phase fault MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345 KV 514801 TO MCNOWND7 345 KV 515444 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MINCO__7__MNCWND37 | 3 Phase fault MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345 KV 514801 TO MNCWND37 345 KV 515549 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MINCO__7__NORMHLL7 | 3 Phase fault MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345 KV 514801 TO NORMHLL7 345 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MINGO_21STTAP | 3 Phase fault MINGO-N4 (509760) 138 kV Bus a. Apply fault at the MINGO-N4 (509760) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGO-N4 138 KV 509760 TO 21STTAP4 138 KV 509828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MINGO_MAYON4 | 3 Phase fault MINGO-N4 (509760) 138 kV Bus a. Apply fault at the MINGO-N4 (509760) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGO-N4 138 KV 509760 TO MAYO--N4 138 KV 509779 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MINGO_MAYOS4 | 3 Phase fault MINGO-S4 (509761) 138 kV Bus a. Apply fault at the MINGO-S4 (509761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGO-S4 138 KV 509761 TO MAYO--S4 138 KV 509780 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MINGO_TSE4 | 3 Phase fault MINGO-S4 (509761) 138 kV Bus a. Apply fault at the MINGO-S4 (509761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGO-S4 138 KV 509761 TO T.S.E.-4 138 KV 509811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MINGORD4__CATOOSA4 | 3 Phase fault MINGORD4 (509802) 138 kV Bus a. Apply fault at the MINGORD4 (509802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSN-N4 138 KV 509787 TO MINGORD4 138 KV 509802 CKT 1 b.2. LOAD 1 509802 b.3. DAWSN-N4 138 KV 509787 TO 141PINE4 138 KV 509892 CKT 1 b.4. LOAD 1 509892 b.5. SPNKY CK4 138 KV 509722 TO 141PINE4 138 KV 509892 CKT 1 b.6. LOAD 1 509892 b.7. SPNKY CK4 138 KV 509722 TO CATOOSA4 138 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MOORE__2__FRNKLNS2 | 3 Phase fault MOORE 2 (520489) 69 kV Bus a. Apply fault at the MOORE 2 (520489) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE 2 69 KV 520489 TO FRNKLNS2 69 KV 520916 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MOORLND4__GEN-2016-020 | 3 Phase fault MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND4 138 KV 520999 TO GEN-2016-020 138 KV 587140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MOUNDRD4__ELIZACK4 | 3 Phase fault MOUNDRD4 (510395) 138 kV Bus a. Apply fault at the MOUNDRD4 (510395) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUNDRD4 138 KV 510395 TO ELIZACK4 138 KV 510435 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MRIETA_2__ROCKYPT4 | 3 Phase fault MRIETA 2 (515160) 138 kV Bus a. Apply fault at the MRIETA 2 (515160) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 2 138 KV 515160 TO ROCKYPT4 138 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MSKPORT5__MSKPTAP5 | 3 Phase fault MSKPORT5 (515184) 161 kV Bus a. Apply fault at the MSKPORT5 (515184) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSKPORT5 161 KV 515184 TO MSKPTAP5 161 KV 515232 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MSKPTAP5__EUCLID_5 | 3 Phase fault MSKPTAP5 (515232) 161 kV Bus a. Apply fault at the MSKPTAP5 (515232) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSKPTAP5 161 KV 515232 TO EUCLID 5 161 KV 515251 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MUNZCTY4__DUGLASV4 | 3 Phase fault MUNZCTY4 (508064) 138 kV Bus a. Apply fault at the MUNZCTY4 (508064) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138 KV 508064 TO DUGLASV4 138 KV 509666 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MUNZCTY4__WILKES_4 | 3 Phase fault MUNZCTY4 (508064) 138 kV Bus a. Apply fault at the MUNZCTY4 (508064) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138 KV 508064 TO WILKES 4 138 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MUSKOGE5__MSKPTAP5 | 3 Phase fault MUSKOGE5 (515222) 161 kV Bus a. Apply fault at the MUSKOGE5 (515222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKOGE5 161 KV 515222 TO MSKPTAP5 161 KV 515232 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MUSKOGE5__TAHLQH_5 | 3 Phase fault MUSKOGE5 (515222) 161 kV Bus a. Apply fault at the MUSKOGE5 (515222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKOGE5 161 KV 515222 TO KETOWAH5 161 KV 516027 CKT 1 b.2. LOAD 1 516027 b.3. 7CLANS 5 161 KV 515956 TO KETOWAH5 161 KV 516027 CKT 1 b.4. LOAD 1 516027 b.5. TAHLQH 5 161 KV 512655 TO 7CLANS 5 161 KV 515956 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MUSKOGE7__FIREWHL | 3 Phase fault MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345 KV 515224 TO FIREWHL-TAP 345 KV 588839 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MUSKOGE7__FTSMITH7 | 3 Phase fault MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345 KV 515224 TO FTSMITH7 345 KV 515302 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MUSKOGE7__PECANCK7 | 3 Phase fault MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345 KV 515224 TO PECANCK7 345 KV 515235 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MUSKTAP5__FT_GIB_5 | 3 Phase fault MUSKTAP5 (505558) 161 kV Bus a. Apply fault at the MUSKTAP5 (505558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKTAP5 161 KV 505558 TO FT GIB 5 161 KV 505560 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MUSKTAP5__MUSKOGE5 | 3 Phase fault MUSKTAP5 (505558) 161 kV Bus a. Apply fault at the MUSKTAP5 (505558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKTAP5 161 KV 505558 TO MUSKOGE5 161 KV 515222 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MUSTANG4__DAYTON_4 | 3 Phase fault MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138 KV 514861 TO DAYTON 4 138 KV 514892 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MUSTANG4__DOUGLTP4 | 3 Phase fault MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138 KV 514861 TO COUNCIL4 138 KV 514865 CKT 1 b.2. LOAD 1 514865 b.3. COUNCIL4 138 KV 514865 TO WESTOAK4 138 KV 514866 CKT 1 b.4. LOAD 1 514866 b.5. WESTOAK4 138 KV 514866 TO MERIDAN4 138 KV 514867 CKT 1 b.6. LOAD 1 514867 b.7. MERIDAN4 138 KV 514867 TO DOUGLTP4 138 KV 514868 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MUSTANG4__GEN-2018-026 | 3 Phase fault MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138 KV 514861 TO GEN-2018-026 138 KV 762614 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MUSTANG4__MORGAN_4 | 3 Phase fault MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138 KV 514861 TO MORGAN 4 138 KV 514896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MUSTANG4__SW_5TH_4 | 3 Phase fault MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138 KV 514861 TO SW 5TH 4 138 KV 514920 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_N.E.S._ALWUETP4 | 3 Phase fault N.E.S.-4 (510396) 138 kV Bus a. Apply fault at the N.E.S.-4 (510396) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.E.S.-4 138 KV 510396 TO HAWTHRN4 138 KV 510413 CKT 1 b.2. LOAD 1 510413 b.3. CHELSA4 138 KV 510410 TO HAWTHRN4 138 KV 510413 CKT 1 b.4. LOAD 1 510413 b.5. CHELSA4 138 KV 510410 TO ALWUETP4 138 KV 510429 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_N.E.S._BVSE4 | 3 Phase fault N.E.S.-4 (510396) 138 kV Bus a. Apply fault at the N.E.S.-4 (510396) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATOVA 4 138 KV 510384 TO N.E.S.-4 138 KV 510396 CKT 1 b.2. LOAD 1 510396 b.3. WATOVA 4 138 KV 510384 TO NOWATA-4 138 KV 510397 CKT 1 b.4. LOAD 1 510397 b.5. BV-SE--4 138 KV 510391 TO NOWATA-4 138 KV 510397 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_N.E.S._CLARMR | 3 Phase fault N.E.S.-4 (510396) 138 kV Bus a. Apply fault at the N.E.S.-4 (510396) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.E.S.-4 138 KV 510396 TO OOLOGAHKM 4 138 KV 513124 CKT 1 b.2. LOAD 1 513124 b.3. CLARMR 4 138 KV 512707 TO OOLOGAHKM 4 138 KV 513124 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_N.E.S._PCATSAT | 3 Phase fault N.E.S.-4 (510396) 138 kV Bus a. Apply fault at the N.E.S.-4 (510396) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCATSAT4 138 KV 509841 TO OWASO2_4 138 KV 509843 CKT 1 b.2. LOAD 1 509843 b.3. OWASO2_4 138 KV 509843 TO N.E.S.-4 138 KV 510396 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_N.E.S._TERNITP4 | 3 Phase fault N.E.S.-4 (510396) 138 kV Bus a. Apply fault at the N.E.S.-4 (510396) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARTOK4 138 KV 509864 TO N.E.S.-4 138 KV 510396 CKT 1 b.2. LOAD 1 510396 b.3. VERDIGS4 138 KV 509854 TO CLARTOK4 138 KV 509864 CKT 1 b.4. LOAD 1 509864 b.5. TERNITP4 138 KV 509835 TO VERDIGS4 138 KV 509854 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NASH___4__ALUMAX_4 | 3 Phase fault NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138 KV 508049 TO ALUMAX 4 138 KV 508091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NASH___4__BANN___4 | 3 Phase fault NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138 KV 508049 TO BANN 4 138 KV 508054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NASH___4__NWTXARK4 | 3 Phase fault NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138 KV 508049 TO NWTXARK4 138 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NBENTON4__G16 | 3 Phase fault NBENTON4 (508811) 138 kV Bus a. Apply fault at the NBENTON4 (508811) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NBENTON4 138 KV 508811 TO G16-167-TAP 138 KV 588404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NE10TH_4__RENO___4 | 3 Phase fault NE10TH 4 (514964) 138 kV Bus a. Apply fault at the NE10TH 4 (514964) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE10TH 4 138 KV 514964 TO RENO 4 138 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NE30TH_2__DEEPFKT2 | 3 Phase fault NE30TH 2 (514969) 69 kV Bus a. Apply fault at the NE30TH 2 (514969) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE30TH 2 69 KV 514969 TO DEEPFKT2 69 KV 514970 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NE30TH_2__RENO___2 | 3 Phase fault NE30TH 2 (514969) 69 kV Bus a. Apply fault at the NE30TH 2 (514969) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE30TH 2 69 KV 514969 TO RENO 2 69 KV 514972 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NE45TAP4__RUSHING4 | 3 Phase fault NE45TAP4 (515062) 138 kV Bus a. Apply fault at the NE45TAP4 (515062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE45TAP4 138 KV 515062 TO RUSHING4 138 KV 515064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NE45TAP4__WOLVRNT4 | 3 Phase fault NE45TAP4 (515062) 138 kV Bus a. Apply fault at the NE45TAP4 (515062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCK CK4 138 KV 515058 TO NE45TAP4 138 KV 515062 CKT 1 b.2. MOBIL 4 138 KV 515057 TO ROCK CK4 138 KV 515058 CKT 1 b.3. LOAD 1 515058 b.4. MOBIL 4 138 KV 515057 TO WOLVRNT4 138 KV 515532 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NEKOOSA2__HOLOX__2 | 3 Phase fault NEKOOSA2 (508065) 69 kV Bus a. Apply fault at the NEKOOSA2 (508065) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEKOOSA2 69 KV 508065 TO HOLOX 2 69 KV 508094 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NEKOSAT2__HOLOX__2 | 3 Phase fault NEKOSAT2 (508066) 69 kV Bus a. Apply fault at the NEKOSAT2 (508066) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEKOSAT2 69 KV 508066 TO HOLOX 2 69 KV 508094 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NEKOSAT2__SUGHLET2 | 3 Phase fault NEKOSAT2 (508066) 69 kV Bus a. Apply fault at the NEKOSAT2 (508066) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEKOSAT2 69 KV 508066 TO SUGHLET2 69 KV 508081 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NEOSHO_7__G17 | 3 Phase fault NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 345 KV 532793 TO G17-209-TAP 345 KV 760921 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NEOSHO_7__GEN | 3 Phase fault NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 345 KV 532793 TO GEN-2018-032 345 KV 762680 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NEWBOST2__DEKALB_2 | 3 Phase fault NEWBOST2 (508067) 69 kV Bus a. Apply fault at the NEWBOST2 (508067) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWBOST2 69 KV 508067 TO DEKALB 2 69 KV 508289 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NEWBOST2__NNBOSTN2 | 3 Phase fault NEWBOST2 (508067) 69 kV Bus a. Apply fault at the NEWBOST2 (508067) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWBOST2 69 KV 508067 TO NNBOSTN2 69 KV 508068 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NEWBOST2__REDRVR | 3 Phase fault NEWBOST2 (508067) 69 kV Bus a. Apply fault at the NEWBOST2 (508067) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWBOST2 69 KV 508067 TO REDRVR-2 69 KV 508074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NNBOSTN4__ANDRSNC4 | 3 Phase fault NNBOSTN4 (508069) 138 kV Bus a. Apply fault at the NNBOSTN4 (508069) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN4 138 KV 508069 TO RIFFIN REC4 138 KV 508104 CKT 1 b.2. LOAD 1 508104 b.3. ANDRSNC4 138 KV 508050 TO RIFFIN REC4 138 KV 508104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NNBOSTN4__G18 | 3 Phase fault NNBOSTN4 (508069) 138 kV Bus a. Apply fault at the NNBOSTN4 (508069) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN4 138 KV 508069 TO G18-003-TAP 138 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NORTWST7__ARCADIA7 | 3 Phase fault NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345 KV 514880 TO ARCADIA7 345 KV 514908 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NORTWST7__CIMARON7 | 3 Phase fault NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345 KV 514880 TO CIMARON7 345 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NORTWST7__MATHWSN7 | 3 Phase fault NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345 KV 514880 TO MATHWSN7 345 KV 515497 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NORTWST7__SPRNGCK7 | 3 Phase fault NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345 KV 514880 TO SPRNGCK7 345 KV 514881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NSHVILR2__NASHVIL2 | 3 Phase fault NSHVILR2 (507413) 69 kV Bus a. Apply fault at the NSHVILR2 (507413) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NSHVILR2 69 KV 507413 TO NASHVIL2 69 KV 507426 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NWT-BNT4_G18-003-TAP | 3 Phase fault NWT-BNT4 (508070) 138 kV Bus a. Apply fault at the NWT-BNT4 (508070) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138 KV 508070 TO G18-003-TAP 138 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NWT-BNT4_NWTXARX4 | 3 Phase fault NWT-BNT4 (508070) 138 kV Bus a. Apply fault at the NWT-BNT4 (508070) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138 KV 508070 TO NWTXARK4 138 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NWTXARK4__SUGARHL4 | 3 Phase fault NWTXARK4 (508071) 138 kV Bus a. Apply fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 138 KV 508071 TO SUGARHL4 138 KV 508080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NWTXARK7__LYDIA__7 | 3 Phase fault NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345 KV 508072 TO LYDIA 7 345 KV 508298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NWTXARK7__VALIANT7 | 3 Phase fault NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345 KV 508072 TO VALIANT7 345 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NWTXARK7__WELSH__7 | 3 Phase fault NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345 KV 508072 TO WELSH 7 345 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_O.K.U._G17-151-TAP | 3 Phase fault O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345 KV 511456 TO G17-151TAP 345 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_O.K.U._G18-015-Tap | 3 Phase fault O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345 KV 511456 TO G18-015-TAP 345 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_O.K.U._GEN-2017-033 | 3 Phase fault O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345 KV 511456 TO GEN-2017-033 345 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_O.K.U._L.E.S. | 3 Phase fault O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345 KV 511456 TO L.E.S.-7 345 KV 511468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_O.K.U._OKLAUN HVDC | 3 Phase fault O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345 KV 511456 TO OKLAUN HVDC7 345 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OAKCRK_4__DRAPER_4 | 3 Phase fault OAKCRK 4 (514960) 138 kV Bus a. Apply fault at the OAKCRK 4 (514960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKCRK 4 138 KV 514960 TO WILDMRY4 138 KV 514984 CKT 1 b.2. LOAD 1 514984 b.3. WILDMRY4 138 KV 514984 TO AIRDEPT4 138 KV 515457 CKT 1 b.4. LOAD 1 515457 b.5. GM 4 138 KV 514961 TO AIRDEPT4 138 KV 515457 CKT 1 b.6. LOAD 1 515457 b.7. DRAPER 4 138 KV 514933 TO GM 4 138 KV 514961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OAKCRK_4__INDNHIL4 | 3 Phase fault OAKCRK 4 (514960) 138 kV Bus a. Apply fault at the OAKCRK 4 (514960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE 4 138 KV 514955 TO OAKCRK 4 138 KV 514960 CKT 1 b.2. MOORE 4 138 KV 514955 TO INDIANH4 138 KV 515380 CKT 1 b.3. LOAD 1 515380 b.4. INDNHIL4 138 KV 514954 TO INDIANH4 138 KV 515380 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OAKCRK_4__SELNDTP4 | 3 Phase fault OAKCRK 4 (514960) 138 kV Bus a. Apply fault at the OAKCRK 4 (514960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKCRK 4 138 KV 514960 TO SELNDTP4 138 KV 515965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OAKS_OASETP | 3 Phase fault OAKS--E4 (509846) 138 kV Bus a. Apply fault at the OAKS--E4 (509846) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKS--E4 138 KV 509846 TO OAKSETP4 138 KV 509850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OAKSWTP4__SAPLPRD4 | 3 Phase fault OAKSWTP4 (509848) 138 kV Bus a. Apply fault at the OAKSWTP4 (509848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKSWTP4 138 KV 509848 TO SAPLPRD4 138 KV 509871 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OAKS__W4__OAKSWTP4 | 3 Phase fault OAKS W4 (509727) 138 kV Bus a. Apply fault at the OAKS W4 (509727) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKS W4 138 KV 509727 TO OAKSWTP4 138 KV 509848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OAKTRET4__SOONRTP4 | 3 Phase fault OAKTRET4 (514930) 138 kV Bus a. Apply fault at the OAKTRET4 (514930) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKTRET4 138 KV 514930 TO SOONRTP4 138 KV 514949 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OGMARTN2__DX | 3 Phase fault OGMARTN2 (509751) 69 kV Bus a. Apply fault at the OGMARTN2 (509751) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGMARTN2 69 KV 509751 TO DX----E2 69 KV 509795 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OGMARTN2__T.P.S. | 3 Phase fault OGMARTN2 (509751) 69 kV Bus a. Apply fault at the OGMARTN2 (509751) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLPIP2 69 KV 509750 TO OGMARTN2 69 KV 509751 CKT 1 b.2. LOAD 1 509751 b.3. WILLPIP2 69 KV 509750 TO T.P.S.-2 69 KV 509789 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OKAYGR_5__WAGNOR_5 | 3 Phase fault OKAYGR 5 (512640) 161 kV Bus a. Apply fault at the OKAYGR 5 (512640) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAYGR 5 161 KV 512640 TO WAGNOR 5 161 KV 512700 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OKAY___2__NASHVIL2 | 3 Phase fault OKAY 2 (507427) 69 kV Bus a. Apply fault at the OKAY 2 (507427) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWAYR2 69 KV 507410 TO TOLETTE2 69 KV 507415 CKT 1 b.2. LOAD A1 507415 b.3. TOLETTE2 69 KV 507415 TO OKAY 2 69 KV 507427 CKT 1 b.4. LOAD 1 507427 b.5. MIDWAYR2 69 KV 507410 TO NASHVIL2 69 KV 507426 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OKAY___4__TURK___4 | 3 Phase fault OKAY 4 (507428) 138 kV Bus a. Apply fault at the OKAY 4 (507428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAY 4 138 KV 507428 TO TURK 4 138 KV 507454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OKEENE_2__TALOGA_2 | 3 Phase fault OKEENE 2 (521015) 69 kV Bus a. Apply fault at the OKEENE 2 (521015) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANTON-2 69 KV 520843 TO OKEENE 2 69 KV 521015 CKT 1 b.2. LOAD 1 521015 b.3. CANTON-2 69 KV 520843 TO TALOGA 2 69 KV 521064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OKMULGE4__EC.HEN | 3 Phase fault OKMULGE4 (510898) 138 kV Bus a. Apply fault at the OKMULGE4 (510898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKMULGE4 138 KV 510898 TO EC.HEN-4 138 KV 510923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OKMULGE4__KELCO_4 | 3 Phase fault OKMULGE4 (510898) 138 kV Bus a. Apply fault at the OKMULGE4 (510898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKMULGE4 138 KV 510898 TO KELCO 4 138 KV 510931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OMAHA__2__DUGLASV2 | 3 Phase fault OMAHA 2 (509644) 69 kV Bus a. Apply fault at the OMAHA 2 (509644) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMAHA 2 69 KV 509644 TO DUGLASV2 69 KV 509645 CKT NO c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ONETA_121LYNN | 3 Phase fault ONETA--4 (509806) 138 kV Bus a. Apply fault at the ONETA--4 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 138 KV 509806 TO 121LYNN4 138 KV 509869 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ONETA_BA81 | 3 Phase fault ONETA--4 (509806) 138 kV Bus a. Apply fault at the ONETA--4 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101-N4 138 KV 509769 TO ONETA--4 138 KV 509806 CKT 1 b.2. LOAD 1 509806 b.3. BA81---4 138 KV 509747 TO BA101-N4 138 KV 509769 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ONETA_BANNTAP4 | 3 Phase fault ONETA--4 (509806) 138 kV Bus a. Apply fault at the ONETA--4 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 138 KV 509806 TO BA_71ST4 138 KV 509891 CKT 1 b.2. LOAD 1 509891 b.3. BANNTAP4 138 KV 509785 TO BA_71ST4 138 KV 509891 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ONETA_NES | 3 Phase fault ONETA--7 (509807) 345 kV Bus a. Apply fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 345 KV 509807 TO N.E.S.-7 345 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ONETA_OEC | 3 Phase fault ONETA--7 (509807) 345 kV Bus a. Apply fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 345 KV 509807 TO OEC 7 345 KV 509836 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ORU_ETP4__WARNTAP4 | 3 Phase fault ORU ETP4 (509849) 138 kV Bus a. Apply fault at the ORU ETP4 (509849) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU ETP4 138 KV 509849 TO WARNTAP4 138 KV 509858 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ORU___E4__ORU_ETP4 | 3 Phase fault ORU E4 (509738) 138 kV Bus a. Apply fault at the ORU E4 (509738) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU E4 138 KV 509738 TO ORU ETP4 138 KV 509849 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ORU___W4__ORU | 3 Phase fault ORU W4 (509732) 138 kV Bus a. Apply fault at the ORU W4 (509732) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU W4 138 KV 509732 TO ORU-WTP4 138 KV 509853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OTTER__4__ARMFTWD4 | 3 Phase fault OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138 KV 514708 TO ARMFTWD4 138 KV 515694 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OTTER__4__WOODRNG4 | 3 Phase fault OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138 KV 514708 TO WOODRNG4 138 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OTTER__4__WRVALLY4 | 3 Phase fault OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138 KV 514708 TO WRVALLY4 138 KV 514713 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OWASO1_4__OWASOTP4 | 3 Phase fault OWASO1_4 (509726) 138 kV Bus a. Apply fault at the OWASO1_4 (509726) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OWASO1_4 138 KV 509726 TO OWASOTP4 138 KV 509844 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OWASOTP4__N.E.S. | 3 Phase fault OWASOTP4 (509844) 138 kV Bus a. Apply fault at the OWASOTP4 (509844) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OWAS1094 138 KV 509860 TO N.E.S.-4 138 KV 510396 CKT 1 b.2. LOAD 1 510396 b.3. OWASOTP4 138 KV 509844 TO OWAS1094 138 KV 509860 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PAOLI | 3 Phase fault PAOLI- 4 (515100) 138 kV Bus a. Apply fault at the PAOLI- 4 (515100) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAOLI- 4 138 KV 515100 TO CHIGLEY4 138 KV 515114 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PAOLI | 3 Phase fault PAOLI- 4 (515100) 138 kV Bus a. Apply fault at the PAOLI- 4 (515100) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAOLI- 4 138 KV 515100 TO MAYSVIL4 138 KV 515124 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PARADSE4__CHERRYRD_4 | 3 Phase fault PARADSE4 (521024) 138 kV Bus a. Apply fault at the PARADSE4 (521024) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARADSE4 138 KV 521024 TO CHERRYRD 4 138 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PARKLN_4__LKKONWA4 | 3 Phase fault PARKLN 4 (515178) 138 kV Bus a. Apply fault at the PARKLN 4 (515178) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKLN 4 138 KV 515178 TO LKKONWA4 138 KV 515977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PARKLN_4__SOTHADA4 | 3 Phase fault PARKLN 4 (515178) 138 kV Bus a. Apply fault at the PARKLN 4 (515178) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKLN 4 138 KV 515178 TO SOTHADA4 138 KV 515318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PARKMEDTP__COLNSGR2 | 3 Phase fault PARKMEDTP (512703) 69 kV Bus a. Apply fault at the PARKMEDTP (512703) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKMEDTP 69 KV 512703 TO COLNSGR2 69 KV 512870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PATTERS2__NEKOOSA2 | 3 Phase fault PATTERS2 (507429) 69 kV Bus a. Apply fault at the PATTERS2 (507429) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS2 69 KV 507429 TO NEKOOSA2 69 KV 508065 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PATTERS2__NEKOSAT2 | 3 Phase fault PATTERS2 (507429) 69 kV Bus a. Apply fault at the PATTERS2 (507429) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS2 69 KV 507429 TO ASHDOWN2 69 KV 508051 CKT 1 b.2. LOAD 1 508051 b.3. ASHDOWN2 69 KV 508051 TO NEKOSAT2 69 KV 508066 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PATTERS4__BARITERDTP_4 | 3 Phase fault PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOCKSBRG 4 138 KV 504123 TO PATTERS4 138 KV 507431 CKT 1 b.2. LOCKSBRG 4 138 KV 504123 TO BARITERDTP 4 138 KV 507463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PATTERS4__CRAIGJT4 | 3 Phase fault PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHDWN_W 4 138 KV 504124 TO PATTERS4 138 KV 507431 CKT 1 b.2. ASHDWN_W 4 138 KV 504124 TO CRAIGJT4 138 KV 510890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PATTERS4__NWTXARK4 | 3 Phase fault PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS4 138 KV 507431 TO NWTXARK4 138 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PATTERS4__OKAY___4 | 3 Phase fault PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHDWNR4 138 KV 507402 TO OKAY 4 138 KV 507428 CKT 1 b.2. ASHDWNR4 138 KV 507402 TO PATTERS4 138 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PATTERS4__SNASHVL4 | 3 Phase fault PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS4 138 KV 507431 TO SNASHVL4 138 KV 507434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PAWNSW4__GLENCOKM_4 | 3 Phase fault PAWNSW4 (512749) 138 kV Bus a. Apply fault at the PAWNSW4 (512749) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAWNSW4 138 KV 512749 TO GLENCOKM 4 138 KV 513095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PCATSAT4__PCATOSA4 | 3 Phase fault PCATSAT4 (509841) 138 kV Bus a. Apply fault at the PCATSAT4 (509841) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCATSAT4 138 KV 509841 TO BIRDCREE-4 138 KV 509899 CKT 1 b.2. LOAD 1 509899 b.3. PCATOSA4 138 KV 509725 TO BIRDCREE-4 138 KV 509899 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PEARLHL2__ROACH__2 | 3 Phase fault PEARLHL2 (509651) 69 kV Bus a. Apply fault at the PEARLHL2 (509651) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEARLHL2 69 KV 509651 TO ROACH 2 69 KV 509668 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PEARSNT2__MAUD___2 | 3 Phase fault PEARSNT2 (515053) 69 kV Bus a. Apply fault at the PEARSNT2 (515053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEARSNT2 69 KV 515053 TO MAUD 2 69 KV 515054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PECANCK4__BRISTOW4 | 3 Phase fault PECANCK4 (515233) 138 kV Bus a. Apply fault at the PECANCK4 (515233) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK4 138 KV 515233 TO BEGGS 4 138 KV 515249 CKT 1 b.2. LOAD 1 515249 b.3. BRISTOW4 138 KV 515035 TO BEGGS 4 138 KV 515249 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PECANCK7__GEN | 3 Phase fault PECANCK7 (515235) 345 kV Bus a. Apply fault at the PECANCK7 (515235) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECANCK7 345 KV 515235 TO GEN-2018-048 345 KV 762823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PENN___2__KENTUKT2 | 3 Phase fault PENN 2 (514924) 69 kV Bus a. Apply fault at the PENN 2 (514924) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENN 2 69 KV 514924 TO KENTUKT2 69 KV 514977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PENN___4__36&MER_4 | 3 Phase fault PENN 4 (514925) 138 kV Bus a. Apply fault at the PENN 4 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRAIRPT4 138 KV 514889 TO PENN 4 138 KV 514925 CKT 1 b.2. LOAD 1 514925 b.3. 36&MER 4 138 KV 514888 TO WRAIRPT4 138 KV 514889 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PENN___4__OAKCRK_4 | 3 Phase fault PENN 4 (514925) 138 kV Bus a. Apply fault at the PENN 4 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENN 4 138 KV 514925 TO SANTAFE4 138 KV 514926 CKT 1 b.2. LOAD 1 514926 b.3. SANTAFE4 138 KV 514926 TO OAKCRK 4 138 KV 514960 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PENSA__5__KETCHUM5 | 3 Phase fault PENSA 5 (512654) 161 kV Bus a. Apply fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 5 161 KV 512654 TO KETCHUM5 161 KV 512669 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PERDUE_4__DIANA__4 | 3 Phase fault PERDUE 4 (508351) 138 kV Bus a. Apply fault at the PERDUE 4 (508351) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERDUE 4 138 KV 508351 TO DIANA 4 138 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PERSIMN7__GUTHRIE7 | 3 Phase fault PERSIMN7 (515951) 345 kV Bus a. Apply fault at the PERSIMN7 (515951) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PERSIMN7 345 KV 515951 TO GUTHRIE7 345 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PETTY__4__CHAPELH4 | 3 Phase fault PETTY 4 (508310) 138 kV Bus a. Apply fault at the PETTY 4 (508310) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PETTY 4 138 KV 508310 TO CHAPELH4 138 KV 508337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PIC4__CDRDLTP4 | 3 Phase fault PIC4 (520425) 138 kV Bus a. Apply fault at the PIC4 (520425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIC4 138 KV 520425 TO CDRDLTP4 138 KV 520848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PIC4__MOORLND4 | 3 Phase fault PIC4 (520425) 138 kV Bus a. Apply fault at the PIC4 (520425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIC4 138 KV 520425 TO MOORLND4 138 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PIEDMNT4__NORTWST4 | 3 Phase fault PIEDMNT4 (514864) 138 kV Bus a. Apply fault at the PIEDMNT4 (514864) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIEDMNT4 138 KV 514864 TO NORTWST4 138 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PINERTP2__WASHITA2 | 3 Phase fault PINERTP2 (521027) 69 kV Bus a. Apply fault at the PINERTP2 (521027) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PINERTP2 69 KV 521027 TO WASHITA2 69 KV 521088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PINK_SW4__SHAWNEE4 | 3 Phase fault PINK SW4 (521028) 138 kV Bus a. Apply fault at the PINK SW4 (521028) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PINK SW4 138 KV 521028 TO SHAWNEE4 138 KV 521048 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PINK___4__PINK_SW4 | 3 Phase fault PINK 4 (520494) 138 kV Bus a. Apply fault at the PINK 4 (520494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PINK 4 138 KV 520494 TO PINK SW4 138 KV 521028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PINTAIL7__KINGWD_7 | 3 Phase fault PINTAIL7 (516010) 345 kV Bus a. Apply fault at the PINTAIL7 (516010) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PINTAIL7 345 KV 516010 TO KINGWD 7 345 KV 516019 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PIRKEY_4__SABMINT4 | 3 Phase fault PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138 KV 508562 TO SABMINT4 138 KV 508566 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PIRKEY_4__WHITNEY4 | 3 Phase fault PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138 KV 508562 TO HALLSVLS4 138 KV 508595 CKT 1 b.2. LOAD 1 508595 b.3. WHITNEY4 138 KV 508575 TO HALLSVLS4 138 KV 508595 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PIRKEY_7__DIANA__7 | 3 Phase fault PIRKEY 7 (508563) 345 kV Bus a. Apply fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345 KV 508563 TO DIANA 7 345 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PIRKEY_7__LEBROCK7 | 3 Phase fault PIRKEY 7 (508563) 345 kV Bus a. Apply fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345 KV 508563 TO LEBROCK7 345 KV 508572 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PITTSB_CRIVER | 3 Phase fault PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345 KV 510907 TO C-RIVER7 345 KV 515422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PITTSB_JOHNCO | 3 Phase fault PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345 KV 510907 TO JOHNCO 7 345 KV 514809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PITTSB_KIOWA | 3 Phase fault PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345 KV 510907 TO KIOWA 7 345 KV 510925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PITTSB_SEMINOL | 3 Phase fault PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345 KV 510907 TO SEMINOL7 345 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PITTSB_VALIANT | 3 Phase fault PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345 KV 510907 TO VALIANT7 345 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_POLECTP4__HICKORY4 | 3 Phase fault POLECTP4 (515218) 138 kV Bus a. Apply fault at the POLECTP4 (515218) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POLECTP4 138 KV 515218 TO HICKORY4 138 KV 515244 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_POLECTP4__POLECAT4 | 3 Phase fault POLECTP4 (515218) 138 kV Bus a. Apply fault at the POLECTP4 (515218) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POLECTP4 138 KV 515218 TO POLECAT4 138 KV 515219 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_POOLVIL4__CARTRCO4 | 3 Phase fault POOLVIL4 (515130) 138 kV Bus a. Apply fault at the POOLVIL4 (515130) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POOLVIL4 138 KV 515130 TO CARTRCO4 138 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_POWELL_4__SW_SHV_4 | 3 Phase fault POWELL 4 (507748) 138 kV Bus a. Apply fault at the POWELL 4 (507748) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POWELL 4 138 KV 507748 TO SW SHV 4 138 KV 507759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PP_YARCHT | 3 Phase fault PP----E4 (509818) 138 kV Bus a. Apply fault at the PP----E4 (509818) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PP----E4 138 KV 509818 TO YARCHT 4 138 KV 509862 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PP_P&PWTP4 | 3 Phase fault PP----W4 (509805) 138 kV Bus a. Apply fault at the PP----W4 (509805) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PP----W4 138 KV 509805 TO P&P WTP4 138 KV 509851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PPTAP__4__46ST | 3 Phase fault PPTAP 4 (509863) 138 kV Bus a. Apply fault at the PPTAP 4 (509863) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PPTAP 4 138 KV 509863 TO 46ST-TP-4 138 KV 509900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_QUAILCK4__LNEOAK_4 | 3 Phase fault QUAILCK4 (514851) 138 kV Bus a. Apply fault at the QUAILCK4 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 138 KV 514851 TO LNEOAK 4 138 KV 514873 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_QUAILCK4__NORTWST4 | 3 Phase fault QUAILCK4 (514851) 138 kV Bus a. Apply fault at the QUAILCK4 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNEOAK 4 138 KV 514873 TO NORTWST4 138 KV 514879 CKT 1 b.2. QUAILCK4 138 KV 514851 TO LNEOAK 4 138 KV 514873 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_QUAILCK4__SLVRLAK4 | 3 Phase fault QUAILCK4 (514851) 138 kV Bus a. Apply fault at the QUAILCK4 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 138 KV 514851 TO SLVRLAK4 138 KV 514852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_R.S.S_5DELT | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138 KV 509783 TO 52DELWT4 138 KV 509814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_R.S.S._KIMCLRK4 | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 136YALE4 138 KV 509775 TO R.S.S.-4 138 KV 509783 CKT 1 b.2. 136YALE4 138 KV 509775 TO KIMCLRK4 138 KV 509845 CKT 1 b.3. LOAD 1 509845 b.4. B111---4 138 KV 509767 TO KIMCLRK4 138 KV 509845 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_R.S.S._EXPGLNT4 | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138 KV 509783 TO EXPGLNT4 138 KV 515473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_R.S.S._OAKSETP4 | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138 KV 509783 TO OAKSETP4 138 KV 509850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_R.S.S._EXP_OKM4 | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138 KV 509783 TO EXP_OKM4 138 KV 510904 CKT 1 b.2. LOAD 1 510904 b.3. OKMULGE4 138 KV 510898 TO EXP_OKM4 138 KV 510904 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_R.S.S._ORU-WTP4 | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138 KV 509783 TO ORU-WTP4 138 KV 509853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_R.S.S._ORU ETP4 | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138 KV 509783 TO ORU ETP4 138 KV 509849 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_R.S.S._RSST2 | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138 KV 509783 TO RSS T2 4 138 KV 509875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_R.S.S._COGENT | 3 Phase fault R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345 KV 509782 TO COGENT 7 345 KV 509834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_R.S.S._G16133G16146 | 3 Phase fault R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345 KV 509782 TO G16133G16146 345 KV 588039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_R.S.S._ONETA | 3 Phase fault R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345 KV 509782 TO ONETA--7 345 KV 509807 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_R.S.S._PECANCK7 | 3 Phase fault R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345 KV 509782 TO PECANCK7 345 KV 515235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_R.S.S._REDBUD | 3 Phase fault R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345 KV 509782 TO REDBUD 7 345 KV 514909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_R.S.S._SAPLPRD | 3 Phase fault R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345 KV 509782 TO SAPLPRD7 345 KV 509870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_RATLIFF4__CARTRCO4 | 3 Phase fault RATLIFF4 (515129) 138 kV Bus a. Apply fault at the RATLIFF4 (515129) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RATLIFF4 138 KV 515129 TO CARTRCO4 138 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_REDBAYOU_6__DOLHILL6 | 3 Phase fault REDBAYOU_6 (500255) 230 kV Bus a. Apply fault at the REDBAYOU_6 (500255) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBAYOU_6 230 KV 500255 TO DOLHILL6 230 KV 500260 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_REDBDPLN4__LEONARD4 | 3 Phase fault REDBDPLN4 (511573) 138 kV Bus a. Apply fault at the REDBDPLN4 (511573) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBDPLN4 138 KV 511573 TO LEONARD4 138 KV 511575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_REDCLFT4__REDCLF_4 | 3 Phase fault REDCLFT4 (515533) 138 kV Bus a. Apply fault at the REDCLFT4 (515533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDCLFT4 138 KV 515533 TO REDCLF 4 138 KV 515863 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_REDNGTN7__REDDIRT7 | 3 Phase fault REDNGTN7 (515875) 345 kV Bus a. Apply fault at the REDNGTN7 (515875) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDNGTN7 345 KV 515875 TO REDDIRT7 345 KV 515877 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_REDSPRG4__EYLAU__4 | 3 Phase fault REDSPRG4 (508075) 138 kV Bus a. Apply fault at the REDSPRG4 (508075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDSPRG4 138 KV 508075 TO EYLAU 4 138 KV 509655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_REDSPRG4__IPC_T__4 | 3 Phase fault REDSPRG4 (508075) 138 kV Bus a. Apply fault at the REDSPRG4 (508075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC-DOM4 138 KV 508060 TO REDSPRG4 138 KV 508075 CKT 1 b.2. LOAD 1 508075 b.3. IPC T 4 138 KV 508059 TO IPC-DOM4 138 KV 508060 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_REDWATR4__EYLAU__4 | 3 Phase fault REDWATR4 (509654) 138 kV Bus a. Apply fault at the REDWATR4 (509654) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDWATR4 138 KV 509654 TO EYLAU 4 138 KV 509655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_REMPKTP4__REMNGPK4 | 3 Phase fault REMPKTP4 (514872) 138 kV Bus a. Apply fault at the REMPKTP4 (514872) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REMPKTP4 138 KV 514872 TO REMNGPK4 138 KV 514874 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_RENO___2__SUNNYLN2 | 3 Phase fault RENO 2 (514972) 69 kV Bus a. Apply fault at the RENO 2 (514972) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 2 69 KV 514972 TO SUNNYLN2 69 KV 514980 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_RENO___4__WASHPRK4 | 3 Phase fault RENO 4 (514973) 138 kV Bus a. Apply fault at the RENO 4 (514973) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 4 138 KV 514973 TO WASHPRK4 138 KV 515156 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_RICHRDS4__PIEDMNT4 | 3 Phase fault RICHRDS4 (514862) 138 kV Bus a. Apply fault at the RICHRDS4 (514862) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHRDS4 138 KV 514862 TO PIEDMNT4 138 KV 514864 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ROCKYPT4__SPRNDAL4 | 3 Phase fault ROCKYPT4 (515164) 138 kV Bus a. Apply fault at the ROCKYPT4 (515164) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT4 138 KV 515164 TO SPRNDAL4 138 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ROKHILL4__NEWPROS4 | 3 Phase fault ROKHILL4 (509083) 138 kV Bus a. Apply fault at the ROKHILL4 (509083) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL4 138 KV 509083 TO NEWPROS4 138 KV 509102 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ROKHILL4__TATUM__4 | 3 Phase fault ROKHILL4 (509083) 138 kV Bus a. Apply fault at the ROKHILL4 (509083) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL4 138 KV 509083 TO TATUM 4 138 KV 509087 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ROMNOSE4__GEARYTP4 | 3 Phase fault ROMNOSE4 (514823) 138 kV Bus a. Apply fault at the ROMNOSE4 (514823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROMNOSE4 138 KV 514823 TO GEARYTP4 138 KV 515931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_RSS_T1_4__R.S.S. | 3 Phase fault RSS T1 4 (509773) 138 kV Bus a. Apply fault at the RSS T1 4 (509773) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T1 4 138 KV 509773 TO R.S.S.-4 138 KV 509783 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_RUSHSPR7__GEN | 3 Phase fault RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345 KV 511571 TO GEN-2018-055 345 KV 762900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_RVRFANT2__MUSKOGE2 | 3 Phase fault RVRFANT2 (515210) 69 kV Bus a. Apply fault at the RVRFANT2 (515210) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RVRFANT2 69 KV 515210 TO MUSKOGE2 69 KV 515221 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_RVRSID_2__MUSKOGE2 | 3 Phase fault RVRSID 2 (515205) 69 kV Bus a. Apply fault at the RVRSID 2 (515205) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RVRSID 2 69 KV 515205 TO MUSKOGE2 69 KV 515221 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_S.HIL_E4__SHILETP4 | 3 Phase fault S.HIL E4 (509731) 138 kV Bus a. Apply fault at the S.HIL E4 (509731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HIL E4 138 KV 509731 TO SHILETP4 138 KV 509813 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_S.S._BLUEBEL4 | 3 Phase fault S.S.---4 (509815) 138 kV Bus a. Apply fault at the S.S.---4 (509815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRATTV-4 138 KV 509758 TO S.S.---4 138 KV 509815 CKT 1 b.2. LOAD 1 509815 b.3. PRATTV-4 138 KV 509758 TO BLUEBEL4 138 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_S.S._DENV_WTAP | 3 Phase fault S.S.---4 (509815) 138 kV Bus a. Apply fault at the S.S.---4 (509815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---4 138 KV 509815 TO DENV_WTAP4 138 KV 509896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_S.S._HWY20-T | 3 Phase fault S.S.---4 (509815) 138 kV Bus a. Apply fault at the S.S.---4 (509815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---4 138 KV 509815 TO HWY20-T4 138 KV 509821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_S.S._WED-TAP4 | 3 Phase fault S.S.---4 (509815) 138 kV Bus a. Apply fault at the S.S.---4 (509815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---4 138 KV 509815 TO WED-TAP4 138 KV 509823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_S.W.S._ANADARK | 3 Phase fault S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138 KV 511477 TO ANADARK4 138 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_S.W.S._CORNVIL4 | 3 Phase fault S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VERDEN 4 138 KV 511421 TO S.W.S.-4 138 KV 511477 CKT 1 b.2. VERDEN 4 138 KV 511421 TO N29CHIK4 138 KV 511502 CKT 1 b.3. LOAD 1 511502 b.4. CORNVIL4 138 KV 511449 TO N29CHIK4 138 KV 511502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_S.W.S._ELGINJT4 | 3 Phase fault S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138 KV 511477 TO ELSWORTH 4 138 KV 511563 CKT 1 b.2. LOAD 1 511563 b.3. LOAD 2 511563 b.4. ELGINJT4 138 KV 511486 TO ELSWORTH 4 138 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_S.W.S._G16-097-TAP | 3 Phase fault S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138 KV 511477 TO G16-097-TAP 138 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_S.W.S._HOBJCT | 3 Phase fault S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNEG-4 138 KV 511445 TO S.W.S.-4 138 KV 511477 CKT 1 b.2. CARNEG-4 138 KV 511445 TO HOB-JCT4 138 KV 511463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_S.W.S._WASHITA | 3 Phase fault S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138 KV 511477 TO WASHITA4 138 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_S52DEL_4__52DELTP4 | 3 Phase fault S52DEL 4 (509716) 138 kV Bus a. Apply fault at the S52DEL 4 (509716) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S52DEL 4 138 KV 509716 TO 52DELTP4 138 KV 509776 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SABMINT4__SABINEM4 | 3 Phase fault SABMINT4 (508566) 138 kV Bus a. Apply fault at the SABMINT4 (508566) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SABMINT4 138 KV 508566 TO SABINEM4 138 KV 508577 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SALINA_5__SALNCRK5 | 3 Phase fault SALINA 5 (512686) 161 kV Bus a. Apply fault at the SALINA 5 (512686) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINA 5 161 KV 512686 TO SALNCRK5 161 KV 512805 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SALISAW5__GORE___5 | 3 Phase fault SALISAW5 (505550) 161 kV Bus a. Apply fault at the SALISAW5 (505550) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALISAW5 161 KV 505550 TO GORE 5 161 KV 505552 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SAPLPRD4__DENV_WTAP4 | 3 Phase fault SAPLPRD4 (509871) 138 kV Bus a. Apply fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 138 KV 509871 TO DENV_WTAP4 138 KV 509896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SAPLPRD4__R.S.S. | 3 Phase fault SAPLPRD4 (509871) 138 kV Bus a. Apply fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENKS--4 138 KV 509759 TO SAPLPRD4 138 KV 509871 CKT 1 b.2. 116JENK4 138 KV 509753 TO JENKS--4 138 KV 509759 CKT 1 b.3. LOAD 1 509759 b.4. 116JENK4 138 KV 509753 TO R.S.S.-4 138 KV 509783 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SAPULPA2__BEELINE2 | 3 Phase fault SAPULPA2 (515236) 69 kV Bus a. Apply fault at the SAPULPA2 (515236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPULPA2 69 KV 515236 TO BEELINE2 69 KV 515246 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SARA_RD4__SUNSHIN4 | 3 Phase fault SARA RD4 (521005) 138 kV Bus a. Apply fault at the SARA RD4 (521005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA RD4 138 KV 521005 TO SUNSHIN4 138 KV 521059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SARA___4__MCCLAIN4 | 3 Phase fault SARA 4 (514895) 138 kV Bus a. Apply fault at the SARA 4 (514895) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA 4 138 KV 514895 TO MCCLAIN4 138 KV 514902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SAWYER4__HUGO_PP4 | 3 Phase fault SAWYER4 (520411) 138 kV Bus a. Apply fault at the SAWYER4 (520411) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAWYER4 138 KV 520411 TO HUGO PP4 138 KV 520948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SCOFCTY4__COFFEYT4 | 3 Phase fault SCOFCTY4 (510378) 138 kV Bus a. Apply fault at the SCOFCTY4 (510378) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOFCTY4 138 KV 510378 TO COFFEYT4 138 KV 510422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SDIERKS2__DIERKSR2 | 3 Phase fault SDIERKS2 (507432) 69 kV Bus a. Apply fault at the SDIERKS2 (507432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SDIERKS2 69 KV 507432 TO DIERKSR2 69 KV 507437 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SDIERKS4__BARITERDTP_4 | 3 Phase fault SDIERKS4 (507433) 138 kV Bus a. Apply fault at the SDIERKS4 (507433) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SDIERKS4 138 KV 507433 TO BARITERDTP 4 138 KV 507463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SE15TH_4__BARNES_4 | 3 Phase fault SE15TH 4 (514993) 138 kV Bus a. Apply fault at the SE15TH 4 (514993) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SE15TH 4 138 KV 514993 TO BARNES 4 138 KV 515003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SE15TH_4__TINKER54 | 3 Phase fault SE15TH 4 (514993) 138 kV Bus a. Apply fault at the SE15TH 4 (514993) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDAL4 138 KV 514986 TO SE15TH 4 138 KV 514993 CKT 1 b.2. LOAD 1 514993 b.3. GLENDAL4 138 KV 514986 TO TINKER74 138 KV 515959 CKT 1 b.4. LOAD 1 515959 b.5. TINKER64 138 KV 515806 TO TINKER74 138 KV 515959 CKT 1 b.6. LOAD 1 515959 b.7. TINKER54 138 KV 514994 TO TINKER64 138 KV 515806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SELNDTP4__SELNDFL4 | 3 Phase fault SELNDTP4 (515965) 138 kV Bus a. Apply fault at the SELNDTP4 (515965) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SELNDTP4 138 KV 515965 TO SELNDFL4 138 KV 515966 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SELNDTP4__TROSPER4 | 3 Phase fault SELNDTP4 (515965) 138 kV Bus a. Apply fault at the SELNDTP4 (515965) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DISCVRY4 138 KV 514962 TO SELNDTP4 138 KV 515965 CKT 1 b.2. FOSTER 4 138 KV 514959 TO DISCVRY4 138 KV 514962 CKT 1 b.3. LOAD 1 514962 b.4. FOSTER 4 138 KV 514959 TO NEWDOMI4 138 KV 515387 CKT 1 b.5. LOAD 1 515387 b.6. TROSPER4 138 KV 514963 TO NEWDOMI4 138 KV 515387 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SEMINOL4__LKKONWA4 | 3 Phase fault SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138 KV 515044 TO LKKONWA4 138 KV 515977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SEMINOL4__MAUD___4 | 3 Phase fault SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138 KV 515044 TO MAUD 4 138 KV 515055 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SEMINOL4__PAOLI | 3 Phase fault SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138 KV 515044 TO PAOLI- 4 138 KV 515100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SEMINOL4__VANOSTP4 | 3 Phase fault SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138 KV 515044 TO VANOSTP4 138 KV 515531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SEMINOL7__FIREWHL | 3 Phase fault SEMINOL7 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 345 KV 515045 TO FIREWHL-TAP 345 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SEQUOYAHJ4__ANADARK4 | 3 Phase fault SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138 KV 520422 TO ANADARK4 138 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SEQUOYAHJ4__CKSHATP4 | 3 Phase fault SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138 KV 520422 TO CKSHATP4 138 KV 520473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SEQUOYAHJ4__SEQOYAH4 | 3 Phase fault SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138 KV 520422 TO SEQOYAH4 138 KV 520547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SETEXAR2__TEXARK_2 | 3 Phase fault SETEXAR2 (508077) 69 kV Bus a. Apply fault at the SETEXAR2 (508077) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETEXAR2 69 KV 508077 TO TEXARK 2 69 KV 508086 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SETEXAR4__MANDEVILTP4 | 3 Phase fault SETEXAR4 (508078) 138 kV Bus a. Apply fault at the SETEXAR4 (508078) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETEXAR4 138 KV 508078 TO MANDEVILTP4 138 KV 508105 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SFOREMAN__4__NNBOSTN4 | 3 Phase fault SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4 (504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 138 KV 504029 TO NNBOSTN4 138 KV 508069 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SFOREMAN__4__PATTERS4 | 3 Phase fault SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4 (504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 138 KV 504029 TO PATTERS4 138 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SHAWNEE2__SINCPNT2 | 3 Phase fault SHAWNEE2 (515068) 69 kV Bus a. Apply fault at the SHAWNEE2 (515068) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHAWNEE2 69 KV 515068 TO SINCPNT2 69 KV 515642 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SHILETP4__ORU | 3 Phase fault SHILETP4 (509813) 138 kV Bus a. Apply fault at the SHILETP4 (509813) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHILETP4 138 KV 509813 TO ORU-WTP4 138 KV 509853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SILSPWW5__KANSATP5 | 3 Phase fault SILSPWW5 (512642) 161 kV Bus a. Apply fault at the SILSPWW5 (512642) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILSPWW5 161 KV 512642 TO KANSATP5 161 KV 512714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SINCPAN2__SINCPNT2 | 3 Phase fault SINCPAN2 (515072) 69 kV Bus a. Apply fault at the SINCPAN2 (515072) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SINCPAN2 69 KV 515072 TO SINCPNT2 69 KV 515642 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SKELTON7__GEN | 3 Phase fault SKELTON7 (515990) 345 kV Bus a. Apply fault at the SKELTON7 (515990) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SKELTON7 345 KV 515990 TO GEN-2016-128 345 KV 588190 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SKYLINE4__FAIRFLD4 | 3 Phase fault SKYLINE4 (514850) 138 kV Bus a. Apply fault at the SKYLINE4 (514850) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SKYLINE4 138 KV 514850 TO CHISHOM4 138 KV 515374 CKT 1 b.2. LOAD 1 515374 b.3. CHISHOM4 138 KV 515374 TO FAIRFLD4 138 KV 515468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SKYLINE4__QUAILCK4 | 3 Phase fault SKYLINE4 (514850) 138 kV Bus a. Apply fault at the SKYLINE4 (514850) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SKYLINE4 138 KV 514850 TO QUAILCK4 138 KV 514851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SLVRLAK4__DVISION4 | 3 Phase fault SLVRLAK4 (514852) 138 kV Bus a. Apply fault at the SLVRLAK4 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 138 KV 514852 TO DVISION4 138 KV 514853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SLVRLAK4__NORTWST4 | 3 Phase fault SLVRLAK4 (514852) 138 kV Bus a. Apply fault at the SLVRLAK4 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 138 KV 514852 TO BRADEN 4 138 KV 514854 CKT 1 b.2. LOAD 1 514854 b.3. BRADEN 4 138 KV 514854 TO NORTWST4 138 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SMITHCO4__DAYTON_4 | 3 Phase fault SMITHCO4 (514891) 138 kV Bus a. Apply fault at the SMITHCO4 (514891) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMITHCO4 138 KV 514891 TO DAYTON 4 138 KV 514892 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SO4TH__2__CHSTNTT2 | 3 Phase fault SO4TH 2 (514730) 69 kV Bus a. Apply fault at the SO4TH 2 (514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 69 KV 514730 TO CHSTNTT2 69 KV 515456 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SO4TH__4__BRECKNR4 | 3 Phase fault SO4TH 4 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138 KV 514731 TO BRECKNR4 138 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SO4TH__4__IMO____4 | 3 Phase fault SO4TH 4 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138 KV 514731 TO IMO 4 138 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SOONER_7__G15 | 3 Phase fault SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345 KV 514803 TO G15-066T 345 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SOONER_7__G16 | 3 Phase fault SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345 KV 514803 TO G16-119-TAP 345 KV 587804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SOONER_7__PINTAIL7 | 3 Phase fault SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345 KV 514803 TO PINTAIL7 345 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SOONER_7__RANCHRD7 | 3 Phase fault SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345 KV 514803 TO RANCHRD7 345 KV 515576 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SOONER_7__THUNDER7 | 3 Phase fault SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345 KV 514803 TO THUNDER7 345 KV 515894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SOUTHRD4__ROMNOSE4 | 3 Phase fault SOUTHRD4 (514822) 138 kV Bus a. Apply fault at the SOUTHRD4 (514822) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOUTHRD4 138 KV 514822 TO ROMNOSE4 138 KV 514823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SPNKY_CK4__CATOOSA4 | 3 Phase fault SPNKY CK4 (509722) 138 kV Bus a. Apply fault at the SPNKY CK4 (509722) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPNKY CK4 138 KV 509722 TO CATOOSA4 138 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SPPMAINBUS__WELSH__7 | 3 Phase fault SPPMAINBUS (5917) 345 kV Bus a. Apply fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPPMAIN345 KV 5917 TO WELSH 7 345 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SPRHILL4__DIANA__4 | 3 Phase fault SPRHILL4 (508571) 138 kV Bus a. Apply fault at the SPRHILL4 (508571) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRHILL4 138 KV 508571 TO DIANA 4 138 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SQUIRCK4__NE45TAP4 | 3 Phase fault SQUIRCK4 (515059) 138 kV Bus a. Apply fault at the SQUIRCK4 (515059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQUIRCK4 138 KV 515059 TO INGLEWD4 138 KV 515060 CKT 1 b.2. LOAD 1 515060 b.3. INGLEWD4 138 KV 515060 TO STGREG 4 138 KV 515061 CKT 1 b.4. LOAD 1 515061 b.5. STGREG 4 138 KV 515061 TO NE45TAP4 138 KV 515062 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SQUIRCK4__STRLGTP4 | 3 Phase fault SQUIRCK4 (515059) 138 kV Bus a. Apply fault at the SQUIRCK4 (515059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQUIRCK4 138 KV 515059 TO STRLGTP4 138 KV 515286 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_STALOGA2__PUTNAM_2 | 3 Phase fault STALOGA2 (520454) 69 kV Bus a. Apply fault at the STALOGA2 (520454) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STALOGA2 69 KV 520454 TO PUTNAM 2 69 KV 521033 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_STNWAL_4__REMPKTP4 | 3 Phase fault STNWAL 4 (514870) 138 kV Bus a. Apply fault at the STNWAL 4 (514870) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNWAL 4 138 KV 514870 TO REMPKTP4 138 KV 514872 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_STNWAL_4__RENO___4 | 3 Phase fault STNWAL 4 (514870) 138 kV Bus a. Apply fault at the STNWAL 4 (514870) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNWAL 4 138 KV 514870 TO OUMED 4 138 KV 514875 CKT 1 b.2. LOAD 1 514875 b.3. OUMED 4 138 KV 514875 TO GATEWAY4 138 KV 515963 CKT 1 b.4. LOAD 1 515963 b.5. WASHPRK4 138 KV 515156 TO GATEWAY4 138 KV 515963 CKT 1 b.6. LOAD 1 515963 b.7. RENO 4 138 KV 514973 TO WASHPRK4 138 KV 515156 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_STRLGTP4__STERLNG4 | 3 Phase fault STRLGTP4 (515286) 138 kV Bus a. Apply fault at the STRLGTP4 (515286) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STRLGTP4 138 KV 515286 TO STERLNG4 138 KV 520449 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_STUBMAN4__HOLLYWD4 | 3 Phase fault STUBMAN4 (514952) 138 kV Bus a. Apply fault at the STUBMAN4 (514952) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STUBMAN4 138 KV 514952 TO HOLLYWD4 138 KV 514953 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SUGARHL2__SUGHLET2 | 3 Phase fault SUGARHL2 (508079) 69 kV Bus a. Apply fault at the SUGARHL2 (508079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGARHL2 69 KV 508079 TO SUGHLET2 69 KV 508081 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SUGARHL2__SUGHLWT2 | 3 Phase fault SUGARHL2 (508079) 69 kV Bus a. Apply fault at the SUGARHL2 (508079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGARHL2 69 KV 508079 TO SUGHLWT2 69 KV 508082 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SUGHLET2__TEXARK_2 | 3 Phase fault SUGHLET2 (508081) 69 kV Bus a. Apply fault at the SUGHLET2 (508081) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGHLET2 69 KV 508081 TO TEX12ST2 69 KV 508084 CKT 1 b.2. LOAD 1 508084 b.3. TEX12ST2 69 KV 508084 TO WASHST 2 69 KV 508088 CKT 1 b.4. LOAD 1 508088 b.5. TEXARK 2 69 KV 508086 TO WASHST 2 69 KV 508088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SUGHLWT2__TEX39ST2 | 3 Phase fault SUGHLWT2 (508082) 69 kV Bus a. Apply fault at the SUGHLWT2 (508082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGHLWT2 69 KV 508082 TO TEX39ST2 69 KV 508085 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SUMMERG2__LEASIDE_2 | 3 Phase fault SUMMERG2 (507758) 69 kV Bus a. Apply fault at the SUMMERG2 (507758) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMERG2 69 KV 507758 TO LEASIDE 2 69 KV 507794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SUNNYLN2__TINKER32 | 3 Phase fault SUNNYLN2 (514980) 69 kV Bus a. Apply fault at the SUNNYLN2 (514980) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYLN2 69 KV 514980 TO TINKER32 69 KV 514981 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SUNNYSD4__ARDWEST4 | 3 Phase fault SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNIROY 4 138 KV 515137 TO ARDWEST4 138 KV 515372 CKT 1 b.2. LOAD 1 515372 b.3. SUNNYSD4 138 KV 515135 TO UNIROY 4 138 KV 515137 CKT 1 b.4. LOAD 1 515137 b.5. CARTER 4 138 KV 515138 TO ARDWEST4 138 KV 515372 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SUNNYSD4__CARTRCO4 | 3 Phase fault SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138 KV 515135 TO CARTRCO4 138 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SUNNYSD4__LONEGRV4 | 3 Phase fault SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138 KV 515135 TO LONEGRV4 138 KV 515144 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SUNNYSD4__ROCKYPT4 | 3 Phase fault SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138 KV 515135 TO ROCKYPT4 138 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SUNNYSD7__G17 | 3 Phase fault SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345 KV 515136 TO G17-075-TAP 345 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SUNNYSD7__GEN | 3 Phase fault SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345 KV 515136 TO GEN-2017-167 345 KV 761859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SW134TP4__MCCLAIN4 | 3 Phase fault SW134TP4 (514876) 138 kV Bus a. Apply fault at the SW134TP4 (514876) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW134TP4 138 KV 514876 TO MCCLAIN4 138 KV 514902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SW134TP4__NORMHLL4 | 3 Phase fault SW134TP4 (514876) 138 kV Bus a. Apply fault at the SW134TP4 (514876) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW134TP4 138 KV 514876 TO SOGATE 4 138 KV 514928 CKT 1 b.2. LOAD 1 514928 b.3. SOGATE 4 138 KV 514928 TO TURNER 4 138 KV 514992 CKT 1 b.4. LOAD 1 514992 b.5. TURNER 4 138 KV 514992 TO NORMHLL4 138 KV 516097 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SW134TP4__PENN___4 | 3 Phase fault SW134TP4 (514876) 138 kV Bus a. Apply fault at the SW134TP4 (514876) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW134TP4 138 KV 514876 TO WESTMOR4 138 KV 514887 CKT 1 b.2. LOAD 1 514887 b.3. WESTMOR4 138 KV 514887 TO PENN 4 138 KV 514925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SWEETWT6__BUFFCK6 | 3 Phase fault SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230 KV 511541 TO BUFFCK6 230 KV 511542 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SWEETWT6__CHISHOLM6 | 3 Phase fault SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230 KV 511541 TO CHISHOLM6 230 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SWEETWT6__DEMPSEY6 | 3 Phase fault SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230 KV 511541 TO DEMPSEY6 230 KV 511544 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SWEETWT6__ROARK6 | 3 Phase fault SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230 KV 511541 TO ROARK6 230 KV 511547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SWEETWT6__STLN | 3 Phase fault SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230 KV 511541 TO STLN-DEMARC6 230 KV 523779 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SWISHER____6__TUCO_INT___6 | 3 Phase fault SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230 KV 525213 TO TUCO_INT 6 230 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SW_5TH_2__38TH_ST2 | 3 Phase fault SW 5TH 2 (514919) 69 kV Bus a. Apply fault at the SW 5TH 2 (514919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAY AVE2 69 KV 514913 TO SW 5TH 2 69 KV 514919 CKT 1 b.2. 38TH ST2 69 KV 514845 TO MAY AVE2 69 KV 514913 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SW_5TH_2__KENTUKT2 | 3 Phase fault SW 5TH 2 (514919) 69 kV Bus a. Apply fault at the SW 5TH 2 (514919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW 5TH 2 69 KV 514919 TO SW22ND 2 69 KV 514975 CKT 1 b.2. LOAD 1 514975 b.3. SW22ND 2 69 KV 514975 TO KENTUKY2 69 KV 514976 CKT 1 b.4. LOAD 1 514976 b.5. KENTUKY2 69 KV 514976 TO KENTUKT2 69 KV 514977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SW_5TH_4__CLASSEN4 | 3 Phase fault SW 5TH 4 (514920) 138 kV Bus a. Apply fault at the SW 5TH 4 (514920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW 5TH 4 138 KV 514920 TO CLASSEN4 138 KV 514922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SW_64TH2__PENN___2 | 3 Phase fault SW 64TH2 (514918) 69 kV Bus a. Apply fault at the SW 64TH2 (514918) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW 64TH2 69 KV 514918 TO PENN 2 69 KV 514924 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SW_SHV_4__FLOURNY4 | 3 Phase fault SW SHV 4 (507759) 138 kV Bus a. Apply fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENMOTR4 138 KV 507732 TO SW SHV 4 138 KV 507759 CKT 1 b.2. FLOURNY4 138 KV 507727 TO GENMOTR4 138 KV 507732 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SW_SHV_4__LEASIDE_4 | 3 Phase fault SW SHV 4 (507759) 138 kV Bus a. Apply fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW SHV 4 138 KV 507759 TO LEASIDE 4 138 KV 507793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SW_SHV_4__ROKHILL4 | 3 Phase fault SW SHV 4 (507759) 138 kV Bus a. Apply fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRIDGE4 138 KV 507757 TO SW SHV 4 138 KV 507759 CKT 1 b.2. SPRIDGE4 138 KV 507757 TO WLNTSPRINGS4 138 KV 509103 CKT 1 b.3. LOAD 1 509103 b.4. ROKHILL4 138 KV 509083 TO WLNTSPRINGS4 138 KV 509103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SW_SHV_7__DIANA__7 | 3 Phase fault SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345 KV 507760 TO DIANA 7 345 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SW_SHV_7__LONGWD_7 | 3 Phase fault SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345 KV 507760 TO LONGWD 7 345 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_S_SHV__4__CEDARGR4 | 3 Phase fault S SHV 4 (507755) 138 kV Bus a. Apply fault at the S SHV 4 (507755) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138 KV 507755 TO CEDARGR4 138 KV 507771 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_S_SHV__4__SW_SHV_4 | 3 Phase fault S SHV 4 (507755) 138 kV Bus a. Apply fault at the S SHV 4 (507755) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138 KV 507755 TO SW SHV 4 138 KV 507759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_S_SHV__4__WALLAKE4 | 3 Phase fault S SHV 4 (507755) 138 kV Bus a. Apply fault at the S SHV 4 (507755) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138 KV 507755 TO WALLAKE4 138 KV 507765 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_S_SHV__4__WESTELC4 | 3 Phase fault S SHV 4 (507755) 138 kV Bus a. Apply fault at the S SHV 4 (507755) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138 KV 507755 TO WESTELC4 138 KV 507767 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TCONCO_CEMRD_TP4 | 3 Phase fault T-CONCO4 (511424) 138 kV Bus a. Apply fault at the T-CONCO4 (511424) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T-CONCO4 138 KV 511424 TO CEMRD_TP4 138 KV 511576 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_T.NO._46STTP4 | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO 46ST-TP-4 138 KV 509900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_T.NO._BARNSAL4 | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO SKIATOK4 138 KV 509884 CKT 1 b.2. LOAD 1 509884 b.3. SKIATOK4 138 KV 509884 TO BARNSAL4 138 KV 510388 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_T.NO._CDC-ET4 | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO CDC-ET 4 138 KV 509839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_T.NO._CDC-WT4 | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO CDC-WT 4 138 KV 509842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_T.NO._NES | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO N.E.S.-4 138 KV 510396 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_T.NO._OWASOTP | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO OWASOTP4 138 KV 509844 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_T.NO._P&PWTP4 | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO P&P WTP4 138 KV 509851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_T.NO._TNO24 | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO T.NO.2-4 138 KV 509895 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_T.NO._CLEVLND7 | 3 Phase fault T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345 KV 509852 TO CLEVLND7 345 KV 512694 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_T.NO._IGLOOV7 | 3 Phase fault T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345 KV 509852 TO IGLOOV 7 345 KV 513596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_T.NO._NES7 | 3 Phase fault T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345 KV 509852 TO N.E.S.-7 345 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_T.NO.2_GEN-2018-028 | 3 Phase fault T.NO.2-4 (509895) 138 kV Bus a. Apply fault at the T.NO.2-4 (509895) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.2-4 138 KV 509895 TO GEN-2018-028 138 KV 762636 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_T.P.S._52DELWT | 3 Phase fault T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138 KV 509788 TO 52DELWT4 138 KV 509814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_T.P.S._CARSN-T4 | 3 Phase fault T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 36&OLY-4 138 KV 509724 TO T.P.S.-4 138 KV 509788 CKT 1 b.2. LOAD 1 509788 b.3. 36&OLY-4 138 KV 509724 TO CARSN-T4 138 KV 509739 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_T.P.S._GEN-2018-027 | 3 Phase fault T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138 KV 509788 TO GEN-2018-027 138 KV 762625 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_T.P.S._OAKSETP4 | 3 Phase fault T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138 KV 509788 TO OAKSETP4 138 KV 509850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_T.P.S._OAKSWTP4 | 3 Phase fault T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138 KV 509788 TO OAKSWTP4 138 KV 509848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_T.P.S._SAPLPRD | 3 Phase fault T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138 KV 509788 TO 72ELWOD4 138 KV 509888 CKT 1 b.2. LOAD 1 509888 b.3. SAPLPRD4 138 KV 509871 TO 72ELWOD4 138 KV 509888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_T.S.E._21STTAP4 | 3 Phase fault T.S.E.-4 (509811) 138 kV Bus a. Apply fault at the T.S.E.-4 (509811) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.S.E.-4 138 KV 509811 TO 21STTAP4 138 KV 509828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_T.S.E._E61ST | 3 Phase fault T.S.E.-4 (509811) 138 kV Bus a. Apply fault at the T.S.E.-4 (509811) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.S.E.-4 138 KV 509811 TO E.61ST-4 138 KV 509831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_T.S.E._KENSHETP4 | 3 Phase fault T.S.E.-4 (509811) 138 kV Bus a. Apply fault at the T.S.E.-4 (509811) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.S.E.-4 138 KV 509811 TO KENSH-E-TP4 138 KV 509830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_T.S.E._SHUD4 | 3 Phase fault T.S.E.-4 (509811) 138 kV Bus a. Apply fault at the T.S.E.-4 (509811) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.S.E.-4 138 KV 509811 TO S.HUD.-4 138 KV 509833 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TAHLQH_5__BRIGSKM_5 | 3 Phase fault TAHLQH 5 (512655) 161 kV Bus a. Apply fault at the TAHLQH 5 (512655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 161 KV 512655 TO BRIGSKM 5 161 KV 513044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TAHLQH_5__HWY59TP5 | 3 Phase fault TAHLQH 5 (512655) 161 kV Bus a. Apply fault at the TAHLQH 5 (512655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 161 KV 512655 TO HWY59TP5 161 KV 515527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TALOGA_2__HMBTTP | 3 Phase fault TALOGA 2 (521064) 69 kV Bus a. Apply fault at the TALOGA 2 (521064) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STALOGA2 69 KV 520454 TO TALOGA 2 69 KV 521064 CKT 1 b.2. STALOGA2 69 KV 520454 TO PUTNAM 2 69 KV 521033 CKT 1 b.3. LOAD 1 521033 b.4. HM-BTTP2 69 KV 520942 TO PUTNAM 2 69 KV 521033 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TALOGA_2__WOODWRD2 | 3 Phase fault TALOGA 2 (521064) 69 kV Bus a. Apply fault at the TALOGA 2 (521064) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALOGA 2 69 KV 521064 TO VICI 2 69 KV 521082 CKT 1 b.2. LOAD 1 521082 b.3. VICI 2 69 KV 521082 TO WOODWRD2 69 KV 521096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TALOGA_4__MOORLND4 | 3 Phase fault TALOGA 4 (521065) 138 kV Bus a. Apply fault at the TALOGA 4 (521065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEILING4 138 KV 520553 TO TALOGA 4 138 KV 521065 CKT 1 b.2. SEILING4 138 KV 520553 TO MOORLND4 138 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TATONGA7__CRSRDSW7 | 3 Phase fault TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345 KV 515407 TO CRSRDSW7 345 KV 515448 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TATONGA7__MAMTHPW7 | 3 Phase fault TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345 KV 515407 TO MAMTHPW7 345 KV 515585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TATONGA7__MATHWSN7 | 3 Phase fault TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345 KV 515407 TO MATHWSN7 345 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TATONGA7__SLNGWND7 | 3 Phase fault TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345 KV 515407 TO SLNGWND7 345 KV 515582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TAYLOR_2__TEX39ST2 | 3 Phase fault TAYLOR 2 (508083) 69 kV Bus a. Apply fault at the TAYLOR 2 (508083) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 2 69 KV 508083 TO TEX39ST2 69 KV 508085 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TAYLOR_2__TEXARK_2 | 3 Phase fault TAYLOR 2 (508083) 69 kV Bus a. Apply fault at the TAYLOR 2 (508083) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 2 69 KV 508083 TO TEXARK 2 69 KV 508086 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TECUMSH2__FRSTHIL2 | 3 Phase fault TECUMSH2 (515071) 69 kV Bus a. Apply fault at the TECUMSH2 (515071) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECUMSH2 69 KV 515071 TO FRSTHIL2 69 KV 515074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TENESTP4__84TH_ST4 | 3 Phase fault TENESTP4 (514837) 138 kV Bus a. Apply fault at the TENESTP4 (514837) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TENESTP4 138 KV 514837 TO 84TH ST4 138 KV 514843 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TERNIT_TERNITP4 | 3 Phase fault TER-NIT4 (509723) 138 kV Bus a. Apply fault at the TER-NIT4 (509723) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TER-NIT4 138 KV 509723 TO PCATOSA4 138 KV 509725 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TERNIT_TERNITP4 | 3 Phase fault TER-NIT4 (509723) 138 kV Bus a. Apply fault at the TER-NIT4 (509723) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TER-NIT4 138 KV 509723 TO TERNITP4 138 KV 509835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TERNITP4__VERDIGS4 | 3 Phase fault TERNITP4 (509835) 138 kV Bus a. Apply fault at the TERNITP4 (509835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERNITP4 138 KV 509835 TO VERDIGS4 138 KV 509854 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TERRYRD7__G17_171_TAP | 3 Phase fault TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345 KV 511568 TO G17-171-TAP 345 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TERRYRD7__RSHSPR1_MPT1 | 3 Phase fault TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345 KV 511568 TO RSHSPR1_MPT1 345 KV 511979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TERRYRD7__RUSHSPR7 | 3 Phase fault TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345 KV 511568 TO RUSHSPR7 345 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TERRYRD7__SUNNYSD7 | 3 Phase fault TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345 KV 511568 TO SUNNYSD7 345 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TEXARK_2__IPC_TAP2 | 3 Phase fault TEXARK 2 (508086) 69 kV Bus a. Apply fault at the TEXARK 2 (508086) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S_TEXARK 2 69 KV 504117 TO PLEASHL2 69 KV 508048 CKT 1 b.2. LOAD 1 508048 b.3. S_TEXARK 2 69 KV 504117 TO TEXARK 2 69 KV 508086 CKT 1 b.4. LOAD 1 508086 b.5. PLEASHL2 69 KV 508048 TO IPC TAP2 69 KV 508058 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_THISTLE7__GEN_2017-018 | 3 Phase fault THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345 KV 539801 TO GEN-2017-018 345 KV 588630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_THISTLE7__GEN-2018-049 | 3 Phase fault THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345 KV 539801 TO GEN-2018-049 345 KV 762834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TINKER54__BARNES_4 | 3 Phase fault TINKER54 (514994) 138 kV Bus a. Apply fault at the TINKER54 (514994) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TINKER54 138 KV 514994 TO BARNES 4 138 KV 515003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TOLK_______6__TUCO_INT___6 | 3 Phase fault TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230 KV 525531 TO TUCO_INT 6 230 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TROSPER4__RENO___4 | 3 Phase fault TROSPER4 (514963) 138 kV Bus a. Apply fault at the TROSPER4 (514963) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROSPER4 138 KV 514963 TO RENO 4 138 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TUCO_INT___6__ANTELOPE_1_6 | 3 Phase fault TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230 KV 525830 TO ANTELOPE_1 6 230 KV 525840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TUCO_INT___6__CARLISLE___6 | 3 Phase fault TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230 KV 525830 TO CARLISLE 6 230 KV 526161 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TUCO_INT___6__HALE_WNDCL16 | 3 Phase fault TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230 KV 525830 TO HALE_WNDCL16 230 KV 525957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TUCO_INT___6__JONES______6 | 3 Phase fault TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230 KV 525830 TO JONES 6 230 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TUCO_INT___7__ELK_CT1 | 3 Phase fault TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345 KV 525832 TO ELK_CT1 345 KV 525850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TUCO_INT___7__G17 | 3 Phase fault TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345 KV 525832 TO G17-151TAP 345 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TUCO_INT___7__YOAKUM_345 | 3 Phase fault TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345 KV 525832 TO YOAKUM_345 345 KV 526936 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TURCRK_2__TURCRKT2 | 3 Phase fault TURCRK 2 (514735) 69 kV Bus a. Apply fault at the TURCRK 2 (514735) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURCRK 2 69 KV 514735 TO TURCRKT2 69 KV 515517 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TURK___3__HOPE___3 | 3 Phase fault TURK 3 (507456) 115 kV Bus a. Apply fault at the TURK 3 (507456) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCNAB 3 115 KV 504122 TO TURK 3 115 KV 507456 CKT 1 b.2. MCNAB 3 115 KV 504122 TO HOPE 3 115 KV 507453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TURK___4__MANDEVILTP4 | 3 Phase fault TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 4 138 KV 507454 TO MANDEVILTP4 138 KV 508105 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TURK___4__SUGARHL4 | 3 Phase fault TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 4 138 KV 507454 TO SUGARHL4 138 KV 508080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TURK___7__NWTXARK7 | 3 Phase fault TURK 7 (507455) 345 kV Bus a. Apply fault at the TURK 7 (507455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURK 7 345 KV 507455 TO NWTXARK7 345 KV 508072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TUTCONT4__CEMRD_TP4 | 3 Phase fault TUTCONT4 (511425) 138 kV Bus a. Apply fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTCONT4 138 KV 511425 TO CEMRD_TP4 138 KV 511576 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TUTCONT4__CIMARON4 | 3 Phase fault TUTCONT4 (511425) 138 kV Bus a. Apply fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTCONT4 138 KV 511425 TO CIMARON4 138 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TUTCONT4__LEONARD4 | 3 Phase fault TUTCONT4 (511425) 138 kV Bus a. Apply fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTCONT4 138 KV 511425 TO TUTTLE4 138 KV 511501 CKT 1 b.2. LOAD 1 511501 b.3. TUTTLE4 138 KV 511501 TO LEONARD4 138 KV 511575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TUTTLE_4__TUTLETP4 | 3 Phase fault TUTTLE 4 (520496) 138 kV Bus a. Apply fault at the TUTTLE 4 (520496) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTTLE 4 138 KV 520496 TO TUTLETP4 138 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TWNLKJT4__TWNLKSW4 | 3 Phase fault TWNLKJT4 (520847) 138 kV Bus a. Apply fault at the TWNLKJT4 (520847) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWNLKJT4 138 KV 520847 TO TWNLKSW4 138 KV 521073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TXPLSTE2__TXPLSTP2 | 3 Phase fault TXPLSTE2 (514989) 69 kV Bus a. Apply fault at the TXPLSTE2 (514989) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXPLSTE2 69 KV 514989 TO TXPLSTP2 69 KV 515516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TXSTELA2__LITLAXT2 | 3 Phase fault TXSTELA2 (514985) 69 kV Bus a. Apply fault at the TXSTELA2 (514985) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXSTELA2 69 KV 514985 TO LITLAXT2 69 KV 515502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TXSTELA2__TXPLSTP2 | 3 Phase fault TXSTELA2 (514985) 69 kV Bus a. Apply fault at the TXSTELA2 (514985) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXSTELA2 69 KV 514985 TO TXPLSTP2 69 KV 515516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_VWEYCO4_VALIANT4 | 3 Phase fault V-WEYCO4 (510866) 138 kV Bus a. Apply fault at the V-WEYCO4 (510866) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. V-WEYCO4 138 KV 510866 TO VALIANT4 138 KV 510918 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_VALIANT4__B.BOWTP4 | 3 Phase fault VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IDABEL-4 138 KV 510886 TO VALIANT4 138 KV 510918 CKT 1 b.2. IDABEL-4 138 KV 510886 TO B.BOWTP4 138 KV 510888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_VALIANT4__HUGO_PP4 | 3 Phase fault VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 138 KV 510918 TO HUGO PP4 138 KV 520948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_VALIANT7__HUGO___7 | 3 Phase fault VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345 KV 510911 TO HUGO 7 345 KV 521157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_VANCE__2__SO4TH__2 | 3 Phase fault VANCE 2 (514718) 69 kV Bus a. Apply fault at the VANCE 2 (514718) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANCE 2 69 KV 514718 TO SO4TH 2 69 KV 514730 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_VANOSS_4__PARKLN_4 | 3 Phase fault VANOSS 4 (515174) 138 kV Bus a. Apply fault at the VANOSS 4 (515174) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANOSS 4 138 KV 515174 TO PARKLN 4 138 KV 515178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_VANOSS_4__VANOSTP4 | 3 Phase fault VANOSS 4 (515174) 138 kV Bus a. Apply fault at the VANOSS 4 (515174) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANOSS 4 138 KV 515174 TO VANOSTP4 138 KV 515531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_VINITA_VINITAJC2 | 3 Phase fault VINITA-2 (510404) 69 kV Bus a. Apply fault at the VINITA-2 (510404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINITA-2 69 KV 510404 TO VINTAJC2 69 KV 510418 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_VINTAJC4__ALWUETP4 | 3 Phase fault VINTAJC4 (510417) 138 kV Bus a. Apply fault at the VINTAJC4 (510417) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC4 138 KV 510417 TO ALWUETP4 138 KV 510429 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_VINTAJC4__HOC404_4 | 3 Phase fault VINTAJC4 (510417) 138 kV Bus a. Apply fault at the VINTAJC4 (510417) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC4 138 KV 510417 TO HOC404 4 138 KV 547486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_W.ED._CARSONT4 | 3 Phase fault W.ED.-W4 (509832) 138 kV Bus a. Apply fault at the W.ED.-W4 (509832) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W.ED.-W4 138 KV 509832 TO CARSONT4 138 KV 509865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WARNTAP4__77MEMW4 | 3 Phase fault WARNTAP4 (509858) 138 kV Bus a. Apply fault at the WARNTAP4 (509858) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 96YALE-4 138 KV 509847 TO WARNTAP4 138 KV 509858 CKT 1 b.2. 77MEM-W4 138 KV 509766 TO 96YALE-4 138 KV 509847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WARWICK4__BELLCOW4 | 3 Phase fault WARWICK4 (515047) 138 kV Bus a. Apply fault at the WARWICK4 (515047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARWICK4 138 KV 515047 TO BELLCOW4 138 KV 515369 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WARWICK4__TRYON_4 | 3 Phase fault WARWICK4 (515047) 138 kV Bus a. Apply fault at the WARWICK4 (515047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARWICK4 138 KV 515047 TO TRYON 4 138 KV 515675 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WARWICK4__WFROSST4 | 3 Phase fault WARWICK4 (515047) 138 kV Bus a. Apply fault at the WARWICK4 (515047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARWICK4 138 KV 515047 TO WFROSST4 138 KV 515366 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WASHITA4__BINGERJ4 | 3 Phase fault WASHITA4 (521089) 138 kV Bus a. Apply fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEY 4 138 KV 521017 TO WASHITA4 138 KV 521089 CKT 1 b.2. BINGERJ4 138 KV 520827 TO ONEY 4 138 KV 521017 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WASHITA4__SLKHILLS_4 | 3 Phase fault WASHITA4 (521089) 138 kV Bus a. Apply fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 138 KV 521089 TO SLKHILLS 4 138 KV 521103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WATLANT4__CASSTP4 | 3 Phase fault WATLANT4 (508090) 138 kV Bus a. Apply fault at the WATLANT4 (508090) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138 KV 508090 TO CASSTP4 138 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WATLANT4__WILKES_4 | 3 Phase fault WATLANT4 (508090) 138 kV Bus a. Apply fault at the WATLANT4 (508090) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138 KV 508090 TO WILKES 4 138 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WATNGSW4__CALUMET4 | 3 Phase fault WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138 KV 520536 TO CALUMET4 138 KV 520839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WATNGSW4__FAY____4 | 3 Phase fault WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138 KV 520536 TO WATONGA4 138 KV 521091 CKT 1 b.2. LOAD 1 521091 b.3. FAY 4 138 KV 520538 TO WATONGA4 138 KV 521091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WATNGSW4__KGFSHSW4 | 3 Phase fault WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138 KV 520536 TO OMEGA 4 138 KV 520964 CKT 1 b.2. LOAD 1 520964 b.3. PARKCOM4 138 KV 520475 TO OMEGA 4 138 KV 520964 CKT 1 b.4. LOAD 1 520964 b.5. PARKCOM4 138 KV 520475 TO KGFSHSW4 138 KV 520533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WATNGSW4__OKEENE_4 | 3 Phase fault WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138 KV 520536 TO OKEENE 4 138 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WAUKOTP4__HENESEY4 | 3 Phase fault WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 138 KV 514710 TO HENESEY4 138 KV 514774 CKT 1 b.2. LOAD 1 514774 b.3. WAUKOMI4 138 KV 514710 TO WAUKOTP4 138 KV 514711 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WAUKOTP4__SO4TH__4 | 3 Phase fault WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138 KV 514711 TO SO4TH 4 138 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WAUKOTP4__WOODRNG4 | 3 Phase fault WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138 KV 514711 TO WOODRNG4 138 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WCITYTP2__VALIANT2 | 3 Phase fault WCITYTP2 (510870) 69 kV Bus a. Apply fault at the WCITYTP2 (510870) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WCITYTP2 69 KV 510870 TO VALIANT2 69 KV 510910 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WED_CARSON4 | 3 Phase fault WED-TAP4 (509823) 138 kV Bus a. Apply fault at the WED-TAP4 (509823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WED-TAP4 138 KV 509823 TO CARSONT4 138 KV 509865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WEKIWA_GEN_2010_055 | 3 Phase fault WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138 KV 509757 TO GEN-2010-055 138 KV 560389 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WEKIWA_P&PWTP4 | 3 Phase fault WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138 KV 509757 TO P&P WTP4 138 KV 509851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WEKIWA_SS4 | 3 Phase fault WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEFFD-4 138 KV 509812 TO S.S.---4 138 KV 509815 CKT 1 b.2. LOAD 1 509815 b.3. WEKIWA-4 138 KV 509757 TO SHEFFD-4 138 KV 509812 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WEKIWA_SHEFFD | 3 Phase fault WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138 KV 509757 TO SHEFFD-4 138 KV 509812 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WEKIWA_SILCTYGR4 | 3 Phase fault WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138 KV 509757 TO SILVCTYGR4 138 KV 512726 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WEKIWA_WEDTAP4 | 3 Phase fault WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138 KV 509757 TO WED-TAP4 138 KV 509823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WEKIWA_SAPLPRD | 3 Phase fault WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345 KV 509755 TO SAPLPRD7 345 KV 509870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WEKIWA_SOONER | 3 Phase fault WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345 KV 509755 TO SOONER 7 345 KV 514803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WEKIWA_TNO7 | 3 Phase fault WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345 KV 509755 TO T.NO.--7 345 KV 509852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WELLSPA2__ONAPA__2 | 3 Phase fault WELLSPA2 (515215) 69 kV Bus a. Apply fault at the WELLSPA2 (515215) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELLSPA2 69 KV 515215 TO ONAPA 2 69 KV 521020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WELSHRE4__WILKES_4 | 3 Phase fault WELSHRE4 (508355) 138 kV Bus a. Apply fault at the WELSHRE4 (508355) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELSHRE4 138 KV 508355 TO WILKES 4 138 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WELSH__7__DIANA__7 | 3 Phase fault WELSH 7 (508359) 345 kV Bus a. Apply fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345 KV 508359 TO DIANA 7 345 KV 508832 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WELSH__7__WILKES_7 | 3 Phase fault WELSH 7 (508359) 345 kV Bus a. Apply fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345 KV 508359 TO WILKES 7 345 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WESTELC4__LEASIDE_4 | 3 Phase fault WESTELC4 (507767) 138 kV Bus a. Apply fault at the WESTELC4 (507767) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTELC4 138 KV 507767 TO LEASIDE 4 138 KV 507793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WESTERN4__STNWAL_4 | 3 Phase fault WESTERN4 (514869) 138 kV Bus a. Apply fault at the WESTERN4 (514869) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTERN4 138 KV 514869 TO STNWAL 4 138 KV 514870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WESTHSE4__INDNHIL4 | 3 Phase fault WESTHSE4 (514904) 138 kV Bus a. Apply fault at the WESTHSE4 (514904) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTHSE4 138 KV 514904 TO INDNHIL4 138 KV 514954 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WFROSST4__LINCOLN4 | 3 Phase fault WFROSST4 (515366) 138 kV Bus a. Apply fault at the WFROSST4 (515366) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WFROSST4 138 KV 515366 TO LINCOLN4 138 KV 515442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WFROSST4__RSSVILE4 | 3 Phase fault WFROSST4 (515366) 138 kV Bus a. Apply fault at the WFROSST4 (515366) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WFROSST4 138 KV 515366 TO RSSVILE4 138 KV 521107 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WHEELER____3__HOWARD_____3 | 3 Phase fault WHEELER 3 (523776) 115 kV Bus a. Apply fault at the WHEELER 3 (523776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 3 115 KV 523776 TO HOWARD 3 115 KV 523797 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WHEELER____6__STLN | 3 Phase fault WHEELER 6 (523777) 230 kV Bus a. Apply fault at the WHEELER 6 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 230 KV 523777 TO STLN-DEMARC6 230 KV 523779 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WHIRLPO4__CDC | 3 Phase fault WHIRLPO4 (509840) 138 kV Bus a. Apply fault at the WHIRLPO4 (509840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHIRLPO4 138 KV 509840 TO CDC-WT 4 138 KV 509842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WHITNEY4__EASTEX_4 | 3 Phase fault WHITNEY4 (508575) 138 kV Bus a. Apply fault at the WHITNEY4 (508575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY4 138 KV 508575 TO EASTEX 4 138 KV 508582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WHORSE_HWY20 | 3 Phase fault WHORSE-4 (509754) 138 kV Bus a. Apply fault at the WHORSE-4 (509754) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHORSE-4 138 KV 509754 TO HWY20-T4 138 KV 509821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WILKES_4__CHAPELH4 | 3 Phase fault WILKES 4 (508840) 138 kV Bus a. Apply fault at the WILKES 4 (508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPELH4 138 KV 508337 TO WELSHRE4 138 KV 508355 CKT 1 b.2. LOAD 1 508355 b.3. WELSHRE4 138 KV 508355 TO WILKES 4 138 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WINDFRM4__MOORLND4 | 3 Phase fault WINDFRM4 (515785) 138 kV Bus a. Apply fault at the WINDFRM4 (515785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 138 KV 515785 TO MOORLND4 138 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WLNUTCK4__PAOLI | 3 Phase fault WLNUTCK4 (515097) 138 kV Bus a. Apply fault at the WLNUTCK4 (515097) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WLNUTCK4 138 KV 515097 TO PAOLI- 4 138 KV 515100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WODWRD_2__WOODWRD2 | 3 Phase fault WODWRD 2 (514782) 69 kV Bus a. Apply fault at the WODWRD 2 (514782) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WODWRD 2 69 KV 514782 TO WOODWRD2 69 KV 521096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WOLFCRK4__CHEEKTP4 | 3 Phase fault WOLFCRK4 (515143) 138 kV Bus a. Apply fault at the WOLFCRK4 (515143) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK4 138 KV 515143 TO CHEEKTP4 138 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WOLVERN4__WOLVRNT4 | 3 Phase fault WOLVERN4 (515056) 138 kV Bus a. Apply fault at the WOLVERN4 (515056) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLVERN4 138 KV 515056 TO WOLVRNT4 138 KV 515532 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WOODRNG4__MARSHL_4 | 3 Phase fault WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 138 KV 514714 TO MARSHL 4 138 KV 514733 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WOODRNG7__GEN-2017-164 | 3 Phase fault WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345 KV 514715 TO GEN-2017-164 345 KV 762321 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WOODRNG7__HUNTERS7 | 3 Phase fault WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345 KV 514715 TO HUNTERS7 345 KV 515476 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WOODRNG7__PINTAIL7 | 3 Phase fault WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345 KV 514715 TO PINTAIL7 345 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WOODRNG7__REDNGTN7 | 3 Phase fault WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345 KV 514715 TO REDNGTN7 345 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WOODRNG7__SKELTON7 | 3 Phase fault WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345 KV 514715 TO SKELTON7 345 KV 515990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WOODWRD2__CRTSJCT2 | 3 Phase fault WOODWRD2 (521096) 69 kV Bus a. Apply fault at the WOODWRD2 (521096) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD2 69 KV 521096 TO CRTSJCT2 69 KV 521197 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WOODWRD2__FARGOJCT2 | 3 Phase fault WOODWRD2 (521096) 69 kV Bus a. Apply fault at the WOODWRD2 (521096) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD2 69 KV 521096 TO FARGOJCT2 69 KV 521196 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WOODWRD4__CENT___4 | 3 Phase fault WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138 KV 514785 TO CENT 4 138 KV 515363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WOODWRD4__WINDFRM4 | 3 Phase fault WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138 KV 514785 TO WINDFRM4 138 KV 515785 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WOODWRD4__WWRDEHV4 | 3 Phase fault WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138 KV 514785 TO WWRDEHV4 138 KV 515376 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WRNMED_WRNMEDT4 | 3 Phase fault WRN-MED4 (509729) 138 kV Bus a. Apply fault at the WRN-MED4 (509729) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRN-MED4 138 KV 509729 TO WRNMEDT4 138 KV 509764 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WRNMEDT4__81YALTP4 | 3 Phase fault WRNMEDT4 (509764) 138 kV Bus a. Apply fault at the WRNMEDT4 (509764) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRNMEDT4 138 KV 509764 TO 81YALTP4 138 KV 509809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WRNMEDT4__S.HUD. | 3 Phase fault WRNMEDT4 (509764) 138 kV Bus a. Apply fault at the WRNMEDT4 (509764) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRNMEDT4 138 KV 509764 TO S.HUD.-4 138 KV 509833 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WWRDEHV4__KEENAN_4 | 3 Phase fault WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138 KV 515376 TO KEENAN 4 138 KV 515394 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WWRDEHV4__OUSPRT_4 | 3 Phase fault WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138 KV 515376 TO OUSPRT 4 138 KV 515398 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WWRDEHV4__REDCLFT4 | 3 Phase fault WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IODINE-4 138 KV 514796 TO WWRDEHV4 138 KV 515376 CKT 1 b.2. IODINE-4 138 KV 514796 TO REDCLFT4 138 KV 515533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WWRDEHV4__WWDPST_4 | 3 Phase fault WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138 KV 515376 TO WWDPST 4 138 KV 515425 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WWRDEHV7__BECKHAM7 | 3 Phase fault WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345 KV 515375 TO BECKHAM7 345 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WWRDEHV7__DGRASSE7 | 3 Phase fault WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345 KV 515375 TO DGRASSE7 345 KV 515852 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WWRDEHV7__G07621119 | 3 Phase fault WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345 KV 515375 TO G07621119-20 345 KV 515599 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WWRDEHV7__G16 | 3 Phase fault WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345 KV 515375 TO G16-003-TAP 345 KV 560071 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WWRDEHV7__GUTHRIE7 | 3 Phase fault WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345 KV 515375 TO GUTHRIE7 345 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WWRDEHV7__TATONGA7 | 3 Phase fault WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345 KV 515375 TO TATONGA7 345 KV 515407 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_YARCH_YARCHT4 | 3 Phase fault YARCH-N4 (509825) 138 kV Bus a. Apply fault at the YARCH-N4 (509825) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YARCH-N4 138 KV 509825 TO YARCHT 4 138 KV 509862 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_YARCH_PPTAP | 3 Phase fault YARCH-S4 (509824) 138 kV Bus a. Apply fault at the YARCH-S4 (509824) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YARCH-S4 138 KV 509824 TO KENSH-E-TP4 138 KV 509830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_YARCHT_4__PPTAP__4 | 3 Phase fault YARCHT 4 (509862) 138 kV Bus a. Apply fault at the YARCHT 4 (509862) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YARCHT 4 138 KV 509862 TO PPTAP 4 138 KV 509863 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_YOAKUM_345__HOBBS_INT__7 | 3 Phase fault YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345 KV 526936 TO HOBBS_INT 7 345 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ZUNIS_FULTONW4 | 3 Phase fault ZUNIS-N4 (509827) 138 kV Bus a. Apply fault at the ZUNIS-N4 (509827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ZUNIS-N4 138 KV 509827 TO FULTONW4 138 KV 509829 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_38TH_ST2__514846 | 3 Phase fault 38TH ST2 (514845) 69 kV Bus a. Apply fault at the 38TH ST2 (514845) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 38TH ST2 514845 TO 38TH ST4 514846 TO 38TH ST1 515768 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_4MURFBORO__337673 | 3 Phase fault 4MURFBORO (337672) 138 kV Bus a. Apply fault at the 4MURFBORO (337672) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MURFBORO 337672 TO 3MURFBORO.S! 337673 TO 1MURFBORO 337671 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_5TRIBES2__515228 | 3 Phase fault 5TRIBES2 (515227) 69 kV Bus a. Apply fault at the 5TRIBES2 (515227) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TRIBES2 515227 TO 5TRIBES5 515228 TO 5TRIBES1 515723 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_8ANO%__337912 | 3 Phase fault 8ANO% (337909) 500 kV Bus a. Apply fault at the 8ANO% (337909) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 337909 TO 5ANO% 337912 TO 1ANO AUX 337913 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_8EL_DORADO%__337539 | 3 Phase fault 8EL DORADO% (337561) 500 kV Bus a. Apply fault at the 8EL DORADO% (337561) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 337561 TO 3EL DORADO! 337539 TO 1EL DORADO3 337566 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_8EL_DORADO%__337562 | 3 Phase fault 8EL DORADO% (337561) 500 kV Bus a. Apply fault at the 8EL DORADO% (337561) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 337561 TO 7EL DORADO 337562 TO 1EL DORADO2 337565 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_8STERLING%__337415 | 3 Phase fault 8STERLING% (337420) 500 kV Bus a. Apply fault at the 8STERLING% (337420) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8STERLING% 337420 TO 3STERLING% 337415 TO 1STERLING3 337412 CKT 3 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_AGENCY_2__515230 | 3 Phase fault AGENCY 2 (515229) 69 kV Bus a. Apply fault at the AGENCY 2 (515229) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AGENCY 2 515229 TO AGENCY 5 515230 TO AGENCY 1 515701 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ANADARK4__520810 | 3 Phase fault ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 520814 TO ANADARK2 520810 TO ADRKTERT 521181 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ARCADIA4__514908 | 3 Phase fault ARCADIA4 (514907) 138 kV Bus a. Apply fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 514907 TO ARCADIA7 514908 TO ARCADI31 515704 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ARSHILL2__507711 | 3 Phase fault ARSHILL2 (507710) 69 kV Bus a. Apply fault at the ARSHILL2 (507710) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL2 507710 TO ARSHILL4 507711 TO ARSH2-1 507714 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BANN___2__508054 | 3 Phase fault BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 508053 TO BANN 4 508054 TO BANN1-1 508097 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BEELINE2__515247 | 3 Phase fault BEELINE2 (515246) 69 kV Bus a. Apply fault at the BEELINE2 (515246) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEELINE2 515246 TO BEELINE4 515247 TO BEELINE1 515705 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BLUEBEL2__515242 | 3 Phase fault BLUEBEL2 (515241) 69 kV Bus a. Apply fault at the BLUEBEL2 (515241) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBEL2 515241 TO BLUEBEL4 515242 TO BLUEBEL1 515706 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BRISTOW2__515035 | 3 Phase fault BRISTOW2 (515034) 69 kV Bus a. Apply fault at the BRISTOW2 (515034) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW2 515034 TO BRISTOW4 515035 TO BRISTOW1 515709 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_BV_XFMR | 3 Phase fault BV-COM-2 (510389) 69 kV Bus a. Apply fault at the BV-COM-2 (510389) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BV-COM-2 510389 TO BV-COM-4 510390 TO BVCOM3-1 510372 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CRIVER_XFMR | 3 Phase fault C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 515422 TO C-RIVER4 510946 TO C-RIVER1 510947 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CANADNS4__520841 | 3 Phase fault CANADNS4 (520842) 138 kV Bus a. Apply fault at the CANADNS4 (520842) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 520842 TO CANADNS2 520841 TO CANTERT 521164 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CATOOSA2__509790 | 3 Phase fault CATOOSA2 (509799) 69 kV Bus a. Apply fault at the CATOOSA2 (509799) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA2 509799 TO CATOOSA4 509790 TO CATOO1-1 509867 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CATSAGR5__509790 | 3 Phase fault CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 512638 TO CATOOSA4 509790 TO 512835 CKT 3 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CHAMSPR5__506945 | 3 Phase fault CHAMSPR5 (506944) 161 kV Bus a. Apply fault at the CHAMSPR5 (506944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAMSPR5 506944 TO CHAMSPR7 506945 TO CHAMSPR1 506919 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CHISHOLM6__511553 | 3 Phase fault CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6 (511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CIMARON4__514901 | 3 Phase fault CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 514898 TO CIMARON7 514901 TO CIMARO21 515715 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CLARMR_5__512679 | 3 Phase fault CLARMR 5 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 512651 TO CLARMR 2 512679 TO CLARMR2 512815 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CLARMR_5__512707 | 3 Phase fault CLARMR 5 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 512651 TO CLARMR 4 512707 TO CLARMR4 512813 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CLEVLND7__512729 | 3 Phase fault CLEVLND7 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 512694 TO CLEVLND 4 512729 TO CLEVLND1 512817 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_COLINS_5__512705 | 3 Phase fault COLINS 5 (512627) 161 kV Bus a. Apply fault at the COLINS 5 (512627) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINS 5 512627 TO COLLINS4 512705 TO COLLIN1 1 512838 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_COLNSGR2__512627 | 3 Phase fault COLNSGR2 (512870) 69 kV Bus a. Apply fault at the COLNSGR2 (512870) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLNSGR2 512870 TO COLINS 5 512627 TO COLLIN3 1 512840 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_CORNVIL2__511449 | 3 Phase fault CORNVIL2 (511450) 69 kV Bus a. Apply fault at the CORNVIL2 (511450) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL2 511450 TO CORNVIL4 511449 TO CORNV2-1 511418 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DAWSON_XFMR | 3 Phase fault DAWSON-2 (509791) 69 kV Bus a. Apply fault at the DAWSON-2 (509791) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSON-2 509791 TO DAWSON-4 509792 TO DAWSN3-1 509877 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DELWARE4__510380 | 3 Phase fault DELWARE4 (510379) 138 kV Bus a. Apply fault at the DELWARE4 (510379) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELWARE4 510379 TO DELWARE7 510380 TO DELAWAR1 510370 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DEQUEEN2__507419 | 3 Phase fault DEQUEEN2 (507418) 69 kV Bus a. Apply fault at the DEQUEEN2 (507418) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEQUEEN2 507418 TO DEQUEEN4 507419 TO DQUEN1-1 507441 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DGRASSE4__515852 | 3 Phase fault DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 515853 TO DGRASSE7 515852 TO DGRASSE1 515854 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DIANA__4__508832 | 3 Phase fault DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 508831 TO DIANA 7 508832 TO DIANA-N1 508845 CKT 3 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DOVERSW4__520881 | 3 Phase fault DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 520882 TO DOVERSW2 520881 TO DVRTERT 521166 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_DRAPER_4__514934 | 3 Phase fault DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 514933 TO DRAPER 7 514934 TO DRAPER21 515792 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ELGINJT2__511486 | 3 Phase fault ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2 (511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ELKCTY_XFMR | 3 Phase fault ELKCTY-2 (511459) 69 kV Bus a. Apply fault at the ELKCTY-2 (511459) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-2 511459 TO ELKCTY-4 511458 TO ELKC4-1 511493 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ELKCTY_XFMR | 3 Phase fault ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 511458 TO ELKCITY6 511490 TO ELKC2-1 511482 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ELRENO_2__514819 | 3 Phase fault ELRENO 2 (514818) 69 kV Bus a. Apply fault at the ELRENO 2 (514818) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELRENO 2 514818 TO EL-RENO4 514819 TO EL RENO1 515722 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FLETCH_XFMR | 3 Phase fault FLETCH-4 (520912) 138 kV Bus a. Apply fault at the FLETCH-4 (520912) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCH-4 520912 TO FLETCHR2 520911 TO FLCHTERT 521168 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FLOURNY2__507727 | 3 Phase fault FLOURNY2 (507726) 69 kV Bus a. Apply fault at the FLOURNY2 (507726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 507726 TO FLOURNY4 507727 TO FLOURNY1 507740 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FRNKLNS4__520916 | 3 Phase fault FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRNKLNS4 520917 TO FRNKLNS2 520916 TO FRNKTERT 521169 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FRSTHIL2__515075 | 3 Phase fault FRSTHIL2 (515074) 69 kV Bus a. Apply fault at the FRSTHIL2 (515074) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRSTHIL2 515074 TO FRSTHIL4 515075 TO FRSTHIL1 515725 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FTSMITH7__515305 | 3 Phase fault FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 515302 TO FTSMITH8 515305 TO FTSMTH11 515726 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FTSMTHE5__515305 | 3 Phase fault FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5 (515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 515300 TO FTSMITH8 515305 TO FTSMTH31 515727 CKT 3 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FTSMTHW5__515302 | 3 Phase fault FTSMTHW5 (515301) 161 kV Bus a. Apply fault at the FTSMTHW5 (515301) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 515301 TO FTSMITH7 515302 TO FTSMTH51 515728 CKT 5 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_FTSMTHW5__515305 | 3 Phase fault FTSMTHW5 (515301) 161 kV Bus a. Apply fault at the FTSMTHW5 (515301) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 515301 TO FTSMITH8 515305 TO FTSMTH41 515791 CKT 4 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GORE___5__512644 | 3 Phase fault GORE 5 (505552) 161 kV Bus a. Apply fault at the GORE 5 (505552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 505552 TO GORE GR2 512644 TO GORTER1 512832 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRACMNT4__515800 | 3 Phase fault GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRAPEVINE__6__523770 | 3 Phase fault GRAPEVINE 6 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 523771 TO GRAPEVINE 3 523770 TO GRAPEVN_TR11 523769 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA1__5__512727 | 3 Phase fault GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 512656 TO GRDA1 2 512727 TO GRDA1 1 512816 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA1__7__512656 | 3 Phase fault GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 512650 TO GRDA1 5 512656 TO GRDA2 1 512826 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRTWSRN7__515820 | 3 Phase fault GRTWSRN7 (515825) 345 kV Bus a. Apply fault at the GRTWSRN7 (515825) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRTWSRN7 515825 TO GRTWSL11 515820 TO GRTWST11 515860 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRTWSRN7__515823 | 3 Phase fault GRTWSRN7 (515825) 345 kV Bus a. Apply fault at the GRTWSRN7 (515825) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRTWSRN7 515825 TO GRTWSL21 515823 TO GRTWST21 515824 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HOB_XFMR | 3 Phase fault HOB-JCT2 (511464) 69 kV Bus a. Apply fault at the HOB-JCT2 (511464) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT2 511464 TO HOB-JCT4 511463 TO HOBJT1-1 511417 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HOC404_5__547486 | 3 Phase fault HOC404 5 (547487) 161 kV Bus a. Apply fault at the HOC404 5 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 547487 TO HOC404 4 547486 TO HOC404A1 547715 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HSLWEST2__514941 | 3 Phase fault HSLWEST2 (514937) 69 kV Bus a. Apply fault at the HSLWEST2 (514937) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLWEST2 514937 TO HSL 4 514941 TO HSL 1 515731 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HUGO_XFMR | 3 Phase fault HUGO---2 (510893) 69 kV Bus a. Apply fault at the HUGO---2 (510893) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGO---2 510893 TO HUGO---4 510901 TO HUGO4-1 510859 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_HUGO___7__520560 | 3 Phase fault HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 521157 TO HUGOITC4 520560 TO HUGO TERTA 521189 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_IGLOOV_7__513593 | 3 Phase fault IGLOOV 7 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 513596 TO IGLOOV1 5 513593 TO IGLOTER1 1 513592 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_IGLOOV_7__513595 | 3 Phase fault IGLOOV 7 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 513596 TO IGLOOV2 5 513595 TO IGLOTER2 1 513594 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_IMO____2__514790 | 3 Phase fault IMO 2 (514721) 69 kV Bus a. Apply fault at the IMO 2 (514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 514721 TO IMO 4 514790 TO IMO 1 515788 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_JOHNCO_4__514809 | 3 Phase fault JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 514808 TO JOHNCO 7 514809 TO JOHNCO11 514810 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_KEENAN_1__515394 | 3 Phase fault KEENAN 1 (515393) 34.5 kV Bus a. Apply fault at the KEENAN 1 (515393) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEENAN 1 515393 TO KEENAN 4 515394 TO KEENAN T 515392 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_KNOXLEE2__508548 | 3 Phase fault KNOXLEE2 (508547) 69 kV Bus a. Apply fault at the KNOXLEE2 (508547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE2 508547 TO KNOXLEE4 508548 TO KXLEE-1 508584 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_L.E.S._XFMR | 3 Phase fault L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_L.E.S._XFMR | 3 Phase fault L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LEASIDE_2__507793 | 3 Phase fault LEASIDE 2 (507794) 69 kV Bus a. Apply fault at the LEASIDE 2 (507794) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEASIDE 2 507794 TO LEASIDE 4 507793 TO LEASIDE 1-1 507795 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LIEBERM2__508806 | 3 Phase fault LIEBERM2 (508805) 69 kV Bus a. Apply fault at the LIEBERM2 (508805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM2 508805 TO LIEBERM4 508806 TO LBMN3-1 508822 CKT 3 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LOGANSP2__509071 | 3 Phase fault LOGANSP2 (509070) 69 kV Bus a. Apply fault at the LOGANSP2 (509070) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGANSP2 509070 TO LOGANSP4 509071 TO 509094 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LONGWD_4__508809 | 3 Phase fault LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 508808 TO LONGWD 7 508809 TO LONGW1-1 508819 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_LSSOUTH2__508297 | 3 Phase fault LSSOUTH2 (508296) 69 kV Bus a. Apply fault at the LSSOUTH2 (508296) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH2 508296 TO LSSOUTH4 508297 TO LSS-1 508325 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MAID___5__512626 | 3 Phase fault MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 512648 TO MAID 2 512626 TO MAITER2 1 512837 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MANDEVILTP4__504363 | 3 Phase fault MANDEVILTP4 (508105) 138 kV Bus a. Apply fault at the MANDEVILTP4 (508105) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANDEVILTP4 508105 TO NE-TEXARK2 504363 TO NE-TEXARK1 504364 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MARAUTO2__508557 | 3 Phase fault MARAUTO2 (508576) 69 kV Bus a. Apply fault at the MARAUTO2 (508576) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARAUTO2 508576 TO MARSHL-4 508557 TO MRSH4#21 508592 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MAUD___4__515054 | 3 Phase fault MAUD 4 (515055) 138 kV Bus a. Apply fault at the MAUD 4 (515055) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 4 515055 TO MAUD 2 515054 TO MAUD 1 515736 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MENA___2__507436 | 3 Phase fault MENA 2 (508301) 69 kV Bus a. Apply fault at the MENA 2 (508301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENA 2 508301 TO MENA 4 507436 TO MENA3-1 507438 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MOORLND4__520995 | 3 Phase fault MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND4 520999 TO MOORLND2 520995 TO MLNDTERT 521180 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MSTANG_2__514861 | 3 Phase fault MSTANG 2 (514860) 69 kV Bus a. Apply fault at the MSTANG 2 (514860) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTANG 2 514860 TO MUSTANG4 514861 TO MUSTANG1 515740 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MSTNG10G__514861 | 3 Phase fault MSTNG10G (515672) 13.8 kV Bus a. Apply fault at the MSTNG10G (515672) 13.8 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTNG10G 515672 TO MUSTANG4 514861 TO MSTNG11G 515673 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MSTNG_8G__514861 | 3 Phase fault MSTNG 8G (515670) 13.8 kV Bus a. Apply fault at the MSTNG 8G (515670) 13.8 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTNG 8G 515670 TO MUSTANG4 514861 TO MSTNG 9G 515671 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_MUSKOGE2__515222 | 3 Phase fault MUSKOGE2 (515221) 69 kV Bus a. Apply fault at the MUSKOGE2 (515221) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKOGE2 515221 TO MUSKOGE5 515222 TO MUSKOG41 515797 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NBENTON2__508811 | 3 Phase fault NBENTON2 (508810) 69 kV Bus a. Apply fault at the NBENTON2 (508810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NBENTON2 508810 TO NBENTON4 508811 TO NBENTON1 508823 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NEOSHO_7__532937 | 3 Phase fault NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 532793 TO NEOSHO 5 532937 TO N345 2 1 532825 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NEOSHO_7__533021 | 3 Phase fault NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 532793 TO NEOSHO 4 533021 TO N345 1 1 532824 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NNBOSTN2__508069 | 3 Phase fault NNBOSTN2 (508068) 69 kV Bus a. Apply fault at the NNBOSTN2 (508068) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN2 508068 TO NNBOSTN4 508069 TO NNBT2-1 508099 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NORMHLL7__516097 | 3 Phase fault NORMHLL7 (516096) 345 kV Bus a. Apply fault at the NORMHLL7 (516096) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORMHLL7 516096 TO NORMHLL4 516097 TO NORMHL21 516099 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NORTWST4__514880 | 3 Phase fault NORTWST4 (514879) 138 kV Bus a. Apply fault at the NORTWST4 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTWST4 514879 TO NORTWST7 514880 TO NORTWS31 515743 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_NWTXARK4__508072 | 3 Phase fault NWTXARK4 (508071) 138 kV Bus a. Apply fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 508071 TO NWTXARK7 508072 TO NWTEX2-1 508101 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OKAY___2__507428 | 3 Phase fault OKAY 2 (507427) 69 kV Bus a. Apply fault at the OKAY 2 (507427) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAY 2 507427 TO OKAY 4 507428 TO OKAY1-1 507442 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OKEENE_4__521015 | 3 Phase fault OKEENE 4 (521016) 138 kV Bus a. Apply fault at the OKEENE 4 (521016) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKEENE 4 521016 TO OKEENE 2 521015 TO OKENTERT 521173 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ONETA_XFMR | 3 Phase fault ONETA--4 (509806) 138 kV Bus a. Apply fault at the ONETA--4 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 509806 TO ONETA--7 509807 TO ONETA1-1 509881 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OUSPRT_1__515398 | 3 Phase fault OUSPRT 1 (515397) 34.5 kV Bus a. Apply fault at the OUSPRT 1 (515397) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OUSPRT 1 515397 TO OUSPRT 4 515398 TO OUSPRT T 515396 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PALIOGE2__515100 | 3 Phase fault PALIOGE2 (515099) 69 kV Bus a. Apply fault at the PALIOGE2 (515099) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PALIOGE2 515099 TO PAOLI- 4 515100 TO PAOLI 1 515746 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PARKLN_2__515178 | 3 Phase fault PARKLN 2 (515177) 69 kV Bus a. Apply fault at the PARKLN 2 (515177) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKLN 2 515177 TO PARKLN 4 515178 TO PARKLN21 515748 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PATTERS2__507431 | 3 Phase fault PATTERS2 (507429) 69 kV Bus a. Apply fault at the PATTERS2 (507429) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS2 507429 TO PATTERS4 507431 TO PATTN2-1 507444 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PECANCK4__515234 | 3 Phase fault PECANCK4 (515233) 138 kV Bus a. Apply fault at the PECANCK4 (515233) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK4 515233 TO PECANCK5 515234 TO PECANC31 515750 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PECANCK5__515235 | 3 Phase fault PECANCK5 (515234) 161 kV Bus a. Apply fault at the PECANCK5 (515234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK5 515234 TO PECANCK7 515235 TO PECANC21 515759 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PENN___2__514925 | 3 Phase fault PENN 2 (514924) 69 kV Bus a. Apply fault at the PENN 2 (514924) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENN 2 514924 TO PENN 4 514925 TO PENN 1 515751 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PENSA__5__512628 | 3 Phase fault PENSA 5 (512654) 161 kV Bus a. Apply fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 5 512654 TO PENSA 2 512628 TO PENSA 1 512841 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_PIRKEY_4__508563 | 3 Phase fault PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY2-1 508588 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_R.S.S.XFMR | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 509783 TO RSS NG3 511844 TO RSS NG4 511845 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_REDBUD1S__514909 | 3 Phase fault REDBUD1S (514899) 18 kV Bus a. Apply fault at the REDBUD1S (514899) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD1S 514899 TO REDBUD 7 514909 TO REDBUD1G 514910 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_REDBUD2S__514909 | 3 Phase fault REDBUD2S (514900) 18 kV Bus a. Apply fault at the REDBUD2S (514900) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD2S 514900 TO REDBUD 7 514909 TO REDBUD2G 514911 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_REDBUD3S__514909 | 3 Phase fault REDBUD3S (514905) 18 kV Bus a. Apply fault at the REDBUD3S (514905) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD3S 514905 TO REDBUD 7 514909 TO REDBUD3G 514912 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_REDBUD4S__514909 | 3 Phase fault REDBUD4S (514940) 18 kV Bus a. Apply fault at the REDBUD4S (514940) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD4S 514940 TO REDBUD 7 514909 TO REDBUD4G 514942 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_RENO___2__514973 | 3 Phase fault RENO 2 (514972) 69 kV Bus a. Apply fault at the RENO 2 (514972) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 2 514972 TO RENO 4 514973 TO RENO 1 515753 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ROCKYPT2__515164 | 3 Phase fault ROCKYPT2 (515163) 69 kV Bus a. Apply fault at the ROCKYPT2 (515163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 515163 TO ROCKYPT4 515164 TO ROCKYPT1 515754 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_ROKHILL2__509083 | 3 Phase fault ROKHILL2 (509082) 69 kV Bus a. Apply fault at the ROKHILL2 (509082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL2 509082 TO ROKHILL4 509083 TO RKHIL2-1 509091 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_RSS_T1_4__509782 | 3 Phase fault RSS T1 4 (509773) 138 kV Bus a. Apply fault at the RSS T1 4 (509773) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T1 4 509773 TO R.S.S.-7 509782 TO RSST1 T1 509882 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_RSS_T2_4__509782 | 3 Phase fault RSS T2 4 (509875) 138 kV Bus a. Apply fault at the RSS T2 4 (509875) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T2 4 509875 TO R.S.S.-7 509782 TO RSST2 T1 509876 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_RUSHING2__515064 | 3 Phase fault RUSHING2 (515063) 69 kV Bus a. Apply fault at the RUSHING2 (515063) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSHING2 515063 TO RUSHING4 515064 TO RUSHING1 515755 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_RUSHSPR7__511965 | 3 Phase fault RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 511571 TO RUSHSPRW1-1 511965 TO RUSHSPR1-1 511572 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_S.S._XFMR | 3 Phase fault S.S.---2 (509816) 69 kV Bus a. Apply fault at the S.S.---2 (509816) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---2 509816 TO S.S.---4 509815 TO SS6-1 509878 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_S.W.S.2_XFMR | 3 Phase fault S.W.S.-2 (511476) 69 kV Bus a. Apply fault at the S.W.S.-2 (511476) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-2 511476 TO S.W.S.-4 511477 TO SWS#1--1 511413 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_S.W.S.4_XFMR | 3 Phase fault S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 511477 TO SWS NG4 511849 TO SWS NG5 511850 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SAPLPRD4__509870 | 3 Phase fault SAPLPRD4 (509871) 138 kV Bus a. Apply fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 509871 TO SAPLPRD7 509870 TO SAPLPRD1 509872 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SDIERKS2__507433 | 3 Phase fault SDIERKS2 (507432) 69 kV Bus a. Apply fault at the SDIERKS2 (507432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SDIERKS2 507432 TO SDIERKS4 507433 TO SDRKS1-1 507446 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SEMINOL4__515045 | 3 Phase fault SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 515044 TO SEMINOL7 515045 TO SEMINO21 515757 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SETEXAR2__508078 | 3 Phase fault SETEXAR2 (508077) 69 kV Bus a. Apply fault at the SETEXAR2 (508077) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETEXAR2 508077 TO SETEXAR4 508078 TO SETEX1-1 508102 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SFOREMAN__4__504030 | 3 Phase fault SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4 (504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 504029 TO SFORE_1 2 504030 TO SFORE_T1 1 504031 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SKELTON7__515991 | 3 Phase fault SKELTON7 (515990) 345 kV Bus a. Apply fault at the SKELTON7 (515990) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SKELTON7 515990 TO SKELTL11 515991 TO SKELTT11 515992 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SO4TH__2__514731 | 3 Phase fault SO4TH 2 (514730) 69 kV Bus a. Apply fault at the SO4TH 2 (514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 514730 TO SO4TH 4 514731 TO SO4TH 1 515758 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SOONER_4__514803 | 3 Phase fault SOONER 4 (514802) 138 kV Bus a. Apply fault at the SOONER 4 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 4 514802 TO SOONER 7 514803 TO SOONER 1 515760 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SUGARHL2__508080 | 3 Phase fault SUGARHL2 (508079) 69 kV Bus a. Apply fault at the SUGARHL2 (508079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGARHL2 508079 TO SUGARHL4 508080 TO SHILL1-1 508103 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SUNNYSD4__515136 | 3 Phase fault SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SUNNYSD7__515135 | 3 Phase fault SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SW_5TH_2__514920 | 3 Phase fault SW 5TH 2 (514919) 69 kV Bus a. Apply fault at the SW 5TH 2 (514919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW 5TH 2 514919 TO SW 5TH 4 514920 TO SW 5TH 1 515763 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SW_SHV_7__507759 | 3 Phase fault SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV1-1 507778 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_S_SHV__2__507755 | 3 Phase fault S SHV 2 (507754) 69 kV Bus a. Apply fault at the S SHV 2 (507754) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 2 507754 TO S SHV 4 507755 TO SSHV2-1 507776 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_T.NO.2_XFMR | 3 Phase fault T.NO.2-4 (509895) 138 kV Bus a. Apply fault at the T.NO.2-4 (509895) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.2-4 509895 TO T.NO.--7 509852 TO TNO2-1 509894 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_T.P.S._XFMR | 3 Phase fault T.P.S.-2 (509789) 69 kV Bus a. Apply fault at the T.P.S.-2 (509789) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-2 509789 TO T.P.S.-4 509788 TO TPS5-1 509880 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_T.S.E._XFMR | 3 Phase fault T.S.E.-2 (509820) 69 kV Bus a. Apply fault at the T.S.E.-2 (509820) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.S.E.-2 509820 TO T.S.E.-4 509811 TO TSE3-1 509873 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TAHLQH_5__512647 | 3 Phase fault TAHLQH 5 (512655) 161 kV Bus a. Apply fault at the TAHLQH 5 (512655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 512655 TO TAHLQH 2 512647 TO TAHLQH1 512851 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TALOGA_4__521064 | 3 Phase fault TALOGA 4 (521065) 138 kV Bus a. Apply fault at the TALOGA 4 (521065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALOGA 4 521065 TO TALOGA 2 521064 TO TLGTERT 521178 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_THISTLE7__539804 | 3 Phase fault THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 539801 TO THISTLE4 539804 TO THISTLE T1 539802 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TUCO_INT___6__525828 | 3 Phase fault TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 525830 TO TUCO_INT 3 525828 TO TUCO_TR4 1 525821 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TUCO_INT___7__525830 | 3 Phase fault TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 525832 TO TUCO_INT 6 525830 TO TUCO_TR2 1 525825 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TURK___3__507454 | 3 Phase fault TURK 3 (507456) 115 kV Bus a. Apply fault at the TURK 3 (507456) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 3 507456 TO TURK 4 507454 TO TURK1 1 507458 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_TURK___4__507455 | 3 Phase fault TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 4 507454 TO TURK 7 507455 TO TURK 1 507457 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_VALIANT2__510918 | 3 Phase fault VALIANT2 (510910) 69 kV Bus a. Apply fault at the VALIANT2 (510910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT2 510910 TO VALIANT4 510918 TO VALN1-1 510937 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_VALIANT4__510911 | 3 Phase fault VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 510918 TO VALIANT7 510911 TO VALN3-1 510939 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_VINTAJC2__510417 | 3 Phase fault VINTAJC2 (510418) 69 kV Bus a. Apply fault at the VINTAJC2 (510418) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC2 510418 TO VINTAJC4 510417 TO VINJT1-1 510367 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WAGNOR_5__512697 | 3 Phase fault WAGNOR 5 (512700) 161 kV Bus a. Apply fault at the WAGNOR 5 (512700) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAGNOR 5 512700 TO WAGNOR 2 512697 TO WAGNOR1 512818 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WASHITA4__521088 | 3 Phase fault WASHITA4 (521089) 138 kV Bus a. Apply fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 521089 TO WASHITA2 521088 TO WASHTERT 521179 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WATLANT2__508090 | 3 Phase fault WATLANT2 (508089) 69 kV Bus a. Apply fault at the WATLANT2 (508089) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT2 508089 TO WATLANT4 508090 TO WATL2-1 508046 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WEKIWA_XFMR | 3 Phase fault WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 509757 TO WEKIWA-7 509755 TO WEKIW1-1 509879 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WHEELER____6__523776 | 3 Phase fault WHEELER 6 (523777) 230 kV Bus a. Apply fault at the WHEELER 6 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 523777 TO WHEELER 3 523776 TO WHEELER_TR11 523774 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WHITNEY2__508575 | 3 Phase fault WHITNEY2 (508574) 69 kV Bus a. Apply fault at the WHITNEY2 (508574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY2 508574 TO WHITNEY4 508575 TO WHIT2-1 508590 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WILKES_4__508841 | 3 Phase fault WILKES 4 (508840) 138 kV Bus a. Apply fault at the WILKES 4 (508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 508840 TO WILKES 7 508841 TO WILKES-1 508826 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WOODRNG4__514715 | 3 Phase fault WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 514714 TO WOODRNG7 514715 TO WOODRNG1 515770 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WOODWRD4__514782 | 3 Phase fault WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 514785 TO WODWRD 2 514782 TO WOODWR21 515771 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WWRDEHV4__515375 | 3 Phase fault WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_YOAKUM_345__526935 | 3 Phase fault YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 526936 TO YOAKUM 6 526935 TO YOAKUM_TR1 526937 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_112GORE4__LAIRGST4 | 3 Phase fault 112GORE4 (511488) 138 kV Bus a. Apply fault at the 112GORE4 (511488) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 138 KV 511488 TO LAIRGST4 138 KV 511510 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_112GORE4__RPPAPER4 | 3 Phase fault 112GORE4 (511488) 138 kV Bus a. Apply fault at the 112GORE4 (511488) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 138 KV 511488 TO RPPAPER4 138 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_2CARNEY__2LUTHER | 3 Phase fault 2CARNEY (300834) 69 kV Bus a. Apply fault at the 2CARNEY (300834) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CARNEY 69 KV 300834 TO 2LUTHER 69 KV 300856 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_2COLINS__COLNSGR2 | 3 Phase fault 2COLINS (300992) 69 kV Bus a. Apply fault at the 2COLINS (300992) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2COLINS 69 KV 300992 TO COLNSGR2 69 KV 512870 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_2MERIDAN__2LUTHER | 3 Phase fault 2MERIDAN (300839) 69 kV Bus a. Apply fault at the 2MERIDAN (300839) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MERIDAN 69 KV 300839 TO 2LUTHER 69 KV 300856 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_2OWASSO__COLNSGR2 | 3 Phase fault 2OWASSO (300998) 69 kV Bus a. Apply fault at the 2OWASSO (300998) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2OWASSO 69 KV 300998 TO COLNSGR2 69 KV 512870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_2OWASSO__DAWSON | 3 Phase fault 2OWASSO (300998) 69 kV Bus a. Apply fault at the 2OWASSO (300998) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2OWASSO 69 KV 300998 TO DAWSON-2 69 KV 509791 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_2VERA__COLNSGR2 | 3 Phase fault 2VERA (301006) 69 kV Bus a. Apply fault at the 2VERA (301006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2VERA 69 KV 301006 TO COLNSGR2 69 KV 512870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_36&MER_4__HOBBYLO4 | 3 Phase fault 36&MER 4 (514888) 138 kV Bus a. Apply fault at the 36&MER 4 (514888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 36&MER 4 138 KV 514888 TO HOBBYLO4 138 KV 515338 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_36&MER_4__SW_5TH_4 | 3 Phase fault 36&MER 4 (514888) 138 kV Bus a. Apply fault at the 36&MER 4 (514888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 36&MER 4 138 KV 514888 TO SW 5TH 4 138 KV 514920 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_38TH_ST2__BETHANY2 | 3 Phase fault 38TH ST2 (514845) 69 kV Bus a. Apply fault at the 38TH ST2 (514845) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 38TH ST2 69 KV 514845 TO BETHANY2 69 KV 514914 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_38TH_ST4__HEFNER_4 | 3 Phase fault 38TH ST4 (514846) 138 kV Bus a. Apply fault at the 38TH ST4 (514846) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TULSA 4 138 KV 514847 TO HEFNER 4 138 KV 514848 CKT 1 b.2. 38TH ST4 138 KV 514846 TO TULSA 4 138 KV 514847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_38TH_ST4__TULSA__4 | 3 Phase fault 38TH ST4 (514846) 138 kV Bus a. Apply fault at the 38TH ST4 (514846) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 38TH ST4 138 KV 514846 TO TULSA 4 138 KV 514847 CKT 1 b.2. LOAD 1 514847 b.3. TULSA 4 138 KV 514847 TO HEFNER 4 138 KV 514848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_3ADA_LA__3MINDEN_LA! | 3 Phase fault 3ADA_LA (337360) 115 kV Bus a. Apply fault at the 3ADA_LA (337360) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3ADA_LA 115 KV 337360 TO 3MINDEN_LA! 115 KV 337361 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_3EL_DORADO!__3ELDORADO.E! | 3 Phase fault 3EL DORADO! (337539) 115 kV Bus a. Apply fault at the 3EL DORADO! (337539) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3EL DORADO! 115 KV 337539 TO 3ELDORADO.E! 115 KV 337553 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_3EL_DORADO!__3ELD_DONAN | 3 Phase fault 3EL DORADO! (337539) 115 kV Bus a. Apply fault at the 3EL DORADO! (337539) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3EL DORADO! 115 KV 337539 TO 3ELD DONAN 115 KV 337540 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_3EL_DORADO!__3ELD_QUINN | 3 Phase fault 3EL DORADO! (337539) 115 kV Bus a. Apply fault at the 3EL DORADO! (337539) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3EL DORADO! 115 KV 337539 TO 3ELD QUINN 115 KV 337560 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_3KERLIN+__3EMERSON! | 3 Phase fault 3KERLIN+ (337524) 115 kV Bus a. Apply fault at the 3KERLIN+ (337524) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3KERLIN+ 115 KV 337524 TO 3EMERSON! 115 KV 337526 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_3MINDEN_LA!__3LA_ORD_PLNT | 3 Phase fault 3MINDEN_LA! (337361) 115 kV Bus a. Apply fault at the 3MINDEN_LA! (337361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MINDEN_LA! 115 KV 337361 TO 3LA_ORD_PLNT 115 KV 337362 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_3MINDEN_LA!__3SAREPTA! | 3 Phase fault 3MINDEN_LA! (337361) 115 kV Bus a. Apply fault at the 3MINDEN_LA! (337361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MINDEN_LA! 115 KV 337361 TO 3SAREPTA! 115 KV 337363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_3MINDEN_LA!__MINDEN | 3 Phase fault 3MINDEN_LA! (337361) 115 kV Bus a. Apply fault at the 3MINDEN_LA! (337361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MINDEN_LA! 115 KV 337361 TO MINDEN-3 115 KV 507788 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_3MINDEN_LG__3MINDEN_LA! | 3 Phase fault 3MINDEN_LG (303302) 115 kV Bus a. Apply fault at the 3MINDEN_LG (303302) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MINDEN_LG 115 KV 303302 TO 3MINDEN_LA! 115 KV 337361 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_3SAREPTA!__3CULLEN | 3 Phase fault 3SAREPTA! (337363) 115 kV Bus a. Apply fault at the 3SAREPTA! (337363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115 KV 337363 TO 3CULLEN 115 KV 337364 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_3SAREPTA!__3EMERSON! | 3 Phase fault 3SAREPTA! (337363) 115 kV Bus a. Apply fault at the 3SAREPTA! (337363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115 KV 337363 TO 3HAYNESVILLE 115 KV 337366 CKT 1 b.2. LOAD 1 337366 b.3. LOAD LG 337366 b.4. 3HAYNESVILLE 115 KV 337366 TO 3EMERSON! 115 KV 337526 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_3SAREPTA!__3SPRINGHILL | 3 Phase fault 3SAREPTA! (337363) 115 kV Bus a. Apply fault at the 3SAREPTA! (337363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115 KV 337363 TO 3SPRINGHILL 115 KV 337365 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_3SMACKOVER+__3EL_DORADO! | 3 Phase fault 3SMACKOVER+ (337537) 115 kV Bus a. Apply fault at the 3SMACKOVER+ (337537) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SMACKOVER+ 115 KV 337537 TO 3EL DORADO! 115 KV 337539 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_3SPRINGHILL__3TAYLOR | 3 Phase fault 3SPRINGHILL (337365) 115 kV Bus a. Apply fault at the 3SPRINGHILL (337365) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SPRINGHILL 115 KV 337365 TO 3TAYLOR 115 KV 337500 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_44&SUNL2__ELMCRK_2 | 3 Phase fault 44&SUNL2 (514979) 69 kV Bus a. Apply fault at the 44&SUNL2 (514979) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 44&SUNL2 69 KV 514979 TO ELMCRK 2 69 KV 514982 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_44&SUNL2__SUNNYLN2 | 3 Phase fault 44&SUNL2 (514979) 69 kV Bus a. Apply fault at the 44&SUNL2 (514979) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 44&SUNL2 69 KV 514979 TO SUNNYLN2 69 KV 514980 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_46ST | 3 Phase fault 46ST--E4 (509837) 138 kV Bus a. Apply fault at the 46ST--E4 (509837) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 46ST--E4 138 KV 509837 TO 46ST-TP-4 138 KV 509900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_4BRISTOW__4SILVCTY | 3 Phase fault 4BRISTOW (300137) 138 kV Bus a. Apply fault at the 4BRISTOW (300137) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4BRISTOW 138 KV 300137 TO 4SILVCTY 138 KV 300140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_4CLEVLND__4SFORKKTP | 3 Phase fault 4CLEVLND (300138) 138 kV Bus a. Apply fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138 KV 300138 TO 4JAVINE 138 KV 300996 CKT 1 b.2. LOAD 1 300996 b.3. LOAD 2 300996 b.4. 4JAVINE 138 KV 300996 TO 4SFORKKTP 138 KV 301339 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_4CLEVLND__4SILVCTY | 3 Phase fault 4CLEVLND (300138) 138 kV Bus a. Apply fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138 KV 300138 TO 4SILVCTY 138 KV 300140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_4CLEVLND__CLEVLND_4 | 3 Phase fault 4CLEVLND (300138) 138 kV Bus a. Apply fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138 KV 300138 TO CLEVLND 4 138 KV 512729 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_4CLEVLND__PAWNSW4 | 3 Phase fault 4CLEVLND (300138) 138 kV Bus a. Apply fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND 138 KV 300138 TO PAWNSW4 138 KV 512749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_4FAIRFAX__PAWNSW4 | 3 Phase fault 4FAIRFAX (300139) 138 kV Bus a. Apply fault at the 4FAIRFAX (300139) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FAIRFAX 138 KV 300139 TO PAWNSW4 138 KV 512749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_4FISHERTP__4SILVCTY | 3 Phase fault 4FISHERTP (300131) 138 kV Bus a. Apply fault at the 4FISHERTP (300131) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FISHERTP 138 KV 300131 TO 4SILVCTY 138 KV 300140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_4LUTHER__4MEMORALT | 3 Phase fault 4LUTHER (300135) 138 kV Bus a. Apply fault at the 4LUTHER (300135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4LUTHER 138 KV 300135 TO 4MEMORALT 138 KV 300136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_4LUTHER__4STROUD138 | 3 Phase fault 4LUTHER (300135) 138 kV Bus a. Apply fault at the 4LUTHER (300135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4LUTHER 138 KV 300135 TO 4LUTHERD 138 KV 301372 CKT 1 b.2. LOAD 1 301372 b.3. 4WARWICK 138 KV 300915 TO 4LUTHERD 138 KV 301372 CKT 1 b.4. LOAD 1 301372 b.5. 4STROUD138 138 KV 300914 TO 4WARWICK 138 KV 300915 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_4MEMORALT__4MEMORAL | 3 Phase fault 4MEMORALT (300136) 138 kV Bus a. Apply fault at the 4MEMORALT (300136) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MEMORALT 138 KV 300136 TO 4MEMORAL 138 KV 301541 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_4MEMORALT__JNSKAMO4 | 3 Phase fault 4MEMORALT (300136) 138 kV Bus a. Apply fault at the 4MEMORALT (300136) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MEMORALT 138 KV 300136 TO JNSKAMO4 138 KV 514906 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_4MURFBORO__SNASHVL4 | 3 Phase fault 4MURFBORO (337672) 138 kV Bus a. Apply fault at the 4MURFBORO (337672) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MURFBORO 138 KV 337672 TO SNASHVL4 138 KV 507434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_4SFORKK__4SFORKKTP | 3 Phase fault 4SFORKK (300165) 138 kV Bus a. Apply fault at the 4SFORKK (300165) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SFORKK 138 KV 300165 TO 4SFORKKTP 138 KV 301339 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_4SILVCTY__4STILWTR | 3 Phase fault 4SILVCTY (300140) 138 kV Bus a. Apply fault at the 4SILVCTY (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY 138 KV 300140 TO 4STILWTR 138 KV 300141 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_4SILVCTY__SILVCTYGR4 | 3 Phase fault 4SILVCTY (300140) 138 kV Bus a. Apply fault at the 4SILVCTY (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY 138 KV 300140 TO SILVCTYGR4 138 KV 512726 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_4SKIAETP__4SFORKKTP | 3 Phase fault 4SKIAETP (300146) 138 kV Bus a. Apply fault at the 4SKIAETP (300146) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SKIAETP 138 KV 300146 TO 4SFORKKTP 138 KV 301339 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_4SKIAETP__COLLINS4 | 3 Phase fault 4SKIAETP (300146) 138 kV Bus a. Apply fault at the 4SKIAETP (300146) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SKIAETP 138 KV 300146 TO COLLINS4 138 KV 512705 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_4STROUDDIST__4STROUD138 | 3 Phase fault 4STROUDDIST (300838) 138 kV Bus a. Apply fault at the 4STROUDDIST (300838) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STROUDDIST 138 KV 300838 TO 4STROUD138 138 KV 300914 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_52DEL | 3 Phase fault 52DEL-W4 (509856) 138 kV Bus a. Apply fault at the 52DEL-W4 (509856) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 52DEL-W4 138 KV 509856 TO S HILLW4 138 KV 509859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_52DELTP4__T.P.S. | 3 Phase fault 52DELTP4 (509776) 138 kV Bus a. Apply fault at the 52DELTP4 (509776) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 52DELTP4 138 KV 509776 TO 36LEWIS4 138 KV 509800 CKT 1 b.2. LOAD 1 509800 b.3. T.P.S.-4 138 KV 509788 TO 36LEWIS4 138 KV 509800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_52DELTP4__T.S.E. | 3 Phase fault 52DELTP4 (509776) 138 kV Bus a. Apply fault at the 52DELTP4 (509776) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 52DELTP4 138 KV 509776 TO T.S.E.-4 138 KV 509811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_52DELTP4__ZUNIS | 3 Phase fault 52DELTP4 (509776) 138 kV Bus a. Apply fault at the 52DELTP4 (509776) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 52DELTP4 138 KV 509776 TO ZUNIS-S4 138 KV 509826 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_52DELWT4__S_HILLW4 | 3 Phase fault 52DELWT4 (509814) 138 kV Bus a. Apply fault at the 52DELWT4 (509814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 52DELWT4 138 KV 509814 TO S HILLW4 138 KV 509859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_53CACHE4__ARTVLTP4 | 3 Phase fault 53CACHE4 (511509) 138 kV Bus a. Apply fault at the 53CACHE4 (511509) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53CACHE4 138 KV 511509 TO ARTVLTP4 138 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_53GARNT4__77MEMTP4 | 3 Phase fault 53GARNT4 (509762) 138 kV Bus a. Apply fault at the 53GARNT4 (509762) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARNT4 138 KV 509762 TO 77MEMTP4 138 KV 509765 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_53GARNT4__T.S.E. | 3 Phase fault 53GARNT4 (509762) 138 kV Bus a. Apply fault at the 53GARNT4 (509762) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARNT4 138 KV 509762 TO T.S.E.-4 138 KV 509811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_53GARN_4__53GARNT4 | 3 Phase fault 53GARN 4 (509734) 138 kV Bus a. Apply fault at the 53GARN 4 (509734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARN 4 138 KV 509734 TO 53GARNT4 138 KV 509762 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_53GARST4__53GARNS4 | 3 Phase fault 53GARST4 (509763) 138 kV Bus a. Apply fault at the 53GARST4 (509763) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARST4 138 KV 509763 TO 53GARNS4 138 KV 509774 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_53GARST4__FORD | 3 Phase fault 53GARST4 (509763) 138 kV Bus a. Apply fault at the 53GARST4 (509763) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARST4 138 KV 509763 TO FORD---4 138 KV 509772 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_53GARST4__T.S.E. | 3 Phase fault 53GARST4 (509763) 138 kV Bus a. Apply fault at the 53GARST4 (509763) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARST4 138 KV 509763 TO T.S.E.-4 138 KV 509811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_5CDRCRST__TAHLQH_5 | 3 Phase fault 5CDRCRST (301344) 161 kV Bus a. Apply fault at the 5CDRCRST (301344) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CDRCRST 161 KV 301344 TO TAHLQH 5 161 KV 512655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_5CHOTEAU1__5CHOTEAU2 | 3 Phase fault 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 161 KV 300069 TO 5CHOTEAU2 161 KV 301348 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_5CHOTEAU1__MAID___5 | 3 Phase fault 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 161 KV 300069 TO MAID 5 161 KV 512648 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_5ELMCRK__CATSAGR5 | 3 Phase fault 5ELMCRK (300993) 161 kV Bus a. Apply fault at the 5ELMCRK (300993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ELMCRK 161 KV 300993 TO CATSAGR5 161 KV 512638 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_5PARK__TAHLQH_5 | 3 Phase fault 5PARK (301307) 161 kV Bus a. Apply fault at the 5PARK (301307) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PARK 161 KV 301307 TO TAHLQH 5 161 KV 512655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_5TRIBES2__AGENCY_2 | 3 Phase fault 5TRIBES2 (515227) 69 kV Bus a. Apply fault at the 5TRIBES2 (515227) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TENYSON2 69 KV 515217 TO 5TRIBES2 69 KV 515227 CKT 1 b.2. HONORHT2 69 KV 515216 TO TENYSON2 69 KV 515217 CKT 1 b.3. LOAD 1 515217 b.4. HONORHT2 69 KV 515216 TO AGENCY 2 69 KV 515229 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_5TRIBES2__WELLSPA2 | 3 Phase fault 5TRIBES2 (515227) 69 kV Bus a. Apply fault at the 5TRIBES2 (515227) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHECOTA2 69 KV 515201 TO WELLS 2 69 KV 515202 CKT 1 b.2. LOAD 1 515202 b.3. CHECOTA2 69 KV 515201 TO 5TRIBES2 69 KV 515227 CKT 1 b.4. WELLS 2 69 KV 515202 TO WELLSPA2 69 KV 515215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_5TRIBES5__MUSKOGE5 | 3 Phase fault 5TRIBES5 (515228) 161 kV Bus a. Apply fault at the 5TRIBES5 (515228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TRIBES5 161 KV 515228 TO HANCOK-5 161 KV 515250 CKT 1 b.2. LOAD 1 515250 b.3. HANCOK-5 161 KV 515250 TO THRERVR5 161 KV 515640 CKT 1 b.4. LOAD 1 515640 b.5. MUSKOGE5 161 KV 515222 TO THRERVR5 161 KV 515640 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_5TRIBES5__PECANCK5 | 3 Phase fault 5TRIBES5 (515228) 161 kV Bus a. Apply fault at the 5TRIBES5 (515228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TRIBES5 161 KV 515228 TO PECANCK5 161 KV 515234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_77MEM | 3 Phase fault 77MEM-E4 (509735) 138 kV Bus a. Apply fault at the 77MEM-E4 (509735) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 77MEM-E4 138 KV 509735 TO 77MEMTP4 138 KV 509765 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_77MEM | 3 Phase fault 77MEM-W4 (509766) 138 kV Bus a. Apply fault at the 77MEM-W4 (509766) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 77MEM-W4 138 KV 509766 TO E.61ST-4 138 KV 509831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_77MEMTP4__81GARN | 3 Phase fault 77MEMTP4 (509765) 138 kV Bus a. Apply fault at the 77MEMTP4 (509765) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 77MEMTP4 138 KV 509765 TO 81GARN-4 138 KV 509855 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_7BLACKBERRY__NEOSHO_7 | 3 Phase fault 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY 345 KV 300739 TO NEOSHO 7 345 KV 532793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_7SAREPTA%__7EL_DORADO | 3 Phase fault 7SAREPTA% (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345 KV 337376 TO 7EL DORADO 345 KV 337562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_7SAREPTA%__LONGWD_7 | 3 Phase fault 7SAREPTA% (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345 KV 337376 TO LONGWD 7 345 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_7SPORTSMAN__GRDA1__7 | 3 Phase fault 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN 345 KV 300740 TO GRDA1 7 345 KV 512650 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_81GARN | 3 Phase fault 81GARN-4 (509855) 138 kV Bus a. Apply fault at the 81GARN-4 (509855) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81GARN-4 138 KV 509855 TO E_121ST4 138 KV 509889 CKT 1 b.2. LOAD 1 509889 b.3. 121LYNN4 138 KV 509869 TO E_121ST4 138 KV 509889 CKT 1 b.4. LOAD 1 509889 b.5. ONETA--4 138 KV 509806 TO 121LYNN4 138 KV 509869 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_81YALEN4__81YALTP4 | 3 Phase fault 81YALEN4 (509730) 138 kV Bus a. Apply fault at the 81YALEN4 (509730) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81YALEN4 138 KV 509730 TO 81YALTP4 138 KV 509809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_81YALES4__WARNTAP4 | 3 Phase fault 81YALES4 (509810) 138 kV Bus a. Apply fault at the 81YALES4 (509810) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81YALES4 138 KV 509810 TO WARNTAP4 138 KV 509858 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_81YALTP4__SHILETP4 | 3 Phase fault 81YALTP4 (509809) 138 kV Bus a. Apply fault at the 81YALTP4 (509809) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81YALTP4 138 KV 509809 TO SHILETP4 138 KV 509813 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_8ANO%__8P.HILL% | 3 Phase fault 8ANO% (337909) 500 kV Bus a. Apply fault at the 8ANO% (337909) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500 KV 337909 TO 8P.HILL% 500 KV 337922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_8ANO%__FTSMITH8 | 3 Phase fault 8ANO% (337909) 500 kV Bus a. Apply fault at the 8ANO% (337909) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500 KV 337909 TO FTSMITH8 500 KV 515305 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_8EL_DORADO%__8PANDA% | 3 Phase fault 8EL DORADO% (337561) 500 kV Bus a. Apply fault at the 8EL DORADO% (337561) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 500 KV 337561 TO 8PANDA% 500 KV 338440 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_8EL_DORADO%__8SHERIDAN% | 3 Phase fault 8EL DORADO% (337561) 500 kV Bus a. Apply fault at the 8EL DORADO% (337561) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 500 KV 337561 TO 8SHERIDAN% 500 KV 337643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_8HAPPYVALY%__8ANO% | 3 Phase fault 8HAPPYVALY% (337811) 500 kV Bus a. Apply fault at the 8HAPPYVALY% (337811) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8HAPPYVALY% 500 KV 337811 TO 8ANO% 500 KV 337909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_8MCNEIL%__8EL_DORADO% | 3 Phase fault 8MCNEIL% (337515) 500 kV Bus a. Apply fault at the 8MCNEIL% (337515) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MCNEIL% 500 KV 337515 TO 8EL DORADO% 500 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_8MCNEIL%__8ETTA% | 3 Phase fault 8MCNEIL% (337515) 500 kV Bus a. Apply fault at the 8MCNEIL% (337515) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MCNEIL% 500 KV 337515 TO 8ETTA% 500 KV 337754 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_8MT_OLIVE%__8EL_DORADO% | 3 Phase fault 8MT_OLIVE% (337368) 500 kV Bus a. Apply fault at the 8MT_OLIVE% (337368) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MT_OLIVE% 500 KV 337368 TO 8EL DORADO% 500 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_8MT_OLIVE%__LAYFLD8 | 3 Phase fault 8MT_OLIVE% (337368) 500 kV Bus a. Apply fault at the 8MT_OLIVE% (337368) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MT_OLIVE% 500 KV 337368 TO LAYFLD8 500 KV 509366 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_8SHERIDAN%__8MABELVALE% | 3 Phase fault 8SHERIDAN% (337643) 500 kV Bus a. Apply fault at the 8SHERIDAN% (337643) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHERIDAN% 500 KV 337643 TO 8MABELVALE% 500 KV 337808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_8SHERIDAN%__8MAGNETCOVE% | 3 Phase fault 8SHERIDAN% (337643) 500 kV Bus a. Apply fault at the 8SHERIDAN% (337643) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHERIDAN% 500 KV 337643 TO 8MAGNETCOVE% 500 KV 337763 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_8SHERIDAN%__8WHT_BLUFF% | 3 Phase fault 8SHERIDAN% (337643) 500 kV Bus a. Apply fault at the 8SHERIDAN% (337643) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHERIDAN% 500 KV 337643 TO 8WHT BLUFF% 500 KV 337651 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_8STERLING%__8EL_DORADO% | 3 Phase fault 8STERLING% (337420) 500 kV Bus a. Apply fault at the 8STERLING% (337420) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8STERLING% 500 KV 337420 TO 8EL DORADO% 500 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_8STERLING%__8PERRYVILLE% | 3 Phase fault 8STERLING% (337420) 500 kV Bus a. Apply fault at the 8STERLING% (337420) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8STERLING% 500 KV 337420 TO 8PERRYVILLE% 500 KV 337427 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_8STERLING2%__8STERLING% | 3 Phase fault 8STERLING2% (337413) 500 kV Bus a. Apply fault at the 8STERLING2% (337413) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8STERLING2% 500 KV 337413 TO 8STERLING% 500 KV 337420 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_A.A. | 3 Phase fault A.A.---4 (509784) 138 kV Bus a. Apply fault at the A.A.---4 (509784) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. A.A.---4 138 KV 509784 TO CDC-WT 4 138 KV 509842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_A.A. | 3 Phase fault A.A.---4 (509784) 138 kV Bus a. Apply fault at the A.A.---4 (509784) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. A.A.---4 138 KV 509784 TO MINGORD4 138 KV 509802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_A.A. | 3 Phase fault A.A.---4 (509784) 138 kV Bus a. Apply fault at the A.A.---4 (509784) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOHAWK 4 138 KV 509801 TO PPTAP 4 138 KV 509863 CKT 1 b.2. A.A.---4 138 KV 509784 TO MOHAWK 4 138 KV 509801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_AGENCY_2__JAMESVL2 | 3 Phase fault AGENCY 2 (515229) 69 kV Bus a. Apply fault at the AGENCY 2 (515229) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AGENCY 2 69 KV 515229 TO JAMESVL2 69 KV 515240 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_AGENCY_5__EUCLID_5 | 3 Phase fault AGENCY 5 (515230) 161 kV Bus a. Apply fault at the AGENCY 5 (515230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AGENCY 5 161 KV 515230 TO EUCLID 5 161 KV 515251 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_AGENCY_5__PECANCK5 | 3 Phase fault AGENCY 5 (515230) 161 kV Bus a. Apply fault at the AGENCY 5 (515230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AGENCY 5 161 KV 515230 TO PECANCK5 161 KV 515234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ALWUETP4__ALLUWE_4 | 3 Phase fault ALWUETP4 (510429) 138 kV Bus a. Apply fault at the ALWUETP4 (510429) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALWUETP4 138 KV 510429 TO ALLUWE 4 138 KV 510430 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ANADARK2__CADDO__2 | 3 Phase fault ANADARK2 (520810) 69 kV Bus a. Apply fault at the ANADARK2 (520810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK2 69 KV 520810 TO CADDO 2 69 KV 520838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ANADARK4__CHERRYRD_4 | 3 Phase fault ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138 KV 520814 TO CHERRYRD 4 138 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ANADARK4__FLETCH | 3 Phase fault ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138 KV 520814 TO GEORGIA4 138 KV 520923 CKT 1 b.2. LOAD 1 520923 b.3. FLETCH-4 138 KV 520912 TO GEORGIA4 138 KV 520923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ANADARK4__TUTLETP4 | 3 Phase fault ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138 KV 520814 TO POCASET4 138 KV 521031 CKT 1 b.2. LOAD 1 521031 b.3. POCASET4 138 KV 521031 TO TUTLETP4 138 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ANDRCKT2__MAUDT__2 | 3 Phase fault ANDRCKT2 (509658) 69 kV Bus a. Apply fault at the ANDRCKT2 (509658) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUDT 2 69 KV 509653 TO MAUD 2 69 KV 509657 CKT 1 b.2. LOAD 1 509657 b.3. MAUD 2 69 KV 509657 TO ANDRCKT2 69 KV 509658 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ANDRCKT2__SPRNGHL2 | 3 Phase fault ANDRCKT2 (509658) 69 kV Bus a. Apply fault at the ANDRCKT2 (509658) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDRCKT2 69 KV 509658 TO SIMMS 2 69 KV 509659 CKT 1 b.2. LOAD 1 509659 b.3. SIMMS 2 69 KV 509659 TO SDEKALB2 69 KV 509660 CKT 1 b.4. LOAD 1 509660 b.5. SDEKALB2 69 KV 509660 TO WDEKALB2 69 KV 509661 CKT 1 b.6. LOAD 1 509661 b.7. WDEKALB2 69 KV 509661 TO SPRNGHL2 69 KV 509662 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ANDRSNC4__MUNZCTY4 | 3 Phase fault ANDRSNC4 (508050) 138 kV Bus a. Apply fault at the ANDRSNC4 (508050) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDRSNC4 138 KV 508050 TO BRYANML4 138 KV 508056 CKT 1 b.2. LOAD 1 508056 b.3. BRYANML4 138 KV 508056 TO MUNZCTY4 138 KV 508064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ARAPAHO2__HM | 3 Phase fault ARAPAHO2 (520815) 69 kV Bus a. Apply fault at the ARAPAHO2 (520815) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARAPAHO2 69 KV 520815 TO HM-BTTP2 69 KV 520942 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ARBUCKL4__VANOSTP4 | 3 Phase fault ARBUCKL4 (515117) 138 kV Bus a. Apply fault at the ARBUCKL4 (515117) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARBUCKL4 138 KV 515117 TO VANOSTP4 138 KV 515531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ARCADIA4__DANFRTH4 | 3 Phase fault ARCADIA4 (514907) 138 kV Bus a. Apply fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 138 KV 514907 TO RNDBARN4 138 KV 515461 CKT 1 b.2. LOAD 1 515461 b.3. BURGETT4 138 KV 514510 TO RNDBARN4 138 KV 515461 CKT 1 b.4. LOAD 1 515461 b.5. BURGETT4 138 KV 514510 TO DANFRTH4 138 KV 514833 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ARCADIA4__LGARBER4 | 3 Phase fault ARCADIA4 (514907) 138 kV Bus a. Apply fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 138 KV 514907 TO LGARBER4 138 KV 515465 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ARCADIA7__GEN | 3 Phase fault ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345 KV 514908 TO GEN-2017-133 345 KV 760032 CKT 4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ARCADIA7__REDBUD_7 | 3 Phase fault ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345 KV 514908 TO REDBUD 7 345 KV 514909 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ARCADIA7__SEMINOL7 | 3 Phase fault ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345 KV 514908 TO SEMINOL7 345 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ARSHILL4__FTHUMBG4 | 3 Phase fault ARSHILL4 (507711) 138 kV Bus a. Apply fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138 KV 507711 TO FTHUMBG4 138 KV 507731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ARSHILL4__LIEBERM4 | 3 Phase fault ARSHILL4 (507711) 138 kV Bus a. Apply fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138 KV 507711 TO LIEBERM4 138 KV 508806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ARSHILL4__MCWILLI4 | 3 Phase fault ARSHILL4 (507711) 138 kV Bus a. Apply fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138 KV 507711 TO MCWILLI4 138 KV 507742 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ARSHILL4__RAINES_4 | 3 Phase fault ARSHILL4 (507711) 138 kV Bus a. Apply fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138 KV 507711 TO RAINES 4 138 KV 507749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ARSHILL4__STLGENS4 | 3 Phase fault ARSHILL4 (507711) 138 kV Bus a. Apply fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138 KV 507711 TO STLGENS4 138 KV 507789 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ARTVLTP4__ARTVILL4 | 3 Phase fault ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTVLTP4 138 KV 511537 TO ARTVILL4 138 KV 511538 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ASPEN__4__MOORLND4 | 3 Phase fault ASPEN 4 (520462) 138 kV Bus a. Apply fault at the ASPEN 4 (520462) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASPEN 4 138 KV 520462 TO MOORLND4 138 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_B.BOWTP4__CRAIGJT4 | 3 Phase fault B.BOWTP4 (510888) 138 kV Bus a. Apply fault at the B.BOWTP4 (510888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B.BOWTP4 138 KV 510888 TO CRAIGJT4 138 KV 510890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_B.BOW__4__B.BOWTP4 | 3 Phase fault B.BOW 4 (510864) 138 kV Bus a. Apply fault at the B.BOW 4 (510864) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B.BOW 4 138 KV 510864 TO B.BOWTP4 138 KV 510888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_B111 | 3 Phase fault B111---4 (509767) 138 kV Bus a. Apply fault at the B111---4 (509767) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B111---4 138 KV 509767 TO BA101ST4 138 KV 509768 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BA.N | 3 Phase fault BA.N-ST4 (509786) 138 kV Bus a. Apply fault at the BA.N-ST4 (509786) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.N-ST4 138 KV 509786 TO LLANETP4 138 KV 509804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BA.N | 3 Phase fault BA.N-ST4 (509786) 138 kV Bus a. Apply fault at the BA.N-ST4 (509786) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.N-ST4 138 KV 509786 TO ONETA--4 138 KV 509806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BA.NO | 3 Phase fault BA.NO-S4 (509721) 138 kV Bus a. Apply fault at the BA.NO-S4 (509721) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.NO-S4 138 KV 509721 TO BA.N-ST4 138 KV 509786 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BA101ST4__ONETA | 3 Phase fault BA101ST4 (509768) 138 kV Bus a. Apply fault at the BA101ST4 (509768) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101ST4 138 KV 509768 TO ONETA--4 138 KV 509806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BA101_S4__BA101ST4 | 3 Phase fault BA101 S4 (509737) 138 kV Bus a. Apply fault at the BA101 S4 (509737) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101 S4 138 KV 509737 TO BA101ST4 138 KV 509768 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BA81 | 3 Phase fault BA81---4 (509747) 138 kV Bus a. Apply fault at the BA81---4 (509747) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA81---4 138 KV 509747 TO BA101-N4 138 KV 509769 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BA81 | 3 Phase fault BA81---4 (509747) 138 kV Bus a. Apply fault at the BA81---4 (509747) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA81---4 138 KV 509747 TO FORD---4 138 KV 509772 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BADGER_7__BLUWND_7 | 3 Phase fault BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345 KV 515677 TO BLUWND 7 345 KV 515686 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BADGER_7__G16 | 3 Phase fault BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345 KV 515677 TO G16-003-TAP 345 KV 560071 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BADGER_7__GEN | 3 Phase fault BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345 KV 515677 TO GEN-2015-082 345 KV 585190 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BANNTAP4__E41ST_E4 | 3 Phase fault BANNTAP4 (509785) 138 kV Bus a. Apply fault at the BANNTAP4 (509785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANNTAP4 138 KV 509785 TO E41ST_E4 138 KV 509861 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BANN___2__LSORDTP2 | 3 Phase fault BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69 KV 508053 TO LSORDTP2 69 KV 508063 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BANN___2__SUGHLWT2 | 3 Phase fault BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69 KV 508053 TO REDLICK2 69 KV 508073 CKT 1 b.2. LOAD 1 508073 b.3. REDLICK2 69 KV 508073 TO RICHMND2 69 KV 508076 CKT 1 b.4. LOAD 1 508076 b.5. NW_TEXAR 2 69 KV 504109 TO RICHMND2 69 KV 508076 CKT 1 b.6. LOAD 1 508076 b.7. NW_TEXAR 2 69 KV 504109 TO SUGHLWT2 69 KV 508082 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BANN___2__TAYLOR_2 | 3 Phase fault BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69 KV 508053 TO KINGHWY2 69 KV 508061 CKT 1 b.2. LOAD 1 508061 b.3. KINGHWY2 69 KV 508061 TO TEXOPER2 69 KV 508087 CKT 1 b.4. LOAD 1 508087 b.5. TAYLOR 2 69 KV 508083 TO TEXOPER2 69 KV 508087 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BANN___4__NWT | 3 Phase fault BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138 KV 508054 TO NWT-BNT4 138 KV 508070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BANN___4__REDSPRG4 | 3 Phase fault BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138 KV 508054 TO REDSPRG4 138 KV 508075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BANN___4__SETEXAR4 | 3 Phase fault BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138 KV 508054 TO SETEXAR4 138 KV 508078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BARITE | 3 Phase fault BARITE-RD 4 (504379) 138 kV Bus a. Apply fault at the BARITE-RD 4 (504379) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARITE-RD 4 138 KV 504379 TO BARITERDTP 4 138 KV 507463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BARNSAL4__MOUNDRD4 | 3 Phase fault BARNSAL4 (510388) 138 kV Bus a. Apply fault at the BARNSAL4 (510388) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARNSAL4 138 KV 510388 TO BARNPMP4 138 KV 510433 CKT 1 b.2. LOAD 1 510433 b.3. MOUNDRD4 138 KV 510395 TO BARNPMP4 138 KV 510433 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BAWATAP2__COWETAP2 | 3 Phase fault BAWATAP2 (509718) 69 kV Bus a. Apply fault at the BAWATAP2 (509718) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAWATAP2 69 KV 509718 TO COWETAP2 69 KV 509781 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BAWATAP2__T.S.E. | 3 Phase fault BAWATAP2 (509718) 69 kV Bus a. Apply fault at the BAWATAP2 (509718) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAWATAP2 69 KV 509718 TO T.S.E.-2 69 KV 509820 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BAWATER2__BAWATAP2 | 3 Phase fault BAWATER2 (509717) 69 kV Bus a. Apply fault at the BAWATER2 (509717) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAWATER2 69 KV 509717 TO BAWATAP2 69 KV 509718 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BCVI_HVB__SLKHILLS_4 | 3 Phase fault BCVI_HVB (520514) 138 kV Bus a. Apply fault at the BCVI_HVB (520514) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BCVI_HVB 138 KV 520514 TO SLKHILLS 4 138 KV 521103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BCV_SW_4__CHERRYRD_4 | 3 Phase fault BCV SW 4 (520513) 138 kV Bus a. Apply fault at the BCV SW 4 (520513) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BCV SW 4 138 KV 520513 TO CHERRYRD 4 138 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BC_SW__4__SLKHILLS_4 | 3 Phase fault BC SW 4 (520512) 138 kV Bus a. Apply fault at the BC SW 4 (520512) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BC SW 4 138 KV 520512 TO SLKHILLS 4 138 KV 521103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BEELINE4__BLUEBEL4 | 3 Phase fault BEELINE4 (515247) 138 kV Bus a. Apply fault at the BEELINE4 (515247) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONESTR4 138 KV 515245 TO BEELINE4 138 KV 515247 CKT 1 b.2. LOAD 1 515247 b.3. KELLYVL4 138 KV 515200 TO LONESTR4 138 KV 515245 CKT 1 b.4. LOAD 1 515245 b.5. KELLYVL4 138 KV 515200 TO BLUEBEL4 138 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BEELINE4__EXPGLNT4 | 3 Phase fault BEELINE4 (515247) 138 kV Bus a. Apply fault at the BEELINE4 (515247) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEELINE4 138 KV 515247 TO EXPGLNT4 138 KV 515473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BEELINE4__POLECTP4 | 3 Phase fault BEELINE4 (515247) 138 kV Bus a. Apply fault at the BEELINE4 (515247) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIBBENS4 138 KV 515237 TO BEELINE4 138 KV 515247 CKT 1 b.2. LOAD 1 515247 b.3. POLECTP4 138 KV 515218 TO TIBBENS4 138 KV 515237 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BELISLE4__38TH_ST4 | 3 Phase fault BELISLE4 (514844) 138 kV Bus a. Apply fault at the BELISLE4 (514844) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELISLE4 138 KV 514844 TO 38TH ST4 138 KV 514846 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BELISLE4__WESTERN4 | 3 Phase fault BELISLE4 (514844) 138 kV Bus a. Apply fault at the BELISLE4 (514844) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELISLE4 138 KV 514844 TO WESTERN4 138 KV 514869 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BEVYTAP5__FTSMTHE5 | 3 Phase fault BEVYTAP5 (515299) 161 kV Bus a. Apply fault at the BEVYTAP5 (515299) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVYTAP5 161 KV 515299 TO FTSMTHE5 161 KV 515300 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BING | 3 Phase fault BING-TP2 (511443) 69 kV Bus a. Apply fault at the BING-TP2 (511443) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BING-TP2 69 KV 511443 TO S.W.S.-2 69 KV 511476 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BINGERJ4__NIJECT_4 | 3 Phase fault BINGERJ4 (520827) 138 kV Bus a. Apply fault at the BINGERJ4 (520827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BINGERJ4 138 KV 520827 TO NIJECT 4 138 KV 521010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BINGERJ4__SICKLES4 | 3 Phase fault BINGERJ4 (520827) 138 kV Bus a. Apply fault at the BINGERJ4 (520827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BINGERJ4 138 KV 520827 TO SICKLES4 138 KV 521050 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BLANCH | 3 Phase fault BLANCH-2 (508801) 69 kV Bus a. Apply fault at the BLANCH-2 (508801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCH-2 69 KV 508801 TO LIEBERM2 69 KV 508805 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BLANCHD4__OU_SW_4 | 3 Phase fault BLANCHD4 (520828) 138 kV Bus a. Apply fault at the BLANCHD4 (520828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCHD4 138 KV 520828 TO OU SW 4 138 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BLOOMBG2__IPC_TAP2 | 3 Phase fault BLOOMBG2 (508055) 69 kV Bus a. Apply fault at the BLOOMBG2 (508055) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLOOMBG2 69 KV 508055 TO IPC TAP2 69 KV 508058 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BLUEBEL4__BOWDEN_4 | 3 Phase fault BLUEBEL4 (515242) 138 kV Bus a. Apply fault at the BLUEBEL4 (515242) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBEL4 138 KV 515242 TO BOWDEN 4 138 KV 515243 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BLUERIV4__PARKLN_4 | 3 Phase fault BLUERIV4 (515133) 138 kV Bus a. Apply fault at the BLUERIV4 (515133) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUERIV4 138 KV 515133 TO PARKLN 4 138 KV 515178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BORDER_____7__BECKHAM7 | 3 Phase fault BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345 KV 515458 TO BECKHAM7 345 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BORDER_____7__TUCO_INT___7 | 3 Phase fault BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345 KV 515458 TO TUCO_INT 7 345 KV 525832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BOWMAN_2__KNGINDT2 | 3 Phase fault BOWMAN 2 (514813) 69 kV Bus a. Apply fault at the BOWMAN 2 (514813) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOWMAN 2 69 KV 514813 TO KNGINDT2 69 KV 515625 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BOWMAN_2__OMKINGF2 | 3 Phase fault BOWMAN 2 (514813) 69 kV Bus a. Apply fault at the BOWMAN 2 (514813) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOWMAN 2 69 KV 514813 TO OMKINGF2 69 KV 529280 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BOWMAN_2__TURCRKT2 | 3 Phase fault BOWMAN 2 (514813) 69 kV Bus a. Apply fault at the BOWMAN 2 (514813) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOWMAN 2 69 KV 514813 TO TURCRKT2 69 KV 515517 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BRANDYBR__PIRKEY_4 | 3 Phase fault BRANDYBR (508596) 138 kV Bus a. Apply fault at the BRANDYBR (508596) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRANDYBR 138 KV 508596 TO EASTON 4 138 KV 509092 CKT 1 b.2. LOAD 1 509092 b.3. PIRKEY 4 138 KV 508562 TO EASTON 4 138 KV 509092 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BRCKWND4__BRECKNR4 | 3 Phase fault BRCKWND4 (514642) 138 kV Bus a. Apply fault at the BRCKWND4 (514642) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRCKWND4 138 KV 514642 TO BRECKNR4 138 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BRECKNR4__ENIDINT4 | 3 Phase fault BRECKNR4 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 138 KV 514815 TO ENIDINT4 138 KV 515383 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BRECKNR4__PLNSMEN4 | 3 Phase fault BRECKNR4 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 138 KV 514815 TO PLNSMEN4 138 KV 515641 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BRIDGCR4__SUNSHIN4 | 3 Phase fault BRIDGCR4 (520501) 138 kV Bus a. Apply fault at the BRIDGCR4 (520501) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRIDGCR4 138 KV 520501 TO SUNSHIN4 138 KV 521059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BRIDGCR4__TUTLETP4 | 3 Phase fault BRIDGCR4 (520501) 138 kV Bus a. Apply fault at the BRIDGCR4 (520501) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRIDGCR4 138 KV 520501 TO TUTLETP4 138 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BRISTOW4__BLUEBEL4 | 3 Phase fault BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 138 KV 515035 TO BLUEBEL4 138 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BRISTOW4__GRNWOOD4 | 3 Phase fault BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 138 KV 515035 TO GRNWOOD4 138 KV 515417 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BRISTOW4__KEYWEST4 | 3 Phase fault BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 138 KV 515035 TO KEYWEST4 138 KV 515048 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BRKN_BW4__BETHEL_4 | 3 Phase fault BRKN BW4 (505614) 138 kV Bus a. Apply fault at the BRKN BW4 (505614) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRKN BW4 138 KV 505614 TO BETHEL 4 138 KV 510928 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BRKN_BW4__CRAIGJT4 | 3 Phase fault BRKN BW4 (505614) 138 kV Bus a. Apply fault at the BRKN BW4 (505614) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRKN BW4 138 KV 505614 TO CRAIGJT4 138 KV 510890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BRKN_BW4__HOCHTWN4 | 3 Phase fault BRKN BW4 (505614) 138 kV Bus a. Apply fault at the BRKN BW4 (505614) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRKN BW4 138 KV 505614 TO HOCHTWN4 138 KV 520943 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BRYANML4__MUNZCTY4 | 3 Phase fault BRYANML4 (508056) 138 kV Bus a. Apply fault at the BRYANML4 (508056) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRYANML4 138 KV 508056 TO MUNZCTY4 138 KV 508064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BTLRJCT2__HM | 3 Phase fault BTLRJCT2 (520457) 69 kV Bus a. Apply fault at the BTLRJCT2 (520457) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BTLRJCT2 69 KV 520457 TO HM-BTTP2 69 KV 520942 CKT NO c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BUFFALO7__THISTLE7 | 3 Phase fault BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345 KV 532782 TO THISTLE7 345 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BUFORDR2__COOKVTP2 | 3 Phase fault BUFORDR2 (508287) 69 kV Bus a. Apply fault at the BUFORDR2 (508287) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFORDR2 69 KV 508287 TO COOKVTP2 69 KV 508338 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BUFORDR2__DEKALB_2 | 3 Phase fault BUFORDR2 (508287) 69 kV Bus a. Apply fault at the BUFORDR2 (508287) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFORDR2 69 KV 508287 TO DEKALB 2 69 KV 508289 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BUFORDR2__NAPLES_2 | 3 Phase fault BUFORDR2 (508287) 69 kV Bus a. Apply fault at the BUFORDR2 (508287) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFORDR2 69 KV 508287 TO NAPLES 2 69 KV 508307 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BULFOOT4__BULFTTP4 | 3 Phase fault BULFOOT4 (515960) 138 kV Bus a. Apply fault at the BULFOOT4 (515960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFOOT4 138 KV 515960 TO BULFTTP4 138 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BULFTTP4__DOVERSW4 | 3 Phase fault BULFTTP4 (520535) 138 kV Bus a. Apply fault at the BULFTTP4 (520535) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFTTP4 138 KV 520535 TO DOVERSW4 138 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BUNCHCK4__BRECKNR4 | 3 Phase fault BUNCHCK4 (514701) 138 kV Bus a. Apply fault at the BUNCHCK4 (514701) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 138 KV 514701 TO BRECKNR4 138 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BV | 3 Phase fault BV-COM-4 (510390) 138 kV Bus a. Apply fault at the BV-COM-4 (510390) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BV-COM-4 138 KV 510390 TO BV-SE--4 138 KV 510391 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BV | 3 Phase fault BV-COM-4 (510390) 138 kV Bus a. Apply fault at the BV-COM-4 (510390) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BV-COM-4 138 KV 510390 TO MOUNDRD4 138 KV 510395 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BV | 3 Phase fault BV-SE--4 (510391) 138 kV Bus a. Apply fault at the BV-SE--4 (510391) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BV-SE--4 138 KV 510391 TO BLUESTM4 138 KV 510394 CKT 1 b.2. LOAD 1 510394 b.3. BV-COM-4 138 KV 510390 TO BLUESTM4 138 KV 510394 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BV | 3 Phase fault BV-SE--4 (510391) 138 kV Bus a. Apply fault at the BV-SE--4 (510391) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NBVILLE4 138 KV 510386 TO BV-SE--4 138 KV 510391 CKT 1 b.2. LOAD 1 510391 b.3. NBVILLE4 138 KV 510386 TO COFFEYT4 138 KV 510422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BVRCNTY7__BADGER_7 | 3 Phase fault BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345 KV 515554 TO BADGER 7 345 KV 515677 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_C | 3 Phase fault C-RIVER4 (510946) 138 kV Bus a. Apply fault at the C-RIVER4 (510946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C-RIVER4 138 KV 510946 TO TALAWANDA 4 138 KV 510951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_C | 3 Phase fault C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 345 KV 515422 TO FIREWHL-TAP 345 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CADDO__2__WASHITA2 | 3 Phase fault CADDO 2 (520838) 69 kV Bus a. Apply fault at the CADDO 2 (520838) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CADDO 2 69 KV 520838 TO WASHITA2 69 KV 521088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CALRYTP2__MUSKOGE2 | 3 Phase fault CALRYTP2 (515211) 69 kV Bus a. Apply fault at the CALRYTP2 (515211) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALRYTP2 69 KV 515211 TO MUSKOGE2 69 KV 515221 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CANADN | 3 Phase fault CANADN-4 (514947) 138 kV Bus a. Apply fault at the CANADN-4 (514947) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADN-4 138 KV 514947 TO CANADNS4 138 KV 520842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CANADN7__FSHRTAP7 | 3 Phase fault CANADN7 (515605) 345 kV Bus a. Apply fault at the CANADN7 (515605) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANADN7 345 KV 515605 TO FSHRTAP7 345 KV 515610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CANADNS4__GOLDSBY4 | 3 Phase fault CANADNS4 (520842) 138 kV Bus a. Apply fault at the CANADNS4 (520842) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 138 KV 520842 TO GOLDSBY4 138 KV 520924 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CANA___4__CALUMET4 | 3 Phase fault CANA 4 (520502) 138 kV Bus a. Apply fault at the CANA 4 (520502) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANA 4 138 KV 520502 TO CALUMET4 138 KV 520839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CAN_GAS4__JENSEN_4 | 3 Phase fault CAN_GAS4 (511540) 138 kV Bus a. Apply fault at the CAN_GAS4 (511540) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 138 KV 511540 TO JENSEN 4 138 KV 514821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CARROLL6__DOLHILL6 | 3 Phase fault CARROLL6 (500140) 230 kV Bus a. Apply fault at the CARROLL6 (500140) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARROLL6 230 KV 500140 TO DOLHILL6 230 KV 500260 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CARSN | 3 Phase fault CARSN-N4 (509741) 138 kV Bus a. Apply fault at the CARSN-N4 (509741) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-N4 138 KV 509741 TO CARSONT4 138 KV 509865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CARSN | 3 Phase fault CARSN-S4 (509756) 138 kV Bus a. Apply fault at the CARSN-S4 (509756) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-S4 138 KV 509756 TO KENSH-W4 138 KV 509777 CKT 1 b.2. LOAD 1 509777 b.3. DENVR-C4 138 KV 509742 TO KENSH-W4 138 KV 509777 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CARSN | 3 Phase fault CARSN-S4 (509756) 138 kV Bus a. Apply fault at the CARSN-S4 (509756) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-S4 138 KV 509756 TO T.P.S.-4 138 KV 509788 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CARSN | 3 Phase fault CARSN-T4 (509739) 138 kV Bus a. Apply fault at the CARSN-T4 (509739) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-T4 138 KV 509739 TO UNIONAV4 138 KV 509740 CKT 1 b.2. LOAD 1 509740 b.3. UNIONAV4 138 KV 509740 TO CARSN-C4 138 KV 509749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CARSN | 3 Phase fault CARSN-T4 (509739) 138 kV Bus a. Apply fault at the CARSN-T4 (509739) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-T4 138 KV 509739 TO S.S.---4 138 KV 509815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CARTER_4__CHIKSAW4 | 3 Phase fault CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138 KV 515138 TO CHIKSAW4 138 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CARTER_4__HONEYCK4 | 3 Phase fault CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138 KV 515138 TO HONEYCK4 138 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CARTHGT4__LOGANSP4 | 3 Phase fault CARTHGT4 (509060) 138 kV Bus a. Apply fault at the CARTHGT4 (509060) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHGT4 138 KV 509060 TO LOGANSP4 138 KV 509071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CARTRCO4__GEN | 3 Phase fault CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138 KV 515561 TO GEN-2017-027 138 KV 588710 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CARTRCO4__ORIGINW4 | 3 Phase fault CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138 KV 515561 TO ORIGINW4 138 KV 515563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CASHION4__TWNLKJT4 | 3 Phase fault CASHION4 (520479) 138 kV Bus a. Apply fault at the CASHION4 (520479) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASHION4 138 KV 520479 TO TWNLKJT4 138 KV 520847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CATOOSA2__DAWSON | 3 Phase fault CATOOSA2 (509799) 69 kV Bus a. Apply fault at the CATOOSA2 (509799) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BCIRCLE2 69 KV 509794 TO CATOOSA2 69 KV 509799 CKT 1 b.2. DAWSON-2 69 KV 509791 TO BCIRCLE2 69 KV 509794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CATOOSA4__CDC | 3 Phase fault CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138 KV 509790 TO OWAS88_4 138 KV 509887 CKT 1 b.2. LOAD 1 509887 b.3. CDC-ET 4 138 KV 509839 TO OWAS88_4 138 KV 509887 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CATOOSA4__LLANETP4 | 3 Phase fault CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138 KV 509790 TO LLANETP4 138 KV 509804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CATOOSA4__PCATSAT4 | 3 Phase fault CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138 KV 509790 TO PCATSAT4 138 KV 509841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CATOOSA4__TERNITP4 | 3 Phase fault CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138 KV 509790 TO TERNITP4 138 KV 509835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CATSAGR5__COLINS_5 | 3 Phase fault CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ELMCRK 161 KV 300993 TO CATSAGR5 161 KV 512638 CKT 1 b.2. 5ELMCRK 161 KV 300993 TO COLINS 5 161 KV 512627 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CATSAGR5__MAID___5 | 3 Phase fault CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 161 KV 512638 TO MAID 5 161 KV 512648 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CDC | 3 Phase fault CDC-ET 4 (509839) 138 kV Bus a. Apply fault at the CDC-ET 4 (509839) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CDC-ET 4 138 KV 509839 TO OWAS88_4 138 KV 509887 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CDRDLTP4__OKEENE_4 | 3 Phase fault CDRDLTP4 (520848) 138 kV Bus a. Apply fault at the CDRDLTP4 (520848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CDRDLTP4 138 KV 520848 TO OKEENE 4 138 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CEDARLN4__SOONRTP4 | 3 Phase fault CEDARLN4 (514948) 138 kV Bus a. Apply fault at the CEDARLN4 (514948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARLN4 138 KV 514948 TO SOONRTP4 138 KV 514949 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CEDRDAL4__CDRDLTP4 | 3 Phase fault CEDRDAL4 (520507) 138 kV Bus a. Apply fault at the CEDRDAL4 (520507) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDRDAL4 138 KV 520507 TO CDRDLTP4 138 KV 520848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CEMRD_TP4__CMTRYRD4 | 3 Phase fault CEMRD_TP4 (511576) 138 kV Bus a. Apply fault at the CEMRD_TP4 (511576) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEMRD_TP4 138 KV 511576 TO CMTRYRD4 138 KV 515864 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CHAMSPR7__CLARKSV7 | 3 Phase fault CHAMSPR7 (506945) 345 kV Bus a. Apply fault at the CHAMSPR7 (506945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAMSPR7 345 KV 506945 TO CLARKSV7 345 KV 509745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CHAMSPR7__TONTITN7 | 3 Phase fault CHAMSPR7 (506945) 345 kV Bus a. Apply fault at the CHAMSPR7 (506945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAMSPR7 345 KV 506945 TO TONTITN7 345 KV 506959 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CHAPELH4__CHAPLHL4 | 3 Phase fault CHAPELH4 (508337) 138 kV Bus a. Apply fault at the CHAPELH4 (508337) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPELH4 138 KV 508337 TO CHAPLHL4 138 KV 509664 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CHCKSHA4__CKSHATP4 | 3 Phase fault CHCKSHA4 (520472) 138 kV Bus a. Apply fault at the CHCKSHA4 (520472) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHCKSHA4 138 KV 520472 TO CKSHATP4 138 KV 520473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CHEEKTP4__CHEEK_4 | 3 Phase fault CHEEKTP4 (515415) 138 kV Bus a. Apply fault at the CHEEKTP4 (515415) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHEEKTP4 138 KV 515415 TO CHEEK_4 138 KV 521125 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CHERYCK4__NORMHLL4 | 3 Phase fault CHERYCK4 (514957) 138 kV Bus a. Apply fault at the CHERYCK4 (514957) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERYCK4 138 KV 514957 TO NORMHLL4 138 KV 516097 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CHISHOLM7__BECKHAM7 | 3 Phase fault CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345 KV 511553 TO BECKHAM7 345 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CHISHOLM7__G16 | 3 Phase fault CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345 KV 511553 TO G16-037-TAP 345 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CHISHOM4__FAIRFLD4 | 3 Phase fault CHISHOM4 (515374) 138 kV Bus a. Apply fault at the CHISHOM4 (515374) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOM4 138 KV 515374 TO FAIRFLD4 138 KV 515468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CHOUTEAUCRK5__GEN | 3 Phase fault CHOUTEAUCRK5 (513570) 161 kV Bus a. Apply fault at the CHOUTEAUCRK5 (513570) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHOUTEAUCRK5 161 KV 513570 TO GEN-2017-061 161 KV 588990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CIMARON4__DVISION4 | 3 Phase fault CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYMAKR4 138 KV 514863 TO CIMARON4 138 KV 514898 CKT 1 b.2. DVISION4 138 KV 514853 TO HAYMAKR4 138 KV 514863 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CIMARON4__MCCLAIN4 | 3 Phase fault CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA 4 138 KV 514895 TO CIMARON4 138 KV 514898 CKT 1 b.2. SARA 4 138 KV 514895 TO MCCLAIN4 138 KV 514902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CIMARON4__MUSTANG4 | 3 Phase fault CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CZECHAL4 138 KV 514894 TO CIMARON4 138 KV 514898 CKT 1 b.2. XEROX 4 138 KV 514893 TO CZECHAL4 138 KV 514894 CKT 1 b.3. LOAD 1 514894 b.4. XEROX 4 138 KV 514893 TO MORGAN 4 138 KV 514896 CKT 1 b.5. LOAD 1 514896 b.6. MUSTANG4 138 KV 514861 TO MORGAN 4 138 KV 514896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CIMARON7__FSHRTAP7 | 3 Phase fault CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345 KV 514901 TO FSHRTAP7 345 KV 515610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CIMARON7__MATHWSN7 | 3 Phase fault CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345 KV 514901 TO MATHWSN7 345 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CIMARON7__NORMHLL7 | 3 Phase fault CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345 KV 514901 TO NORMHLL7 345 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CIP____4__CDC | 3 Phase fault CIP 4 (509714) 138 kV Bus a. Apply fault at the CIP 4 (509714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIP 4 138 KV 509714 TO CDC-ET 4 138 KV 509839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CIP____4__CDC____4 | 3 Phase fault CIP 4 (509714) 138 kV Bus a. Apply fault at the CIP 4 (509714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIP 4 138 KV 509714 TO CDC 4 138 KV 509715 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CKSHATP4__CORN_TP4 | 3 Phase fault CKSHATP4 (520473) 138 kV Bus a. Apply fault at the CKSHATP4 (520473) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CKSHATP4 138 KV 520473 TO CORN TP4 138 KV 520867 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CL | 3 Phase fault CL-AFTP4 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 138 KV 511446 TO ELKCTY-4 138 KV 511458 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CL | 3 Phase fault CL-AFTP4 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 138 KV 511446 TO HOB-JCT4 138 KV 511463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CLARKCOUNTY7__THISTLE7 | 3 Phase fault CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345 KV 539800 TO THISTLE7 345 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CLARKSV7__GEN | 3 Phase fault CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345 KV 509745 TO GEN-2017-140 345 KV 760389 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CLARKSV7__MUSKOGE7 | 3 Phase fault CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345 KV 509745 TO MUSKOGE7 345 KV 515224 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CLARKSV7__ONETA | 3 Phase fault CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345 KV 509745 TO ONETA--7 345 KV 509807 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CLARMR_5__CHOUTEAUCRK5 | 3 Phase fault CLARMR 5 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 161 KV 512651 TO CHOUTEAUCRK5 161 KV 513570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CLASSEN4__TROSPER4 | 3 Phase fault CLASSEN4 (514922) 138 kV Bus a. Apply fault at the CLASSEN4 (514922) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLASSEN4 138 KV 514922 TO CROSTWN4 138 KV 515851 CKT 1 b.2. LOAD 1 515851 b.3. LIGHTCK4 138 KV 514923 TO CROSTWN4 138 KV 515851 CKT 1 b.4. LOAD 1 515851 b.5. LIGHTCK4 138 KV 514923 TO TROSPER4 138 KV 514963 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CLEOSW_2__RNGWODJ2 | 3 Phase fault CLEOSW 2 (520855) 69 kV Bus a. Apply fault at the CLEOSW 2 (520855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOSW 2 69 KV 520855 TO RNGWODJ2 69 KV 521039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CLEVETP2__SO4TH__2 | 3 Phase fault CLEVETP2 (514722) 69 kV Bus a. Apply fault at the CLEVETP2 (514722) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVETP2 69 KV 514722 TO SO4TH 2 69 KV 514730 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CLEVLND7__G15 | 3 Phase fault CLEVLND7 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 345 KV 512694 TO G15-066T 345 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CLVLDSW4__AMBERTP4 | 3 Phase fault CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138 KV 520508 TO AMBERTP4 138 KV 520530 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CLVLDSW4__ANADARK4 | 3 Phase fault CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138 KV 520508 TO ANADARK4 138 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CLVLDSW4__COGAR__4 | 3 Phase fault CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138 KV 520508 TO COGAR 4 138 KV 520859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CMBLCRK4__CMBLTP_4 | 3 Phase fault CMBLCRK4 (515930) 138 kV Bus a. Apply fault at the CMBLCRK4 (515930) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMBLCRK4 138 KV 515930 TO CMBLTP 4 138 KV 520474 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CMBLTP_4__FOURCTP4 | 3 Phase fault CMBLTP 4 (520474) 138 kV Bus a. Apply fault at the CMBLTP 4 (520474) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMBLTP 4 138 KV 520474 TO FOURCTP4 138 KV 520545 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_COBRN_CREEK3__WHEELER____3 | 3 Phase fault COBRN_CREEK3 (523772) 115 kV Bus a. Apply fault at the COBRN_CREEK3 (523772) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COBRN_CREEK3 115 KV 523772 TO WHEELER 3 115 KV 523776 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_COFFEYT4__DEARING4 | 3 Phase fault COFFEYT4 (510422) 138 kV Bus a. Apply fault at the COFFEYT4 (510422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COFFEYT4 138 KV 510422 TO DEARING4 138 KV 533002 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_COLE___4__OU_SW_4 | 3 Phase fault COLE 4 (520861) 138 kV Bus a. Apply fault at the COLE 4 (520861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLE 4 138 KV 520861 TO OU SW 4 138 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_COLINS_5__CLARMR_5 | 3 Phase fault COLINS 5 (512627) 161 kV Bus a. Apply fault at the COLINS 5 (512627) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5KETONVL 161 KV 300997 TO COLINS 5 161 KV 512627 CKT 1 b.2. 5KETONVL 161 KV 300997 TO CLARMR 5 161 KV 512651 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_COMANC | 3 Phase fault COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69 KV 511436 TO L.E.S.-2 69 KV 511466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_COMANC | 3 Phase fault COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138 KV 511437 TO 112GORE4 138 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_COMANC | 3 Phase fault COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138 KV 511437 TO COMMTAP4 138 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_COMANC | 3 Phase fault COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138 KV 511437 TO L.E.S.-4 138 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_COMMTAP4__OMDUNCN4 | 3 Phase fault COMMTAP4 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMMTAP4 138 KV 511494 TO OMDUNCN4 138 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CORNVIL4__ALEX_BR4 | 3 Phase fault CORNVIL4 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138 KV 511449 TO ALEX BR4 138 KV 511516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CORNVIL4__CORN_TP4 | 3 Phase fault CORNVIL4 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138 KV 511449 TO CORN TP4 138 KV 520867 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CORNVIL4__LEONARD4 | 3 Phase fault CORNVIL4 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138 KV 511449 TO LEONARD4 138 KV 511575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CORNVIL4__MAUD___4 | 3 Phase fault CORNVIL4 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCHD4 138 KV 511508 TO MAUD 4 138 KV 515055 CKT 1 b.2. CORNVIL4 138 KV 511449 TO BLANCHD4 138 KV 511508 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CORNVIL4__N29CHIK4 | 3 Phase fault CORNVIL4 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138 KV 511449 TO N29CHIK4 138 KV 511502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CORNVIL4__NORGE | 3 Phase fault CORNVIL4 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138 KV 511449 TO NORGE--4 138 KV 511483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CORNVIL4__SANTAFE4 | 3 Phase fault CORNVIL4 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 138 KV 511449 TO SANTAFE4 138 KV 511492 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CRAIGJT4__HOCHJCT4 | 3 Phase fault CRAIGJT4 (510890) 138 kV Bus a. Apply fault at the CRAIGJT4 (510890) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIGJT4 138 KV 510890 TO MTRIVER4 138 KV 521004 CKT 1 b.2. LOAD 1 521004 b.3. HOCHJCT4 138 KV 520823 TO MTRIVER4 138 KV 521004 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CRAIGJT4__MENA___4 | 3 Phase fault CRAIGJT4 (510890) 138 kV Bus a. Apply fault at the CRAIGJT4 (510890) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENA 4 138 KV 507436 TO GORDON TAP 4 138 KV 507461 CKT 1 b.2. LOAD A1 507461 b.3. GORDON TAP 4 138 KV 507461 TO CRAIGJT4 138 KV 510890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CRESENT4__GEN | 3 Phase fault CRESENT4 (515377) 138 kV Bus a. Apply fault at the CRESENT4 (515377) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESENT4 138 KV 515377 TO GEN-2016-032 138 KV 587210 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CRESENT4__TWNLKSW4 | 3 Phase fault CRESENT4 (515377) 138 kV Bus a. Apply fault at the CRESENT4 (515377) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESENT4 138 KV 515377 TO TWNLKSW4 138 KV 521073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CTNWOOD4__ARCADIA4 | 3 Phase fault CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138 KV 514827 TO ARCADIA4 138 KV 514907 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CTNWOOD4__CRESENT4 | 3 Phase fault CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138 KV 514827 TO CRESENT4 138 KV 515377 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CTNWOOD4__KETCHTP4 | 3 Phase fault CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138 KV 514827 TO LBRTYLK4 138 KV 515373 CKT 1 b.2. LOAD 1 515373 b.3. WATRLOO4 138 KV 514831 TO LBRTYLK4 138 KV 515373 CKT 1 b.4. LOAD 1 515373 b.5. WATRLOO4 138 KV 514831 TO WHITESB4 138 KV 515467 CKT 1 b.6. LOAD 1 515467 b.7. MITCHSB4 138 KV 515466 TO WHITESB4 138 KV 515467 CKT 1 b.8. LOAD 1 515467 b.9. KETCHTP4 138 KV 514828 TO MITCHSB4 138 KV 515466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CTNWOOD4__KINZE__4 | 3 Phase fault CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138 KV 514827 TO PINE ST4 138 KV 514829 CKT 1 b.2. LOAD 1 514829 b.3. LOAD 2 514829 b.4. PINE ST4 138 KV 514829 TO FITZGRD4 138 KV 514830 CKT 1 b.5. LOAD 1 514830 b.6. FITZGRD4 138 KV 514830 TO KINZE 4 138 KV 515008 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CTNWOOD4__LBRTYLK4 | 3 Phase fault CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138 KV 514827 TO LBRTYLK4 138 KV 515373 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CUSTDAY1_5__HERRON_5 | 3 Phase fault CUSTDAY1 5 (513590) 161 kV Bus a. Apply fault at the CUSTDAY1 5 (513590) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTDAY1 5 161 KV 513590 TO HERRON 5 161 KV 513591 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DANFRTH4__KETCH__4 | 3 Phase fault DANFRTH4 (514833) 138 kV Bus a. Apply fault at the DANFRTH4 (514833) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DANFRTH4 138 KV 514833 TO KETCH 4 138 KV 514834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DARENCT2__ALAMANC2 | 3 Phase fault DARENCT2 (509647) 69 kV Bus a. Apply fault at the DARENCT2 (509647) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DARENCT2 69 KV 509647 TO ALAMANC2 69 KV 509649 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DARENCT2__DARENCO2 | 3 Phase fault DARENCT2 (509647) 69 kV Bus a. Apply fault at the DARENCT2 (509647) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DARENCT2 69 KV 509647 TO DARENCO2 69 KV 509648 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DAWSON | 3 Phase fault DAWSON-4 (509792) 138 kV Bus a. Apply fault at the DAWSON-4 (509792) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSON-4 138 KV 509792 TO DAWSONT4 138 KV 509803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DAWSONT4__N21ST | 3 Phase fault DAWSONT4 (509803) 138 kV Bus a. Apply fault at the DAWSONT4 (509803) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONT4 138 KV 509803 TO N21ST--4 138 KV 509866 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DAYTON_4__HOBBYLO4 | 3 Phase fault DAYTON 4 (514892) 138 kV Bus a. Apply fault at the DAYTON 4 (514892) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAYTON 4 138 KV 514892 TO HOBBYLO4 138 KV 515338 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DEEPFKT2__DEEPFRK2 | 3 Phase fault DEEPFKT2 (514970) 69 kV Bus a. Apply fault at the DEEPFKT2 (514970) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEEPFKT2 69 KV 514970 TO DEEPFRK2 69 KV 514974 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DELWARE4__FARML__4 | 3 Phase fault DELWARE4 (510379) 138 kV Bus a. Apply fault at the DELWARE4 (510379) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELWARE4 138 KV 510379 TO FARML 4 138 KV 512734 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DELWARE7__N.E.S. | 3 Phase fault DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 345 KV 510380 TO N.E.S.-7 345 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DELWARE7__NEOSHO_7 | 3 Phase fault DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 345 KV 510380 TO NEOSHO 7 345 KV 532793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DENVR | 3 Phase fault DENVR-E4 (509743) 138 kV Bus a. Apply fault at the DENVR-E4 (509743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVR-E4 138 KV 509743 TO DENVTAP4 138 KV 509746 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DENVR | 3 Phase fault DENVR-W4 (509748) 138 kV Bus a. Apply fault at the DENVR-W4 (509748) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVR-W4 138 KV 509748 TO DENV_WTAP4 138 KV 509896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DENVTAP4__T.NO. | 3 Phase fault DENVTAP4 (509746) 138 kV Bus a. Apply fault at the DENVTAP4 (509746) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVTAP4 138 KV 509746 TO T.NO.--4 138 KV 509817 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DENVTAP4__W.ED. | 3 Phase fault DENVTAP4 (509746) 138 kV Bus a. Apply fault at the DENVTAP4 (509746) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVTAP4 138 KV 509746 TO W.ED.-E4 138 KV 509822 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DEQUEEN2__LOCKESB2 | 3 Phase fault DEQUEEN2 (507418) 69 kV Bus a. Apply fault at the DEQUEEN2 (507418) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEQUEEN2 69 KV 507418 TO LOCKESB2 69 KV 507422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DEQUEEN4__CRAIGJT4 | 3 Phase fault DEQUEEN4 (507419) 138 kV Bus a. Apply fault at the DEQUEEN4 (507419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEQUEEN4 138 KV 507419 TO CRAIGJT4 138 KV 510890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DEWEY__4__CANTNLK4 | 3 Phase fault DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138 KV 514787 TO CANTNLK4 138 KV 515964 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DEWEY__4__REDCLFT4 | 3 Phase fault DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138 KV 514787 TO REDCLFT4 138 KV 515533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DEWEY__4__TALOGA_4 | 3 Phase fault DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138 KV 514787 TO TALOGA 4 138 KV 521065 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DEWEY__4__TLGAWND4 | 3 Phase fault DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138 KV 514787 TO TLGAWND4 138 KV 515390 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DGRASSE4__MOORLND4 | 3 Phase fault DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138 KV 515853 TO MOORLND4 138 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DGRASSE4__ROSEVLY4 | 3 Phase fault DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138 KV 515853 TO ROSEVLY4 138 KV 520436 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DGRASSE7__THISTLE7 | 3 Phase fault DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 345 KV 515852 TO THISTLE7 345 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DIANA__4__DIANASW4 | 3 Phase fault DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 138 KV 508831 TO DIANASW4 138 KV 509639 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DIANA__4__NGPLTAP4 | 3 Phase fault DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 138 KV 508831 TO NGPLTAP4 138 KV 508837 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DILLARD4__WOLFCRK4 | 3 Phase fault DILLARD4 (515142) 138 kV Bus a. Apply fault at the DILLARD4 (515142) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DILLARD4 138 KV 515142 TO WOLFCRK4 138 KV 515143 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DOLHILL7__SW_SHV_7 | 3 Phase fault DOLHILL7 (500250) 345 kV Bus a. Apply fault at the DOLHILL7 (500250) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DOLHILL7 345 KV 500250 TO SW SHV 7 345 KV 507760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DOUGLTP4__CLASSEN4 | 3 Phase fault DOUGLTP4 (514868) 138 kV Bus a. Apply fault at the DOUGLTP4 (514868) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOUGLTP4 138 KV 514868 TO CLASSEN4 138 KV 514922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DOUGLTP4__WESTERN4 | 3 Phase fault DOUGLTP4 (514868) 138 kV Bus a. Apply fault at the DOUGLTP4 (514868) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOUGLTP4 138 KV 514868 TO WESTERN4 138 KV 514869 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DOVERSW2__HENESEY2 | 3 Phase fault DOVERSW2 (520881) 69 kV Bus a. Apply fault at the DOVERSW2 (520881) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW2 69 KV 520881 TO HENESEY2 69 KV 520940 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DOVERSW2__LACEY__2 | 3 Phase fault DOVERSW2 (520881) 69 kV Bus a. Apply fault at the DOVERSW2 (520881) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW2 69 KV 520881 TO LACEY 2 69 KV 520967 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DOVERSW4__GEN | 3 Phase fault DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138 KV 520882 TO GEN-2016-118 138 KV 587940 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DOVERSW4__GEN | 3 Phase fault DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138 KV 520882 TO GEN-2018-011 138 KV 762493 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DOVERSW4__KGFSJCT4 | 3 Phase fault DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKNGFSH4 138 KV 520603 TO DOVERSW4 138 KV 520882 CKT 1 b.2. KGFSJCT4 138 KV 520405 TO NKNGFSH4 138 KV 520603 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DOVERSW4__OKEENE_4 | 3 Phase fault DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138 KV 520882 TO OKEENE 4 138 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DOVERSW4__TWNLKSW4 | 3 Phase fault DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVER 4 138 KV 520879 TO DOVERSW4 138 KV 520882 CKT 1 b.2. TWNLAKE4 138 KV 520540 TO DOVER 4 138 KV 520879 CKT 1 b.3. LOAD 1 520879 b.4. TWNLAKE4 138 KV 520540 TO TWNLKSW4 138 KV 521073 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DOVERTP2__DOVERSW2 | 3 Phase fault DOVERTP2 (514772) 69 kV Bus a. Apply fault at the DOVERTP2 (514772) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERTP2 69 KV 514772 TO DOVERSW2 69 KV 520881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DOVERTP2__REDWING2 | 3 Phase fault DOVERTP2 (514772) 69 kV Bus a. Apply fault at the DOVERTP2 (514772) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERTP2 69 KV 514772 TO REDWING2 69 KV 515976 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DOVERTP2__TURCRKT2 | 3 Phase fault DOVERTP2 (514772) 69 kV Bus a. Apply fault at the DOVERTP2 (514772) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERTP2 69 KV 514772 TO TURCRKT2 69 KV 515517 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DRAPER_4__BARNES_4 | 3 Phase fault DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138 KV 514933 TO BARNES 4 138 KV 515003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DRAPER_4__GM_____4 | 3 Phase fault DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138 KV 514933 TO GM 4 138 KV 514961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DRAPER_4__MIDWEST4 | 3 Phase fault DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138 KV 514933 TO MIDWEST4 138 KV 514946 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DRAPER_4__SOONRTP4 | 3 Phase fault DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138 KV 514933 TO SOONRTP4 138 KV 514949 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DRAPER_7__NORMHLL7 | 3 Phase fault DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345 KV 514934 TO NORMHLL7 345 KV 516096 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DRAPER_7__SEMINOL7 | 3 Phase fault DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345 KV 514934 TO SEMINOL7 345 KV 515045 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DRYGULCH5__GEN | 3 Phase fault DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 161 KV 512629 TO GEN-2017-073 161 KV 589110 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DUGLASV2__DARENCT2 | 3 Phase fault DUGLASV2 (509645) 69 kV Bus a. Apply fault at the DUGLASV2 (509645) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUGLASV2 69 KV 509645 TO BLALOCK2 69 KV 509646 CKT 1 b.2. LOAD 1 509646 b.3. BLALOCK2 69 KV 509646 TO DARENCT2 69 KV 509647 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DUGLASV2__MAUDT__2 | 3 Phase fault DUGLASV2 (509645) 69 kV Bus a. Apply fault at the DUGLASV2 (509645) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUGLASV2 69 KV 509645 TO MAUDT 2 69 KV 509653 CKT NO c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DUGLASV2__ROACH__2 | 3 Phase fault DUGLASV2 (509645) 69 kV Bus a. Apply fault at the DUGLASV2 (509645) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUGLASV2 69 KV 509645 TO NLINDEN2 69 KV 509652 CKT 1 b.2. LOAD 1 509652 b.3. NLINDEN2 69 KV 509652 TO ROACH 2 69 KV 509668 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DUNCAN | 3 Phase fault DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138 KV 511453 TO OMDUNCN4 138 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DVISION4__HAYMAKR4 | 3 Phase fault DVISION4 (514853) 138 kV Bus a. Apply fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 138 KV 514853 TO HAYMAKR4 138 KV 514863 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DVISION4__HEFNER_4 | 3 Phase fault DVISION4 (514853) 138 kV Bus a. Apply fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKESID4 138 KV 514849 TO DVISION4 138 KV 514853 CKT 1 b.2. LOAD 1 514853 b.3. HEFNER 4 138 KV 514848 TO LAKESID4 138 KV 514849 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DVISION4__MUSTANG4 | 3 Phase fault DVISION4 (514853) 138 kV Bus a. Apply fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 138 KV 514853 TO MUSTANG4 138 KV 514861 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DVISION4__NORTWST4 | 3 Phase fault DVISION4 (514853) 138 kV Bus a. Apply fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 138 KV 514853 TO RICHRDS4 138 KV 514862 CKT 1 b.2. LOAD 1 514862 b.3. RICHRDS4 138 KV 514862 TO PIEDMNT4 138 KV 514864 CKT 1 b.4. LOAD 1 514864 b.5. PIEDMNT4 138 KV 514864 TO NORTWST4 138 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DVISION4__RICHRDS4 | 3 Phase fault DVISION4 (514853) 138 kV Bus a. Apply fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 138 KV 514853 TO RICHRDS4 138 KV 514862 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DX | 3 Phase fault DX----W2 (509796) 69 kV Bus a. Apply fault at the DX----W2 (509796) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DX----W2 69 KV 509796 TO S.S.---2 69 KV 509816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_EAGLCHF2__RNGWODJ2 | 3 Phase fault EAGLCHF2 (520890) 69 kV Bus a. Apply fault at the EAGLCHF2 (520890) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLCHF2 69 KV 520890 TO RNGWODJ2 69 KV 521039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_EKNGFSH4__EKFSHTP4 | 3 Phase fault EKNGFSH4 (520484) 138 kV Bus a. Apply fault at the EKNGFSH4 (520484) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EKNGFSH4 138 KV 520484 TO EKFSHTP4 138 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ELRENO_CIMARON | 3 Phase fault EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138 KV 514819 TO CIMARON4 138 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ELRENO_JENSENT | 3 Phase fault EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138 KV 514819 TO JENSENT4 138 KV 514820 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ELRENO_ROMNOSE | 3 Phase fault EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138 KV 514819 TO OMEGA 4 138 KV 515962 CKT 1 b.2. LOAD 1 515962 b.3. ROMNOSE4 138 KV 514823 TO OMEGA 4 138 KV 515962 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ELKCITY6__CHISHOLM6 | 3 Phase fault ELKCITY6 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 230 KV 511490 TO CHISHOLM6 230 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ELKCTY_CLINTJC4 | 3 Phase fault ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 138 KV 511458 TO CLINTJC4 138 KV 511485 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ELKCTY_FALCNRD | 3 Phase fault ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 138 KV 511458 TO FALCNRD4 138 KV 511511 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ELKCTY_REDHLSW | 3 Phase fault ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 138 KV 511458 TO REDHLSW4 138 KV 521116 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_EMPIRE_4__FLETCH | 3 Phase fault EMPIRE 4 (520900) 138 kV Bus a. Apply fault at the EMPIRE 4 (520900) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMPIRE 4 138 KV 520900 TO FLETCH-4 138 KV 520912 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ENID___2__SO4TH__2 | 3 Phase fault ENID 2 (514727) 69 kV Bus a. Apply fault at the ENID 2 (514727) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENID 2 69 KV 514727 TO SO4TH 2 69 KV 514730 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ERLSBOR2__FRSTHIL2 | 3 Phase fault ERLSBOR2 (515073) 69 kV Bus a. Apply fault at the ERLSBOR2 (515073) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ERLSBOR2 69 KV 515073 TO FRSTHIL2 69 KV 515074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_EUFREST2__WELLSPA2 | 3 Phase fault EUFREST2 (515214) 69 kV Bus a. Apply fault at the EUFREST2 (515214) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUFREST2 69 KV 515214 TO WELLSPA2 69 KV 515215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_EXCLART4__EXPCLAR4 | 3 Phase fault EXCLART4 (510401) 138 kV Bus a. Apply fault at the EXCLART4 (510401) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXCLART4 138 KV 510401 TO EXPCLAR4 138 KV 510405 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_EXCLART4__G17 | 3 Phase fault EXCLART4 (510401) 138 kV Bus a. Apply fault at the EXCLART4 (510401) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXCLART4 138 KV 510401 TO G17-077-TAP 138 KV 589154 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_EXPLGLN4__EXPGLNT4 | 3 Phase fault EXPLGLN4 (515248) 138 kV Bus a. Apply fault at the EXPLGLN4 (515248) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXPLGLN4 138 KV 515248 TO EXPGLNT4 138 KV 515473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_EYLAU__4__BUCHANN4 | 3 Phase fault EYLAU 4 (509655) 138 kV Bus a. Apply fault at the EYLAU 4 (509655) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EYLAU 4 138 KV 509655 TO BUCHANN4 138 KV 509656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FAIRVEW2__OKEENE_2 | 3 Phase fault FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69 KV 520909 TO OKEENE 2 69 KV 521015 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FAIRVEW2__OMFAIRV2 | 3 Phase fault FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69 KV 520909 TO OMFAIRV2 69 KV 529343 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FAIRVEW2__RNGWODJ2 | 3 Phase fault FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69 KV 520909 TO RNGWODJ2 69 KV 521039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FIXCT4__FIXICO_4 | 3 Phase fault FIXCT4 (510877) 138 kV Bus a. Apply fault at the FIXCT4 (510877) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIXCT4 138 KV 510877 TO FIXICO 4 138 KV 515078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FIXCT4__WELETK4 | 3 Phase fault FIXCT4 (510877) 138 kV Bus a. Apply fault at the FIXCT4 (510877) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIXCT4 138 KV 510877 TO WELETK4 138 KV 510902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FLETCHR4__FLE_TAP4 | 3 Phase fault FLETCHR4 (511422) 138 kV Bus a. Apply fault at the FLETCHR4 (511422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR4 138 KV 511422 TO FLE TAP4 138 KV 511423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FLE_TAP4__G16 | 3 Phase fault FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138 KV 511423 TO G16-097-TAP 138 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FLE_TAP4__L.E.S. | 3 Phase fault FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138 KV 511423 TO L.E.S.-4 138 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FLOURNY2__PINESRD2 | 3 Phase fault FLOURNY2 (507726) 69 kV Bus a. Apply fault at the FLOURNY2 (507726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 69 KV 507726 TO PINESRD2 69 KV 507747 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FLOURNY2__WASKOM_2 | 3 Phase fault FLOURNY2 (507726) 69 kV Bus a. Apply fault at the FLOURNY2 (507726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 69 KV 507726 TO WASKOM 2 69 KV 508839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FLOURNY2__WOOLWTP2 | 3 Phase fault FLOURNY2 (507726) 69 kV Bus a. Apply fault at the FLOURNY2 (507726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 69 KV 507726 TO WOOLWTP2 69 KV 507770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FOREMAN2__DEQUEEN2 | 3 Phase fault FOREMAN2 (507421) 69 kV Bus a. Apply fault at the FOREMAN2 (507421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORMANR2 69 KV 507407 TO FOREMAN2 69 KV 507421 CKT 1 b.2. LOAD 1 507421 b.3. DEQUEEN 2 69 KV 504120 TO FORMANR2 69 KV 507407 CKT 1 b.4. LOAD A1 507407 b.5. DEQUEEN 2 69 KV 504120 TO DEQUEEN2 69 KV 507418 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FOREMAN2__FOREMAG2 | 3 Phase fault FOREMAN2 (507421) 69 kV Bus a. Apply fault at the FOREMAN2 (507421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOREMAN2 69 KV 507421 TO FOREMAG2 69 KV 507440 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FOREMAN2__PATTERS2 | 3 Phase fault FOREMAN2 (507421) 69 kV Bus a. Apply fault at the FOREMAN2 (507421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOREMAN2 69 KV 507421 TO PATTERS2 69 KV 507429 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FOURCTP4__FOURCNT4 | 3 Phase fault FOURCTP4 (520545) 138 kV Bus a. Apply fault at the FOURCTP4 (520545) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOURCTP4 138 KV 520545 TO FOURCNT4 138 KV 520546 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FOURCTP4__TWNLKJT4 | 3 Phase fault FOURCTP4 (520545) 138 kV Bus a. Apply fault at the FOURCTP4 (520545) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOURCTP4 138 KV 520545 TO TWNLKJT4 138 KV 520847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FRMNTAP4__FAIRMON4 | 3 Phase fault FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138 KV 514709 TO FAIRMON4 138 KV 514712 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FRMNTAP4__SO4TH__4 | 3 Phase fault FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138 KV 514709 TO SO4TH 4 138 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FRMNTAP4__WOODRNG4 | 3 Phase fault FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138 KV 514709 TO WOODRNG4 138 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FRNKLNS4__CANADNS4 | 3 Phase fault FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRNKLNS4 138 KV 520917 TO LIDDELL4 138 KV 520975 CKT 1 b.2. LOAD 1 520975 b.3. NOBLE4 138 KV 520400 TO LIDDELL4 138 KV 520975 CKT 1 b.4. LOAD 1 520975 b.5. NOBLE4 138 KV 520400 TO CANADNS4 138 KV 520842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FRNKLNS4__OU_SW_4 | 3 Phase fault FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ACME 4 138 KV 520802 TO FRNKLNS4 138 KV 520917 CKT 1 b.2. ACME 4 138 KV 520802 TO WNORMAN4 138 KV 521095 CKT 1 b.3. LOAD 1 521095 b.4. LAMAR4 138 KV 520403 TO WNORMAN4 138 KV 521095 CKT 1 b.5. LOAD 1 521095 b.6. LAMAR4 138 KV 520403 TO OU SW 4 138 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FRNKLNS4__PINK_SW4 | 3 Phase fault FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLN4 138 KV 520913 TO FRNKLNS4 138 KV 520917 CKT 1 b.2. FRANKLN4 138 KV 520913 TO PINK SW4 138 KV 521028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FRNKLNS4__SUNSHIN4 | 3 Phase fault FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRNKLNS4 138 KV 520917 TO WMOORE 4 138 KV 521123 CKT 1 b.2. LOAD 1 521123 b.3. BAILEY4 138 KV 520401 TO WMOORE 4 138 KV 521123 CKT 1 b.4. LOAD 1 521123 b.5. BAILEY4 138 KV 520401 TO SUNSHIN4 138 KV 521059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FROGVIL4__HUGO_PP4 | 3 Phase fault FROGVIL4 (520918) 138 kV Bus a. Apply fault at the FROGVIL4 (520918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FROGVIL4 138 KV 520918 TO HUGO PP4 138 KV 520948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FRSTHIL4__STRLGTP4 | 3 Phase fault FRSTHIL4 (515075) 138 kV Bus a. Apply fault at the FRSTHIL4 (515075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRSTHIL4 138 KV 515075 TO STRLGTP4 138 KV 515286 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FTSMTHE5__COLONY_5 | 3 Phase fault FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5 (515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161 KV 515300 TO COLONY 5 161 KV 515345 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FTSMTHE5__FTSMTHW5 | 3 Phase fault FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5 (515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161 KV 515300 TO FTSMTHW5 161 KV 515301 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FTSMTHE5__QUANXTP5 | 3 Phase fault FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5 (515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161 KV 515300 TO QUANXTP5 161 KV 515310 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FTSMTHW5__ARKOMA_5 | 3 Phase fault FTSMTHW5 (515301) 161 kV Bus a. Apply fault at the FTSMTHW5 (515301) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 161 KV 515301 TO ARKOMA 5 161 KV 515306 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FT_GIB_5__OKAYGR_5 | 3 Phase fault FT GIB 5 (505560) 161 kV Bus a. Apply fault at the FT GIB 5 (505560) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FT GIB 5 161 KV 505560 TO OKAYGR 5 161 KV 512640 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FULTONE4__21STTAP4 | 3 Phase fault FULTONE4 (509797) 138 kV Bus a. Apply fault at the FULTONE4 (509797) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FULTONE4 138 KV 509797 TO S21ST--4 138 KV 509808 CKT 1 b.2. LOAD 1 509808 b.3. S21ST--4 138 KV 509808 TO 21STTAP4 138 KV 509828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FULTONW4__KENSH | 3 Phase fault FULTONW4 (509829) 138 kV Bus a. Apply fault at the FULTONW4 (509829) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FULTONW4 138 KV 509829 TO KENSH-E-TP4 138 KV 509830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FULTON____3__HOPE___3 | 3 Phase fault FULTON 3 (503912) 115 kV Bus a. Apply fault at the FULTON 3 (503912) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FULTON 3 115 KV 503912 TO HOPE 3 115 KV 507453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_G07621119 | 3 Phase fault G07621119-20 (515599) 345 kV Bus a. Apply fault at the G07621119-20 (515599) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G07621119-20 345 KV 515599 TO GREAT_WESTRN 345 KV 585410 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_G07621119 | 3 Phase fault G07621119-20 (515599) 345 kV Bus a. Apply fault at the G07621119-20 (515599) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G07621119-20 345 KV 515599 TO PRSIMN_CRK1 345 KV 585430 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_G15 | 3 Phase fault G15-066T (560056) 345 kV Bus a. Apply fault at the G15-066T (560056) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G15-066T 345 KV 560056 TO GEN-2015-066 345 KV 585040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_G16 | 3 Phase fault G16-003-TAP (560071) 345 kV Bus a. Apply fault at the G16-003-TAP (560071) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP 345 KV 560071 TO GEN-2017-011 345 KV 588560 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_G16 | 3 Phase fault G16-037-TAP (560078) 345 kV Bus a. Apply fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345 KV 560078 TO GEN-2016-037 345 KV 587230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_G16 | 3 Phase fault G16-091-TAP (587744) 345 kV Bus a. Apply fault at the G16-091-TAP (587744) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-091-TAP 345 KV 587744 TO GEN-2016-095 345 KV 587770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_G16133G16146__G16133_345GS | 3 Phase fault G16133G16146 (588039) 345 kV Bus a. Apply fault at the G16133G16146 (588039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16133G16146 345 KV 588039 TO G16133_345GS 345 KV 588040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_G17-009_NESHO | 3 Phase fault G17-009-TAP (532777) 345 kV Bus a. Apply fault at the G17-009-TAP (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP 345 KV 532777 TO NEOSHO 7 345 KV 532793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_G17-092_FIREWHLTAP | 3 Phase fault G17-092-SWYD (588838) 345 kV Bus a. Apply fault at the G17-092-SWYD (588838) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-092-SWYD 345 KV 588838 TO FIREWHL-TAP 345 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_G17_151_G18-015 | 3 Phase fault G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345 KV 762216 TO G18-015-TAP 345 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GLASMTN4__MOORLND4 | 3 Phase fault GLASMTN4 (514788) 138 kV Bus a. Apply fault at the GLASMTN4 (514788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLASMTN4 138 KV 514788 TO MOORLND4 138 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GLENWD_4__IMO____4 | 3 Phase fault GLENWD 4 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 138 KV 514734 TO IMO 4 138 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GOLDSBY4__OU_SW_4 | 3 Phase fault GOLDSBY4 (520924) 138 kV Bus a. Apply fault at the GOLDSBY4 (520924) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOLDSBY4 138 KV 520924 TO OU SW 4 138 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GORE___5__EUFAULA5 | 3 Phase fault GORE 5 (505552) 161 kV Bus a. Apply fault at the GORE 5 (505552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161 KV 505552 TO EUFAULA5 161 KV 505570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GORE___5__MUSKTAP5 | 3 Phase fault GORE 5 (505552) 161 kV Bus a. Apply fault at the GORE 5 (505552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161 KV 505552 TO MUSKTAP5 161 KV 505558 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GORE___5__TENKIL_5 | 3 Phase fault GORE 5 (505552) 161 kV Bus a. Apply fault at the GORE 5 (505552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161 KV 505552 TO TENKIL 5 161 KV 505566 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GORE___5__WEBFALL5 | 3 Phase fault GORE 5 (505552) 161 kV Bus a. Apply fault at the GORE 5 (505552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161 KV 505552 TO WEBFALL5 161 KV 505554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GORE___5__WELEETK5 | 3 Phase fault GORE 5 (505552) 161 kV Bus a. Apply fault at the GORE 5 (505552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161 KV 505552 TO WELEETK5 161 KV 505590 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRACMNT4__ANADARK4 | 3 Phase fault GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138 KV 515802 TO ANADARK4 138 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRACMNT4__WASHITA4 | 3 Phase fault GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138 KV 515802 TO WASHITA4 138 KV 521089 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRACMNT7__G16 | 3 Phase fault GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345 KV 515800 TO G16-037-TAP 345 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRACMNT7__G16 | 3 Phase fault GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345 KV 515800 TO G16-091-TAP 345 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRACMNT7__GEN | 3 Phase fault GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345 KV 515800 TO GEN-2015-093 345 KV 563269 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRANNIS___2__DEQUEEN2 | 3 Phase fault GRANNIS 2 (504129) 69 kV Bus a. Apply fault at the GRANNIS 2 (504129) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANNIS 2 69 KV 504129 TO DEQUEEN2 69 KV 507418 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRAPEVINE__6__NICHOLS____6 | 3 Phase fault GRAPEVINE 6 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 230 KV 523771 TO NICHOLS 6 230 KV 524044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRAPEVINE__6__WHEELER____6 | 3 Phase fault GRAPEVINE 6 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 230 KV 523771 TO WHEELER 6 230 KV 523777 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA1__5__CHOUTEAUCRK5 | 3 Phase fault GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 161 KV 512656 TO CHOUTEAUCRK5 161 KV 513570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA1__5__MAID___5 | 3 Phase fault GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 161 KV 512656 TO WMAIN ST5 161 KV 512742 CKT 1 b.2. LOAD 1 512742 b.3. WMAIN ST5 161 KV 512742 TO NWMAID5 161 KV 512757 CKT 1 b.4. LOAD 1 512757 b.5. NWMAID5 161 KV 512757 TO GERALDGAY5 161 KV 512760 CKT 1 b.6. LOAD 1 512760 b.7. MAID 5 161 KV 512648 TO GERALDGAY5 161 KV 512760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA1__5__WAGNOR_5 | 3 Phase fault GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 161 KV 512656 TO WAGNOR 5 161 KV 512700 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA1__7__GREC_TAP5 | 3 Phase fault GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 345 KV 512650 TO GREC TAP5 345 KV 512865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA1__7__TONECE7 | 3 Phase fault GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 345 KV 512650 TO TONECE7 345 KV 512750 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDGVTP4__MEEKRSW4 | 3 Phase fault GRDGVTP4 (520526) 138 kV Bus a. Apply fault at the GRDGVTP4 (520526) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDGVTP4 138 KV 520526 TO MEEKRSW4 138 KV 520994 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GREAT_WESTRN__COWBOY_RIDGE | 3 Phase fault GREAT_WESTRN (585410) 345 kV Bus a. Apply fault at the GREAT_WESTRN (585410) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GREAT_WESTRN 345 KV 585410 TO COWBOY_RIDGE 345 KV 585420 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GREC_TAP5__IGLOOV_7 | 3 Phase fault GREC TAP5 (512865) 345 kV Bus a. Apply fault at the GREC TAP5 (512865) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GREC TAP5 345 KV 512865 TO IGLOOV 7 345 KV 513596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRTWSRN7__GUTHRIE7 | 3 Phase fault GRTWSRN7 (515825) 345 kV Bus a. Apply fault at the GRTWSRN7 (515825) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRTWSRN7 345 KV 515825 TO GUTHRIE7 345 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HAMMTAP4__HAMMETT4 | 3 Phase fault HAMMTAP4 (515046) 138 kV Bus a. Apply fault at the HAMMTAP4 (515046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMMTAP4 138 KV 515046 TO HAMMETT4 138 KV 520951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HAMMTAP4__LINCOLN4 | 3 Phase fault HAMMTAP4 (515046) 138 kV Bus a. Apply fault at the HAMMTAP4 (515046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMMTAP4 138 KV 515046 TO LINCOLN4 138 KV 515442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HARPER2__ANADARK2 | 3 Phase fault HARPER2 (520440) 69 kV Bus a. Apply fault at the HARPER2 (520440) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER2 69 KV 520440 TO ANADARK2 69 KV 520810 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HARRISN4__KNOXLEE4 | 3 Phase fault HARRISN4 (508544) 138 kV Bus a. Apply fault at the HARRISN4 (508544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRISN4 138 KV 508544 TO KNOXLEE4 138 KV 508548 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HARTSIS4__S_SHV__4 | 3 Phase fault HARTSIS4 (507735) 138 kV Bus a. Apply fault at the HARTSIS4 (507735) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARTSIS4 138 KV 507735 TO S SHV 4 138 KV 507755 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HEFNER_4__TENESTP4 | 3 Phase fault HEFNER 4 (514848) 138 kV Bus a. Apply fault at the HEFNER 4 (514848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILSHIR4 138 KV 514836 TO HEFNER 4 138 KV 514848 CKT 1 b.2. WILSHIR4 138 KV 514836 TO TENNESE4 138 KV 514838 CKT 1 b.3. LOAD 1 514838 b.4. TENESTP4 138 KV 514837 TO TENNESE4 138 KV 514838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HENESEY4__BULFTTP4 | 3 Phase fault HENESEY4 (514774) 138 kV Bus a. Apply fault at the HENESEY4 (514774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 138 KV 514774 TO BULFTTP4 138 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HENESEY4__DOVERSW4 | 3 Phase fault HENESEY4 (514774) 138 kV Bus a. Apply fault at the HENESEY4 (514774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 138 KV 514774 TO DOVERSW4 138 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HERRON_5__IGLOOV1_5 | 3 Phase fault HERRON 5 (513591) 161 kV Bus a. Apply fault at the HERRON 5 (513591) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HERRON 5 161 KV 513591 TO IGLOOV1 5 161 KV 513593 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HERRON_5__IGLOOV2_5 | 3 Phase fault HERRON 5 (513591) 161 kV Bus a. Apply fault at the HERRON 5 (513591) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HERRON 5 161 KV 513591 TO IGLOOV2 5 161 KV 513595 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HIGHLND4__PINK_SW4 | 3 Phase fault HIGHLND4 (520941) 138 kV Bus a. Apply fault at the HIGHLND4 (520941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGHLND4 138 KV 520941 TO PINK SW4 138 KV 521028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HLTOPTP__BEELINE2 | 3 Phase fault HLTOPTP (514200) 69 kV Bus a. Apply fault at the HLTOPTP (514200) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLTOPTP 69 KV 514200 TO BEELINE2 69 KV 515246 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HOB | 3 Phase fault HOB-JCT4 (511463) 138 kV Bus a. Apply fault at the HOB-JCT4 (511463) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT4 138 KV 511463 TO MARTHA 4 138 KV 511564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HOB | 3 Phase fault HOB-JCT4 (511463) 138 kV Bus a. Apply fault at the HOB-JCT4 (511463) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT4 138 KV 511463 TO RKY_RDG4 138 KV 511554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HOBBYLO4__CHEMTRN4 | 3 Phase fault HOBBYLO4 (515338) 138 kV Bus a. Apply fault at the HOBBYLO4 (515338) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBYLO4 138 KV 515338 TO CHEMTRN4 138 KV 515367 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HOCHJCT4__DOMINJCT4 | 3 Phase fault HOCHJCT4 (520823) 138 kV Bus a. Apply fault at the HOCHJCT4 (520823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOCHJCT4 138 KV 520823 TO DOMINJCT4 138 KV 521195 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HOCHJCT4__HOCHTWN4 | 3 Phase fault HOCHJCT4 (520823) 138 kV Bus a. Apply fault at the HOCHJCT4 (520823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOCHJCT4 138 KV 520823 TO HOCHTWN4 138 KV 520943 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HOLLYWD4__INDNHIL4 | 3 Phase fault HOLLYWD4 (514953) 138 kV Bus a. Apply fault at the HOLLYWD4 (514953) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLLYWD4 138 KV 514953 TO INDNHIL4 138 KV 514954 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HOOKS__2__LSORDTP2 | 3 Phase fault HOOKS 2 (508057) 69 kV Bus a. Apply fault at the HOOKS 2 (508057) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOKS 2 69 KV 508057 TO LSORDTP2 69 KV 508063 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HOOKS__2__REDRVR | 3 Phase fault HOOKS 2 (508057) 69 kV Bus a. Apply fault at the HOOKS 2 (508057) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOKS 2 69 KV 508057 TO REDRVR-2 69 KV 508074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HOPESWI3__HOPE___3 | 3 Phase fault HOPESWI3 (507452) 115 kV Bus a. Apply fault at the HOPESWI3 (507452) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOPESWI3 115 KV 507452 TO HOPE 3 115 KV 507453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HSLEAST2__DEEPFKT2 | 3 Phase fault HSLEAST2 (514927) 69 kV Bus a. Apply fault at the HSLEAST2 (514927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69 KV 514927 TO GRNPAST2 69 KV 514971 CKT 1 b.2. LOAD 1 514971 b.3. DEEPFKT2 69 KV 514970 TO GRNPAST2 69 KV 514971 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HSLEAST2__HSLWEST2 | 3 Phase fault HSLEAST2 (514927) 69 kV Bus a. Apply fault at the HSLEAST2 (514927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69 KV 514927 TO HSLWEST2 69 KV 514937 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HSLEAST2__MCLOUDT2 | 3 Phase fault HSLEAST2 (514927) 69 kV Bus a. Apply fault at the HSLEAST2 (514927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69 KV 514927 TO MCLOUDT2 69 KV 515504 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HSLEAST2__TXSTELA2 | 3 Phase fault HSLEAST2 (514927) 69 kV Bus a. Apply fault at the HSLEAST2 (514927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69 KV 514927 TO TXSTELA2 69 KV 514985 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HSL____4__GEN | 3 Phase fault HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138 KV 514941 TO GEN-2018-029 138 KV 762647 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HSL____4__HAMMTAP4 | 3 Phase fault HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138 KV 514941 TO HAMMTAP4 138 KV 515046 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HSL____4__JONESSB4 | 3 Phase fault HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138 KV 514941 TO JONESSB4 138 KV 515480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HSL____4__RENO___4 | 3 Phase fault HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138 KV 514941 TO MIDWAY 4 138 KV 514966 CKT 1 b.2. LOAD 1 514966 b.3. NE10TH 4 138 KV 514964 TO MIDWAY 4 138 KV 514966 CKT 1 b.4. LOAD 1 514966 b.5. NE10TH 4 138 KV 514964 TO RENO 4 138 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HSL____4__SE15TH_4 | 3 Phase fault HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138 KV 514941 TO SE15TH 4 138 KV 514993 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HSL____4__SQUIRCK4 | 3 Phase fault HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138 KV 514941 TO DALE 4 138 KV 514987 CKT 1 b.2. LOAD 1 514987 b.3. DALE 4 138 KV 514987 TO SQUIRCK4 138 KV 515059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HUGO | 3 Phase fault HUGO---4 (510901) 138 kV Bus a. Apply fault at the HUGO---4 (510901) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGO---4 138 KV 510901 TO VALIANT4 138 KV 510918 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HUGOITC4__HUGO_PP4 | 3 Phase fault HUGOITC4 (520560) 138 kV Bus a. Apply fault at the HUGOITC4 (520560) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOITC4 138 KV 520560 TO HUGO PP4 138 KV 520948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HUGO_PP4__GEN | 3 Phase fault HUGO PP4 (520948) 138 kV Bus a. Apply fault at the HUGO PP4 (520948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGO PP4 138 KV 520948 TO GEN-2017-023 138 KV 588670 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HUGO_PP4__VALLANT4 | 3 Phase fault HUGO PP4 (520948) 138 kV Bus a. Apply fault at the HUGO PP4 (520948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGO PP4 138 KV 520948 TO VALLANT4 138 KV 521079 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HUGO___7__G17 | 3 Phase fault HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 345 KV 521157 TO G17-075-TAP 345 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HUNTERS7__CHSHLMV7 | 3 Phase fault HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 345 KV 515476 TO CHSHLMV7 345 KV 515477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HUNTERS7__RENFROW7 | 3 Phase fault HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 345 KV 515476 TO RENFROW7 345 KV 515543 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HWY20 | 3 Phase fault HWY20-T4 (509821) 138 kV Bus a. Apply fault at the HWY20-T4 (509821) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HWY20-T4 138 KV 509821 TO WLDCT_HIL4 138 KV 509897 CKT 1 b.2. LOAD 1 509897 b.3. HWY20--4 138 KV 509798 TO WLDCT_HIL4 138 KV 509897 CKT 1 b.4. LOAD 1 509897 b.5. HWY20--4 138 KV 509798 TO OMHOMNY4 138 KV 529306 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_INOLATP4__CATOOSA4 | 3 Phase fault INOLATP4 (509752) 138 kV Bus a. Apply fault at the INOLATP4 (509752) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INOLATP4 138 KV 509752 TO CATOOSA4 138 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_INOLATP4__EXCLART4 | 3 Phase fault INOLATP4 (509752) 138 kV Bus a. Apply fault at the INOLATP4 (509752) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INOLATP4 138 KV 509752 TO ROCKPT-4 138 KV 510437 CKT 1 b.2. LOAD 1 510437 b.3. CHOUTEA4 138 KV 510373 TO ROCKPT-4 138 KV 510437 CKT 1 b.4. LOAD 1 510437 b.5. CHOUTEA4 138 KV 510373 TO EXCLART4 138 KV 510401 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_INOLA__4__INOLATP4 | 3 Phase fault INOLA 4 (509736) 138 kV Bus a. Apply fault at the INOLA 4 (509736) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INOLA 4 138 KV 509736 TO INOLATP4 138 KV 509752 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_IODINE_4__MOORLND4 | 3 Phase fault IODINE 4 (520957) 138 kV Bus a. Apply fault at the IODINE 4 (520957) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IODINE 4 138 KV 520957 TO MOORLND4 138 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_IPC_TAP2__IPC____2 | 3 Phase fault IPC TAP2 (508058) 69 kV Bus a. Apply fault at the IPC TAP2 (508058) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC TAP2 69 KV 508058 TO IPC 2 69 KV 508092 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_IPC_T__4__CASSTP4 | 3 Phase fault IPC T 4 (508059) 138 kV Bus a. Apply fault at the IPC T 4 (508059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138 KV 508059 TO CASSTP4 138 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_IPC_T__4__IPC____4 | 3 Phase fault IPC T 4 (508059) 138 kV Bus a. Apply fault at the IPC T 4 (508059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138 KV 508059 TO IPC 4 138 KV 508095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_JEFFRSN4__LAKEPIN4 | 3 Phase fault JEFFRSN4 (508835) 138 kV Bus a. Apply fault at the JEFFRSN4 (508835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138 KV 508835 TO LAKEPIN4 138 KV 509624 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_JEFFRSN4__WILKES_4 | 3 Phase fault JEFFRSN4 (508835) 138 kV Bus a. Apply fault at the JEFFRSN4 (508835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138 KV 508835 TO WILKES 4 138 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_JENSENT4__CIMARON4 | 3 Phase fault JENSENT4 (514820) 138 kV Bus a. Apply fault at the JENSENT4 (514820) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSENT4 138 KV 514820 TO CIMARON4 138 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_JENSENT4__JENSEN_4 | 3 Phase fault JENSENT4 (514820) 138 kV Bus a. Apply fault at the JENSENT4 (514820) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSENT4 138 KV 514820 TO JENSEN 4 138 KV 514821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_JENSEN_4__EL_RENO4 | 3 Phase fault JENSEN 4 (514821) 138 kV Bus a. Apply fault at the JENSEN 4 (514821) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSEN 4 138 KV 514821 TO EL RENO4 138 KV 520893 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_JNSKAMO4__ARCADIA4 | 3 Phase fault JNSKAMO4 (514906) 138 kV Bus a. Apply fault at the JNSKAMO4 (514906) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 138 KV 514906 TO ARCADIA4 138 KV 514907 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_JNSKAMO4__HSL____4 | 3 Phase fault JNSKAMO4 (514906) 138 kV Bus a. Apply fault at the JNSKAMO4 (514906) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 138 KV 514906 TO HSL 4 138 KV 514941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_JOHNCO_4__CANEYCK4 | 3 Phase fault JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138 KV 514808 TO CANEYCK4 138 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_JOHNCO_4__RUSSET | 3 Phase fault JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138 KV 514808 TO RUSSET-4 138 KV 515120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_JOHNCO_4__SXMLCKT4 | 3 Phase fault JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138 KV 514808 TO SXMLCKT4 138 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_JOHNCO_7__DMNDSPG7 | 3 Phase fault JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345 KV 514809 TO DMNDSPG7 345 KV 516006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_JOHNCO_7__GEN | 3 Phase fault JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345 KV 514809 TO GEN-2017-149 345 KV 760830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_JOHNCO_7__SUNNYSD7 | 3 Phase fault JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345 KV 514809 TO SUNNYSD7 345 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_JONESSB4__LGARBER4 | 3 Phase fault JONESSB4 (515480) 138 kV Bus a. Apply fault at the JONESSB4 (515480) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHTWOOD4 138 KV 514842 TO JONESSB4 138 KV 515480 CKT 1 b.2. CHTWOOD4 138 KV 514842 TO LGARBER4 138 KV 515465 CKT 1 b.3. LOAD 1 515465 b.4. ARCADIA4 138 KV 514907 TO LGARBER4 138 KV 515465 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_KANSATP5__KANSAS_5 | 3 Phase fault KANSATP5 (512714) 161 kV Bus a. Apply fault at the KANSATP5 (512714) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KANSATP5 161 KV 512714 TO KANSAS 5 161 KV 512716 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_KELLYAV4__MEMRIAL4 | 3 Phase fault KELLYAV4 (514501) 138 kV Bus a. Apply fault at the KELLYAV4 (514501) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLYAV4 138 KV 514501 TO MEMRIAL4 138 KV 514835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_KENSH | 3 Phase fault KENSH-E4 (509744) 138 kV Bus a. Apply fault at the KENSH-E4 (509744) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENSH-E4 138 KV 509744 TO ZUNIS-N4 138 KV 509827 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_KENTUKT2__44&SUNL2 | 3 Phase fault KENTUKT2 (514977) 69 kV Bus a. Apply fault at the KENTUKT2 (514977) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENTUKT2 69 KV 514977 TO SAGE 2 69 KV 514978 CKT 1 b.2. LOAD 1 514978 b.3. SAGE 2 69 KV 514978 TO 44&SUNL2 69 KV 514979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_KERR_GR5__KANSATP5 | 3 Phase fault KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161 KV 512635 TO 412SUB 5 161 KV 512637 CKT 1 b.2. LOAD 1 512637 b.3. 412SUB 5 161 KV 512637 TO KANSATP5 161 KV 512714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_KERR_GR5__KERR_BRK1_5 | 3 Phase fault KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161 KV 512635 TO KERR BRK1 5 161 KV 512770 CKT Z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_KERR_GR5__MAID___5 | 3 Phase fault KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161 KV 512635 TO MAID 5 161 KV 512648 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_KERR_GR5__PENSA__5 | 3 Phase fault KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161 KV 512635 TO PENSA 5 161 KV 512654 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_KERR_GR5__SALNCRK5 | 3 Phase fault KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161 KV 512635 TO SALNCRK5 161 KV 512805 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_KETCHTP4__KETCH__4 | 3 Phase fault KETCHTP4 (514828) 138 kV Bus a. Apply fault at the KETCHTP4 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 138 KV 514828 TO KETCH 4 138 KV 514834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_KETCHTP4__NORTWST4 | 3 Phase fault KETCHTP4 (514828) 138 kV Bus a. Apply fault at the KETCHTP4 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 138 KV 514828 TO NORTWST4 138 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_KETCH__4__FAIRFLD4 | 3 Phase fault KETCH 4 (514834) 138 kV Bus a. Apply fault at the KETCH 4 (514834) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCH 4 138 KV 514834 TO FAIRFLD4 138 KV 515468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_KEYSTON4__WEKIWA | 3 Phase fault KEYSTON4 (505610) 138 kV Bus a. Apply fault at the KEYSTON4 (505610) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON4 138 KV 505610 TO WEKIWA-4 138 KV 509757 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_KGFSHSW4__CALUMET4 | 3 Phase fault KGFSHSW4 (520533) 138 kV Bus a. Apply fault at the KGFSHSW4 (520533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSHSW4 138 KV 520533 TO CONCHO 4 138 KV 520865 CKT 1 b.2. LOAD 1 520865 b.3. CALUMET4 138 KV 520839 TO CONCHO 4 138 KV 520865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_KGFSHSW4__CMBLTP_4 | 3 Phase fault KGFSHSW4 (520533) 138 kV Bus a. Apply fault at the KGFSHSW4 (520533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSHSW4 138 KV 520533 TO REEDING4 138 KV 521037 CKT 1 b.2. LOAD 1 521037 b.3. CMBLTP 4 138 KV 520474 TO REEDING4 138 KV 521037 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_KGFSHSW4__EKFSHTP4 | 3 Phase fault KGFSHSW4 (520533) 138 kV Bus a. Apply fault at the KGFSHSW4 (520533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSHSW4 138 KV 520533 TO EKFSHTP4 138 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_KGFSJCT4__EKFSHTP4 | 3 Phase fault KGFSJCT4 (520405) 138 kV Bus a. Apply fault at the KGFSJCT4 (520405) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSJCT4 138 KV 520405 TO EKFSHTP4 138 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_KINZEGR4__KINZE__4 | 3 Phase fault KINZEGR4 (512710) 138 kV Bus a. Apply fault at the KINZEGR4 (512710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZEGR4 138 KV 512710 TO KINZE 4 138 KV 515008 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_KINZE__4__UNVRSTY4 | 3 Phase fault KINZE 4 (515008) 138 kV Bus a. Apply fault at the KINZE 4 (515008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZE 4 138 KV 515008 TO UNVRSTY4 138 KV 515181 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_KIPUMPT2__FTOWSON2 | 3 Phase fault KIPUMPT2 (510876) 69 kV Bus a. Apply fault at the KIPUMPT2 (510876) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KIPUMPT2 69 KV 510876 TO FTOWSON2 69 KV 510917 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_KIPUMPT2__VALIANT2 | 3 Phase fault KIPUMPT2 (510876) 69 kV Bus a. Apply fault at the KIPUMPT2 (510876) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KIPUMPT2 69 KV 510876 TO VALIANT2 69 KV 510910 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_KI_PMPN2__KIPUMPT2 | 3 Phase fault KI PMPN2 (510875) 69 kV Bus a. Apply fault at the KI PMPN2 (510875) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KI PMPN2 69 KV 510875 TO KIPUMPT2 69 KV 510876 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_KNGFSHR7__FSHRTAP7 | 3 Phase fault KNGFSHR7 (515600) 345 kV Bus a. Apply fault at the KNGFSHR7 (515600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KNGFSHR7 345 KV 515600 TO FSHRTAP7 345 KV 515610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_KNOBHIL4__DGRASSE4 | 3 Phase fault KNOBHIL4 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 138 KV 514795 TO DGRASSE4 138 KV 515853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_KNOXLEE4__BRANDYBR | 3 Phase fault KNOXLEE4 (508548) 138 kV Bus a. Apply fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138 KV 508548 TO BRANDYBR 138 KV 508596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_KNOXLEE4__CHEROKE4 | 3 Phase fault KNOXLEE4 (508548) 138 kV Bus a. Apply fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138 KV 508548 TO CHEROKE4 138 KV 509059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_KNOXLEE4__MONROER4 | 3 Phase fault KNOXLEE4 (508548) 138 kV Bus a. Apply fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138 KV 508548 TO MONROER4 138 KV 509073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_KNOXLEE4__OAK2HIL4 | 3 Phase fault KNOXLEE4 (508548) 138 kV Bus a. Apply fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138 KV 508548 TO OAK2HIL4 138 KV 509078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_KNOXLEE4__SOTXEST4 | 3 Phase fault KNOXLEE4 (508548) 138 kV Bus a. Apply fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138 KV 508548 TO SOTXEST4 138 KV 508570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_L.E.S._LGOREN2 | 3 Phase fault L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69 KV 511466 TO LGORE-N2 69 KV 511469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_L.E.S._LGORES2 | 3 Phase fault L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69 KV 511466 TO LGORE-S2 69 KV 511470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_L.E.S._ARTVLTP4 | 3 Phase fault L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138 KV 511467 TO SHERID4 138 KV 511474 CKT 1 b.2. LOAD 1 511474 b.3. SHERID4 138 KV 511474 TO ARTVLTP4 138 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_L.E.S._COMMTAP4 | 3 Phase fault L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138 KV 511467 TO COMMTAP4 138 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_L.E.S._ELGINJT4 | 3 Phase fault L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138 KV 511467 TO ELGINJT4 138 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_L.E.S._SHERID4 | 3 Phase fault L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138 KV 511467 TO SHERID4 138 KV 511474 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_L.E.S._G16-091-TAP | 3 Phase fault L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345 KV 511468 TO G16-091-TAP 345 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_L.E.S._G17-171-TAP | 3 Phase fault L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345 KV 511468 TO G17-171-TAP 345 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LEASIDE_4__LOGANSP4 | 3 Phase fault LEASIDE 4 (507793) 138 kV Bus a. Apply fault at the LEASIDE 4 (507793) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEASIDE 4 138 KV 507793 TO STONWAL4 138 KV 509052 CKT 1 b.2. LOAD 1 509052 b.3. KEATCHI4 138 KV 509050 TO STONWAL4 138 KV 509052 CKT 1 b.4. LOAD 1 509052 b.5. KEATCHI4 138 KV 509050 TO GEORPAC4 138 KV 509064 CKT 1 b.6. GEORPAC4 138 KV 509064 TO LOGANSP4 138 KV 509071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LEONARD4__MLCLMRD4 | 3 Phase fault LEONARD4 (511575) 138 kV Bus a. Apply fault at the LEONARD4 (511575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEONARD4 138 KV 511575 TO MLCLMRD4 138 KV 515933 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LGYEAR_112GORE | 3 Phase fault LG-YEAR4 (511428) 138 kV Bus a. Apply fault at the LG-YEAR4 (511428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-YEAR4 138 KV 511428 TO 112GORE4 138 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LIEBERM2__OILCITY2 | 3 Phase fault LIEBERM2 (508805) 69 kV Bus a. Apply fault at the LIEBERM2 (508805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM2 69 KV 508805 TO OILCITY2 69 KV 508812 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LIEBERM4__G16 | 3 Phase fault LIEBERM4 (508806) 138 kV Bus a. Apply fault at the LIEBERM4 (508806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138 KV 508806 TO G16-167-TAP 138 KV 588404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LIEBERM4__JEFFRSN4 | 3 Phase fault LIEBERM4 (508806) 138 kV Bus a. Apply fault at the LIEBERM4 (508806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138 KV 508806 TO IPCJEFF4 138 KV 508833 CKT 1 b.2. LOAD 1 508833 b.3. IPCJEFF4 138 KV 508833 TO JEFFRSN4 138 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LIEBERM4__LONGWD_4 | 3 Phase fault LIEBERM4 (508806) 138 kV Bus a. Apply fault at the LIEBERM4 (508806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138 KV 508806 TO LONGWD 4 138 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LINCOLN4__MEEKRSW4 | 3 Phase fault LINCOLN4 (515442) 138 kV Bus a. Apply fault at the LINCOLN4 (515442) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINCOLN4 138 KV 515442 TO MEEKER 4 138 KV 520464 CKT 1 b.2. LOAD 1 520464 b.3. MEEKER 4 138 KV 520464 TO MEEKRSW4 138 KV 520994 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LINCOLN4__WOLVRNT4 | 3 Phase fault LINCOLN4 (515442) 138 kV Bus a. Apply fault at the LINCOLN4 (515442) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JACKTWN4 138 KV 515051 TO LINCOLN4 138 KV 515442 CKT 1 b.2. JACKTWN4 138 KV 515051 TO WOLVRNT4 138 KV 515532 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LINTNRD4__NBENTON4 | 3 Phase fault LINTNRD4 (508807) 138 kV Bus a. Apply fault at the LINTNRD4 (508807) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINTNRD4 138 KV 508807 TO NBENTON4 138 KV 508811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LINWOOD4__POWELL_4 | 3 Phase fault LINWOOD4 (507738) 138 kV Bus a. Apply fault at the LINWOOD4 (507738) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINWOOD4 138 KV 507738 TO POWELL 4 138 KV 507748 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LITTLAX2__LITLAXT2 | 3 Phase fault LITTLAX2 (514951) 69 kV Bus a. Apply fault at the LITTLAX2 (514951) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTLAX2 69 KV 514951 TO LITLAXT2 69 KV 515502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LLANE_LLANET | 3 Phase fault LLANE-E4 (509728) 138 kV Bus a. Apply fault at the LLANE-E4 (509728) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LLANE-E4 138 KV 509728 TO LLAN ET4 138 KV 509771 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LLANE_LLANWT | 3 Phase fault LLANE-W4 (509720) 138 kV Bus a. Apply fault at the LLANE-W4 (509720) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LLANE-W4 138 KV 509720 TO LLAN WT4 138 KV 509770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LLAN_ET4__CATOOSA4 | 3 Phase fault LLAN ET4 (509771) 138 kV Bus a. Apply fault at the LLAN ET4 (509771) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LLAN ET4 138 KV 509771 TO CATOOSA4 138 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LLAN_WT4__DAWSONT4 | 3 Phase fault LLAN WT4 (509770) 138 kV Bus a. Apply fault at the LLAN WT4 (509770) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LLAN WT4 138 KV 509770 TO DAWSONT4 138 KV 509803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LLAN_WT4__LLANETP4 | 3 Phase fault LLAN WT4 (509770) 138 kV Bus a. Apply fault at the LLAN WT4 (509770) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LLAN WT4 138 KV 509770 TO LLANETP4 138 KV 509804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LNEOAK_4__NORTWST4 | 3 Phase fault LNEOAK 4 (514873) 138 kV Bus a. Apply fault at the LNEOAK 4 (514873) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNEOAK 4 138 KV 514873 TO NORTWST4 138 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LOCKESB2__NASHVIL2 | 3 Phase fault LOCKESB2 (507422) 69 kV Bus a. Apply fault at the LOCKESB2 (507422) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOCKESB2 69 KV 507422 TO NASHVIL2 69 KV 507426 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LONEGRV4__CHEEKTP4 | 3 Phase fault LONEGRV4 (515144) 138 kV Bus a. Apply fault at the LONEGRV4 (515144) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONEGRV4 138 KV 515144 TO CHEEKTP4 138 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LONGVHT4__WHITNEY4 | 3 Phase fault LONGVHT4 (508554) 138 kV Bus a. Apply fault at the LONGVHT4 (508554) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGVHT4 138 KV 508554 TO WHITNEY4 138 KV 508575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LONGWD_4__FLOURNY4 | 3 Phase fault LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 138 KV 508808 TO OAKPH 4 138 KV 508816 CKT 1 b.2. LOAD 1 508816 b.3. FLOURNY4 138 KV 507727 TO OAKPH 4 138 KV 508816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LONGWD_4__RAINES_4 | 3 Phase fault LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORAM 4 138 KV 507774 TO LONGWD 4 138 KV 508808 CKT 1 b.2. RAINES 4 138 KV 507749 TO NORAM 4 138 KV 507774 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LONGWD_4__SABMINT4 | 3 Phase fault LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SABMINT4 138 KV 508566 TO SEMRSHL4 138 KV 508569 CKT 1 b.2. LOAD 1 508569 b.3. SCOTTSV4 138 KV 508567 TO SEMRSHL4 138 KV 508569 CKT 1 b.4. LOAD 1 508569 b.5. SCOTTSV4 138 KV 508567 TO LONGWD 4 138 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LONGWD_7__GEN | 3 Phase fault LONGWD 7 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345 KV 508809 TO GEN-2018-050 345 KV 762845 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LONGWD_7__WILKES_7 | 3 Phase fault LONGWD 7 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345 KV 508809 TO WILKES 7 345 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LSORDTP2__LSORD__2 | 3 Phase fault LSORDTP2 (508063) 69 kV Bus a. Apply fault at the LSORDTP2 (508063) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSORDTP2 69 KV 508063 TO LSORD 2 69 KV 508093 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LSSOUTH4__DIANA__4 | 3 Phase fault LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138 KV 508297 TO DIANA 4 138 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LSSOUTH4__PITTSB_4 | 3 Phase fault LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138 KV 508297 TO PITTSB_4 138 KV 508313 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LSSOUTH4__WILKES_4 | 3 Phase fault LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138 KV 508297 TO WILKES 4 138 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LTLRLKT2__TXPLSTP2 | 3 Phase fault LTLRLKT2 (514983) 69 kV Bus a. Apply fault at the LTLRLKT2 (514983) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LTLRLKT2 69 KV 514983 TO TXPLSTP2 69 KV 515516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LWS_112GORE | 3 Phase fault LWS-NTP4 (511471) 138 kV Bus a. Apply fault at the LWS-NTP4 (511471) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS-NTP4 138 KV 511471 TO 112GORE4 138 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LWSTAP_4__L.E.S. | 3 Phase fault LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138 KV 511439 TO L.E.S.-4 138 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LWSTAP_4__RPPAPER4 | 3 Phase fault LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138 KV 511439 TO RPPAPER4 138 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LWS___S4__LWSTAP_4 | 3 Phase fault LWS S4 (511431) 138 kV Bus a. Apply fault at the LWS S4 (511431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS S4 138 KV 511431 TO LWSTAP 4 138 KV 511439 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LYDIA__7__VALIANT7 | 3 Phase fault LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345 KV 508298 TO VALIANT7 345 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LYDIA__7__WELSH__7 | 3 Phase fault LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345 KV 508298 TO WELSH 7 345 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MACOCTP2__LITLAXT2 | 3 Phase fault MACOCTP2 (514956) 69 kV Bus a. Apply fault at the MACOCTP2 (514956) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MACOCTP2 69 KV 514956 TO LITLAXT2 69 KV 515502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MAIDTP2__GRDA1_2 | 3 Phase fault MAIDTP2 (512625) 69 kV Bus a. Apply fault at the MAIDTP2 (512625) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIDTP2 69 KV 512625 TO GRDA1 2 69 KV 512727 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MAID___2__AMERCAST_S2 | 3 Phase fault MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 69 KV 512626 TO AMERCAST S2 69 KV 512681 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MAID___2__REDDEN_2 | 3 Phase fault MAID 2 (512626) 69 kV Bus a. Apply fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 69 KV 512626 TO REDDEN 2 69 KV 512698 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MAID___5__5CDRCRST | 3 Phase fault MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 161 KV 512648 TO LOCSTGVKM 5 161 KV 513050 CKT 1 b.2. LOAD 1 513050 b.3. 5CDRCRST 161 KV 301344 TO LOCSTGVKM 5 161 KV 513050 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MAID___5__GERALDGAY5 | 3 Phase fault MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 161 KV 512648 TO GERALDGAY5 161 KV 512760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MAID___5__GRDA1__5 | 3 Phase fault MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 161 KV 512648 TO GRDA1 5 161 KV 512656 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MAID___5__PENSA__5 | 3 Phase fault MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 161 KV 512629 TO MAID 5 161 KV 512648 CKT 1 b.2. DRYGULCH5 161 KV 512629 TO PENSA 5 161 KV 512654 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MARSHL_JEFFRSN | 3 Phase fault MARSHL-4 (508557) 138 kV Bus a. Apply fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138 KV 508557 TO JEFFRSN4 138 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MARSHL_PIRKEY | 3 Phase fault MARSHL-4 (508557) 138 kV Bus a. Apply fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138 KV 508557 TO PIRKEY 4 138 KV 508562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MARSHL_4__CTNWOOD4 | 3 Phase fault MARSHL 4 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138 KV 514733 TO CTNWOOD4 138 KV 514827 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MARSHL_4__MARSHAL4 | 3 Phase fault MARSHL 4 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138 KV 514733 TO MARSHAL4 138 KV 521006 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MATHWSN7__REDNGTN7 | 3 Phase fault MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345 KV 515497 TO REDNGTN7 345 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MATHWSN7__TRAVERSE3 | 3 Phase fault MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345 KV 515497 TO TRAVERSE3 345 KV 900001 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MAUDT__2__REDWATR2 | 3 Phase fault MAUDT 2 (509653) 69 kV Bus a. Apply fault at the MAUDT 2 (509653) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUDT 2 69 KV 509653 TO REDWATR2 69 KV 509667 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MAUD___2__ERLSBOR2 | 3 Phase fault MAUD 2 (515054) 69 kV Bus a. Apply fault at the MAUD 2 (515054) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 2 69 KV 515054 TO ERLSBOR2 69 KV 515073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MAUD___2__KNAWATP2 | 3 Phase fault MAUD 2 (515054) 69 kV Bus a. Apply fault at the MAUD 2 (515054) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 2 69 KV 515054 TO KNAWATP2 69 KV 515496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MAUD___2__LTRIVRT2 | 3 Phase fault MAUD 2 (515054) 69 kV Bus a. Apply fault at the MAUD 2 (515054) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 2 69 KV 515054 TO LTRIVRT2 69 KV 515503 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MAUD___4__FIXCT4 | 3 Phase fault MAUD 4 (515055) 138 kV Bus a. Apply fault at the MAUD 4 (515055) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EARLSBORO 4 138 KV 510948 TO MAUD 4 138 KV 515055 CKT 1 b.2. FIXCT4 138 KV 510877 TO EARLSBORO 4 138 KV 510948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MAUD___4__FRSTHIL4 | 3 Phase fault MAUD 4 (515055) 138 kV Bus a. Apply fault at the MAUD 4 (515055) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 4 138 KV 515055 TO FRSTHIL4 138 KV 515075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MAYO_LLANET | 3 Phase fault MAYO--N4 (509779) 138 kV Bus a. Apply fault at the MAYO--N4 (509779) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYO--N4 138 KV 509779 TO E41ST_W4 138 KV 509886 CKT 1 b.2. LOAD 1 509886 b.3. LLAN ET4 138 KV 509771 TO E41ST_W4 138 KV 509886 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MAYO_BANNTP4 | 3 Phase fault MAYO--S4 (509780) 138 kV Bus a. Apply fault at the MAYO--S4 (509780) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYO--S4 138 KV 509780 TO BANNTAP4 138 KV 509785 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MCALEST4__TALAWANDA__4 | 3 Phase fault MCALEST4 (510908) 138 kV Bus a. Apply fault at the MCALEST4 (510908) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCALEST4 138 KV 510908 TO TALAWANDA 4 138 KV 510951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MCALESTIND_4__TALAWANDA__4 | 3 Phase fault MCALESTIND 4 (510909) 138 kV Bus a. Apply fault at the MCALESTIND 4 (510909) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCALESTIND 4 138 KV 510909 TO TALAWANDA 4 138 KV 510951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MCCLAIN4__NORMHLL4 | 3 Phase fault MCCLAIN4 (514902) 138 kV Bus a. Apply fault at the MCCLAIN4 (514902) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCLAIN4 138 KV 514902 TO NORMHLL4 138 KV 516097 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MCLOUDT2__SINCPNT2 | 3 Phase fault MCLOUDT2 (515504) 69 kV Bus a. Apply fault at the MCLOUDT2 (515504) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCLOUDT2 69 KV 515504 TO SINCPNT2 69 KV 515642 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MCLOUD_2__MCLOUDT2 | 3 Phase fault MCLOUD 2 (515065) 69 kV Bus a. Apply fault at the MCLOUD 2 (515065) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCLOUD 2 69 KV 515065 TO MCLOUDT2 69 KV 515504 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MEEKRSW4__WREDHIL4 | 3 Phase fault MEEKRSW4 (520994) 138 kV Bus a. Apply fault at the MEEKRSW4 (520994) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEEKRSW4 138 KV 520994 TO WREDHIL4 138 KV 521097 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MEMRIAL4__DANFRTH4 | 3 Phase fault MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTERN4 138 KV 514832 TO MEMRIAL4 138 KV 514835 CKT 1 b.2. LOAD 1 514835 b.3. EASTERN4 138 KV 514832 TO HAFERSB4 138 KV 515469 CKT 1 b.4. LOAD 1 515469 b.5. DANFRTH4 138 KV 514833 TO HAFERSB4 138 KV 515469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MEMRIAL4__JONESSB4 | 3 Phase fault MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138 KV 514835 TO BRYANT 4 138 KV 514839 CKT 1 b.2. LOAD 1 514839 b.3. BRYANT 4 138 KV 514839 TO ACORN 4 138 KV 515459 CKT 1 b.4. LOAD 1 515459 b.5. ACORN 4 138 KV 515459 TO JONESSB4 138 KV 515480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MEMRIAL4__REMPKTP4 | 3 Phase fault MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLYAV4 138 KV 514501 TO MEMRIAL4 138 KV 514835 CKT 1 b.2. LOAD 1 514835 b.3. KELLYAV4 138 KV 514501 TO REMPKTP4 138 KV 514872 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MEMRIAL4__SKYLINE4 | 3 Phase fault MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138 KV 514835 TO SKYLINE4 138 KV 514850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MEMRIAL4__TENESTP4 | 3 Phase fault MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138 KV 514835 TO TENESTP4 138 KV 514837 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MENOTAP4__IMO____4 | 3 Phase fault MENOTAP4 (514789) 138 kV Bus a. Apply fault at the MENOTAP4 (514789) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENOTAP4 138 KV 514789 TO IMO 4 138 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MIDWEST4__FRNKLNS4 | 3 Phase fault MIDWEST4 (514946) 138 kV Bus a. Apply fault at the MIDWEST4 (514946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWEST4 138 KV 514946 TO FRNKLNS4 138 KV 520917 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MIDWEST4__HOLLYWD4 | 3 Phase fault MIDWEST4 (514946) 138 kV Bus a. Apply fault at the MIDWEST4 (514946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWEST4 138 KV 514946 TO HOLLYWD4 138 KV 514953 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MINCO__7__CIMARON7 | 3 Phase fault MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345 KV 514801 TO CIMARON7 345 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MINCO__7__GEN-2017-233 | 3 Phase fault MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345 KV 514801 TO GEN-2017-233 345 KV 761250 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MINCO__7__GRACMNT7 | 3 Phase fault MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345 KV 514801 TO GRACMNT7 345 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MINCO__7__MCNOWND7 | 3 Phase fault MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345 KV 514801 TO MCNOWND7 345 KV 515444 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MINCO__7__MNCWND37 | 3 Phase fault MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345 KV 514801 TO MNCWND37 345 KV 515549 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MINCO__7__NORMHLL7 | 3 Phase fault MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345 KV 514801 TO NORMHLL7 345 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MINGO_21STTAP | 3 Phase fault MINGO-N4 (509760) 138 kV Bus a. Apply fault at the MINGO-N4 (509760) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGO-N4 138 KV 509760 TO 21STTAP4 138 KV 509828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MINGO_MAYON4 | 3 Phase fault MINGO-N4 (509760) 138 kV Bus a. Apply fault at the MINGO-N4 (509760) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGO-N4 138 KV 509760 TO MAYO--N4 138 KV 509779 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MINGO_MAYOS4 | 3 Phase fault MINGO-S4 (509761) 138 kV Bus a. Apply fault at the MINGO-S4 (509761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGO-S4 138 KV 509761 TO MAYO--S4 138 KV 509780 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MINGO_TSE4 | 3 Phase fault MINGO-S4 (509761) 138 kV Bus a. Apply fault at the MINGO-S4 (509761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGO-S4 138 KV 509761 TO T.S.E.-4 138 KV 509811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MINGORD4__CATOOSA4 | 3 Phase fault MINGORD4 (509802) 138 kV Bus a. Apply fault at the MINGORD4 (509802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSN-N4 138 KV 509787 TO MINGORD4 138 KV 509802 CKT 1 b.2. LOAD 1 509802 b.3. DAWSN-N4 138 KV 509787 TO 141PINE4 138 KV 509892 CKT 1 b.4. LOAD 1 509892 b.5. SPNKY CK4 138 KV 509722 TO 141PINE4 138 KV 509892 CKT 1 b.6. LOAD 1 509892 b.7. SPNKY CK4 138 KV 509722 TO CATOOSA4 138 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MOORE__2__FRNKLNS2 | 3 Phase fault MOORE 2 (520489) 69 kV Bus a. Apply fault at the MOORE 2 (520489) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE 2 69 KV 520489 TO FRNKLNS2 69 KV 520916 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MOORLND4__GEN-2016-020 | 3 Phase fault MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND4 138 KV 520999 TO GEN-2016-020 138 KV 587140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MOUNDRD4__ELIZACK4 | 3 Phase fault MOUNDRD4 (510395) 138 kV Bus a. Apply fault at the MOUNDRD4 (510395) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUNDRD4 138 KV 510395 TO ELIZACK4 138 KV 510435 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MRIETA_2__ROCKYPT4 | 3 Phase fault MRIETA 2 (515160) 138 kV Bus a. Apply fault at the MRIETA 2 (515160) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 2 138 KV 515160 TO ROCKYPT4 138 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MSKPORT5__MSKPTAP5 | 3 Phase fault MSKPORT5 (515184) 161 kV Bus a. Apply fault at the MSKPORT5 (515184) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSKPORT5 161 KV 515184 TO MSKPTAP5 161 KV 515232 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MSKPTAP5__EUCLID_5 | 3 Phase fault MSKPTAP5 (515232) 161 kV Bus a. Apply fault at the MSKPTAP5 (515232) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSKPTAP5 161 KV 515232 TO EUCLID 5 161 KV 515251 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MUNZCTY4__DUGLASV4 | 3 Phase fault MUNZCTY4 (508064) 138 kV Bus a. Apply fault at the MUNZCTY4 (508064) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138 KV 508064 TO DUGLASV4 138 KV 509666 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MUNZCTY4__WILKES_4 | 3 Phase fault MUNZCTY4 (508064) 138 kV Bus a. Apply fault at the MUNZCTY4 (508064) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138 KV 508064 TO WILKES 4 138 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MUSKOGE5__MSKPTAP5 | 3 Phase fault MUSKOGE5 (515222) 161 kV Bus a. Apply fault at the MUSKOGE5 (515222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKOGE5 161 KV 515222 TO MSKPTAP5 161 KV 515232 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MUSKOGE5__TAHLQH_5 | 3 Phase fault MUSKOGE5 (515222) 161 kV Bus a. Apply fault at the MUSKOGE5 (515222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKOGE5 161 KV 515222 TO KETOWAH5 161 KV 516027 CKT 1 b.2. LOAD 1 516027 b.3. 7CLANS 5 161 KV 515956 TO KETOWAH5 161 KV 516027 CKT 1 b.4. LOAD 1 516027 b.5. TAHLQH 5 161 KV 512655 TO 7CLANS 5 161 KV 515956 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MUSKOGE7__FIREWHL | 3 Phase fault MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345 KV 515224 TO FIREWHL-TAP 345 KV 588839 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MUSKOGE7__FTSMITH7 | 3 Phase fault MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345 KV 515224 TO FTSMITH7 345 KV 515302 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MUSKOGE7__PECANCK7 | 3 Phase fault MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345 KV 515224 TO PECANCK7 345 KV 515235 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MUSKTAP5__FT_GIB_5 | 3 Phase fault MUSKTAP5 (505558) 161 kV Bus a. Apply fault at the MUSKTAP5 (505558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKTAP5 161 KV 505558 TO FT GIB 5 161 KV 505560 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MUSKTAP5__MUSKOGE5 | 3 Phase fault MUSKTAP5 (505558) 161 kV Bus a. Apply fault at the MUSKTAP5 (505558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKTAP5 161 KV 505558 TO MUSKOGE5 161 KV 515222 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MUSTANG4__DAYTON_4 | 3 Phase fault MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138 KV 514861 TO DAYTON 4 138 KV 514892 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MUSTANG4__DOUGLTP4 | 3 Phase fault MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138 KV 514861 TO COUNCIL4 138 KV 514865 CKT 1 b.2. LOAD 1 514865 b.3. COUNCIL4 138 KV 514865 TO WESTOAK4 138 KV 514866 CKT 1 b.4. LOAD 1 514866 b.5. WESTOAK4 138 KV 514866 TO MERIDAN4 138 KV 514867 CKT 1 b.6. LOAD 1 514867 b.7. MERIDAN4 138 KV 514867 TO DOUGLTP4 138 KV 514868 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MUSTANG4__GEN-2018-026 | 3 Phase fault MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138 KV 514861 TO GEN-2018-026 138 KV 762614 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MUSTANG4__MORGAN_4 | 3 Phase fault MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138 KV 514861 TO MORGAN 4 138 KV 514896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MUSTANG4__SW_5TH_4 | 3 Phase fault MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138 KV 514861 TO SW 5TH 4 138 KV 514920 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_N.E.S._ALWUETP4 | 3 Phase fault N.E.S.-4 (510396) 138 kV Bus a. Apply fault at the N.E.S.-4 (510396) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.E.S.-4 138 KV 510396 TO HAWTHRN4 138 KV 510413 CKT 1 b.2. LOAD 1 510413 b.3. CHELSA4 138 KV 510410 TO HAWTHRN4 138 KV 510413 CKT 1 b.4. LOAD 1 510413 b.5. CHELSA4 138 KV 510410 TO ALWUETP4 138 KV 510429 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_N.E.S._BVSE4 | 3 Phase fault N.E.S.-4 (510396) 138 kV Bus a. Apply fault at the N.E.S.-4 (510396) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATOVA 4 138 KV 510384 TO N.E.S.-4 138 KV 510396 CKT 1 b.2. LOAD 1 510396 b.3. WATOVA 4 138 KV 510384 TO NOWATA-4 138 KV 510397 CKT 1 b.4. LOAD 1 510397 b.5. BV-SE--4 138 KV 510391 TO NOWATA-4 138 KV 510397 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_N.E.S._CLARMR | 3 Phase fault N.E.S.-4 (510396) 138 kV Bus a. Apply fault at the N.E.S.-4 (510396) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.E.S.-4 138 KV 510396 TO OOLOGAHKM 4 138 KV 513124 CKT 1 b.2. LOAD 1 513124 b.3. CLARMR 4 138 KV 512707 TO OOLOGAHKM 4 138 KV 513124 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_N.E.S._PCATSAT | 3 Phase fault N.E.S.-4 (510396) 138 kV Bus a. Apply fault at the N.E.S.-4 (510396) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCATSAT4 138 KV 509841 TO OWASO2_4 138 KV 509843 CKT 1 b.2. LOAD 1 509843 b.3. OWASO2_4 138 KV 509843 TO N.E.S.-4 138 KV 510396 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_N.E.S._TERNITP4 | 3 Phase fault N.E.S.-4 (510396) 138 kV Bus a. Apply fault at the N.E.S.-4 (510396) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARTOK4 138 KV 509864 TO N.E.S.-4 138 KV 510396 CKT 1 b.2. LOAD 1 510396 b.3. VERDIGS4 138 KV 509854 TO CLARTOK4 138 KV 509864 CKT 1 b.4. LOAD 1 509864 b.5. TERNITP4 138 KV 509835 TO VERDIGS4 138 KV 509854 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NASH___4__ALUMAX_4 | 3 Phase fault NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138 KV 508049 TO ALUMAX 4 138 KV 508091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NASH___4__BANN___4 | 3 Phase fault NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138 KV 508049 TO BANN 4 138 KV 508054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NASH___4__NWTXARK4 | 3 Phase fault NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138 KV 508049 TO NWTXARK4 138 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NBENTON4__G16 | 3 Phase fault NBENTON4 (508811) 138 kV Bus a. Apply fault at the NBENTON4 (508811) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NBENTON4 138 KV 508811 TO G16-167-TAP 138 KV 588404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NE10TH_4__RENO___4 | 3 Phase fault NE10TH 4 (514964) 138 kV Bus a. Apply fault at the NE10TH 4 (514964) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE10TH 4 138 KV 514964 TO RENO 4 138 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NE30TH_2__DEEPFKT2 | 3 Phase fault NE30TH 2 (514969) 69 kV Bus a. Apply fault at the NE30TH 2 (514969) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE30TH 2 69 KV 514969 TO DEEPFKT2 69 KV 514970 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NE30TH_2__RENO___2 | 3 Phase fault NE30TH 2 (514969) 69 kV Bus a. Apply fault at the NE30TH 2 (514969) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE30TH 2 69 KV 514969 TO RENO 2 69 KV 514972 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NE45TAP4__RUSHING4 | 3 Phase fault NE45TAP4 (515062) 138 kV Bus a. Apply fault at the NE45TAP4 (515062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE45TAP4 138 KV 515062 TO RUSHING4 138 KV 515064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NE45TAP4__WOLVRNT4 | 3 Phase fault NE45TAP4 (515062) 138 kV Bus a. Apply fault at the NE45TAP4 (515062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCK CK4 138 KV 515058 TO NE45TAP4 138 KV 515062 CKT 1 b.2. MOBIL 4 138 KV 515057 TO ROCK CK4 138 KV 515058 CKT 1 b.3. LOAD 1 515058 b.4. MOBIL 4 138 KV 515057 TO WOLVRNT4 138 KV 515532 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NEKOOSA2__HOLOX__2 | 3 Phase fault NEKOOSA2 (508065) 69 kV Bus a. Apply fault at the NEKOOSA2 (508065) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEKOOSA2 69 KV 508065 TO HOLOX 2 69 KV 508094 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NEKOSAT2__HOLOX__2 | 3 Phase fault NEKOSAT2 (508066) 69 kV Bus a. Apply fault at the NEKOSAT2 (508066) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEKOSAT2 69 KV 508066 TO HOLOX 2 69 KV 508094 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NEKOSAT2__SUGHLET2 | 3 Phase fault NEKOSAT2 (508066) 69 kV Bus a. Apply fault at the NEKOSAT2 (508066) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEKOSAT2 69 KV 508066 TO SUGHLET2 69 KV 508081 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NEOSHO_7__G17 | 3 Phase fault NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 345 KV 532793 TO G17-209-TAP 345 KV 760921 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NEOSHO_7__GEN | 3 Phase fault NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 345 KV 532793 TO GEN-2018-032 345 KV 762680 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NEWBOST2__DEKALB_2 | 3 Phase fault NEWBOST2 (508067) 69 kV Bus a. Apply fault at the NEWBOST2 (508067) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWBOST2 69 KV 508067 TO DEKALB 2 69 KV 508289 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NEWBOST2__NNBOSTN2 | 3 Phase fault NEWBOST2 (508067) 69 kV Bus a. Apply fault at the NEWBOST2 (508067) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWBOST2 69 KV 508067 TO NNBOSTN2 69 KV 508068 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NEWBOST2__REDRVR | 3 Phase fault NEWBOST2 (508067) 69 kV Bus a. Apply fault at the NEWBOST2 (508067) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWBOST2 69 KV 508067 TO REDRVR-2 69 KV 508074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NNBOSTN4__ANDRSNC4 | 3 Phase fault NNBOSTN4 (508069) 138 kV Bus a. Apply fault at the NNBOSTN4 (508069) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN4 138 KV 508069 TO RIFFIN REC4 138 KV 508104 CKT 1 b.2. LOAD 1 508104 b.3. ANDRSNC4 138 KV 508050 TO RIFFIN REC4 138 KV 508104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NNBOSTN4__G18 | 3 Phase fault NNBOSTN4 (508069) 138 kV Bus a. Apply fault at the NNBOSTN4 (508069) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN4 138 KV 508069 TO G18-003-TAP 138 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NORTWST7__ARCADIA7 | 3 Phase fault NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345 KV 514880 TO ARCADIA7 345 KV 514908 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NORTWST7__CIMARON7 | 3 Phase fault NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345 KV 514880 TO CIMARON7 345 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NORTWST7__MATHWSN7 | 3 Phase fault NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345 KV 514880 TO MATHWSN7 345 KV 515497 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NORTWST7__SPRNGCK7 | 3 Phase fault NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345 KV 514880 TO SPRNGCK7 345 KV 514881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NSHVILR2__NASHVIL2 | 3 Phase fault NSHVILR2 (507413) 69 kV Bus a. Apply fault at the NSHVILR2 (507413) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NSHVILR2 69 KV 507413 TO NASHVIL2 69 KV 507426 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NWT-BNT4_G18-003-TAP | 3 Phase fault NWT-BNT4 (508070) 138 kV Bus a. Apply fault at the NWT-BNT4 (508070) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138 KV 508070 TO G18-003-TAP 138 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NWT-BNT4_NWTXARX4 | 3 Phase fault NWT-BNT4 (508070) 138 kV Bus a. Apply fault at the NWT-BNT4 (508070) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138 KV 508070 TO NWTXARK4 138 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NWTXARK4__SUGARHL4 | 3 Phase fault NWTXARK4 (508071) 138 kV Bus a. Apply fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 138 KV 508071 TO SUGARHL4 138 KV 508080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NWTXARK7__LYDIA__7 | 3 Phase fault NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345 KV 508072 TO LYDIA 7 345 KV 508298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NWTXARK7__VALIANT7 | 3 Phase fault NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345 KV 508072 TO VALIANT7 345 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NWTXARK7__WELSH__7 | 3 Phase fault NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345 KV 508072 TO WELSH 7 345 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_O.K.U._G17-151-TAP | 3 Phase fault O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345 KV 511456 TO G17-151TAP 345 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_O.K.U._G18-015-Tap | 3 Phase fault O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345 KV 511456 TO G18-015-TAP 345 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_O.K.U._GEN-2017-033 | 3 Phase fault O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345 KV 511456 TO GEN-2017-033 345 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_O.K.U._L.E.S. | 3 Phase fault O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345 KV 511456 TO L.E.S.-7 345 KV 511468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_O.K.U._OKLAUN HVDC | 3 Phase fault O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345 KV 511456 TO OKLAUN HVDC7 345 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OAKCRK_4__DRAPER_4 | 3 Phase fault OAKCRK 4 (514960) 138 kV Bus a. Apply fault at the OAKCRK 4 (514960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKCRK 4 138 KV 514960 TO WILDMRY4 138 KV 514984 CKT 1 b.2. LOAD 1 514984 b.3. WILDMRY4 138 KV 514984 TO AIRDEPT4 138 KV 515457 CKT 1 b.4. LOAD 1 515457 b.5. GM 4 138 KV 514961 TO AIRDEPT4 138 KV 515457 CKT 1 b.6. LOAD 1 515457 b.7. DRAPER 4 138 KV 514933 TO GM 4 138 KV 514961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OAKCRK_4__INDNHIL4 | 3 Phase fault OAKCRK 4 (514960) 138 kV Bus a. Apply fault at the OAKCRK 4 (514960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE 4 138 KV 514955 TO OAKCRK 4 138 KV 514960 CKT 1 b.2. MOORE 4 138 KV 514955 TO INDIANH4 138 KV 515380 CKT 1 b.3. LOAD 1 515380 b.4. INDNHIL4 138 KV 514954 TO INDIANH4 138 KV 515380 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OAKCRK_4__SELNDTP4 | 3 Phase fault OAKCRK 4 (514960) 138 kV Bus a. Apply fault at the OAKCRK 4 (514960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKCRK 4 138 KV 514960 TO SELNDTP4 138 KV 515965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OAKS_OASETP | 3 Phase fault OAKS--E4 (509846) 138 kV Bus a. Apply fault at the OAKS--E4 (509846) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKS--E4 138 KV 509846 TO OAKSETP4 138 KV 509850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OAKSWTP4__SAPLPRD4 | 3 Phase fault OAKSWTP4 (509848) 138 kV Bus a. Apply fault at the OAKSWTP4 (509848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKSWTP4 138 KV 509848 TO SAPLPRD4 138 KV 509871 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OAKS__W4__OAKSWTP4 | 3 Phase fault OAKS W4 (509727) 138 kV Bus a. Apply fault at the OAKS W4 (509727) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKS W4 138 KV 509727 TO OAKSWTP4 138 KV 509848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OAKTRET4__SOONRTP4 | 3 Phase fault OAKTRET4 (514930) 138 kV Bus a. Apply fault at the OAKTRET4 (514930) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKTRET4 138 KV 514930 TO SOONRTP4 138 KV 514949 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OGMARTN2__DX | 3 Phase fault OGMARTN2 (509751) 69 kV Bus a. Apply fault at the OGMARTN2 (509751) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGMARTN2 69 KV 509751 TO DX----E2 69 KV 509795 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OGMARTN2__T.P.S. | 3 Phase fault OGMARTN2 (509751) 69 kV Bus a. Apply fault at the OGMARTN2 (509751) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLPIP2 69 KV 509750 TO OGMARTN2 69 KV 509751 CKT 1 b.2. LOAD 1 509751 b.3. WILLPIP2 69 KV 509750 TO T.P.S.-2 69 KV 509789 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OKAYGR_5__WAGNOR_5 | 3 Phase fault OKAYGR 5 (512640) 161 kV Bus a. Apply fault at the OKAYGR 5 (512640) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAYGR 5 161 KV 512640 TO WAGNOR 5 161 KV 512700 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OKAY___2__NASHVIL2 | 3 Phase fault OKAY 2 (507427) 69 kV Bus a. Apply fault at the OKAY 2 (507427) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWAYR2 69 KV 507410 TO TOLETTE2 69 KV 507415 CKT 1 b.2. LOAD A1 507415 b.3. TOLETTE2 69 KV 507415 TO OKAY 2 69 KV 507427 CKT 1 b.4. LOAD 1 507427 b.5. MIDWAYR2 69 KV 507410 TO NASHVIL2 69 KV 507426 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OKAY___4__TURK___4 | 3 Phase fault OKAY 4 (507428) 138 kV Bus a. Apply fault at the OKAY 4 (507428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAY 4 138 KV 507428 TO TURK 4 138 KV 507454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OKEENE_2__TALOGA_2 | 3 Phase fault OKEENE 2 (521015) 69 kV Bus a. Apply fault at the OKEENE 2 (521015) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANTON-2 69 KV 520843 TO OKEENE 2 69 KV 521015 CKT 1 b.2. LOAD 1 521015 b.3. CANTON-2 69 KV 520843 TO TALOGA 2 69 KV 521064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OKMULGE4__EC.HEN | 3 Phase fault OKMULGE4 (510898) 138 kV Bus a. Apply fault at the OKMULGE4 (510898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKMULGE4 138 KV 510898 TO EC.HEN-4 138 KV 510923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OKMULGE4__KELCO_4 | 3 Phase fault OKMULGE4 (510898) 138 kV Bus a. Apply fault at the OKMULGE4 (510898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKMULGE4 138 KV 510898 TO KELCO 4 138 KV 510931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OMAHA__2__DUGLASV2 | 3 Phase fault OMAHA 2 (509644) 69 kV Bus a. Apply fault at the OMAHA 2 (509644) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMAHA 2 69 KV 509644 TO DUGLASV2 69 KV 509645 CKT NO c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ONETA_121LYNN | 3 Phase fault ONETA--4 (509806) 138 kV Bus a. Apply fault at the ONETA--4 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 138 KV 509806 TO 121LYNN4 138 KV 509869 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ONETA_BA81 | 3 Phase fault ONETA--4 (509806) 138 kV Bus a. Apply fault at the ONETA--4 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101-N4 138 KV 509769 TO ONETA--4 138 KV 509806 CKT 1 b.2. LOAD 1 509806 b.3. BA81---4 138 KV 509747 TO BA101-N4 138 KV 509769 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ONETA_BANNTAP4 | 3 Phase fault ONETA--4 (509806) 138 kV Bus a. Apply fault at the ONETA--4 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 138 KV 509806 TO BA_71ST4 138 KV 509891 CKT 1 b.2. LOAD 1 509891 b.3. BANNTAP4 138 KV 509785 TO BA_71ST4 138 KV 509891 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ONETA_NES | 3 Phase fault ONETA--7 (509807) 345 kV Bus a. Apply fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 345 KV 509807 TO N.E.S.-7 345 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ONETA_OEC | 3 Phase fault ONETA--7 (509807) 345 kV Bus a. Apply fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 345 KV 509807 TO OEC 7 345 KV 509836 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ORU_ETP4__WARNTAP4 | 3 Phase fault ORU ETP4 (509849) 138 kV Bus a. Apply fault at the ORU ETP4 (509849) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU ETP4 138 KV 509849 TO WARNTAP4 138 KV 509858 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ORU___E4__ORU_ETP4 | 3 Phase fault ORU E4 (509738) 138 kV Bus a. Apply fault at the ORU E4 (509738) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU E4 138 KV 509738 TO ORU ETP4 138 KV 509849 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ORU___W4__ORU | 3 Phase fault ORU W4 (509732) 138 kV Bus a. Apply fault at the ORU W4 (509732) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU W4 138 KV 509732 TO ORU-WTP4 138 KV 509853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OTTER__4__ARMFTWD4 | 3 Phase fault OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138 KV 514708 TO ARMFTWD4 138 KV 515694 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OTTER__4__WOODRNG4 | 3 Phase fault OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138 KV 514708 TO WOODRNG4 138 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OTTER__4__WRVALLY4 | 3 Phase fault OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138 KV 514708 TO WRVALLY4 138 KV 514713 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OWASO1_4__OWASOTP4 | 3 Phase fault OWASO1_4 (509726) 138 kV Bus a. Apply fault at the OWASO1_4 (509726) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OWASO1_4 138 KV 509726 TO OWASOTP4 138 KV 509844 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OWASOTP4__N.E.S. | 3 Phase fault OWASOTP4 (509844) 138 kV Bus a. Apply fault at the OWASOTP4 (509844) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OWAS1094 138 KV 509860 TO N.E.S.-4 138 KV 510396 CKT 1 b.2. LOAD 1 510396 b.3. OWASOTP4 138 KV 509844 TO OWAS1094 138 KV 509860 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PAOLI | 3 Phase fault PAOLI- 4 (515100) 138 kV Bus a. Apply fault at the PAOLI- 4 (515100) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAOLI- 4 138 KV 515100 TO CHIGLEY4 138 KV 515114 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PAOLI | 3 Phase fault PAOLI- 4 (515100) 138 kV Bus a. Apply fault at the PAOLI- 4 (515100) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAOLI- 4 138 KV 515100 TO MAYSVIL4 138 KV 515124 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PARADSE4__CHERRYRD_4 | 3 Phase fault PARADSE4 (521024) 138 kV Bus a. Apply fault at the PARADSE4 (521024) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARADSE4 138 KV 521024 TO CHERRYRD 4 138 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PARKLN_4__LKKONWA4 | 3 Phase fault PARKLN 4 (515178) 138 kV Bus a. Apply fault at the PARKLN 4 (515178) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKLN 4 138 KV 515178 TO LKKONWA4 138 KV 515977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PARKLN_4__SOTHADA4 | 3 Phase fault PARKLN 4 (515178) 138 kV Bus a. Apply fault at the PARKLN 4 (515178) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKLN 4 138 KV 515178 TO SOTHADA4 138 KV 515318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PARKMEDTP__COLNSGR2 | 3 Phase fault PARKMEDTP (512703) 69 kV Bus a. Apply fault at the PARKMEDTP (512703) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKMEDTP 69 KV 512703 TO COLNSGR2 69 KV 512870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PATTERS2__NEKOOSA2 | 3 Phase fault PATTERS2 (507429) 69 kV Bus a. Apply fault at the PATTERS2 (507429) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS2 69 KV 507429 TO NEKOOSA2 69 KV 508065 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PATTERS2__NEKOSAT2 | 3 Phase fault PATTERS2 (507429) 69 kV Bus a. Apply fault at the PATTERS2 (507429) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS2 69 KV 507429 TO ASHDOWN2 69 KV 508051 CKT 1 b.2. LOAD 1 508051 b.3. ASHDOWN2 69 KV 508051 TO NEKOSAT2 69 KV 508066 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PATTERS4__BARITERDTP_4 | 3 Phase fault PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOCKSBRG 4 138 KV 504123 TO PATTERS4 138 KV 507431 CKT 1 b.2. LOCKSBRG 4 138 KV 504123 TO BARITERDTP 4 138 KV 507463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PATTERS4__CRAIGJT4 | 3 Phase fault PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHDWN_W 4 138 KV 504124 TO PATTERS4 138 KV 507431 CKT 1 b.2. ASHDWN_W 4 138 KV 504124 TO CRAIGJT4 138 KV 510890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PATTERS4__NWTXARK4 | 3 Phase fault PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS4 138 KV 507431 TO NWTXARK4 138 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PATTERS4__OKAY___4 | 3 Phase fault PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHDWNR4 138 KV 507402 TO OKAY 4 138 KV 507428 CKT 1 b.2. ASHDWNR4 138 KV 507402 TO PATTERS4 138 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PATTERS4__SNASHVL4 | 3 Phase fault PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS4 138 KV 507431 TO SNASHVL4 138 KV 507434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PAWNSW4__GLENCOKM_4 | 3 Phase fault PAWNSW4 (512749) 138 kV Bus a. Apply fault at the PAWNSW4 (512749) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAWNSW4 138 KV 512749 TO GLENCOKM 4 138 KV 513095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PCATSAT4__PCATOSA4 | 3 Phase fault PCATSAT4 (509841) 138 kV Bus a. Apply fault at the PCATSAT4 (509841) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCATSAT4 138 KV 509841 TO BIRDCREE-4 138 KV 509899 CKT 1 b.2. LOAD 1 509899 b.3. PCATOSA4 138 KV 509725 TO BIRDCREE-4 138 KV 509899 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PEARLHL2__ROACH__2 | 3 Phase fault PEARLHL2 (509651) 69 kV Bus a. Apply fault at the PEARLHL2 (509651) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEARLHL2 69 KV 509651 TO ROACH 2 69 KV 509668 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PEARSNT2__MAUD___2 | 3 Phase fault PEARSNT2 (515053) 69 kV Bus a. Apply fault at the PEARSNT2 (515053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEARSNT2 69 KV 515053 TO MAUD 2 69 KV 515054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PECANCK4__BRISTOW4 | 3 Phase fault PECANCK4 (515233) 138 kV Bus a. Apply fault at the PECANCK4 (515233) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK4 138 KV 515233 TO BEGGS 4 138 KV 515249 CKT 1 b.2. LOAD 1 515249 b.3. BRISTOW4 138 KV 515035 TO BEGGS 4 138 KV 515249 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PECANCK7__GEN | 3 Phase fault PECANCK7 (515235) 345 kV Bus a. Apply fault at the PECANCK7 (515235) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECANCK7 345 KV 515235 TO GEN-2018-048 345 KV 762823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PENN___2__KENTUKT2 | 3 Phase fault PENN 2 (514924) 69 kV Bus a. Apply fault at the PENN 2 (514924) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENN 2 69 KV 514924 TO KENTUKT2 69 KV 514977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PENN___4__36&MER_4 | 3 Phase fault PENN 4 (514925) 138 kV Bus a. Apply fault at the PENN 4 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRAIRPT4 138 KV 514889 TO PENN 4 138 KV 514925 CKT 1 b.2. LOAD 1 514925 b.3. 36&MER 4 138 KV 514888 TO WRAIRPT4 138 KV 514889 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PENN___4__OAKCRK_4 | 3 Phase fault PENN 4 (514925) 138 kV Bus a. Apply fault at the PENN 4 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENN 4 138 KV 514925 TO SANTAFE4 138 KV 514926 CKT 1 b.2. LOAD 1 514926 b.3. SANTAFE4 138 KV 514926 TO OAKCRK 4 138 KV 514960 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PENSA__5__KETCHUM5 | 3 Phase fault PENSA 5 (512654) 161 kV Bus a. Apply fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 5 161 KV 512654 TO KETCHUM5 161 KV 512669 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PERDUE_4__DIANA__4 | 3 Phase fault PERDUE 4 (508351) 138 kV Bus a. Apply fault at the PERDUE 4 (508351) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERDUE 4 138 KV 508351 TO DIANA 4 138 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PERSIMN7__GUTHRIE7 | 3 Phase fault PERSIMN7 (515951) 345 kV Bus a. Apply fault at the PERSIMN7 (515951) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PERSIMN7 345 KV 515951 TO GUTHRIE7 345 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PETTY__4__CHAPELH4 | 3 Phase fault PETTY 4 (508310) 138 kV Bus a. Apply fault at the PETTY 4 (508310) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PETTY 4 138 KV 508310 TO CHAPELH4 138 KV 508337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PIC4__CDRDLTP4 | 3 Phase fault PIC4 (520425) 138 kV Bus a. Apply fault at the PIC4 (520425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIC4 138 KV 520425 TO CDRDLTP4 138 KV 520848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PIC4__MOORLND4 | 3 Phase fault PIC4 (520425) 138 kV Bus a. Apply fault at the PIC4 (520425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIC4 138 KV 520425 TO MOORLND4 138 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PIEDMNT4__NORTWST4 | 3 Phase fault PIEDMNT4 (514864) 138 kV Bus a. Apply fault at the PIEDMNT4 (514864) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIEDMNT4 138 KV 514864 TO NORTWST4 138 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PINERTP2__WASHITA2 | 3 Phase fault PINERTP2 (521027) 69 kV Bus a. Apply fault at the PINERTP2 (521027) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PINERTP2 69 KV 521027 TO WASHITA2 69 KV 521088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PINK_SW4__SHAWNEE4 | 3 Phase fault PINK SW4 (521028) 138 kV Bus a. Apply fault at the PINK SW4 (521028) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PINK SW4 138 KV 521028 TO SHAWNEE4 138 KV 521048 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PINK___4__PINK_SW4 | 3 Phase fault PINK 4 (520494) 138 kV Bus a. Apply fault at the PINK 4 (520494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PINK 4 138 KV 520494 TO PINK SW4 138 KV 521028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PINTAIL7__KINGWD_7 | 3 Phase fault PINTAIL7 (516010) 345 kV Bus a. Apply fault at the PINTAIL7 (516010) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PINTAIL7 345 KV 516010 TO KINGWD 7 345 KV 516019 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PIRKEY_4__SABMINT4 | 3 Phase fault PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138 KV 508562 TO SABMINT4 138 KV 508566 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PIRKEY_4__WHITNEY4 | 3 Phase fault PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138 KV 508562 TO HALLSVLS4 138 KV 508595 CKT 1 b.2. LOAD 1 508595 b.3. WHITNEY4 138 KV 508575 TO HALLSVLS4 138 KV 508595 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PIRKEY_7__DIANA__7 | 3 Phase fault PIRKEY 7 (508563) 345 kV Bus a. Apply fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345 KV 508563 TO DIANA 7 345 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PIRKEY_7__LEBROCK7 | 3 Phase fault PIRKEY 7 (508563) 345 kV Bus a. Apply fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345 KV 508563 TO LEBROCK7 345 KV 508572 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PITTSB_CRIVER | 3 Phase fault PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345 KV 510907 TO C-RIVER7 345 KV 515422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PITTSB_JOHNCO | 3 Phase fault PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345 KV 510907 TO JOHNCO 7 345 KV 514809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PITTSB_KIOWA | 3 Phase fault PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345 KV 510907 TO KIOWA 7 345 KV 510925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PITTSB_SEMINOL | 3 Phase fault PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345 KV 510907 TO SEMINOL7 345 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PITTSB_VALIANT | 3 Phase fault PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345 KV 510907 TO VALIANT7 345 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_POLECTP4__HICKORY4 | 3 Phase fault POLECTP4 (515218) 138 kV Bus a. Apply fault at the POLECTP4 (515218) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POLECTP4 138 KV 515218 TO HICKORY4 138 KV 515244 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_POLECTP4__POLECAT4 | 3 Phase fault POLECTP4 (515218) 138 kV Bus a. Apply fault at the POLECTP4 (515218) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POLECTP4 138 KV 515218 TO POLECAT4 138 KV 515219 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_POOLVIL4__CARTRCO4 | 3 Phase fault POOLVIL4 (515130) 138 kV Bus a. Apply fault at the POOLVIL4 (515130) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POOLVIL4 138 KV 515130 TO CARTRCO4 138 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_POWELL_4__SW_SHV_4 | 3 Phase fault POWELL 4 (507748) 138 kV Bus a. Apply fault at the POWELL 4 (507748) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POWELL 4 138 KV 507748 TO SW SHV 4 138 KV 507759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PP_YARCHT | 3 Phase fault PP----E4 (509818) 138 kV Bus a. Apply fault at the PP----E4 (509818) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PP----E4 138 KV 509818 TO YARCHT 4 138 KV 509862 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PP_P&PWTP4 | 3 Phase fault PP----W4 (509805) 138 kV Bus a. Apply fault at the PP----W4 (509805) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PP----W4 138 KV 509805 TO P&P WTP4 138 KV 509851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PPTAP__4__46ST | 3 Phase fault PPTAP 4 (509863) 138 kV Bus a. Apply fault at the PPTAP 4 (509863) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PPTAP 4 138 KV 509863 TO 46ST-TP-4 138 KV 509900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_QUAILCK4__LNEOAK_4 | 3 Phase fault QUAILCK4 (514851) 138 kV Bus a. Apply fault at the QUAILCK4 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 138 KV 514851 TO LNEOAK 4 138 KV 514873 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_QUAILCK4__NORTWST4 | 3 Phase fault QUAILCK4 (514851) 138 kV Bus a. Apply fault at the QUAILCK4 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNEOAK 4 138 KV 514873 TO NORTWST4 138 KV 514879 CKT 1 b.2. QUAILCK4 138 KV 514851 TO LNEOAK 4 138 KV 514873 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_QUAILCK4__SLVRLAK4 | 3 Phase fault QUAILCK4 (514851) 138 kV Bus a. Apply fault at the QUAILCK4 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 138 KV 514851 TO SLVRLAK4 138 KV 514852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_R.S.S_5DELT | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138 KV 509783 TO 52DELWT4 138 KV 509814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_R.S.S._KIMCLRK4 | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 136YALE4 138 KV 509775 TO R.S.S.-4 138 KV 509783 CKT 1 b.2. 136YALE4 138 KV 509775 TO KIMCLRK4 138 KV 509845 CKT 1 b.3. LOAD 1 509845 b.4. B111---4 138 KV 509767 TO KIMCLRK4 138 KV 509845 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_R.S.S._EXPGLNT4 | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138 KV 509783 TO EXPGLNT4 138 KV 515473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_R.S.S._OAKSETP4 | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138 KV 509783 TO OAKSETP4 138 KV 509850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_R.S.S._EXP_OKM4 | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138 KV 509783 TO EXP_OKM4 138 KV 510904 CKT 1 b.2. LOAD 1 510904 b.3. OKMULGE4 138 KV 510898 TO EXP_OKM4 138 KV 510904 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_R.S.S._ORU-WTP4 | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138 KV 509783 TO ORU-WTP4 138 KV 509853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_R.S.S._ORU ETP4 | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138 KV 509783 TO ORU ETP4 138 KV 509849 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_R.S.S._RSST2 | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138 KV 509783 TO RSS T2 4 138 KV 509875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_R.S.S._COGENT | 3 Phase fault R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345 KV 509782 TO COGENT 7 345 KV 509834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_R.S.S._G16133G16146 | 3 Phase fault R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345 KV 509782 TO G16133G16146 345 KV 588039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_R.S.S._ONETA | 3 Phase fault R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345 KV 509782 TO ONETA--7 345 KV 509807 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_R.S.S._PECANCK7 | 3 Phase fault R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345 KV 509782 TO PECANCK7 345 KV 515235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_R.S.S._REDBUD | 3 Phase fault R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345 KV 509782 TO REDBUD 7 345 KV 514909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_R.S.S._SAPLPRD | 3 Phase fault R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345 KV 509782 TO SAPLPRD7 345 KV 509870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_RATLIFF4__CARTRCO4 | 3 Phase fault RATLIFF4 (515129) 138 kV Bus a. Apply fault at the RATLIFF4 (515129) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RATLIFF4 138 KV 515129 TO CARTRCO4 138 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_REDBAYOU_6__DOLHILL6 | 3 Phase fault REDBAYOU_6 (500255) 230 kV Bus a. Apply fault at the REDBAYOU_6 (500255) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBAYOU_6 230 KV 500255 TO DOLHILL6 230 KV 500260 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_REDBDPLN4__LEONARD4 | 3 Phase fault REDBDPLN4 (511573) 138 kV Bus a. Apply fault at the REDBDPLN4 (511573) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBDPLN4 138 KV 511573 TO LEONARD4 138 KV 511575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_REDCLFT4__REDCLF_4 | 3 Phase fault REDCLFT4 (515533) 138 kV Bus a. Apply fault at the REDCLFT4 (515533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDCLFT4 138 KV 515533 TO REDCLF 4 138 KV 515863 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_REDNGTN7__REDDIRT7 | 3 Phase fault REDNGTN7 (515875) 345 kV Bus a. Apply fault at the REDNGTN7 (515875) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDNGTN7 345 KV 515875 TO REDDIRT7 345 KV 515877 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_REDSPRG4__EYLAU__4 | 3 Phase fault REDSPRG4 (508075) 138 kV Bus a. Apply fault at the REDSPRG4 (508075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDSPRG4 138 KV 508075 TO EYLAU 4 138 KV 509655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_REDSPRG4__IPC_T__4 | 3 Phase fault REDSPRG4 (508075) 138 kV Bus a. Apply fault at the REDSPRG4 (508075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC-DOM4 138 KV 508060 TO REDSPRG4 138 KV 508075 CKT 1 b.2. LOAD 1 508075 b.3. IPC T 4 138 KV 508059 TO IPC-DOM4 138 KV 508060 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_REDWATR4__EYLAU__4 | 3 Phase fault REDWATR4 (509654) 138 kV Bus a. Apply fault at the REDWATR4 (509654) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDWATR4 138 KV 509654 TO EYLAU 4 138 KV 509655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_REMPKTP4__REMNGPK4 | 3 Phase fault REMPKTP4 (514872) 138 kV Bus a. Apply fault at the REMPKTP4 (514872) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REMPKTP4 138 KV 514872 TO REMNGPK4 138 KV 514874 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_RENO___2__SUNNYLN2 | 3 Phase fault RENO 2 (514972) 69 kV Bus a. Apply fault at the RENO 2 (514972) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 2 69 KV 514972 TO SUNNYLN2 69 KV 514980 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_RENO___4__WASHPRK4 | 3 Phase fault RENO 4 (514973) 138 kV Bus a. Apply fault at the RENO 4 (514973) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 4 138 KV 514973 TO WASHPRK4 138 KV 515156 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_RICHRDS4__PIEDMNT4 | 3 Phase fault RICHRDS4 (514862) 138 kV Bus a. Apply fault at the RICHRDS4 (514862) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHRDS4 138 KV 514862 TO PIEDMNT4 138 KV 514864 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ROCKYPT4__SPRNDAL4 | 3 Phase fault ROCKYPT4 (515164) 138 kV Bus a. Apply fault at the ROCKYPT4 (515164) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT4 138 KV 515164 TO SPRNDAL4 138 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ROKHILL4__NEWPROS4 | 3 Phase fault ROKHILL4 (509083) 138 kV Bus a. Apply fault at the ROKHILL4 (509083) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL4 138 KV 509083 TO NEWPROS4 138 KV 509102 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ROKHILL4__TATUM__4 | 3 Phase fault ROKHILL4 (509083) 138 kV Bus a. Apply fault at the ROKHILL4 (509083) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL4 138 KV 509083 TO TATUM 4 138 KV 509087 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ROMNOSE4__GEARYTP4 | 3 Phase fault ROMNOSE4 (514823) 138 kV Bus a. Apply fault at the ROMNOSE4 (514823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROMNOSE4 138 KV 514823 TO GEARYTP4 138 KV 515931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_RSS_T1_4__R.S.S. | 3 Phase fault RSS T1 4 (509773) 138 kV Bus a. Apply fault at the RSS T1 4 (509773) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T1 4 138 KV 509773 TO R.S.S.-4 138 KV 509783 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_RUSHSPR7__GEN | 3 Phase fault RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345 KV 511571 TO GEN-2018-055 345 KV 762900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_RVRFANT2__MUSKOGE2 | 3 Phase fault RVRFANT2 (515210) 69 kV Bus a. Apply fault at the RVRFANT2 (515210) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RVRFANT2 69 KV 515210 TO MUSKOGE2 69 KV 515221 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_RVRSID_2__MUSKOGE2 | 3 Phase fault RVRSID 2 (515205) 69 kV Bus a. Apply fault at the RVRSID 2 (515205) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RVRSID 2 69 KV 515205 TO MUSKOGE2 69 KV 515221 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_S.HIL_E4__SHILETP4 | 3 Phase fault S.HIL E4 (509731) 138 kV Bus a. Apply fault at the S.HIL E4 (509731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HIL E4 138 KV 509731 TO SHILETP4 138 KV 509813 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_S.S._BLUEBEL4 | 3 Phase fault S.S.---4 (509815) 138 kV Bus a. Apply fault at the S.S.---4 (509815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRATTV-4 138 KV 509758 TO S.S.---4 138 KV 509815 CKT 1 b.2. LOAD 1 509815 b.3. PRATTV-4 138 KV 509758 TO BLUEBEL4 138 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_S.S._DENV_WTAP | 3 Phase fault S.S.---4 (509815) 138 kV Bus a. Apply fault at the S.S.---4 (509815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---4 138 KV 509815 TO DENV_WTAP4 138 KV 509896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_S.S._HWY20-T | 3 Phase fault S.S.---4 (509815) 138 kV Bus a. Apply fault at the S.S.---4 (509815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---4 138 KV 509815 TO HWY20-T4 138 KV 509821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_S.S._WED-TAP4 | 3 Phase fault S.S.---4 (509815) 138 kV Bus a. Apply fault at the S.S.---4 (509815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---4 138 KV 509815 TO WED-TAP4 138 KV 509823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_S.W.S._ANADARK | 3 Phase fault S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138 KV 511477 TO ANADARK4 138 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_S.W.S._CORNVIL4 | 3 Phase fault S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VERDEN 4 138 KV 511421 TO S.W.S.-4 138 KV 511477 CKT 1 b.2. VERDEN 4 138 KV 511421 TO N29CHIK4 138 KV 511502 CKT 1 b.3. LOAD 1 511502 b.4. CORNVIL4 138 KV 511449 TO N29CHIK4 138 KV 511502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_S.W.S._ELGINJT4 | 3 Phase fault S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138 KV 511477 TO ELSWORTH 4 138 KV 511563 CKT 1 b.2. LOAD 1 511563 b.3. LOAD 2 511563 b.4. ELGINJT4 138 KV 511486 TO ELSWORTH 4 138 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_S.W.S._G16-097-TAP | 3 Phase fault S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138 KV 511477 TO G16-097-TAP 138 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_S.W.S._HOBJCT | 3 Phase fault S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNEG-4 138 KV 511445 TO S.W.S.-4 138 KV 511477 CKT 1 b.2. CARNEG-4 138 KV 511445 TO HOB-JCT4 138 KV 511463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_S.W.S._WASHITA | 3 Phase fault S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138 KV 511477 TO WASHITA4 138 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_S52DEL_4__52DELTP4 | 3 Phase fault S52DEL 4 (509716) 138 kV Bus a. Apply fault at the S52DEL 4 (509716) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S52DEL 4 138 KV 509716 TO 52DELTP4 138 KV 509776 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SABMINT4__SABINEM4 | 3 Phase fault SABMINT4 (508566) 138 kV Bus a. Apply fault at the SABMINT4 (508566) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SABMINT4 138 KV 508566 TO SABINEM4 138 KV 508577 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SALINA_5__SALNCRK5 | 3 Phase fault SALINA 5 (512686) 161 kV Bus a. Apply fault at the SALINA 5 (512686) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINA 5 161 KV 512686 TO SALNCRK5 161 KV 512805 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SALISAW5__GORE___5 | 3 Phase fault SALISAW5 (505550) 161 kV Bus a. Apply fault at the SALISAW5 (505550) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALISAW5 161 KV 505550 TO GORE 5 161 KV 505552 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SAPLPRD4__DENV_WTAP4 | 3 Phase fault SAPLPRD4 (509871) 138 kV Bus a. Apply fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 138 KV 509871 TO DENV_WTAP4 138 KV 509896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SAPLPRD4__R.S.S. | 3 Phase fault SAPLPRD4 (509871) 138 kV Bus a. Apply fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENKS--4 138 KV 509759 TO SAPLPRD4 138 KV 509871 CKT 1 b.2. 116JENK4 138 KV 509753 TO JENKS--4 138 KV 509759 CKT 1 b.3. LOAD 1 509759 b.4. 116JENK4 138 KV 509753 TO R.S.S.-4 138 KV 509783 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SAPULPA2__BEELINE2 | 3 Phase fault SAPULPA2 (515236) 69 kV Bus a. Apply fault at the SAPULPA2 (515236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPULPA2 69 KV 515236 TO BEELINE2 69 KV 515246 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SARA_RD4__SUNSHIN4 | 3 Phase fault SARA RD4 (521005) 138 kV Bus a. Apply fault at the SARA RD4 (521005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA RD4 138 KV 521005 TO SUNSHIN4 138 KV 521059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SARA___4__MCCLAIN4 | 3 Phase fault SARA 4 (514895) 138 kV Bus a. Apply fault at the SARA 4 (514895) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA 4 138 KV 514895 TO MCCLAIN4 138 KV 514902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SAWYER4__HUGO_PP4 | 3 Phase fault SAWYER4 (520411) 138 kV Bus a. Apply fault at the SAWYER4 (520411) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAWYER4 138 KV 520411 TO HUGO PP4 138 KV 520948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SCOFCTY4__COFFEYT4 | 3 Phase fault SCOFCTY4 (510378) 138 kV Bus a. Apply fault at the SCOFCTY4 (510378) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOFCTY4 138 KV 510378 TO COFFEYT4 138 KV 510422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SDIERKS2__DIERKSR2 | 3 Phase fault SDIERKS2 (507432) 69 kV Bus a. Apply fault at the SDIERKS2 (507432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SDIERKS2 69 KV 507432 TO DIERKSR2 69 KV 507437 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SDIERKS4__BARITERDTP_4 | 3 Phase fault SDIERKS4 (507433) 138 kV Bus a. Apply fault at the SDIERKS4 (507433) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SDIERKS4 138 KV 507433 TO BARITERDTP 4 138 KV 507463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SE15TH_4__BARNES_4 | 3 Phase fault SE15TH 4 (514993) 138 kV Bus a. Apply fault at the SE15TH 4 (514993) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SE15TH 4 138 KV 514993 TO BARNES 4 138 KV 515003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SE15TH_4__TINKER54 | 3 Phase fault SE15TH 4 (514993) 138 kV Bus a. Apply fault at the SE15TH 4 (514993) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDAL4 138 KV 514986 TO SE15TH 4 138 KV 514993 CKT 1 b.2. LOAD 1 514993 b.3. GLENDAL4 138 KV 514986 TO TINKER74 138 KV 515959 CKT 1 b.4. LOAD 1 515959 b.5. TINKER64 138 KV 515806 TO TINKER74 138 KV 515959 CKT 1 b.6. LOAD 1 515959 b.7. TINKER54 138 KV 514994 TO TINKER64 138 KV 515806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SELNDTP4__SELNDFL4 | 3 Phase fault SELNDTP4 (515965) 138 kV Bus a. Apply fault at the SELNDTP4 (515965) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SELNDTP4 138 KV 515965 TO SELNDFL4 138 KV 515966 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SELNDTP4__TROSPER4 | 3 Phase fault SELNDTP4 (515965) 138 kV Bus a. Apply fault at the SELNDTP4 (515965) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DISCVRY4 138 KV 514962 TO SELNDTP4 138 KV 515965 CKT 1 b.2. FOSTER 4 138 KV 514959 TO DISCVRY4 138 KV 514962 CKT 1 b.3. LOAD 1 514962 b.4. FOSTER 4 138 KV 514959 TO NEWDOMI4 138 KV 515387 CKT 1 b.5. LOAD 1 515387 b.6. TROSPER4 138 KV 514963 TO NEWDOMI4 138 KV 515387 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SEMINOL4__LKKONWA4 | 3 Phase fault SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138 KV 515044 TO LKKONWA4 138 KV 515977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SEMINOL4__MAUD___4 | 3 Phase fault SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138 KV 515044 TO MAUD 4 138 KV 515055 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SEMINOL4__PAOLI | 3 Phase fault SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138 KV 515044 TO PAOLI- 4 138 KV 515100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SEMINOL4__VANOSTP4 | 3 Phase fault SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138 KV 515044 TO VANOSTP4 138 KV 515531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SEMINOL7__FIREWHL | 3 Phase fault SEMINOL7 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 345 KV 515045 TO FIREWHL-TAP 345 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SEQUOYAHJ4__ANADARK4 | 3 Phase fault SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138 KV 520422 TO ANADARK4 138 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SEQUOYAHJ4__CKSHATP4 | 3 Phase fault SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138 KV 520422 TO CKSHATP4 138 KV 520473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SEQUOYAHJ4__SEQOYAH4 | 3 Phase fault SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138 KV 520422 TO SEQOYAH4 138 KV 520547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SETEXAR2__TEXARK_2 | 3 Phase fault SETEXAR2 (508077) 69 kV Bus a. Apply fault at the SETEXAR2 (508077) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETEXAR2 69 KV 508077 TO TEXARK 2 69 KV 508086 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SETEXAR4__MANDEVILTP4 | 3 Phase fault SETEXAR4 (508078) 138 kV Bus a. Apply fault at the SETEXAR4 (508078) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETEXAR4 138 KV 508078 TO MANDEVILTP4 138 KV 508105 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SFOREMAN__4__NNBOSTN4 | 3 Phase fault SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4 (504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 138 KV 504029 TO NNBOSTN4 138 KV 508069 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SFOREMAN__4__PATTERS4 | 3 Phase fault SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4 (504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 138 KV 504029 TO PATTERS4 138 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SHAWNEE2__SINCPNT2 | 3 Phase fault SHAWNEE2 (515068) 69 kV Bus a. Apply fault at the SHAWNEE2 (515068) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHAWNEE2 69 KV 515068 TO SINCPNT2 69 KV 515642 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SHILETP4__ORU | 3 Phase fault SHILETP4 (509813) 138 kV Bus a. Apply fault at the SHILETP4 (509813) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHILETP4 138 KV 509813 TO ORU-WTP4 138 KV 509853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SILSPWW5__KANSATP5 | 3 Phase fault SILSPWW5 (512642) 161 kV Bus a. Apply fault at the SILSPWW5 (512642) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILSPWW5 161 KV 512642 TO KANSATP5 161 KV 512714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SINCPAN2__SINCPNT2 | 3 Phase fault SINCPAN2 (515072) 69 kV Bus a. Apply fault at the SINCPAN2 (515072) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SINCPAN2 69 KV 515072 TO SINCPNT2 69 KV 515642 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SKELTON7__GEN | 3 Phase fault SKELTON7 (515990) 345 kV Bus a. Apply fault at the SKELTON7 (515990) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SKELTON7 345 KV 515990 TO GEN-2016-128 345 KV 588190 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SKYLINE4__FAIRFLD4 | 3 Phase fault SKYLINE4 (514850) 138 kV Bus a. Apply fault at the SKYLINE4 (514850) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SKYLINE4 138 KV 514850 TO CHISHOM4 138 KV 515374 CKT 1 b.2. LOAD 1 515374 b.3. CHISHOM4 138 KV 515374 TO FAIRFLD4 138 KV 515468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SKYLINE4__QUAILCK4 | 3 Phase fault SKYLINE4 (514850) 138 kV Bus a. Apply fault at the SKYLINE4 (514850) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SKYLINE4 138 KV 514850 TO QUAILCK4 138 KV 514851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SLVRLAK4__DVISION4 | 3 Phase fault SLVRLAK4 (514852) 138 kV Bus a. Apply fault at the SLVRLAK4 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 138 KV 514852 TO DVISION4 138 KV 514853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SLVRLAK4__NORTWST4 | 3 Phase fault SLVRLAK4 (514852) 138 kV Bus a. Apply fault at the SLVRLAK4 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 138 KV 514852 TO BRADEN 4 138 KV 514854 CKT 1 b.2. LOAD 1 514854 b.3. BRADEN 4 138 KV 514854 TO NORTWST4 138 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SMITHCO4__DAYTON_4 | 3 Phase fault SMITHCO4 (514891) 138 kV Bus a. Apply fault at the SMITHCO4 (514891) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMITHCO4 138 KV 514891 TO DAYTON 4 138 KV 514892 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SO4TH__2__CHSTNTT2 | 3 Phase fault SO4TH 2 (514730) 69 kV Bus a. Apply fault at the SO4TH 2 (514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 69 KV 514730 TO CHSTNTT2 69 KV 515456 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SO4TH__4__BRECKNR4 | 3 Phase fault SO4TH 4 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138 KV 514731 TO BRECKNR4 138 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SO4TH__4__IMO____4 | 3 Phase fault SO4TH 4 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138 KV 514731 TO IMO 4 138 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SOONER_7__G15 | 3 Phase fault SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345 KV 514803 TO G15-066T 345 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SOONER_7__G16 | 3 Phase fault SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345 KV 514803 TO G16-119-TAP 345 KV 587804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SOONER_7__PINTAIL7 | 3 Phase fault SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345 KV 514803 TO PINTAIL7 345 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SOONER_7__RANCHRD7 | 3 Phase fault SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345 KV 514803 TO RANCHRD7 345 KV 515576 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SOONER_7__THUNDER7 | 3 Phase fault SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345 KV 514803 TO THUNDER7 345 KV 515894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SOUTHRD4__ROMNOSE4 | 3 Phase fault SOUTHRD4 (514822) 138 kV Bus a. Apply fault at the SOUTHRD4 (514822) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOUTHRD4 138 KV 514822 TO ROMNOSE4 138 KV 514823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SPNKY_CK4__CATOOSA4 | 3 Phase fault SPNKY CK4 (509722) 138 kV Bus a. Apply fault at the SPNKY CK4 (509722) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPNKY CK4 138 KV 509722 TO CATOOSA4 138 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SPPMAINBUS__WELSH__7 | 3 Phase fault SPPMAINBUS (5917) 345 kV Bus a. Apply fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPPMAIN345 KV 5917 TO WELSH 7 345 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SPRHILL4__DIANA__4 | 3 Phase fault SPRHILL4 (508571) 138 kV Bus a. Apply fault at the SPRHILL4 (508571) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRHILL4 138 KV 508571 TO DIANA 4 138 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SQUIRCK4__NE45TAP4 | 3 Phase fault SQUIRCK4 (515059) 138 kV Bus a. Apply fault at the SQUIRCK4 (515059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQUIRCK4 138 KV 515059 TO INGLEWD4 138 KV 515060 CKT 1 b.2. LOAD 1 515060 b.3. INGLEWD4 138 KV 515060 TO STGREG 4 138 KV 515061 CKT 1 b.4. LOAD 1 515061 b.5. STGREG 4 138 KV 515061 TO NE45TAP4 138 KV 515062 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SQUIRCK4__STRLGTP4 | 3 Phase fault SQUIRCK4 (515059) 138 kV Bus a. Apply fault at the SQUIRCK4 (515059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQUIRCK4 138 KV 515059 TO STRLGTP4 138 KV 515286 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_STALOGA2__PUTNAM_2 | 3 Phase fault STALOGA2 (520454) 69 kV Bus a. Apply fault at the STALOGA2 (520454) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STALOGA2 69 KV 520454 TO PUTNAM 2 69 KV 521033 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_STNWAL_4__REMPKTP4 | 3 Phase fault STNWAL 4 (514870) 138 kV Bus a. Apply fault at the STNWAL 4 (514870) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNWAL 4 138 KV 514870 TO REMPKTP4 138 KV 514872 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_STNWAL_4__RENO___4 | 3 Phase fault STNWAL 4 (514870) 138 kV Bus a. Apply fault at the STNWAL 4 (514870) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNWAL 4 138 KV 514870 TO OUMED 4 138 KV 514875 CKT 1 b.2. LOAD 1 514875 b.3. OUMED 4 138 KV 514875 TO GATEWAY4 138 KV 515963 CKT 1 b.4. LOAD 1 515963 b.5. WASHPRK4 138 KV 515156 TO GATEWAY4 138 KV 515963 CKT 1 b.6. LOAD 1 515963 b.7. RENO 4 138 KV 514973 TO WASHPRK4 138 KV 515156 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_STRLGTP4__STERLNG4 | 3 Phase fault STRLGTP4 (515286) 138 kV Bus a. Apply fault at the STRLGTP4 (515286) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STRLGTP4 138 KV 515286 TO STERLNG4 138 KV 520449 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_STUBMAN4__HOLLYWD4 | 3 Phase fault STUBMAN4 (514952) 138 kV Bus a. Apply fault at the STUBMAN4 (514952) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STUBMAN4 138 KV 514952 TO HOLLYWD4 138 KV 514953 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SUGARHL2__SUGHLET2 | 3 Phase fault SUGARHL2 (508079) 69 kV Bus a. Apply fault at the SUGARHL2 (508079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGARHL2 69 KV 508079 TO SUGHLET2 69 KV 508081 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SUGARHL2__SUGHLWT2 | 3 Phase fault SUGARHL2 (508079) 69 kV Bus a. Apply fault at the SUGARHL2 (508079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGARHL2 69 KV 508079 TO SUGHLWT2 69 KV 508082 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SUGHLET2__TEXARK_2 | 3 Phase fault SUGHLET2 (508081) 69 kV Bus a. Apply fault at the SUGHLET2 (508081) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGHLET2 69 KV 508081 TO TEX12ST2 69 KV 508084 CKT 1 b.2. LOAD 1 508084 b.3. TEX12ST2 69 KV 508084 TO WASHST 2 69 KV 508088 CKT 1 b.4. LOAD 1 508088 b.5. TEXARK 2 69 KV 508086 TO WASHST 2 69 KV 508088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SUGHLWT2__TEX39ST2 | 3 Phase fault SUGHLWT2 (508082) 69 kV Bus a. Apply fault at the SUGHLWT2 (508082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGHLWT2 69 KV 508082 TO TEX39ST2 69 KV 508085 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SUMMERG2__LEASIDE_2 | 3 Phase fault SUMMERG2 (507758) 69 kV Bus a. Apply fault at the SUMMERG2 (507758) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMERG2 69 KV 507758 TO LEASIDE 2 69 KV 507794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SUNNYLN2__TINKER32 | 3 Phase fault SUNNYLN2 (514980) 69 kV Bus a. Apply fault at the SUNNYLN2 (514980) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYLN2 69 KV 514980 TO TINKER32 69 KV 514981 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SUNNYSD4__ARDWEST4 | 3 Phase fault SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNIROY 4 138 KV 515137 TO ARDWEST4 138 KV 515372 CKT 1 b.2. LOAD 1 515372 b.3. SUNNYSD4 138 KV 515135 TO UNIROY 4 138 KV 515137 CKT 1 b.4. LOAD 1 515137 b.5. CARTER 4 138 KV 515138 TO ARDWEST4 138 KV 515372 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SUNNYSD4__CARTRCO4 | 3 Phase fault SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138 KV 515135 TO CARTRCO4 138 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SUNNYSD4__LONEGRV4 | 3 Phase fault SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138 KV 515135 TO LONEGRV4 138 KV 515144 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SUNNYSD4__ROCKYPT4 | 3 Phase fault SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138 KV 515135 TO ROCKYPT4 138 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SUNNYSD7__G17 | 3 Phase fault SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345 KV 515136 TO G17-075-TAP 345 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SUNNYSD7__GEN | 3 Phase fault SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345 KV 515136 TO GEN-2017-167 345 KV 761859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SW134TP4__MCCLAIN4 | 3 Phase fault SW134TP4 (514876) 138 kV Bus a. Apply fault at the SW134TP4 (514876) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW134TP4 138 KV 514876 TO MCCLAIN4 138 KV 514902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SW134TP4__NORMHLL4 | 3 Phase fault SW134TP4 (514876) 138 kV Bus a. Apply fault at the SW134TP4 (514876) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW134TP4 138 KV 514876 TO SOGATE 4 138 KV 514928 CKT 1 b.2. LOAD 1 514928 b.3. SOGATE 4 138 KV 514928 TO TURNER 4 138 KV 514992 CKT 1 b.4. LOAD 1 514992 b.5. TURNER 4 138 KV 514992 TO NORMHLL4 138 KV 516097 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SW134TP4__PENN___4 | 3 Phase fault SW134TP4 (514876) 138 kV Bus a. Apply fault at the SW134TP4 (514876) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW134TP4 138 KV 514876 TO WESTMOR4 138 KV 514887 CKT 1 b.2. LOAD 1 514887 b.3. WESTMOR4 138 KV 514887 TO PENN 4 138 KV 514925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SWEETWT6__BUFFCK6 | 3 Phase fault SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230 KV 511541 TO BUFFCK6 230 KV 511542 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SWEETWT6__CHISHOLM6 | 3 Phase fault SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230 KV 511541 TO CHISHOLM6 230 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SWEETWT6__DEMPSEY6 | 3 Phase fault SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230 KV 511541 TO DEMPSEY6 230 KV 511544 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SWEETWT6__ROARK6 | 3 Phase fault SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230 KV 511541 TO ROARK6 230 KV 511547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SWEETWT6__STLN | 3 Phase fault SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230 KV 511541 TO STLN-DEMARC6 230 KV 523779 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SWISHER____6__TUCO_INT___6 | 3 Phase fault SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230 KV 525213 TO TUCO_INT 6 230 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SW_5TH_2__38TH_ST2 | 3 Phase fault SW 5TH 2 (514919) 69 kV Bus a. Apply fault at the SW 5TH 2 (514919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAY AVE2 69 KV 514913 TO SW 5TH 2 69 KV 514919 CKT 1 b.2. 38TH ST2 69 KV 514845 TO MAY AVE2 69 KV 514913 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SW_5TH_2__KENTUKT2 | 3 Phase fault SW 5TH 2 (514919) 69 kV Bus a. Apply fault at the SW 5TH 2 (514919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW 5TH 2 69 KV 514919 TO SW22ND 2 69 KV 514975 CKT 1 b.2. LOAD 1 514975 b.3. SW22ND 2 69 KV 514975 TO KENTUKY2 69 KV 514976 CKT 1 b.4. LOAD 1 514976 b.5. KENTUKY2 69 KV 514976 TO KENTUKT2 69 KV 514977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SW_5TH_4__CLASSEN4 | 3 Phase fault SW 5TH 4 (514920) 138 kV Bus a. Apply fault at the SW 5TH 4 (514920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW 5TH 4 138 KV 514920 TO CLASSEN4 138 KV 514922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SW_64TH2__PENN___2 | 3 Phase fault SW 64TH2 (514918) 69 kV Bus a. Apply fault at the SW 64TH2 (514918) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW 64TH2 69 KV 514918 TO PENN 2 69 KV 514924 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SW_SHV_4__FLOURNY4 | 3 Phase fault SW SHV 4 (507759) 138 kV Bus a. Apply fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENMOTR4 138 KV 507732 TO SW SHV 4 138 KV 507759 CKT 1 b.2. FLOURNY4 138 KV 507727 TO GENMOTR4 138 KV 507732 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SW_SHV_4__LEASIDE_4 | 3 Phase fault SW SHV 4 (507759) 138 kV Bus a. Apply fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW SHV 4 138 KV 507759 TO LEASIDE 4 138 KV 507793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SW_SHV_4__ROKHILL4 | 3 Phase fault SW SHV 4 (507759) 138 kV Bus a. Apply fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRIDGE4 138 KV 507757 TO SW SHV 4 138 KV 507759 CKT 1 b.2. SPRIDGE4 138 KV 507757 TO WLNTSPRINGS4 138 KV 509103 CKT 1 b.3. LOAD 1 509103 b.4. ROKHILL4 138 KV 509083 TO WLNTSPRINGS4 138 KV 509103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SW_SHV_7__DIANA__7 | 3 Phase fault SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345 KV 507760 TO DIANA 7 345 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SW_SHV_7__LONGWD_7 | 3 Phase fault SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345 KV 507760 TO LONGWD 7 345 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_S_SHV__4__CEDARGR4 | 3 Phase fault S SHV 4 (507755) 138 kV Bus a. Apply fault at the S SHV 4 (507755) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138 KV 507755 TO CEDARGR4 138 KV 507771 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_S_SHV__4__SW_SHV_4 | 3 Phase fault S SHV 4 (507755) 138 kV Bus a. Apply fault at the S SHV 4 (507755) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138 KV 507755 TO SW SHV 4 138 KV 507759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_S_SHV__4__WALLAKE4 | 3 Phase fault S SHV 4 (507755) 138 kV Bus a. Apply fault at the S SHV 4 (507755) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138 KV 507755 TO WALLAKE4 138 KV 507765 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_S_SHV__4__WESTELC4 | 3 Phase fault S SHV 4 (507755) 138 kV Bus a. Apply fault at the S SHV 4 (507755) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138 KV 507755 TO WESTELC4 138 KV 507767 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TCONCO_CEMRD_TP4 | 3 Phase fault T-CONCO4 (511424) 138 kV Bus a. Apply fault at the T-CONCO4 (511424) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T-CONCO4 138 KV 511424 TO CEMRD_TP4 138 KV 511576 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_T.NO._46STTP4 | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO 46ST-TP-4 138 KV 509900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_T.NO._BARNSAL4 | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO SKIATOK4 138 KV 509884 CKT 1 b.2. LOAD 1 509884 b.3. SKIATOK4 138 KV 509884 TO BARNSAL4 138 KV 510388 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_T.NO._CDC-ET4 | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO CDC-ET 4 138 KV 509839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_T.NO._CDC-WT4 | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO CDC-WT 4 138 KV 509842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_T.NO._NES | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO N.E.S.-4 138 KV 510396 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_T.NO._OWASOTP | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO OWASOTP4 138 KV 509844 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_T.NO._P&PWTP4 | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO P&P WTP4 138 KV 509851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_T.NO._TNO24 | 3 Phase fault T.NO.--4 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 138 KV 509817 TO T.NO.2-4 138 KV 509895 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_T.NO._CLEVLND7 | 3 Phase fault T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345 KV 509852 TO CLEVLND7 345 KV 512694 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_T.NO._IGLOOV7 | 3 Phase fault T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345 KV 509852 TO IGLOOV 7 345 KV 513596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_T.NO._NES7 | 3 Phase fault T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345 KV 509852 TO N.E.S.-7 345 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_T.NO.2_GEN-2018-028 | 3 Phase fault T.NO.2-4 (509895) 138 kV Bus a. Apply fault at the T.NO.2-4 (509895) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.2-4 138 KV 509895 TO GEN-2018-028 138 KV 762636 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_T.P.S._52DELWT | 3 Phase fault T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138 KV 509788 TO 52DELWT4 138 KV 509814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_T.P.S._CARSN-T4 | 3 Phase fault T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 36&OLY-4 138 KV 509724 TO T.P.S.-4 138 KV 509788 CKT 1 b.2. LOAD 1 509788 b.3. 36&OLY-4 138 KV 509724 TO CARSN-T4 138 KV 509739 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_T.P.S._GEN-2018-027 | 3 Phase fault T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138 KV 509788 TO GEN-2018-027 138 KV 762625 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_T.P.S._OAKSETP4 | 3 Phase fault T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138 KV 509788 TO OAKSETP4 138 KV 509850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_T.P.S._OAKSWTP4 | 3 Phase fault T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138 KV 509788 TO OAKSWTP4 138 KV 509848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_T.P.S._SAPLPRD | 3 Phase fault T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138 KV 509788 TO 72ELWOD4 138 KV 509888 CKT 1 b.2. LOAD 1 509888 b.3. SAPLPRD4 138 KV 509871 TO 72ELWOD4 138 KV 509888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_T.S.E._21STTAP4 | 3 Phase fault T.S.E.-4 (509811) 138 kV Bus a. Apply fault at the T.S.E.-4 (509811) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.S.E.-4 138 KV 509811 TO 21STTAP4 138 KV 509828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_T.S.E._E61ST | 3 Phase fault T.S.E.-4 (509811) 138 kV Bus a. Apply fault at the T.S.E.-4 (509811) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.S.E.-4 138 KV 509811 TO E.61ST-4 138 KV 509831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_T.S.E._KENSHETP4 | 3 Phase fault T.S.E.-4 (509811) 138 kV Bus a. Apply fault at the T.S.E.-4 (509811) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.S.E.-4 138 KV 509811 TO KENSH-E-TP4 138 KV 509830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_T.S.E._SHUD4 | 3 Phase fault T.S.E.-4 (509811) 138 kV Bus a. Apply fault at the T.S.E.-4 (509811) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.S.E.-4 138 KV 509811 TO S.HUD.-4 138 KV 509833 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TAHLQH_5__BRIGSKM_5 | 3 Phase fault TAHLQH 5 (512655) 161 kV Bus a. Apply fault at the TAHLQH 5 (512655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 161 KV 512655 TO BRIGSKM 5 161 KV 513044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TAHLQH_5__HWY59TP5 | 3 Phase fault TAHLQH 5 (512655) 161 kV Bus a. Apply fault at the TAHLQH 5 (512655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 161 KV 512655 TO HWY59TP5 161 KV 515527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TALOGA_2__HMBTTP | 3 Phase fault TALOGA 2 (521064) 69 kV Bus a. Apply fault at the TALOGA 2 (521064) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STALOGA2 69 KV 520454 TO TALOGA 2 69 KV 521064 CKT 1 b.2. STALOGA2 69 KV 520454 TO PUTNAM 2 69 KV 521033 CKT 1 b.3. LOAD 1 521033 b.4. HM-BTTP2 69 KV 520942 TO PUTNAM 2 69 KV 521033 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TALOGA_2__WOODWRD2 | 3 Phase fault TALOGA 2 (521064) 69 kV Bus a. Apply fault at the TALOGA 2 (521064) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALOGA 2 69 KV 521064 TO VICI 2 69 KV 521082 CKT 1 b.2. LOAD 1 521082 b.3. VICI 2 69 KV 521082 TO WOODWRD2 69 KV 521096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TALOGA_4__MOORLND4 | 3 Phase fault TALOGA 4 (521065) 138 kV Bus a. Apply fault at the TALOGA 4 (521065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEILING4 138 KV 520553 TO TALOGA 4 138 KV 521065 CKT 1 b.2. SEILING4 138 KV 520553 TO MOORLND4 138 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TATONGA7__CRSRDSW7 | 3 Phase fault TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345 KV 515407 TO CRSRDSW7 345 KV 515448 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TATONGA7__MAMTHPW7 | 3 Phase fault TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345 KV 515407 TO MAMTHPW7 345 KV 515585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TATONGA7__MATHWSN7 | 3 Phase fault TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345 KV 515407 TO MATHWSN7 345 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TATONGA7__SLNGWND7 | 3 Phase fault TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345 KV 515407 TO SLNGWND7 345 KV 515582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TAYLOR_2__TEX39ST2 | 3 Phase fault TAYLOR 2 (508083) 69 kV Bus a. Apply fault at the TAYLOR 2 (508083) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 2 69 KV 508083 TO TEX39ST2 69 KV 508085 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TAYLOR_2__TEXARK_2 | 3 Phase fault TAYLOR 2 (508083) 69 kV Bus a. Apply fault at the TAYLOR 2 (508083) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 2 69 KV 508083 TO TEXARK 2 69 KV 508086 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TECUMSH2__FRSTHIL2 | 3 Phase fault TECUMSH2 (515071) 69 kV Bus a. Apply fault at the TECUMSH2 (515071) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECUMSH2 69 KV 515071 TO FRSTHIL2 69 KV 515074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TENESTP4__84TH_ST4 | 3 Phase fault TENESTP4 (514837) 138 kV Bus a. Apply fault at the TENESTP4 (514837) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TENESTP4 138 KV 514837 TO 84TH ST4 138 KV 514843 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TERNIT_TERNITP4 | 3 Phase fault TER-NIT4 (509723) 138 kV Bus a. Apply fault at the TER-NIT4 (509723) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TER-NIT4 138 KV 509723 TO PCATOSA4 138 KV 509725 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TERNIT_TERNITP4 | 3 Phase fault TER-NIT4 (509723) 138 kV Bus a. Apply fault at the TER-NIT4 (509723) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TER-NIT4 138 KV 509723 TO TERNITP4 138 KV 509835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TERNITP4__VERDIGS4 | 3 Phase fault TERNITP4 (509835) 138 kV Bus a. Apply fault at the TERNITP4 (509835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERNITP4 138 KV 509835 TO VERDIGS4 138 KV 509854 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TERRYRD7__G17_171_TAP | 3 Phase fault TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345 KV 511568 TO G17-171-TAP 345 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TERRYRD7__RSHSPR1_MPT1 | 3 Phase fault TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345 KV 511568 TO RSHSPR1_MPT1 345 KV 511979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TERRYRD7__RUSHSPR7 | 3 Phase fault TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345 KV 511568 TO RUSHSPR7 345 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TERRYRD7__SUNNYSD7 | 3 Phase fault TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345 KV 511568 TO SUNNYSD7 345 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TEXARK_2__IPC_TAP2 | 3 Phase fault TEXARK 2 (508086) 69 kV Bus a. Apply fault at the TEXARK 2 (508086) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S_TEXARK 2 69 KV 504117 TO PLEASHL2 69 KV 508048 CKT 1 b.2. LOAD 1 508048 b.3. S_TEXARK 2 69 KV 504117 TO TEXARK 2 69 KV 508086 CKT 1 b.4. LOAD 1 508086 b.5. PLEASHL2 69 KV 508048 TO IPC TAP2 69 KV 508058 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_THISTLE7__GEN_2017-018 | 3 Phase fault THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345 KV 539801 TO GEN-2017-018 345 KV 588630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_THISTLE7__GEN-2018-049 | 3 Phase fault THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345 KV 539801 TO GEN-2018-049 345 KV 762834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TINKER54__BARNES_4 | 3 Phase fault TINKER54 (514994) 138 kV Bus a. Apply fault at the TINKER54 (514994) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TINKER54 138 KV 514994 TO BARNES 4 138 KV 515003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TOLK_______6__TUCO_INT___6 | 3 Phase fault TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230 KV 525531 TO TUCO_INT 6 230 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TROSPER4__RENO___4 | 3 Phase fault TROSPER4 (514963) 138 kV Bus a. Apply fault at the TROSPER4 (514963) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROSPER4 138 KV 514963 TO RENO 4 138 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TUCO_INT___6__ANTELOPE_1_6 | 3 Phase fault TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230 KV 525830 TO ANTELOPE_1 6 230 KV 525840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TUCO_INT___6__CARLISLE___6 | 3 Phase fault TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230 KV 525830 TO CARLISLE 6 230 KV 526161 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TUCO_INT___6__HALE_WNDCL16 | 3 Phase fault TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230 KV 525830 TO HALE_WNDCL16 230 KV 525957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TUCO_INT___6__JONES______6 | 3 Phase fault TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230 KV 525830 TO JONES 6 230 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TUCO_INT___7__ELK_CT1 | 3 Phase fault TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345 KV 525832 TO ELK_CT1 345 KV 525850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TUCO_INT___7__G17 | 3 Phase fault TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345 KV 525832 TO G17-151TAP 345 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TUCO_INT___7__YOAKUM_345 | 3 Phase fault TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345 KV 525832 TO YOAKUM_345 345 KV 526936 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TURCRK_2__TURCRKT2 | 3 Phase fault TURCRK 2 (514735) 69 kV Bus a. Apply fault at the TURCRK 2 (514735) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURCRK 2 69 KV 514735 TO TURCRKT2 69 KV 515517 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TURK___3__HOPE___3 | 3 Phase fault TURK 3 (507456) 115 kV Bus a. Apply fault at the TURK 3 (507456) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCNAB 3 115 KV 504122 TO TURK 3 115 KV 507456 CKT 1 b.2. MCNAB 3 115 KV 504122 TO HOPE 3 115 KV 507453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TURK___4__MANDEVILTP4 | 3 Phase fault TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 4 138 KV 507454 TO MANDEVILTP4 138 KV 508105 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TURK___4__SUGARHL4 | 3 Phase fault TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 4 138 KV 507454 TO SUGARHL4 138 KV 508080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TURK___7__NWTXARK7 | 3 Phase fault TURK 7 (507455) 345 kV Bus a. Apply fault at the TURK 7 (507455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURK 7 345 KV 507455 TO NWTXARK7 345 KV 508072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TUTCONT4__CEMRD_TP4 | 3 Phase fault TUTCONT4 (511425) 138 kV Bus a. Apply fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTCONT4 138 KV 511425 TO CEMRD_TP4 138 KV 511576 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TUTCONT4__CIMARON4 | 3 Phase fault TUTCONT4 (511425) 138 kV Bus a. Apply fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTCONT4 138 KV 511425 TO CIMARON4 138 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TUTCONT4__LEONARD4 | 3 Phase fault TUTCONT4 (511425) 138 kV Bus a. Apply fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTCONT4 138 KV 511425 TO TUTTLE4 138 KV 511501 CKT 1 b.2. LOAD 1 511501 b.3. TUTTLE4 138 KV 511501 TO LEONARD4 138 KV 511575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TUTTLE_4__TUTLETP4 | 3 Phase fault TUTTLE 4 (520496) 138 kV Bus a. Apply fault at the TUTTLE 4 (520496) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTTLE 4 138 KV 520496 TO TUTLETP4 138 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TWNLKJT4__TWNLKSW4 | 3 Phase fault TWNLKJT4 (520847) 138 kV Bus a. Apply fault at the TWNLKJT4 (520847) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWNLKJT4 138 KV 520847 TO TWNLKSW4 138 KV 521073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TXPLSTE2__TXPLSTP2 | 3 Phase fault TXPLSTE2 (514989) 69 kV Bus a. Apply fault at the TXPLSTE2 (514989) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXPLSTE2 69 KV 514989 TO TXPLSTP2 69 KV 515516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TXSTELA2__LITLAXT2 | 3 Phase fault TXSTELA2 (514985) 69 kV Bus a. Apply fault at the TXSTELA2 (514985) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXSTELA2 69 KV 514985 TO LITLAXT2 69 KV 515502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TXSTELA2__TXPLSTP2 | 3 Phase fault TXSTELA2 (514985) 69 kV Bus a. Apply fault at the TXSTELA2 (514985) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXSTELA2 69 KV 514985 TO TXPLSTP2 69 KV 515516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_VWEYCO4_VALIANT4 | 3 Phase fault V-WEYCO4 (510866) 138 kV Bus a. Apply fault at the V-WEYCO4 (510866) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. V-WEYCO4 138 KV 510866 TO VALIANT4 138 KV 510918 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_VALIANT4__B.BOWTP4 | 3 Phase fault VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IDABEL-4 138 KV 510886 TO VALIANT4 138 KV 510918 CKT 1 b.2. IDABEL-4 138 KV 510886 TO B.BOWTP4 138 KV 510888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_VALIANT4__HUGO_PP4 | 3 Phase fault VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 138 KV 510918 TO HUGO PP4 138 KV 520948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_VALIANT7__HUGO___7 | 3 Phase fault VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345 KV 510911 TO HUGO 7 345 KV 521157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_VANCE__2__SO4TH__2 | 3 Phase fault VANCE 2 (514718) 69 kV Bus a. Apply fault at the VANCE 2 (514718) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANCE 2 69 KV 514718 TO SO4TH 2 69 KV 514730 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_VANOSS_4__PARKLN_4 | 3 Phase fault VANOSS 4 (515174) 138 kV Bus a. Apply fault at the VANOSS 4 (515174) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANOSS 4 138 KV 515174 TO PARKLN 4 138 KV 515178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_VANOSS_4__VANOSTP4 | 3 Phase fault VANOSS 4 (515174) 138 kV Bus a. Apply fault at the VANOSS 4 (515174) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANOSS 4 138 KV 515174 TO VANOSTP4 138 KV 515531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_VINITA_VINITAJC2 | 3 Phase fault VINITA-2 (510404) 69 kV Bus a. Apply fault at the VINITA-2 (510404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINITA-2 69 KV 510404 TO VINTAJC2 69 KV 510418 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_VINTAJC4__ALWUETP4 | 3 Phase fault VINTAJC4 (510417) 138 kV Bus a. Apply fault at the VINTAJC4 (510417) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC4 138 KV 510417 TO ALWUETP4 138 KV 510429 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_VINTAJC4__HOC404_4 | 3 Phase fault VINTAJC4 (510417) 138 kV Bus a. Apply fault at the VINTAJC4 (510417) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC4 138 KV 510417 TO HOC404 4 138 KV 547486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_W.ED._CARSONT4 | 3 Phase fault W.ED.-W4 (509832) 138 kV Bus a. Apply fault at the W.ED.-W4 (509832) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W.ED.-W4 138 KV 509832 TO CARSONT4 138 KV 509865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WARNTAP4__77MEMW4 | 3 Phase fault WARNTAP4 (509858) 138 kV Bus a. Apply fault at the WARNTAP4 (509858) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 96YALE-4 138 KV 509847 TO WARNTAP4 138 KV 509858 CKT 1 b.2. 77MEM-W4 138 KV 509766 TO 96YALE-4 138 KV 509847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WARWICK4__BELLCOW4 | 3 Phase fault WARWICK4 (515047) 138 kV Bus a. Apply fault at the WARWICK4 (515047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARWICK4 138 KV 515047 TO BELLCOW4 138 KV 515369 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WARWICK4__TRYON_4 | 3 Phase fault WARWICK4 (515047) 138 kV Bus a. Apply fault at the WARWICK4 (515047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARWICK4 138 KV 515047 TO TRYON 4 138 KV 515675 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WARWICK4__WFROSST4 | 3 Phase fault WARWICK4 (515047) 138 kV Bus a. Apply fault at the WARWICK4 (515047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARWICK4 138 KV 515047 TO WFROSST4 138 KV 515366 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WASHITA4__BINGERJ4 | 3 Phase fault WASHITA4 (521089) 138 kV Bus a. Apply fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEY 4 138 KV 521017 TO WASHITA4 138 KV 521089 CKT 1 b.2. BINGERJ4 138 KV 520827 TO ONEY 4 138 KV 521017 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WASHITA4__SLKHILLS_4 | 3 Phase fault WASHITA4 (521089) 138 kV Bus a. Apply fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 138 KV 521089 TO SLKHILLS 4 138 KV 521103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WATLANT4__CASSTP4 | 3 Phase fault WATLANT4 (508090) 138 kV Bus a. Apply fault at the WATLANT4 (508090) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138 KV 508090 TO CASSTP4 138 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WATLANT4__WILKES_4 | 3 Phase fault WATLANT4 (508090) 138 kV Bus a. Apply fault at the WATLANT4 (508090) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138 KV 508090 TO WILKES 4 138 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WATNGSW4__CALUMET4 | 3 Phase fault WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138 KV 520536 TO CALUMET4 138 KV 520839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WATNGSW4__FAY____4 | 3 Phase fault WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138 KV 520536 TO WATONGA4 138 KV 521091 CKT 1 b.2. LOAD 1 521091 b.3. FAY 4 138 KV 520538 TO WATONGA4 138 KV 521091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WATNGSW4__KGFSHSW4 | 3 Phase fault WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138 KV 520536 TO OMEGA 4 138 KV 520964 CKT 1 b.2. LOAD 1 520964 b.3. PARKCOM4 138 KV 520475 TO OMEGA 4 138 KV 520964 CKT 1 b.4. LOAD 1 520964 b.5. PARKCOM4 138 KV 520475 TO KGFSHSW4 138 KV 520533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WATNGSW4__OKEENE_4 | 3 Phase fault WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138 KV 520536 TO OKEENE 4 138 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WAUKOTP4__HENESEY4 | 3 Phase fault WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 138 KV 514710 TO HENESEY4 138 KV 514774 CKT 1 b.2. LOAD 1 514774 b.3. WAUKOMI4 138 KV 514710 TO WAUKOTP4 138 KV 514711 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WAUKOTP4__SO4TH__4 | 3 Phase fault WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138 KV 514711 TO SO4TH 4 138 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WAUKOTP4__WOODRNG4 | 3 Phase fault WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138 KV 514711 TO WOODRNG4 138 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WCITYTP2__VALIANT2 | 3 Phase fault WCITYTP2 (510870) 69 kV Bus a. Apply fault at the WCITYTP2 (510870) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WCITYTP2 69 KV 510870 TO VALIANT2 69 KV 510910 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WED_CARSON4 | 3 Phase fault WED-TAP4 (509823) 138 kV Bus a. Apply fault at the WED-TAP4 (509823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WED-TAP4 138 KV 509823 TO CARSONT4 138 KV 509865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WEKIWA_GEN_2010_055 | 3 Phase fault WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138 KV 509757 TO GEN-2010-055 138 KV 560389 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WEKIWA_P&PWTP4 | 3 Phase fault WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138 KV 509757 TO P&P WTP4 138 KV 509851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WEKIWA_SS4 | 3 Phase fault WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEFFD-4 138 KV 509812 TO S.S.---4 138 KV 509815 CKT 1 b.2. LOAD 1 509815 b.3. WEKIWA-4 138 KV 509757 TO SHEFFD-4 138 KV 509812 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WEKIWA_SHEFFD | 3 Phase fault WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138 KV 509757 TO SHEFFD-4 138 KV 509812 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WEKIWA_SILCTYGR4 | 3 Phase fault WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138 KV 509757 TO SILVCTYGR4 138 KV 512726 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WEKIWA_WEDTAP4 | 3 Phase fault WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138 KV 509757 TO WED-TAP4 138 KV 509823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WEKIWA_SAPLPRD | 3 Phase fault WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345 KV 509755 TO SAPLPRD7 345 KV 509870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WEKIWA_SOONER | 3 Phase fault WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345 KV 509755 TO SOONER 7 345 KV 514803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WEKIWA_TNO7 | 3 Phase fault WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345 KV 509755 TO T.NO.--7 345 KV 509852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WELLSPA2__ONAPA__2 | 3 Phase fault WELLSPA2 (515215) 69 kV Bus a. Apply fault at the WELLSPA2 (515215) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELLSPA2 69 KV 515215 TO ONAPA 2 69 KV 521020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WELSHRE4__WILKES_4 | 3 Phase fault WELSHRE4 (508355) 138 kV Bus a. Apply fault at the WELSHRE4 (508355) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELSHRE4 138 KV 508355 TO WILKES 4 138 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WELSH__7__DIANA__7 | 3 Phase fault WELSH 7 (508359) 345 kV Bus a. Apply fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345 KV 508359 TO DIANA 7 345 KV 508832 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WELSH__7__WILKES_7 | 3 Phase fault WELSH 7 (508359) 345 kV Bus a. Apply fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345 KV 508359 TO WILKES 7 345 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WESTELC4__LEASIDE_4 | 3 Phase fault WESTELC4 (507767) 138 kV Bus a. Apply fault at the WESTELC4 (507767) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTELC4 138 KV 507767 TO LEASIDE 4 138 KV 507793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WESTERN4__STNWAL_4 | 3 Phase fault WESTERN4 (514869) 138 kV Bus a. Apply fault at the WESTERN4 (514869) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTERN4 138 KV 514869 TO STNWAL 4 138 KV 514870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WESTHSE4__INDNHIL4 | 3 Phase fault WESTHSE4 (514904) 138 kV Bus a. Apply fault at the WESTHSE4 (514904) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTHSE4 138 KV 514904 TO INDNHIL4 138 KV 514954 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WFROSST4__LINCOLN4 | 3 Phase fault WFROSST4 (515366) 138 kV Bus a. Apply fault at the WFROSST4 (515366) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WFROSST4 138 KV 515366 TO LINCOLN4 138 KV 515442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WFROSST4__RSSVILE4 | 3 Phase fault WFROSST4 (515366) 138 kV Bus a. Apply fault at the WFROSST4 (515366) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WFROSST4 138 KV 515366 TO RSSVILE4 138 KV 521107 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WHEELER____3__HOWARD_____3 | 3 Phase fault WHEELER 3 (523776) 115 kV Bus a. Apply fault at the WHEELER 3 (523776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 3 115 KV 523776 TO HOWARD 3 115 KV 523797 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WHEELER____6__STLN | 3 Phase fault WHEELER 6 (523777) 230 kV Bus a. Apply fault at the WHEELER 6 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 230 KV 523777 TO STLN-DEMARC6 230 KV 523779 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WHIRLPO4__CDC | 3 Phase fault WHIRLPO4 (509840) 138 kV Bus a. Apply fault at the WHIRLPO4 (509840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHIRLPO4 138 KV 509840 TO CDC-WT 4 138 KV 509842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WHITNEY4__EASTEX_4 | 3 Phase fault WHITNEY4 (508575) 138 kV Bus a. Apply fault at the WHITNEY4 (508575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY4 138 KV 508575 TO EASTEX 4 138 KV 508582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WHORSE_HWY20 | 3 Phase fault WHORSE-4 (509754) 138 kV Bus a. Apply fault at the WHORSE-4 (509754) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHORSE-4 138 KV 509754 TO HWY20-T4 138 KV 509821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WILKES_4__CHAPELH4 | 3 Phase fault WILKES 4 (508840) 138 kV Bus a. Apply fault at the WILKES 4 (508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPELH4 138 KV 508337 TO WELSHRE4 138 KV 508355 CKT 1 b.2. LOAD 1 508355 b.3. WELSHRE4 138 KV 508355 TO WILKES 4 138 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WINDFRM4__MOORLND4 | 3 Phase fault WINDFRM4 (515785) 138 kV Bus a. Apply fault at the WINDFRM4 (515785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 138 KV 515785 TO MOORLND4 138 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WLNUTCK4__PAOLI | 3 Phase fault WLNUTCK4 (515097) 138 kV Bus a. Apply fault at the WLNUTCK4 (515097) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WLNUTCK4 138 KV 515097 TO PAOLI- 4 138 KV 515100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WODWRD_2__WOODWRD2 | 3 Phase fault WODWRD 2 (514782) 69 kV Bus a. Apply fault at the WODWRD 2 (514782) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WODWRD 2 69 KV 514782 TO WOODWRD2 69 KV 521096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WOLFCRK4__CHEEKTP4 | 3 Phase fault WOLFCRK4 (515143) 138 kV Bus a. Apply fault at the WOLFCRK4 (515143) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK4 138 KV 515143 TO CHEEKTP4 138 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WOLVERN4__WOLVRNT4 | 3 Phase fault WOLVERN4 (515056) 138 kV Bus a. Apply fault at the WOLVERN4 (515056) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLVERN4 138 KV 515056 TO WOLVRNT4 138 KV 515532 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WOODRNG4__MARSHL_4 | 3 Phase fault WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 138 KV 514714 TO MARSHL 4 138 KV 514733 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WOODRNG7__GEN-2017-164 | 3 Phase fault WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345 KV 514715 TO GEN-2017-164 345 KV 762321 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WOODRNG7__HUNTERS7 | 3 Phase fault WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345 KV 514715 TO HUNTERS7 345 KV 515476 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WOODRNG7__PINTAIL7 | 3 Phase fault WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345 KV 514715 TO PINTAIL7 345 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WOODRNG7__REDNGTN7 | 3 Phase fault WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345 KV 514715 TO REDNGTN7 345 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WOODRNG7__SKELTON7 | 3 Phase fault WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345 KV 514715 TO SKELTON7 345 KV 515990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WOODWRD2__CRTSJCT2 | 3 Phase fault WOODWRD2 (521096) 69 kV Bus a. Apply fault at the WOODWRD2 (521096) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD2 69 KV 521096 TO CRTSJCT2 69 KV 521197 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WOODWRD2__FARGOJCT2 | 3 Phase fault WOODWRD2 (521096) 69 kV Bus a. Apply fault at the WOODWRD2 (521096) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD2 69 KV 521096 TO FARGOJCT2 69 KV 521196 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WOODWRD4__CENT___4 | 3 Phase fault WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138 KV 514785 TO CENT 4 138 KV 515363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WOODWRD4__WINDFRM4 | 3 Phase fault WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138 KV 514785 TO WINDFRM4 138 KV 515785 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WOODWRD4__WWRDEHV4 | 3 Phase fault WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138 KV 514785 TO WWRDEHV4 138 KV 515376 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WRNMED_WRNMEDT4 | 3 Phase fault WRN-MED4 (509729) 138 kV Bus a. Apply fault at the WRN-MED4 (509729) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRN-MED4 138 KV 509729 TO WRNMEDT4 138 KV 509764 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WRNMEDT4__81YALTP4 | 3 Phase fault WRNMEDT4 (509764) 138 kV Bus a. Apply fault at the WRNMEDT4 (509764) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRNMEDT4 138 KV 509764 TO 81YALTP4 138 KV 509809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WRNMEDT4__S.HUD. | 3 Phase fault WRNMEDT4 (509764) 138 kV Bus a. Apply fault at the WRNMEDT4 (509764) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRNMEDT4 138 KV 509764 TO S.HUD.-4 138 KV 509833 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WWRDEHV4__KEENAN_4 | 3 Phase fault WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138 KV 515376 TO KEENAN 4 138 KV 515394 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WWRDEHV4__OUSPRT_4 | 3 Phase fault WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138 KV 515376 TO OUSPRT 4 138 KV 515398 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WWRDEHV4__REDCLFT4 | 3 Phase fault WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IODINE-4 138 KV 514796 TO WWRDEHV4 138 KV 515376 CKT 1 b.2. IODINE-4 138 KV 514796 TO REDCLFT4 138 KV 515533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WWRDEHV4__WWDPST_4 | 3 Phase fault WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138 KV 515376 TO WWDPST 4 138 KV 515425 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WWRDEHV7__BECKHAM7 | 3 Phase fault WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345 KV 515375 TO BECKHAM7 345 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WWRDEHV7__DGRASSE7 | 3 Phase fault WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345 KV 515375 TO DGRASSE7 345 KV 515852 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WWRDEHV7__G07621119 | 3 Phase fault WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345 KV 515375 TO G07621119-20 345 KV 515599 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WWRDEHV7__G16 | 3 Phase fault WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345 KV 515375 TO G16-003-TAP 345 KV 560071 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WWRDEHV7__GUTHRIE7 | 3 Phase fault WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345 KV 515375 TO GUTHRIE7 345 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WWRDEHV7__TATONGA7 | 3 Phase fault WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345 KV 515375 TO TATONGA7 345 KV 515407 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_YARCH_YARCHT4 | 3 Phase fault YARCH-N4 (509825) 138 kV Bus a. Apply fault at the YARCH-N4 (509825) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YARCH-N4 138 KV 509825 TO YARCHT 4 138 KV 509862 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_YARCH_PPTAP | 3 Phase fault YARCH-S4 (509824) 138 kV Bus a. Apply fault at the YARCH-S4 (509824) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YARCH-S4 138 KV 509824 TO KENSH-E-TP4 138 KV 509830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_YARCHT_4__PPTAP__4 | 3 Phase fault YARCHT 4 (509862) 138 kV Bus a. Apply fault at the YARCHT 4 (509862) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YARCHT 4 138 KV 509862 TO PPTAP 4 138 KV 509863 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_YOAKUM_345__HOBBS_INT__7 | 3 Phase fault YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345 KV 526936 TO HOBBS_INT 7 345 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ZUNIS_FULTONW4 | 3 Phase fault ZUNIS-N4 (509827) 138 kV Bus a. Apply fault at the ZUNIS-N4 (509827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ZUNIS-N4 138 KV 509827 TO FULTONW4 138 KV 509829 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_38TH_ST2__514846 | 3 Phase fault 38TH ST2 (514845) 69 kV Bus a. Apply fault at the 38TH ST2 (514845) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 38TH ST2 514845 TO 38TH ST4 514846 TO 38TH ST1 515768 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_4MURFBORO__337673 | 3 Phase fault 4MURFBORO (337672) 138 kV Bus a. Apply fault at the 4MURFBORO (337672) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MURFBORO 337672 TO 3MURFBORO.S! 337673 TO 1MURFBORO 337671 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_5TRIBES2__515228 | 3 Phase fault 5TRIBES2 (515227) 69 kV Bus a. Apply fault at the 5TRIBES2 (515227) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TRIBES2 515227 TO 5TRIBES5 515228 TO 5TRIBES1 515723 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_8ANO%__337912 | 3 Phase fault 8ANO% (337909) 500 kV Bus a. Apply fault at the 8ANO% (337909) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 337909 TO 5ANO% 337912 TO 1ANO AUX 337913 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_8EL_DORADO%__337539 | 3 Phase fault 8EL DORADO% (337561) 500 kV Bus a. Apply fault at the 8EL DORADO% (337561) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 337561 TO 3EL DORADO! 337539 TO 1EL DORADO3 337566 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_8EL_DORADO%__337562 | 3 Phase fault 8EL DORADO% (337561) 500 kV Bus a. Apply fault at the 8EL DORADO% (337561) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 337561 TO 7EL DORADO 337562 TO 1EL DORADO2 337565 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_8STERLING%__337415 | 3 Phase fault 8STERLING% (337420) 500 kV Bus a. Apply fault at the 8STERLING% (337420) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8STERLING% 337420 TO 3STERLING% 337415 TO 1STERLING3 337412 CKT 3 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_AGENCY_2__515230 | 3 Phase fault AGENCY 2 (515229) 69 kV Bus a. Apply fault at the AGENCY 2 (515229) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AGENCY 2 515229 TO AGENCY 5 515230 TO AGENCY 1 515701 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ANADARK4__520810 | 3 Phase fault ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 520814 TO ANADARK2 520810 TO ADRKTERT 521181 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ARCADIA4__514908 | 3 Phase fault ARCADIA4 (514907) 138 kV Bus a. Apply fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 514907 TO ARCADIA7 514908 TO ARCADI31 515704 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ARSHILL2__507711 | 3 Phase fault ARSHILL2 (507710) 69 kV Bus a. Apply fault at the ARSHILL2 (507710) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL2 507710 TO ARSHILL4 507711 TO ARSH2-1 507714 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BANN___2__508054 | 3 Phase fault BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 508053 TO BANN 4 508054 TO BANN1-1 508097 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BEELINE2__515247 | 3 Phase fault BEELINE2 (515246) 69 kV Bus a. Apply fault at the BEELINE2 (515246) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEELINE2 515246 TO BEELINE4 515247 TO BEELINE1 515705 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BLUEBEL2__515242 | 3 Phase fault BLUEBEL2 (515241) 69 kV Bus a. Apply fault at the BLUEBEL2 (515241) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBEL2 515241 TO BLUEBEL4 515242 TO BLUEBEL1 515706 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BRISTOW2__515035 | 3 Phase fault BRISTOW2 (515034) 69 kV Bus a. Apply fault at the BRISTOW2 (515034) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW2 515034 TO BRISTOW4 515035 TO BRISTOW1 515709 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_BV_XFMR | 3 Phase fault BV-COM-2 (510389) 69 kV Bus a. Apply fault at the BV-COM-2 (510389) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BV-COM-2 510389 TO BV-COM-4 510390 TO BVCOM3-1 510372 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CRIVER_XFMR | 3 Phase fault C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 515422 TO C-RIVER4 510946 TO C-RIVER1 510947 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CANADNS4__520841 | 3 Phase fault CANADNS4 (520842) 138 kV Bus a. Apply fault at the CANADNS4 (520842) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 520842 TO CANADNS2 520841 TO CANTERT 521164 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CATOOSA2__509790 | 3 Phase fault CATOOSA2 (509799) 69 kV Bus a. Apply fault at the CATOOSA2 (509799) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA2 509799 TO CATOOSA4 509790 TO CATOO1-1 509867 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CATSAGR5__509790 | 3 Phase fault CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 512638 TO CATOOSA4 509790 TO 512835 CKT 3 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CHAMSPR5__506945 | 3 Phase fault CHAMSPR5 (506944) 161 kV Bus a. Apply fault at the CHAMSPR5 (506944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAMSPR5 506944 TO CHAMSPR7 506945 TO CHAMSPR1 506919 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CHISHOLM6__511553 | 3 Phase fault CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6 (511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CIMARON4__514901 | 3 Phase fault CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 514898 TO CIMARON7 514901 TO CIMARO21 515715 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CLARMR_5__512679 | 3 Phase fault CLARMR 5 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 512651 TO CLARMR 2 512679 TO CLARMR2 512815 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CLARMR_5__512707 | 3 Phase fault CLARMR 5 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 512651 TO CLARMR 4 512707 TO CLARMR4 512813 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CLEVLND7__512729 | 3 Phase fault CLEVLND7 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 512694 TO CLEVLND 4 512729 TO CLEVLND1 512817 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_COLINS_5__512705 | 3 Phase fault COLINS 5 (512627) 161 kV Bus a. Apply fault at the COLINS 5 (512627) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINS 5 512627 TO COLLINS4 512705 TO COLLIN1 1 512838 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_COLNSGR2__512627 | 3 Phase fault COLNSGR2 (512870) 69 kV Bus a. Apply fault at the COLNSGR2 (512870) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLNSGR2 512870 TO COLINS 5 512627 TO COLLIN3 1 512840 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_CORNVIL2__511449 | 3 Phase fault CORNVIL2 (511450) 69 kV Bus a. Apply fault at the CORNVIL2 (511450) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL2 511450 TO CORNVIL4 511449 TO CORNV2-1 511418 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DAWSON_XFMR | 3 Phase fault DAWSON-2 (509791) 69 kV Bus a. Apply fault at the DAWSON-2 (509791) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSON-2 509791 TO DAWSON-4 509792 TO DAWSN3-1 509877 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DELWARE4__510380 | 3 Phase fault DELWARE4 (510379) 138 kV Bus a. Apply fault at the DELWARE4 (510379) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELWARE4 510379 TO DELWARE7 510380 TO DELAWAR1 510370 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DEQUEEN2__507419 | 3 Phase fault DEQUEEN2 (507418) 69 kV Bus a. Apply fault at the DEQUEEN2 (507418) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEQUEEN2 507418 TO DEQUEEN4 507419 TO DQUEN1-1 507441 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DGRASSE4__515852 | 3 Phase fault DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 515853 TO DGRASSE7 515852 TO DGRASSE1 515854 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DIANA__4__508832 | 3 Phase fault DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 508831 TO DIANA 7 508832 TO DIANA-N1 508845 CKT 3 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DOVERSW4__520881 | 3 Phase fault DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 520882 TO DOVERSW2 520881 TO DVRTERT 521166 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_DRAPER_4__514934 | 3 Phase fault DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 514933 TO DRAPER 7 514934 TO DRAPER21 515792 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ELGINJT2__511486 | 3 Phase fault ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2 (511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ELKCTY_XFMR | 3 Phase fault ELKCTY-2 (511459) 69 kV Bus a. Apply fault at the ELKCTY-2 (511459) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-2 511459 TO ELKCTY-4 511458 TO ELKC4-1 511493 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ELKCTY_XFMR | 3 Phase fault ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 511458 TO ELKCITY6 511490 TO ELKC2-1 511482 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ELRENO_2__514819 | 3 Phase fault ELRENO 2 (514818) 69 kV Bus a. Apply fault at the ELRENO 2 (514818) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELRENO 2 514818 TO EL-RENO4 514819 TO EL RENO1 515722 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FLETCH_XFMR | 3 Phase fault FLETCH-4 (520912) 138 kV Bus a. Apply fault at the FLETCH-4 (520912) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCH-4 520912 TO FLETCHR2 520911 TO FLCHTERT 521168 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FLOURNY2__507727 | 3 Phase fault FLOURNY2 (507726) 69 kV Bus a. Apply fault at the FLOURNY2 (507726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 507726 TO FLOURNY4 507727 TO FLOURNY1 507740 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FRNKLNS4__520916 | 3 Phase fault FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRNKLNS4 520917 TO FRNKLNS2 520916 TO FRNKTERT 521169 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FRSTHIL2__515075 | 3 Phase fault FRSTHIL2 (515074) 69 kV Bus a. Apply fault at the FRSTHIL2 (515074) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRSTHIL2 515074 TO FRSTHIL4 515075 TO FRSTHIL1 515725 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FTSMITH7__515305 | 3 Phase fault FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 515302 TO FTSMITH8 515305 TO FTSMTH11 515726 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FTSMTHE5__515305 | 3 Phase fault FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5 (515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 515300 TO FTSMITH8 515305 TO FTSMTH31 515727 CKT 3 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FTSMTHW5__515302 | 3 Phase fault FTSMTHW5 (515301) 161 kV Bus a. Apply fault at the FTSMTHW5 (515301) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 515301 TO FTSMITH7 515302 TO FTSMTH51 515728 CKT 5 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_FTSMTHW5__515305 | 3 Phase fault FTSMTHW5 (515301) 161 kV Bus a. Apply fault at the FTSMTHW5 (515301) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 515301 TO FTSMITH8 515305 TO FTSMTH41 515791 CKT 4 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GORE___5__512644 | 3 Phase fault GORE 5 (505552) 161 kV Bus a. Apply fault at the GORE 5 (505552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 505552 TO GORE GR2 512644 TO GORTER1 512832 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRACMNT4__515800 | 3 Phase fault GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRAPEVINE__6__523770 | 3 Phase fault GRAPEVINE 6 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 523771 TO GRAPEVINE 3 523770 TO GRAPEVN_TR11 523769 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA1__5__512727 | 3 Phase fault GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 512656 TO GRDA1 2 512727 TO GRDA1 1 512816 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA1__7__512656 | 3 Phase fault GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 512650 TO GRDA1 5 512656 TO GRDA2 1 512826 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRTWSRN7__515820 | 3 Phase fault GRTWSRN7 (515825) 345 kV Bus a. Apply fault at the GRTWSRN7 (515825) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRTWSRN7 515825 TO GRTWSL11 515820 TO GRTWST11 515860 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRTWSRN7__515823 | 3 Phase fault GRTWSRN7 (515825) 345 kV Bus a. Apply fault at the GRTWSRN7 (515825) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRTWSRN7 515825 TO GRTWSL21 515823 TO GRTWST21 515824 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HOB_XFMR | 3 Phase fault HOB-JCT2 (511464) 69 kV Bus a. Apply fault at the HOB-JCT2 (511464) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT2 511464 TO HOB-JCT4 511463 TO HOBJT1-1 511417 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HOC404_5__547486 | 3 Phase fault HOC404 5 (547487) 161 kV Bus a. Apply fault at the HOC404 5 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 547487 TO HOC404 4 547486 TO HOC404A1 547715 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HSLWEST2__514941 | 3 Phase fault HSLWEST2 (514937) 69 kV Bus a. Apply fault at the HSLWEST2 (514937) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLWEST2 514937 TO HSL 4 514941 TO HSL 1 515731 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HUGO_XFMR | 3 Phase fault HUGO---2 (510893) 69 kV Bus a. Apply fault at the HUGO---2 (510893) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGO---2 510893 TO HUGO---4 510901 TO HUGO4-1 510859 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_HUGO___7__520560 | 3 Phase fault HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 521157 TO HUGOITC4 520560 TO HUGO TERTA 521189 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_IGLOOV_7__513593 | 3 Phase fault IGLOOV 7 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 513596 TO IGLOOV1 5 513593 TO IGLOTER1 1 513592 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_IGLOOV_7__513595 | 3 Phase fault IGLOOV 7 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 513596 TO IGLOOV2 5 513595 TO IGLOTER2 1 513594 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_IMO____2__514790 | 3 Phase fault IMO 2 (514721) 69 kV Bus a. Apply fault at the IMO 2 (514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 514721 TO IMO 4 514790 TO IMO 1 515788 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_JOHNCO_4__514809 | 3 Phase fault JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 514808 TO JOHNCO 7 514809 TO JOHNCO11 514810 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_KEENAN_1__515394 | 3 Phase fault KEENAN 1 (515393) 34.5 kV Bus a. Apply fault at the KEENAN 1 (515393) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEENAN 1 515393 TO KEENAN 4 515394 TO KEENAN T 515392 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_KNOXLEE2__508548 | 3 Phase fault KNOXLEE2 (508547) 69 kV Bus a. Apply fault at the KNOXLEE2 (508547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE2 508547 TO KNOXLEE4 508548 TO KXLEE-1 508584 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_L.E.S._XFMR | 3 Phase fault L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_L.E.S._XFMR | 3 Phase fault L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LEASIDE_2__507793 | 3 Phase fault LEASIDE 2 (507794) 69 kV Bus a. Apply fault at the LEASIDE 2 (507794) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEASIDE 2 507794 TO LEASIDE 4 507793 TO LEASIDE 1-1 507795 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LIEBERM2__508806 | 3 Phase fault LIEBERM2 (508805) 69 kV Bus a. Apply fault at the LIEBERM2 (508805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM2 508805 TO LIEBERM4 508806 TO LBMN3-1 508822 CKT 3 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LOGANSP2__509071 | 3 Phase fault LOGANSP2 (509070) 69 kV Bus a. Apply fault at the LOGANSP2 (509070) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGANSP2 509070 TO LOGANSP4 509071 TO 509094 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LONGWD_4__508809 | 3 Phase fault LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 508808 TO LONGWD 7 508809 TO LONGW1-1 508819 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_LSSOUTH2__508297 | 3 Phase fault LSSOUTH2 (508296) 69 kV Bus a. Apply fault at the LSSOUTH2 (508296) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH2 508296 TO LSSOUTH4 508297 TO LSS-1 508325 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MAID___5__512626 | 3 Phase fault MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 512648 TO MAID 2 512626 TO MAITER2 1 512837 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MANDEVILTP4__504363 | 3 Phase fault MANDEVILTP4 (508105) 138 kV Bus a. Apply fault at the MANDEVILTP4 (508105) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANDEVILTP4 508105 TO NE-TEXARK2 504363 TO NE-TEXARK1 504364 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MARAUTO2__508557 | 3 Phase fault MARAUTO2 (508576) 69 kV Bus a. Apply fault at the MARAUTO2 (508576) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARAUTO2 508576 TO MARSHL-4 508557 TO MRSH4#21 508592 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MAUD___4__515054 | 3 Phase fault MAUD 4 (515055) 138 kV Bus a. Apply fault at the MAUD 4 (515055) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 4 515055 TO MAUD 2 515054 TO MAUD 1 515736 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MENA___2__507436 | 3 Phase fault MENA 2 (508301) 69 kV Bus a. Apply fault at the MENA 2 (508301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENA 2 508301 TO MENA 4 507436 TO MENA3-1 507438 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MOORLND4__520995 | 3 Phase fault MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND4 520999 TO MOORLND2 520995 TO MLNDTERT 521180 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MSTANG_2__514861 | 3 Phase fault MSTANG 2 (514860) 69 kV Bus a. Apply fault at the MSTANG 2 (514860) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTANG 2 514860 TO MUSTANG4 514861 TO MUSTANG1 515740 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MSTNG10G__514861 | 3 Phase fault MSTNG10G (515672) 13.8 kV Bus a. Apply fault at the MSTNG10G (515672) 13.8 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTNG10G 515672 TO MUSTANG4 514861 TO MSTNG11G 515673 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MSTNG_8G__514861 | 3 Phase fault MSTNG 8G (515670) 13.8 kV Bus a. Apply fault at the MSTNG 8G (515670) 13.8 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTNG 8G 515670 TO MUSTANG4 514861 TO MSTNG 9G 515671 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_MUSKOGE2__515222 | 3 Phase fault MUSKOGE2 (515221) 69 kV Bus a. Apply fault at the MUSKOGE2 (515221) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKOGE2 515221 TO MUSKOGE5 515222 TO MUSKOG41 515797 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NBENTON2__508811 | 3 Phase fault NBENTON2 (508810) 69 kV Bus a. Apply fault at the NBENTON2 (508810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NBENTON2 508810 TO NBENTON4 508811 TO NBENTON1 508823 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NEOSHO_7__532937 | 3 Phase fault NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 532793 TO NEOSHO 5 532937 TO N345 2 1 532825 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NEOSHO_7__533021 | 3 Phase fault NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 532793 TO NEOSHO 4 533021 TO N345 1 1 532824 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NNBOSTN2__508069 | 3 Phase fault NNBOSTN2 (508068) 69 kV Bus a. Apply fault at the NNBOSTN2 (508068) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN2 508068 TO NNBOSTN4 508069 TO NNBT2-1 508099 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NORMHLL7__516097 | 3 Phase fault NORMHLL7 (516096) 345 kV Bus a. Apply fault at the NORMHLL7 (516096) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORMHLL7 516096 TO NORMHLL4 516097 TO NORMHL21 516099 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NORTWST4__514880 | 3 Phase fault NORTWST4 (514879) 138 kV Bus a. Apply fault at the NORTWST4 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTWST4 514879 TO NORTWST7 514880 TO NORTWS31 515743 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_NWTXARK4__508072 | 3 Phase fault NWTXARK4 (508071) 138 kV Bus a. Apply fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 508071 TO NWTXARK7 508072 TO NWTEX2-1 508101 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OKAY___2__507428 | 3 Phase fault OKAY 2 (507427) 69 kV Bus a. Apply fault at the OKAY 2 (507427) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAY 2 507427 TO OKAY 4 507428 TO OKAY1-1 507442 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OKEENE_4__521015 | 3 Phase fault OKEENE 4 (521016) 138 kV Bus a. Apply fault at the OKEENE 4 (521016) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKEENE 4 521016 TO OKEENE 2 521015 TO OKENTERT 521173 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ONETA_XFMR | 3 Phase fault ONETA--4 (509806) 138 kV Bus a. Apply fault at the ONETA--4 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 509806 TO ONETA--7 509807 TO ONETA1-1 509881 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OUSPRT_1__515398 | 3 Phase fault OUSPRT 1 (515397) 34.5 kV Bus a. Apply fault at the OUSPRT 1 (515397) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OUSPRT 1 515397 TO OUSPRT 4 515398 TO OUSPRT T 515396 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PALIOGE2__515100 | 3 Phase fault PALIOGE2 (515099) 69 kV Bus a. Apply fault at the PALIOGE2 (515099) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PALIOGE2 515099 TO PAOLI- 4 515100 TO PAOLI 1 515746 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PARKLN_2__515178 | 3 Phase fault PARKLN 2 (515177) 69 kV Bus a. Apply fault at the PARKLN 2 (515177) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKLN 2 515177 TO PARKLN 4 515178 TO PARKLN21 515748 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PATTERS2__507431 | 3 Phase fault PATTERS2 (507429) 69 kV Bus a. Apply fault at the PATTERS2 (507429) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS2 507429 TO PATTERS4 507431 TO PATTN2-1 507444 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PECANCK4__515234 | 3 Phase fault PECANCK4 (515233) 138 kV Bus a. Apply fault at the PECANCK4 (515233) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK4 515233 TO PECANCK5 515234 TO PECANC31 515750 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PECANCK5__515235 | 3 Phase fault PECANCK5 (515234) 161 kV Bus a. Apply fault at the PECANCK5 (515234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK5 515234 TO PECANCK7 515235 TO PECANC21 515759 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PENN___2__514925 | 3 Phase fault PENN 2 (514924) 69 kV Bus a. Apply fault at the PENN 2 (514924) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENN 2 514924 TO PENN 4 514925 TO PENN 1 515751 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PENSA__5__512628 | 3 Phase fault PENSA 5 (512654) 161 kV Bus a. Apply fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 5 512654 TO PENSA 2 512628 TO PENSA 1 512841 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_PIRKEY_4__508563 | 3 Phase fault PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY2-1 508588 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_R.S.S.XFMR | 3 Phase fault R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 509783 TO RSS NG3 511844 TO RSS NG4 511845 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_REDBUD1S__514909 | 3 Phase fault REDBUD1S (514899) 18 kV Bus a. Apply fault at the REDBUD1S (514899) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD1S 514899 TO REDBUD 7 514909 TO REDBUD1G 514910 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_REDBUD2S__514909 | 3 Phase fault REDBUD2S (514900) 18 kV Bus a. Apply fault at the REDBUD2S (514900) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD2S 514900 TO REDBUD 7 514909 TO REDBUD2G 514911 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_REDBUD3S__514909 | 3 Phase fault REDBUD3S (514905) 18 kV Bus a. Apply fault at the REDBUD3S (514905) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD3S 514905 TO REDBUD 7 514909 TO REDBUD3G 514912 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_REDBUD4S__514909 | 3 Phase fault REDBUD4S (514940) 18 kV Bus a. Apply fault at the REDBUD4S (514940) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD4S 514940 TO REDBUD 7 514909 TO REDBUD4G 514942 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_RENO___2__514973 | 3 Phase fault RENO 2 (514972) 69 kV Bus a. Apply fault at the RENO 2 (514972) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 2 514972 TO RENO 4 514973 TO RENO 1 515753 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ROCKYPT2__515164 | 3 Phase fault ROCKYPT2 (515163) 69 kV Bus a. Apply fault at the ROCKYPT2 (515163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 515163 TO ROCKYPT4 515164 TO ROCKYPT1 515754 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_ROKHILL2__509083 | 3 Phase fault ROKHILL2 (509082) 69 kV Bus a. Apply fault at the ROKHILL2 (509082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL2 509082 TO ROKHILL4 509083 TO RKHIL2-1 509091 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_RSS_T1_4__509782 | 3 Phase fault RSS T1 4 (509773) 138 kV Bus a. Apply fault at the RSS T1 4 (509773) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T1 4 509773 TO R.S.S.-7 509782 TO RSST1 T1 509882 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_RSS_T2_4__509782 | 3 Phase fault RSS T2 4 (509875) 138 kV Bus a. Apply fault at the RSS T2 4 (509875) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T2 4 509875 TO R.S.S.-7 509782 TO RSST2 T1 509876 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_RUSHING2__515064 | 3 Phase fault RUSHING2 (515063) 69 kV Bus a. Apply fault at the RUSHING2 (515063) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSHING2 515063 TO RUSHING4 515064 TO RUSHING1 515755 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_RUSHSPR7__511965 | 3 Phase fault RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 511571 TO RUSHSPRW1-1 511965 TO RUSHSPR1-1 511572 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_S.S._XFMR | 3 Phase fault S.S.---2 (509816) 69 kV Bus a. Apply fault at the S.S.---2 (509816) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---2 509816 TO S.S.---4 509815 TO SS6-1 509878 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_S.W.S.2_XFMR | 3 Phase fault S.W.S.-2 (511476) 69 kV Bus a. Apply fault at the S.W.S.-2 (511476) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-2 511476 TO S.W.S.-4 511477 TO SWS#1--1 511413 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_S.W.S.4_XFMR | 3 Phase fault S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 511477 TO SWS NG4 511849 TO SWS NG5 511850 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SAPLPRD4__509870 | 3 Phase fault SAPLPRD4 (509871) 138 kV Bus a. Apply fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 509871 TO SAPLPRD7 509870 TO SAPLPRD1 509872 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SDIERKS2__507433 | 3 Phase fault SDIERKS2 (507432) 69 kV Bus a. Apply fault at the SDIERKS2 (507432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SDIERKS2 507432 TO SDIERKS4 507433 TO SDRKS1-1 507446 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SEMINOL4__515045 | 3 Phase fault SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 515044 TO SEMINOL7 515045 TO SEMINO21 515757 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SETEXAR2__508078 | 3 Phase fault SETEXAR2 (508077) 69 kV Bus a. Apply fault at the SETEXAR2 (508077) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETEXAR2 508077 TO SETEXAR4 508078 TO SETEX1-1 508102 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SFOREMAN__4__504030 | 3 Phase fault SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4 (504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 504029 TO SFORE_1 2 504030 TO SFORE_T1 1 504031 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SKELTON7__515991 | 3 Phase fault SKELTON7 (515990) 345 kV Bus a. Apply fault at the SKELTON7 (515990) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SKELTON7 515990 TO SKELTL11 515991 TO SKELTT11 515992 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SO4TH__2__514731 | 3 Phase fault SO4TH 2 (514730) 69 kV Bus a. Apply fault at the SO4TH 2 (514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 514730 TO SO4TH 4 514731 TO SO4TH 1 515758 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SOONER_4__514803 | 3 Phase fault SOONER 4 (514802) 138 kV Bus a. Apply fault at the SOONER 4 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 4 514802 TO SOONER 7 514803 TO SOONER 1 515760 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SUGARHL2__508080 | 3 Phase fault SUGARHL2 (508079) 69 kV Bus a. Apply fault at the SUGARHL2 (508079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGARHL2 508079 TO SUGARHL4 508080 TO SHILL1-1 508103 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SUNNYSD4__515136 | 3 Phase fault SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SUNNYSD7__515135 | 3 Phase fault SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SW_5TH_2__514920 | 3 Phase fault SW 5TH 2 (514919) 69 kV Bus a. Apply fault at the SW 5TH 2 (514919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW 5TH 2 514919 TO SW 5TH 4 514920 TO SW 5TH 1 515763 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SW_SHV_7__507759 | 3 Phase fault SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV1-1 507778 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_S_SHV__2__507755 | 3 Phase fault S SHV 2 (507754) 69 kV Bus a. Apply fault at the S SHV 2 (507754) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 2 507754 TO S SHV 4 507755 TO SSHV2-1 507776 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_T.NO.2_XFMR | 3 Phase fault T.NO.2-4 (509895) 138 kV Bus a. Apply fault at the T.NO.2-4 (509895) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.2-4 509895 TO T.NO.--7 509852 TO TNO2-1 509894 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_T.P.S._XFMR | 3 Phase fault T.P.S.-2 (509789) 69 kV Bus a. Apply fault at the T.P.S.-2 (509789) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-2 509789 TO T.P.S.-4 509788 TO TPS5-1 509880 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_T.S.E._XFMR | 3 Phase fault T.S.E.-2 (509820) 69 kV Bus a. Apply fault at the T.S.E.-2 (509820) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.S.E.-2 509820 TO T.S.E.-4 509811 TO TSE3-1 509873 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TAHLQH_5__512647 | 3 Phase fault TAHLQH 5 (512655) 161 kV Bus a. Apply fault at the TAHLQH 5 (512655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 512655 TO TAHLQH 2 512647 TO TAHLQH1 512851 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TALOGA_4__521064 | 3 Phase fault TALOGA 4 (521065) 138 kV Bus a. Apply fault at the TALOGA 4 (521065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALOGA 4 521065 TO TALOGA 2 521064 TO TLGTERT 521178 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_THISTLE7__539804 | 3 Phase fault THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 539801 TO THISTLE4 539804 TO THISTLE T1 539802 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TUCO_INT___6__525828 | 3 Phase fault TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 525830 TO TUCO_INT 3 525828 TO TUCO_TR4 1 525821 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TUCO_INT___7__525830 | 3 Phase fault TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 525832 TO TUCO_INT 6 525830 TO TUCO_TR2 1 525825 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TURK___3__507454 | 3 Phase fault TURK 3 (507456) 115 kV Bus a. Apply fault at the TURK 3 (507456) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 3 507456 TO TURK 4 507454 TO TURK1 1 507458 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_TURK___4__507455 | 3 Phase fault TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 4 507454 TO TURK 7 507455 TO TURK 1 507457 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_VALIANT2__510918 | 3 Phase fault VALIANT2 (510910) 69 kV Bus a. Apply fault at the VALIANT2 (510910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT2 510910 TO VALIANT4 510918 TO VALN1-1 510937 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_VALIANT4__510911 | 3 Phase fault VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 510918 TO VALIANT7 510911 TO VALN3-1 510939 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_VINTAJC2__510417 | 3 Phase fault VINTAJC2 (510418) 69 kV Bus a. Apply fault at the VINTAJC2 (510418) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC2 510418 TO VINTAJC4 510417 TO VINJT1-1 510367 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WAGNOR_5__512697 | 3 Phase fault WAGNOR 5 (512700) 161 kV Bus a. Apply fault at the WAGNOR 5 (512700) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAGNOR 5 512700 TO WAGNOR 2 512697 TO WAGNOR1 512818 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WASHITA4__521088 | 3 Phase fault WASHITA4 (521089) 138 kV Bus a. Apply fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 521089 TO WASHITA2 521088 TO WASHTERT 521179 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WATLANT2__508090 | 3 Phase fault WATLANT2 (508089) 69 kV Bus a. Apply fault at the WATLANT2 (508089) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT2 508089 TO WATLANT4 508090 TO WATL2-1 508046 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WEKIWA_XFMR | 3 Phase fault WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 509757 TO WEKIWA-7 509755 TO WEKIW1-1 509879 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WHEELER____6__523776 | 3 Phase fault WHEELER 6 (523777) 230 kV Bus a. Apply fault at the WHEELER 6 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 523777 TO WHEELER 3 523776 TO WHEELER_TR11 523774 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WHITNEY2__508575 | 3 Phase fault WHITNEY2 (508574) 69 kV Bus a. Apply fault at the WHITNEY2 (508574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY2 508574 TO WHITNEY4 508575 TO WHIT2-1 508590 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WILKES_4__508841 | 3 Phase fault WILKES 4 (508840) 138 kV Bus a. Apply fault at the WILKES 4 (508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 508840 TO WILKES 7 508841 TO WILKES-1 508826 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WOODRNG4__514715 | 3 Phase fault WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 514714 TO WOODRNG7 514715 TO WOODRNG1 515770 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WOODWRD4__514782 | 3 Phase fault WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 514785 TO WODWRD 2 514782 TO WOODWR21 515771 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WWRDEHV4__515375 | 3 Phase fault WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_YOAKUM_345__526935 | 3 Phase fault YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 526936 TO YOAKUM 6 526935 TO YOAKUM_TR1 526937 CKT 1 | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_AEPW_2022_10_P4_SWShreveport | Apply single-phase fault on SW SHV7 345.0 KV 507760 TO DIANA7 345.0 KV 508832 CKT 1, near SW SHV 7 for 5 cycles with stuck breaker at SW SHV 7 (507760) 345 kV Bus. Clear Fault after 10 cycles and trip SW SHV7 345.0 KV 507760 TO LONGWD7 345.0 KV 508809 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_AEPW_2022_3_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO NWTXARK7 345.0 KV 508072 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO WILKES7 345.0 KV 508841 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_AEPW_2022_4_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 2 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_AEPW_2022_5_P4_Wilkes | Apply single-phase fault on LINE 508841 TO 508809 CKT 1, near WILKES 7 for 5 cycles with stuck breaker at WILKES 7 (508841) 345 kV Bus. Clear Fault after 10 cycles and trip LINE 508841 TO 508359 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_AEPW_2022_6_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO PIRKEY7 345.0 KV 508563 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_AEPW_2022_7_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO WELSH7 345.0 KV 508359 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_AEPW_2022_8_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO WILKES7 345.0 KV 508841 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_AEPW_2022_82_P4_Oneta | Apply single-phase fault on ONETA7 345.0 KV 509807 TO RSS7 345.0 KV 509782 CKT 1, near ONETA--7 for 5 cycles with stuck breaker at ONETA--7 (509807) 345 kV Bus. Clear Fault after 10 cycles and trip ONETA7 345.0 KV 509807 TO CLARKSV7 345.0 KV 509745 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_AEPW_2022_83_P4_Riverside | Apply single-phase fault on RSS7 345.0 KV 509782 TO REDBUD7 345.0 KV 514909 CKT 1, near R.S.S.-7 for 5 cycles with stuck breaker at R.S.S.-7 (509782) 345 kV Bus. Clear Fault after 10 cycles and trip RSS7 345.0 KV 509782 TO SAPLPRD7 345.0 KV 509870 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_AEPW_2022_84_P4_SantaFe | Apply single-phase fault on SANTAFE4 345.0 KV 511492 TO CORNVIL4 345.0 KV 511449 CKT 1, near SANTAFE4 for 5 cycles with stuck breaker at SANTAFE4 (511492) 138 kV Bus. Clear Fault after 10 cycles and trip SANTAFE4 345.0 KV 511492 TO RUSHSPT4 345.0 KV 511491 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_AEPW_2022_9_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO 7SAREPTA% 345.0 KV 337376 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_46_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_47_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_48_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_49_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_50_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_51_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_52_P4_IGLOOV7 | Apply single-phase fault on and DISCONNECT 527964, near IGLOOV 7 for 15 cycles with stuck breaker at IGLOOV 7 (513596) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_53_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_54_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_55_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_56_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_57_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_58_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_59_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_60_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_61_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_62_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_63_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_64_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_65_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_66_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_67_P4_KERRGR3 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR3 for 15 cycles with stuck breaker at KERR GR3 (512634) 115 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_68_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_69_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_70_P4_KETCHUM5 | Apply single-phase fault on and DISCONNECT 527964, near KETCHUM5 for 15 cycles with stuck breaker at KETCHUM5 (512669) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_71_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_72_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_73_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_74_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_75_P4_SALNCRK5 | Apply single-phase fault on and DISCONNECT 527964, near SALNCRK5 for 15 cycles with stuck breaker at SALNCRK5 (512805) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_76_P4_TONECE5 | Apply single-phase fault on and DISCONNECT 527964, near TONECE5 for 15 cycles with stuck breaker at TONECE5 (512751) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_77_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_GRDA_All_78_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OKGE_All_16_P4_2_BVRCNTY7 | Apply single-phase fault on and DISCONNECT 527964, near BVRCNTY7 for 16 cycles with stuck breaker at BVRCNTY7 (515554) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OKGE_All_17_P4_2_WINDFRM4 | Apply single-phase fault on and DISCONNECT 527964, near WINDFRM4 for 16 cycles with stuck breaker at WINDFRM4 (515785) 138 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OKGE_All_18_P4_2_SUNNYSD7 | Apply single-phase fault on and DISCONNECT 527964, near SUNNYSD7 for 16 cycles with stuck breaker at SUNNYSD7 (515136) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OKGE_All_19_P4_2_DRAPER4 | Apply single-phase fault on and DISCONNECT 527964, near DRAPER 4 for 16 cycles with stuck breaker at DRAPER 4 (514933) 138 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OKGE_All_20_P4_2_WAUKOTP4 | Apply single-phase fault on LINE 514711 TO 514731 CKT 1 and LINE 514710 TO 514711 CKT 1, near WAUKOTP4 for 6 cycles with stuck breaker at WAUKOTP4 (514711) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514711 TO 514714 CKT 1 and LINE 514709 TO 514712 CKT 1 and LINE 514709 TO 514714 CKT 1 and LINE 514709 TO 514731 CKT 1 and DISCONNECT 514711 and DISCONNECT 514709 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OKGE_All_21_P4_2_JOHNCO7 | Apply single-phase fault on and DISCONNECT 527964, near JOHNCO 7 for 16 cycles with stuck breaker at JOHNCO 7 (514809) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OKGE_All_22_P4_2_GRACMNT7 | Apply single-phase fault on and DISCONNECT 527964, near GRACMNT7 for 16 cycles with stuck breaker at GRACMNT7 (515800) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OKGE_All_23_P4_2_OPENSKY7 | Apply single-phase fault on and DISCONNECT 527964, near OPENSKY7 for 16 cycles with stuck breaker at OPENSKY7 (515621) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OKGE_All_24_P4_2_PECANCK7 | Apply single-phase fault on and DISCONNECT 527964, near PECANCK7 for 16 cycles with stuck breaker at PECANCK7 (515235) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OKGE_All_25_P4_2_RANCHRD7 | Apply single-phase fault on and DISCONNECT 527964, near RANCHRD7 for 16 cycles with stuck breaker at RANCHRD7 (515576) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OKGE_All_26_P4_2_REDBUD7 | Apply single-phase fault on and DISCONNECT 527964, near REDBUD 7 for 16 cycles with stuck breaker at REDBUD 7 (514909) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OKGE_All_27_P4_2_FTSMITH8 | Apply single-phase fault on and DISCONNECT 527964, near FTSMITH8 for 16 cycles with stuck breaker at FTSMITH8 (515305) 500 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OKGE_All_28_P4_3_SEMINOL7 | Apply single-phase fault on and DISCONNECT 527964, near SEMINOL7 for 16 cycles with stuck breaker at SEMINOL7 (515045) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OKGE_All_29_P4_3_SOONER7 | Apply single-phase fault on and DISCONNECT 527964, near SOONER 7 for 16 cycles with stuck breaker at SOONER 7 (514803) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OKGE_All_30_P4_2_NORTWST7 | Apply single-phase fault on and DISCONNECT 527964, near NORTWST7 for 16 cycles with stuck breaker at NORTWST7 (514880) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OKGE_All_31_P4_2_BORDER7 | Apply single-phase fault on and DISCONNECT 527964, near BORDER 7 for 16 cycles with stuck breaker at BORDER 7 (515458) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_OKGE_All_35_P4_6_SO4TH4 | Apply single-phase fault on LINE 514731 TO 514790 CKT 1 and LINE 514711 TO 514731 CKT 1, near SO4TH 4 for 6 cycles with stuck breaker at SO4TH 4 (514731) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514709 TO 514731 CKT 1 and LINE 514731 TO 514815 CKT 1 and DISCONNECT 515758 and LOAD 1 514731 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SPA_All_10_P4_2_BullShoals | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SPA_All_11_P4_2_BullShoals | Apply single-phase fault on LINE 338104 TO 338121 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338121 and drop LOAD 1 338122 and drop LOAD 1 338124 and DISCONNECT 338121 and DISCONNECT 338122 and DISCONNECT 338123 and DISCONNECT 338124 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SPA_All_12_P4_2_BullShoals | Apply single-phase fault on LINE 300095 TO 301057 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and trip DISCONNECT 505462 and trip DISCONNECT 505464 and trip DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SPA_All_13_P4_2_TableRock | Apply single-phase fault on LINE 505461 TO 338110 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SPA_All_14_P4_2_TableRock | Apply single-phase fault on LINE 300130 TO 300727 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SPA_All_15_P4_2_TableRock | Apply single-phase fault on LINE 338099 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SPA_All_16_P4_2_TableRock | Apply single-phase fault on LINE 505496 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SPA_All_17_P4_2_TableRock | Apply single-phase fault on LINE 547497 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SPA_All_18_P4_2_TableRock | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and trip LINE 505474 TO 300735 CKT 1 and DISCONNECT 505473 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SPA_All_19_P4_2_Norfork | Apply single-phase fault on LINE 505460 TO 300081 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SPA_All_20_P4_2_Norfork | Apply single-phase fault on LINE 505461 TO 504440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SPA_All_21_P4_2_Norfork | Apply single-phase fault on LINE 301549 TO 505448 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SPA_All_22_P4_2_Norfork | Apply single-phase fault on LINE 338132 TO 338129 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338130 and drop LOAD 1 338131 and DISCONNECT 338130 and DISCONNECT 338131 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SPA_All_23_P4_2_Norfork | Apply single-phase fault on LINE 505442 TO 505440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338220 and drop LOAD A1 504080 and DISCONNECT 338220 and DISCONNECT 504080 and DISCONNECT 504081 and DISCONNECT 504082 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SPA_All_24_P4_2_Norfork | Apply single-phase fault on LINE 301121 TO 505458 CKT 1, near NORFORK2 for 5 cycles with stuck breaker at NORFORK2 (505450) 69 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505450 and drop LOAD A1 504448 and drop LOAD 1 505458 and DISCONNECT 504448 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505458 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SPA_All_7_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505468 and DISCONNECT 505470 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SPA_All_8_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505468 and DISCONNECT 505470 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_SPA_All_9_P4_2_BullShoalsWest | Apply single-phase fault on LINE 338110 TO 505461 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and DISCONNECT 505468 and DISCONNECT 505470 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WFEC_All_50_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520422 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WFEC_All_51_P4_2_ANADARK4 | Apply single-phase fault on LINE 521059 TO 520501 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 520814 CKT 1 and LINE 520812 TO 520814 CKT 1 and LINE 520814 TO 520923 CKT 1 and trip GENERATOR 1 520812 and drop LOAD F1 520812 and drop LOAD V1 520812 and DISCONNECT 520812 and drop LOAD 1 520496 and drop LOAD 1 520501 and drop LOAD 1 521031 and DISCONNECT 520496 and DISCONNECT 520501 and DISCONNECT 521031 and DISCONNECT 521072 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WFEC_All_52_P4_2_ANADARK4 | Apply single-phase fault on LINE 521129 TO 521024 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 511477 TO 520814 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WFEC_All_53_P4_2_CANADNS4 | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near CANADNS4 for 6 cycles with stuck breaker at CANADNS4 (520842) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 514947 TO 520842 CKT 1 and LINE 520842 TO 514947 CKT 1 and drop LOAD 1 520924 and DISCONNECT 520924 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WFEC_All_54_P4_2_FRNKLNS4 | Apply single-phase fault on LINE 520842 TO 514947 CKT 1, near FRNKLNS4 for 6 cycles with stuck breaker at FRNKLNS4 (520917) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 514946 and LINE 520917 TO 514946 CKT 1 and drop LOAD 1 520400 and drop LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WFEC_All_55_P4_2_FTSUPLY4 | Apply single-phase fault on LINE 520922 TO 520920 CKT 1 and trip GENERATOR 1 521145 and DISCONNECT 520922 and DISCONNECT 521141 and DISCONNECT 521144 and DISCONNECT 521145 and DISCONNECT 521151, near FTSUPLY4 for 6 cycles with stuck breaker at FTSUPLY4 (520920) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and LINE 520920 TO 520957 CKT 1 and drop LOAD 1 520957 and DISCONNECT 520957 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WFEC_All_56_P4_2_HUGOPP4 | Apply single-phase fault on LINE 510887 TO 520448 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 505602 TO 521044 CKT 1 and drop LOAD 1 515370 and drop LOAD 1 515568 and drop LOAD 1 520463 and drop LOAD 1 520483 and drop LOAD 1 520497 and drop LOAD 1 520918 and drop LOAD 1 521077 and drop LOAD 1 521115 and DISCONNECT 515370 and DISCONNECT 515568 and DISCONNECT 520463 and DISCONNECT 520483 and DISCONNECT 520497 and DISCONNECT 520826 and DISCONNECT 520884 and DISCONNECT 520918 and DISCONNECT 521049 and DISCONNECT 521077 and DISCONNECT 521098 and DISCONNECT 521115 and drop LOAD 1 520411 and drop LOAD 1 520874 and drop LOAD 1 520968 and drop LOAD 1 521036 and DISCONNECT 520411 and DISCONNECT 520874 and DISCONNECT 520968 and DISCONNECT 521036 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WFEC_All_57_P4_2_HUGOPP4 | Apply single-phase fault on LINE 521194 TO 521195 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 520948 TO 521079 CKT 1 and trip GENERATOR 1 520947 and drop LOAD F1 520947 and drop LOAD V1 520947 and DISCONNECT 520947 and drop LOAD 1 520419 and drop LOAD 1 520466 and drop LOAD 1 520834 and drop LOAD 1 520946 and drop LOAD 1 521079 and DISCONNECT 520419 and DISCONNECT 520466 and DISCONNECT 520834 and DISCONNECT 520946 and DISCONNECT 520953 and DISCONNECT 521079 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WFEC_All_58_P4_2_MARIETTAS4 | Apply single-phase fault on LINE 515150 TO 514808 CKT 1, near MARIETA4 for 6 cycles with stuck breaker at MARIETA4 (520988) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520988 TO 515160 CKT 1 and LINE 520981 TO 520864 CKT 1 and drop LOAD 1 520455 and drop LOAD 1 520487 and drop LOAD 1 520488 and drop LOAD 1 520511 and drop LOAD 1 520901 and drop LOAD 1 521038 and drop LOAD 1 521061 and drop LOAD 1 521066 and DISCONNECT 520455 and DISCONNECT 520467 and DISCONNECT 520487 and DISCONNECT 520488 and DISCONNECT 520511 and DISCONNECT 520901 and DISCONNECT 520939 and DISCONNECT 520972 and DISCONNECT 521038 and DISCONNECT 521061 and DISCONNECT 521066 and DISCONNECT 521067 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WFEC_All_59_P4_2_NOELSW4 | Apply single-phase fault on LINE 521200 TO 520431 CKT 1, near NOELSW 4 for 6 cycles with stuck breaker at NOELSW 4 (520430) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520436 TO 515853 CKT 1 and LINE 520430 TO 520437 CKT 1 and drop LOAD 1 520431 and drop LOAD 1 520437 and drop LOAD 2 520437 and DISCONNECT 520431 and DISCONNECT 520437 and drop LOAD 1 520436 and drop LOAD 1 520601 and DISCONNECT 520436 and DISCONNECT 520601 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WFEC_All_60_P4_2_OKEENE4 | Apply single-phase fault on LINE 520882 TO 521016 CKT 1, near OKEENE 4 for 6 cycles with stuck breaker at OKEENE 4 (521016) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and drop LOAD 1 520425 and drop LOAD 1 520507 and DISCONNECT 520425 and DISCONNECT 520848 and DISCONNECT 520507 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WFEC_All_61_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 520510 CKT 1 and LINE 511449 TO 511483 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WFEC_All_62_P4_2_PHAROAH4 | Apply single-phase fault on LINE 300686 TO 300137 CKT 1, near PHAROAH4 for 6 cycles with stuck breaker at PHAROAH4 (521026) 138 kV Bus. Clear Fault after 9 cycles and trip DISCONNECT 301553 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WFEC_All_63_P4_2_TWNLKSW4 | Apply single-phase fault on LINE 520882 TO 520535 CKT 1, near TWNLKSW4 for 6 cycles with stuck breaker at TWNLKSW4 (521073) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520533 TO 520865 CKT 1 and LINE 521073 TO 520540 CKT Z1 and drop LOAD 1 520879 and drop LOAD 1 520540 and DISCONNECT 520879 and DISCONNECT 520540 and drop LOAD 1 521037 and drop LOAD 1 515930 and drop LOAD 1 520546 and drop LOAD 1 520479 and DISCONNECT 521037 and DISCONNECT 520474 and DISCONNECT 515930 and DISCONNECT 520545 and DISCONNECT 520546 and DISCONNECT 520847 and DISCONNECT 520479 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WFEC_All_64_P4_2_WAKTASW4 | Apply single-phase fault on LINE 515544 TO 515546 CKT 1, near WAKTASW4 for 6 cycles with stuck breaker at WAKTASW4 (520434) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 520434 and drop LOAD 1 520409 and drop LOAD 1A 520409 and DISCONNECT 520409 and DISCONNECT 520435 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WFEC_All_65_P4_2_WASHITA4 | Apply single-phase fault on LINE 511485 TO 520856 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 1 and LINE 521089 TO 521017 CKT 1 and drop LOAD 1 520468 and drop LOAD 1 520503 and drop LOAD 1 520856 and drop LOAD 1 520950 and drop LOAD 1 521010 and drop LOAD 2 521010 and drop LOAD 1 521017 and drop LOAD 1 521050 and drop LOAD 1 521092 and DISCONNECT 520468 and DISCONNECT 520503 and DISCONNECT 520827 and DISCONNECT 520856 and DISCONNECT 520950 and DISCONNECT 521010 and DISCONNECT 521017 and DISCONNECT 521050 and DISCONNECT 521092 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WFEC_All_66_P4_2_WASHITA4 | Apply single-phase fault on LINE 515802 TO 521089 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 2 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WFEC_All_75_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 and LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520923 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FAULT_WFEC_All_76_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 511449 TO 511502 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_AEPW_2022_10_P4_SWShreveport | Apply single-phase fault on SW SHV7 345.0 KV 507760 TO DIANA7 345.0 KV 508832 CKT 1, near SW SHV 7 for 5 cycles with stuck breaker at SW SHV 7 (507760) 345 kV Bus. Clear Fault after 10 cycles and trip SW SHV7 345.0 KV 507760 TO LONGWD7 345.0 KV 508809 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_AEPW_2022_3_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO NWTXARK7 345.0 KV 508072 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO WILKES7 345.0 KV 508841 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_AEPW_2022_4_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 2 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_AEPW_2022_5_P4_Wilkes | Apply single-phase fault on LINE 508841 TO 508809 CKT 1, near WILKES 7 for 5 cycles with stuck breaker at WILKES 7 (508841) 345 kV Bus. Clear Fault after 10 cycles and trip LINE 508841 TO 508359 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_AEPW_2022_6_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO PIRKEY7 345.0 KV 508563 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_AEPW_2022_7_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO WELSH7 345.0 KV 508359 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_AEPW_2022_8_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO WILKES7 345.0 KV 508841 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_AEPW_2022_82_P4_Oneta | Apply single-phase fault on ONETA7 345.0 KV 509807 TO RSS7 345.0 KV 509782 CKT 1, near ONETA--7 for 5 cycles with stuck breaker at ONETA--7 (509807) 345 kV Bus. Clear Fault after 10 cycles and trip ONETA7 345.0 KV 509807 TO CLARKSV7 345.0 KV 509745 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_AEPW_2022_83_P4_Riverside | Apply single-phase fault on RSS7 345.0 KV 509782 TO REDBUD7 345.0 KV 514909 CKT 1, near R.S.S.-7 for 5 cycles with stuck breaker at R.S.S.-7 (509782) 345 kV Bus. Clear Fault after 10 cycles and trip RSS7 345.0 KV 509782 TO SAPLPRD7 345.0 KV 509870 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_AEPW_2022_84_P4_SantaFe | Apply single-phase fault on SANTAFE4 345.0 KV 511492 TO CORNVIL4 345.0 KV 511449 CKT 1, near SANTAFE4 for 5 cycles with stuck breaker at SANTAFE4 (511492) 138 kV Bus. Clear Fault after 10 cycles and trip SANTAFE4 345.0 KV 511492 TO RUSHSPT4 345.0 KV 511491 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_AEPW_2022_9_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO 7SAREPTA% 345.0 KV 337376 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_46_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_47_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_48_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_49_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_50_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_51_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_52_P4_IGLOOV7 | Apply single-phase fault on and DISCONNECT 527964, near IGLOOV 7 for 15 cycles with stuck breaker at IGLOOV 7 (513596) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_53_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_54_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_55_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_56_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_57_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_58_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_59_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_60_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_61_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_62_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_63_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_64_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_65_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_66_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_67_P4_KERRGR3 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR3 for 15 cycles with stuck breaker at KERR GR3 (512634) 115 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_68_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_69_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_70_P4_KETCHUM5 | Apply single-phase fault on and DISCONNECT 527964, near KETCHUM5 for 15 cycles with stuck breaker at KETCHUM5 (512669) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_71_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_72_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_73_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_74_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_75_P4_SALNCRK5 | Apply single-phase fault on and DISCONNECT 527964, near SALNCRK5 for 15 cycles with stuck breaker at SALNCRK5 (512805) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_76_P4_TONECE5 | Apply single-phase fault on and DISCONNECT 527964, near TONECE5 for 15 cycles with stuck breaker at TONECE5 (512751) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_77_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_GRDA_All_78_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OKGE_All_16_P4_2_BVRCNTY7 | Apply single-phase fault on and DISCONNECT 527964, near BVRCNTY7 for 16 cycles with stuck breaker at BVRCNTY7 (515554) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OKGE_All_17_P4_2_WINDFRM4 | Apply single-phase fault on and DISCONNECT 527964, near WINDFRM4 for 16 cycles with stuck breaker at WINDFRM4 (515785) 138 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OKGE_All_18_P4_2_SUNNYSD7 | Apply single-phase fault on and DISCONNECT 527964, near SUNNYSD7 for 16 cycles with stuck breaker at SUNNYSD7 (515136) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OKGE_All_19_P4_2_DRAPER4 | Apply single-phase fault on and DISCONNECT 527964, near DRAPER 4 for 16 cycles with stuck breaker at DRAPER 4 (514933) 138 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OKGE_All_20_P4_2_WAUKOTP4 | Apply single-phase fault on LINE 514711 TO 514731 CKT 1 and LINE 514710 TO 514711 CKT 1, near WAUKOTP4 for 6 cycles with stuck breaker at WAUKOTP4 (514711) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514711 TO 514714 CKT 1 and LINE 514709 TO 514712 CKT 1 and LINE 514709 TO 514714 CKT 1 and LINE 514709 TO 514731 CKT 1 and DISCONNECT 514711 and DISCONNECT 514709 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OKGE_All_21_P4_2_JOHNCO7 | Apply single-phase fault on and DISCONNECT 527964, near JOHNCO 7 for 16 cycles with stuck breaker at JOHNCO 7 (514809) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OKGE_All_22_P4_2_GRACMNT7 | Apply single-phase fault on and DISCONNECT 527964, near GRACMNT7 for 16 cycles with stuck breaker at GRACMNT7 (515800) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OKGE_All_23_P4_2_OPENSKY7 | Apply single-phase fault on and DISCONNECT 527964, near OPENSKY7 for 16 cycles with stuck breaker at OPENSKY7 (515621) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OKGE_All_24_P4_2_PECANCK7 | Apply single-phase fault on and DISCONNECT 527964, near PECANCK7 for 16 cycles with stuck breaker at PECANCK7 (515235) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OKGE_All_25_P4_2_RANCHRD7 | Apply single-phase fault on and DISCONNECT 527964, near RANCHRD7 for 16 cycles with stuck breaker at RANCHRD7 (515576) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OKGE_All_26_P4_2_REDBUD7 | Apply single-phase fault on and DISCONNECT 527964, near REDBUD 7 for 16 cycles with stuck breaker at REDBUD 7 (514909) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OKGE_All_27_P4_2_FTSMITH8 | Apply single-phase fault on and DISCONNECT 527964, near FTSMITH8 for 16 cycles with stuck breaker at FTSMITH8 (515305) 500 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OKGE_All_28_P4_3_SEMINOL7 | Apply single-phase fault on and DISCONNECT 527964, near SEMINOL7 for 16 cycles with stuck breaker at SEMINOL7 (515045) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OKGE_All_29_P4_3_SOONER7 | Apply single-phase fault on and DISCONNECT 527964, near SOONER 7 for 16 cycles with stuck breaker at SOONER 7 (514803) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OKGE_All_30_P4_2_NORTWST7 | Apply single-phase fault on and DISCONNECT 527964, near NORTWST7 for 16 cycles with stuck breaker at NORTWST7 (514880) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OKGE_All_31_P4_2_BORDER7 | Apply single-phase fault on and DISCONNECT 527964, near BORDER 7 for 16 cycles with stuck breaker at BORDER 7 (515458) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_OKGE_All_35_P4_6_SO4TH4 | Apply single-phase fault on LINE 514731 TO 514790 CKT 1 and LINE 514711 TO 514731 CKT 1, near SO4TH 4 for 6 cycles with stuck breaker at SO4TH 4 (514731) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514709 TO 514731 CKT 1 and LINE 514731 TO 514815 CKT 1 and DISCONNECT 515758 and LOAD 1 514731 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SPA_All_10_P4_2_BullShoals | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SPA_All_11_P4_2_BullShoals | Apply single-phase fault on LINE 338104 TO 338121 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338121 and drop LOAD 1 338122 and drop LOAD 1 338124 and DISCONNECT 338121 and DISCONNECT 338122 and DISCONNECT 338123 and DISCONNECT 338124 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SPA_All_12_P4_2_BullShoals | Apply single-phase fault on LINE 300095 TO 301057 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and trip DISCONNECT 505462 and trip DISCONNECT 505464 and trip DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SPA_All_13_P4_2_TableRock | Apply single-phase fault on LINE 505461 TO 338110 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SPA_All_14_P4_2_TableRock | Apply single-phase fault on LINE 300130 TO 300727 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SPA_All_15_P4_2_TableRock | Apply single-phase fault on LINE 338099 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SPA_All_16_P4_2_TableRock | Apply single-phase fault on LINE 505496 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SPA_All_17_P4_2_TableRock | Apply single-phase fault on LINE 547497 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SPA_All_18_P4_2_TableRock | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and trip LINE 505474 TO 300735 CKT 1 and DISCONNECT 505473 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SPA_All_19_P4_2_Norfork | Apply single-phase fault on LINE 505460 TO 300081 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SPA_All_20_P4_2_Norfork | Apply single-phase fault on LINE 505461 TO 504440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SPA_All_21_P4_2_Norfork | Apply single-phase fault on LINE 301549 TO 505448 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SPA_All_22_P4_2_Norfork | Apply single-phase fault on LINE 338132 TO 338129 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338130 and drop LOAD 1 338131 and DISCONNECT 338130 and DISCONNECT 338131 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SPA_All_23_P4_2_Norfork | Apply single-phase fault on LINE 505442 TO 505440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338220 and drop LOAD A1 504080 and DISCONNECT 338220 and DISCONNECT 504080 and DISCONNECT 504081 and DISCONNECT 504082 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SPA_All_24_P4_2_Norfork | Apply single-phase fault on LINE 301121 TO 505458 CKT 1, near NORFORK2 for 5 cycles with stuck breaker at NORFORK2 (505450) 69 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505450 and drop LOAD A1 504448 and drop LOAD 1 505458 and DISCONNECT 504448 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505458 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SPA_All_7_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505468 and DISCONNECT 505470 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SPA_All_8_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505468 and DISCONNECT 505470 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_SPA_All_9_P4_2_BullShoalsWest | Apply single-phase fault on LINE 338110 TO 505461 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and DISCONNECT 505468 and DISCONNECT 505470 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WFEC_All_50_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520422 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WFEC_All_51_P4_2_ANADARK4 | Apply single-phase fault on LINE 521059 TO 520501 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 520814 CKT 1 and LINE 520812 TO 520814 CKT 1 and LINE 520814 TO 520923 CKT 1 and trip GENERATOR 1 520812 and drop LOAD F1 520812 and drop LOAD V1 520812 and DISCONNECT 520812 and drop LOAD 1 520496 and drop LOAD 1 520501 and drop LOAD 1 521031 and DISCONNECT 520496 and DISCONNECT 520501 and DISCONNECT 521031 and DISCONNECT 521072 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WFEC_All_52_P4_2_ANADARK4 | Apply single-phase fault on LINE 521129 TO 521024 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 511477 TO 520814 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WFEC_All_53_P4_2_CANADNS4 | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near CANADNS4 for 6 cycles with stuck breaker at CANADNS4 (520842) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 514947 TO 520842 CKT 1 and LINE 520842 TO 514947 CKT 1 and drop LOAD 1 520924 and DISCONNECT 520924 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WFEC_All_54_P4_2_FRNKLNS4 | Apply single-phase fault on LINE 520842 TO 514947 CKT 1, near FRNKLNS4 for 6 cycles with stuck breaker at FRNKLNS4 (520917) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 514946 and LINE 520917 TO 514946 CKT 1 and drop LOAD 1 520400 and drop LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WFEC_All_55_P4_2_FTSUPLY4 | Apply single-phase fault on LINE 520922 TO 520920 CKT 1 and trip GENERATOR 1 521145 and DISCONNECT 520922 and DISCONNECT 521141 and DISCONNECT 521144 and DISCONNECT 521145 and DISCONNECT 521151, near FTSUPLY4 for 6 cycles with stuck breaker at FTSUPLY4 (520920) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and LINE 520920 TO 520957 CKT 1 and drop LOAD 1 520957 and DISCONNECT 520957 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WFEC_All_56_P4_2_HUGOPP4 | Apply single-phase fault on LINE 510887 TO 520448 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 505602 TO 521044 CKT 1 and drop LOAD 1 515370 and drop LOAD 1 515568 and drop LOAD 1 520463 and drop LOAD 1 520483 and drop LOAD 1 520497 and drop LOAD 1 520918 and drop LOAD 1 521077 and drop LOAD 1 521115 and DISCONNECT 515370 and DISCONNECT 515568 and DISCONNECT 520463 and DISCONNECT 520483 and DISCONNECT 520497 and DISCONNECT 520826 and DISCONNECT 520884 and DISCONNECT 520918 and DISCONNECT 521049 and DISCONNECT 521077 and DISCONNECT 521098 and DISCONNECT 521115 and drop LOAD 1 520411 and drop LOAD 1 520874 and drop LOAD 1 520968 and drop LOAD 1 521036 and DISCONNECT 520411 and DISCONNECT 520874 and DISCONNECT 520968 and DISCONNECT 521036 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WFEC_All_57_P4_2_HUGOPP4 | Apply single-phase fault on LINE 521194 TO 521195 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 520948 TO 521079 CKT 1 and trip GENERATOR 1 520947 and drop LOAD F1 520947 and drop LOAD V1 520947 and DISCONNECT 520947 and drop LOAD 1 520419 and drop LOAD 1 520466 and drop LOAD 1 520834 and drop LOAD 1 520946 and drop LOAD 1 521079 and DISCONNECT 520419 and DISCONNECT 520466 and DISCONNECT 520834 and DISCONNECT 520946 and DISCONNECT 520953 and DISCONNECT 521079 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WFEC_All_58_P4_2_MARIETTAS4 | Apply single-phase fault on LINE 515150 TO 514808 CKT 1, near MARIETA4 for 6 cycles with stuck breaker at MARIETA4 (520988) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520988 TO 515160 CKT 1 and LINE 520981 TO 520864 CKT 1 and drop LOAD 1 520455 and drop LOAD 1 520487 and drop LOAD 1 520488 and drop LOAD 1 520511 and drop LOAD 1 520901 and drop LOAD 1 521038 and drop LOAD 1 521061 and drop LOAD 1 521066 and DISCONNECT 520455 and DISCONNECT 520467 and DISCONNECT 520487 and DISCONNECT 520488 and DISCONNECT 520511 and DISCONNECT 520901 and DISCONNECT 520939 and DISCONNECT 520972 and DISCONNECT 521038 and DISCONNECT 521061 and DISCONNECT 521066 and DISCONNECT 521067 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WFEC_All_59_P4_2_NOELSW4 | Apply single-phase fault on LINE 521200 TO 520431 CKT 1, near NOELSW 4 for 6 cycles with stuck breaker at NOELSW 4 (520430) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520436 TO 515853 CKT 1 and LINE 520430 TO 520437 CKT 1 and drop LOAD 1 520431 and drop LOAD 1 520437 and drop LOAD 2 520437 and DISCONNECT 520431 and DISCONNECT 520437 and drop LOAD 1 520436 and drop LOAD 1 520601 and DISCONNECT 520436 and DISCONNECT 520601 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WFEC_All_60_P4_2_OKEENE4 | Apply single-phase fault on LINE 520882 TO 521016 CKT 1, near OKEENE 4 for 6 cycles with stuck breaker at OKEENE 4 (521016) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and drop LOAD 1 520425 and drop LOAD 1 520507 and DISCONNECT 520425 and DISCONNECT 520848 and DISCONNECT 520507 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WFEC_All_61_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 520510 CKT 1 and LINE 511449 TO 511483 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WFEC_All_62_P4_2_PHAROAH4 | Apply single-phase fault on LINE 300686 TO 300137 CKT 1, near PHAROAH4 for 6 cycles with stuck breaker at PHAROAH4 (521026) 138 kV Bus. Clear Fault after 9 cycles and trip DISCONNECT 301553 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WFEC_All_63_P4_2_TWNLKSW4 | Apply single-phase fault on LINE 520882 TO 520535 CKT 1, near TWNLKSW4 for 6 cycles with stuck breaker at TWNLKSW4 (521073) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520533 TO 520865 CKT 1 and LINE 521073 TO 520540 CKT Z1 and drop LOAD 1 520879 and drop LOAD 1 520540 and DISCONNECT 520879 and DISCONNECT 520540 and drop LOAD 1 521037 and drop LOAD 1 515930 and drop LOAD 1 520546 and drop LOAD 1 520479 and DISCONNECT 521037 and DISCONNECT 520474 and DISCONNECT 515930 and DISCONNECT 520545 and DISCONNECT 520546 and DISCONNECT 520847 and DISCONNECT 520479 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WFEC_All_64_P4_2_WAKTASW4 | Apply single-phase fault on LINE 515544 TO 515546 CKT 1, near WAKTASW4 for 6 cycles with stuck breaker at WAKTASW4 (520434) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 520434 and drop LOAD 1 520409 and drop LOAD 1A 520409 and DISCONNECT 520409 and DISCONNECT 520435 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WFEC_All_65_P4_2_WASHITA4 | Apply single-phase fault on LINE 511485 TO 520856 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 1 and LINE 521089 TO 521017 CKT 1 and drop LOAD 1 520468 and drop LOAD 1 520503 and drop LOAD 1 520856 and drop LOAD 1 520950 and drop LOAD 1 521010 and drop LOAD 2 521010 and drop LOAD 1 521017 and drop LOAD 1 521050 and drop LOAD 1 521092 and DISCONNECT 520468 and DISCONNECT 520503 and DISCONNECT 520827 and DISCONNECT 520856 and DISCONNECT 520950 and DISCONNECT 521010 and DISCONNECT 521017 and DISCONNECT 521050 and DISCONNECT 521092 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WFEC_All_66_P4_2_WASHITA4 | Apply single-phase fault on LINE 515802 TO 521089 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 2 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WFEC_All_75_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 and LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520923 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FAULT_WFEC_All_76_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 511449 TO 511502 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | 21STTAP4_508911 | a. Apply single-phase fault on a.1. 21STTAP4 138.0 KV 509828 TO 509811 CKT 1 b. with stuck breaker near 21STTAP4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. 21STTAP4 138.0 KV 509828 TO MINGO-N4 138.0 KV 509760 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | 36MER_4_515338 | a. Apply single-phase fault on a.1. 36&MER 4 138.0 KV 514888 TO HOBBYLO4 138.0 KV 515338 CKT 1 b. with stuck breaker near 36&MER 4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. 36&MER 4 138.0 KV 514888 TO SW 5TH 4 138.0 KV 514920 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | 52DELTP4_509811 | a. Apply single-phase fault on a.1. 52DELTP4 138.0 KV 509776 TO 36LEWIS4 138.0 KV 509800 CKT 1 a.2. LOAD 1 509800 a.3. 36LEWIS4 138.0 KV 509800 TO T.P.S.-4 138.0 KV 509788 CKT 1 b. with stuck breaker near 52DELTP4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. 52DELTP4 138.0 KV 509776 TO T.S.E.-4 138.0 KV 509811 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | 52DELWT4_509788 | a. Apply single-phase fault on a.1. 52DELWT4 138.0 KV 509814 TO T.P.S.-4 138.0 KV 509788 CKT 1 b. with stuck breaker near 52DELWT4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. R.S.S.-4 138.0 KV 509783 TO 52DELWT4 138.0 KV 509814 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | 7SAREPTA_337562 | a. Apply single-phase fault on a.1. 7SAREPTA% 345.0 KV 337376 TO 7EL DORADO 345.0 KV 337562 CKT 1 b. with stuck breaker near 7SAREPTA%345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. 7SAREPTA% 345.0 KV 337376 TO LONGWD 7 345.0 KV 508809 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | ARCADIA4_514833 | a. Apply single-phase fault on a.1. DANFRTH4 138.0 KV 514833 TO BURGETT4 138.0 KV 514510 CKT 1 a.2. LOAD 1 514510 a.3. BURGETT4 138.0 KV 514510 TO RNDBARN4 138.0 KV 515461 CKT 1 a.4. LOAD 1 515461 a.5. RNDBARN4 138.0 KV 515461 TO ARCADIA4 138.0 KV 514907 CKT 1 b. with stuck breaker near ARCADIA4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. ARCADIA4 138.0 KV 514907 TO JNSKAMO4 138.0 KV 514906 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | ARCADIA7_514880 | a. Apply single-phase fault on a.1. ARCADIA7 345.0 KV 514908 TO NORTWST7 345.0 KV 514880 CKT 1 b. with stuck breaker near ARCADIA7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. ARCADIA7 345.0 KV 514908 TO REDBUD 7 345.0 KV 514909 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | BARNES_4_514994.0 | a. Apply single-phase fault on a.1. BARNES 4 138.0 KV 515003 TO TINKER54 138.0 KV 514994 CKT 1 b. with stuck breaker near BARNES 4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. BARNES 4 138.0 KV 515003 TO DRAPER 4 138.0 KV 514933 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | BECKHAM7_511553 | a. Apply single-phase fault on a.1. BECKHAM7 345.0 KV 516059 TO CHISHOLM7 345.0 KV 511553 CKT 1 b. with stuck breaker near BECKHAM7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. BECKHAM7 345.0 KV 516059 TO BORDER 7 345.0 KV 515458 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | CATOOSA4_509752 | a. Apply single-phase fault on a.1. CATOOSA4 138.0 KV 509790 TO INOLATP4 138.0 KV 509752 CKT 1 b. with stuck breaker near CATOOSA4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. CATOOSA4 138.0 KV 509790 TO LLANETP4 138.0 KV 509804 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | CIMARON4_514853 | a. Apply single-phase fault on a.1. CIMARON4 138.0 KV 514898 TO HAYMAKR4 138.0 KV 514863 CKT 1 a.2. LOAD 1 514863 a.3. HAYMAKR4 138.0 KV 514863 TO DVISION4 138.0 KV 514853 CKT 1 b. with stuck breaker near CIMARON4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. CIMARON4 138.0 KV 514898 TO CZECHAL4 138.0 KV 514894 CKT 1 c.2. LOAD 1 514894 c.3. CZECHAL4 138.0 KV 514894 TO XEROX 4 138.0 KV 514893 CKT 1 c.4. LOAD 1 514893 c.5. XEROX 4 138.0 KV 514893 TO MORGAN 4 138.0 KV 514896 CKT 1 c.6. LOAD 1 514896 c.7. MORGAN 4 138.0 KV 514896 TO MUSTANG4 138.0 KV 514861 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | CLASSEN4_514920.0 | a. Apply single-phase fault on a.1. CLASSEN4 138.0 KV 514922 TO SW 5TH 4 138.0 KV 514920 CKT 1 b. with stuck breaker near CLASSEN4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. CLASSEN4 138.0 KV 514922 TO CROSTWN4 138.0 KV 515851 CKT 1 c.2. LOAD 1 515851 c.3. CROSTWN4 138.0 KV 515851 TO LIGHTCK4 138.0 KV 514923 CKT 1 c.4. LOAD 1 514923 c.5. LIGHTCK4 138.0 KV 514923 TO TROSPER4 138.0 KV 514963 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | DOUGLTP4_514861 | a. Apply single-phase fault on a.1. MUSTANG4 138.0 KV 514861 TO COUNCIL4 138.0 KV 514865 CKT 1 a.2. LOAD 1 514865 a.3. COUNCIL4 138.0 KV 514865 TO WESTOAK4 138.0 KV 514866 CKT 1 a.4. LOAD 1 514866 a.5. MERIDAN4 138.0 KV 514867 TO WESTOAK4 138.0 KV 514866 CKT 1 a.6. LOAD 1 514866 a.7. MERIDAN4 138.0 KV 514867 TO DOUGLTP4 138.0 KV 514868 CKT 1 b. with stuck breaker near DOUGLTP4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. DOUGLTP4 138.0 KV 514868 TO WESTERN4 138.0 KV 514869 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | DOVERSW4_520405 | a. Apply single-phase fault on a.1. DOVERSW4 138.0 KV 520882 TO NKNGFSH4 138.0 KV 520603 CKT 1 a.2. LOAD 1A 520603 a.3. LOAD 1B 520603 a.4. NKNGFSH4 138.0 KV 520603 TO KGFSJCT4 138.0 KV 520405 CKT 1 b. with stuck breaker near DOVERSW4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. DOVERSW4 138.0 KV 520882 TO DOVER 4 138.0 KV 520879 CKT 1 c.2. LOAD 1 520879 c.3. DOVER 4 138.0 KV 520879 TO TWNLAKE4 138.0 KV 520540 CKT 1 c.4. LOAD 1 520540 c.5. TWNLAKE4 138.0 KV 520540 TO TWNLKSW4 138.0 KV 521073 CKT Z1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | DVISION4_514848 | a. Apply single-phase fault on a.1. DVISION4 138.0 KV 514853 TO LAKESID4 138.0 KV 514849 CKT 1 a.2. LOAD 1 514849 a.3. LAKESID4 138.0 KV 514849 TO HEFNER 4 138.0 KV 514848 CKT 1 b. with stuck breaker near DVISION4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. CIMARON4 138.0 KV 514898 TO HAYMAKR4 138.0 KV 514863 CKT 1 c.2. LOAD 1 514863 c.3. HAYMAKR4 138.0 KV 514863 TO DVISION4 138.0 KV 514853 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | FIREWHL_TAP_515422 | a. Apply single-phase fault on a.1. FIREWHL-TAP 345.0 KV 588839 TO C-RIVER7 345.0 KV 515422 CKT 1 b. with stuck breaker near FIREWHL-TAP345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. FIREWHL-TAP 345.0 KV 588839 TO MUSKOGE7 345.0 KV 515224 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | GRACMNT7_514801 | a. Apply single-phase fault on a.1. GRACMNT7 345.0 KV 515800 TO MINCO 7 345.0 KV 514801 CKT 1 b. with stuck breaker near GRACMNT7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. GRACMNT7 345.0 KV 515800 TO G16-091-TAP 345.0 KV 587744 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | HENESEY4_520882.0 | a. Apply single-phase fault on a.1. HENESEY4 138.0 KV 514774 TO DOVERSW4 138.0 KV 520882 CKT 1 b. with stuck breaker near HENESEY4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. HENESEY4 138.0 KV 514774 TO WAUKOMI4 138.0 KV 514710 CKT 1 c.2. LOAD 1 514710 c.3. HENESEY4 138.0 KV 514774 TO WAUKOMI4 138.0 KV 514710 CKT 1 c.4. LOAD 1 514710 c.5. WAUKOMI4 138.0 KV 514710 TO WAUKOTP4 138.0 KV 514711 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | HSL_4_515046 | a. Apply single-phase fault on a.1. HSL 4 138.0 KV 514941 TO HAMMTAP4 138.0 KV 515046 CKT 1 b. with stuck breaker near HSL 4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. HSL 4 138.0 KV 514941 TO JNSKAMO4 138.0 KV 514906 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | JNSKAMO4_514907 | a. Apply single-phase fault on a.1. JNSKAMO4 138.0 KV 514906 TO ARCADIA4 138.0 KV 514907 CKT 1 b. with stuck breaker near JNSKAMO4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. JNSKAMO4 138.0 KV 514906 TO 4MEMORALT 138.0 KV 300136 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | JONESSB4_514835 | a. Apply single-phase fault on a.1. MEMRIAL4 138.0 KV 514835 TO BRYANT 4 138.0 KV 514839 CKT 1 a.2. LOAD 1 514839 a.3. BRYANT 4 138.0 KV 514839 TO ACORN 4 138.0 KV 515459 CKT 1 a.4. LOAD 1 515459 a.5. ACORN 4 138.0 KV 515459 TO JONESSB4 138.0 KV 515480 CKT 1 b. with stuck breaker near JONESSB4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. JONESSB4 138.0 KV 515480 TO CHTWOOD4 138.0 KV 514842 CKT 1 c.2. LOAD 1 514842 c.3. CHTWOOD4 138.0 KV 514842 TO LGARBER4 138.0 KV 515465 CKT 1 c.4. LOAD 1 515465 c.5. LGARBER4 138.0 KV 515465 TO ARCADIA4 138.0 KV 514907 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | KENSH_E_TP4_509829 | a. Apply single-phase fault on a.1. KENSH-E-TP4 138.0 KV 509830 TO FULTONW4 138.0 KV 509829 CKT 1 b. with stuck breaker near KENSH-E-TP4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. KENSH-E-TP4 138.0 KV 509830 TO T.S.E.-4 138.0 KV 509811 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | LLANETP4_509786 | a. Apply single-phase fault on a.1. LLANETP4 138.0 KV 509804 TO BA.N-ST4 138.0 KV 509786 CKT 1 b. with stuck breaker near LLANETP4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. LLANETP4 138.0 KV 509804 TO CATOOSA4 138.0 KV 509790 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | LONGWD_7_508841 | a. Apply single-phase fault on a.1. LONGWD 7 345.0 KV 508809 TO WILKES 7 345.0 KV 508841 CKT 1 b. with stuck breaker near LONGWD 7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. LONGWD 7 345.0 KV 508809 TO SW SHV 7 345.0 KV 507760 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | MEMRIAL4_514837 | a. Apply single-phase fault on a.1. MEMRIAL4 138.0 KV 514835 TO TENESTP4 138.0 KV 514837 CKT 1 b. with stuck breaker near MEMRIAL4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. MEMRIAL4 138.0 KV 514835 TO BRYANT 4 138.0 KV 514839 CKT 1 c.2. LOAD 1 514839 c.3. BRYANT 4 138.0 KV 514839 TO ACORN 4 138.0 KV 515459 CKT 1 c.4. LOAD 1 515459 c.5. ACORN 4 138.0 KV 515459 TO JONESSB4 138.0 KV 515480 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | MINCO_7_514901 | a. Apply single-phase fault on a.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 b. with stuck breaker near MINCO 7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. MINCO 7 345.0 KV 514801 TO NORMHLL7 345.0 KV 516096 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | MUSKOGE7_515302 | a. Apply single-phase fault on a.1. MUSKOGE7 345.0 KV 515224 TO CLARKSV7 345.0 KV 509745 CKT 1 b. with stuck breaker near MUSKOGE7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. MUSKOGE7 345.0 KV 515224 TO FTSMITH7 345.0 KV 515302 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | MUSTANG4_514920 | a. Apply single-phase fault on a.1. MUSTANG4 138.0 KV 514861 TO SW 5TH 4 138.0 KV 514920 CKT 1 b. with stuck breaker near MUSTANG4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. MUSTANG4 138.0 KV 514861 TO COUNCIL4 138.0 KV 514865 CKT 1 c.2. LOAD 1 514865 c.3. COUNCIL4 138.0 KV 514865 TO WESTOAK4 138.0 KV 514866 CKT 1 c.4. LOAD 1 514866 c.5. MERIDAN4 138.0 KV 514867 TO WESTOAK4 138.0 KV 514866 CKT 1 c.6. LOAD 1 514866 c.7. MERIDAN4 138.0 KV 514867 TO DOUGLTP4 138.0 KV 514868 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | NES4_510385 | a. Apply single-phase fault on a.1. N.E.S.-4 138.0 KV 510396 TO RICE CK4 138.0 KV 510385 CKT 1 a.2. LOAD M1 510385 a.3. RICE CK4 138.0 KV 510385 TO BV-SE--4 138.0 KV 510391 CKT 1 b. with stuck breaker near N.E.S.-4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. N.E.S.-4 138.0 KV 510396 TO HAWTHRN4 138.0 KV 510413 CKT 1 c.2. LOAD 1 510413 c.3. HAWTHRN4 138.0 KV 510413 TO CHELSA4 138.0 KV 510410 CKT 1 c.4. LOAD 1 510410 c.5. CHELSA4 138.0 KV 510410 TO ALWUETP4 138.0 KV 510429 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | NNBOSTN4_762431.0 | a. Apply single-phase fault on a.1. NNBOSTN4 138.0 KV 508069 TO G18-003-TAP 138.0 KV 762431 CKT 1 b. with stuck breaker near NNBOSTN4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. NNBOSTN4 138.0 KV 508069 TO 508104 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | NWTXARK4_508049 | a. Apply single-phase fault on a.1. NWTXARK4 138.0 KV 508071 TO NASH 4 138.0 KV 508049 CKT 1 b. with stuck breaker near NWTXARK4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. NWT-BNT4 138.0 KV 508070 TO NWTXARK4 138.0 KV 508071 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | NWT_BNT4_508071 | a. Apply single-phase fault on a.1. NWT-BNT4 138.0 KV 508070 TO NWTXARK4 138.0 KV 508071 CKT 1 b. with stuck breaker near NWT-BNT4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. NWT-BNT4 138.0 KV 508070 TO BANN 4 138.0 KV 508054 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | OKEENE_4_520536.0 | a. Apply single-phase fault on a.1. OKEENE 4 138.0 KV 521016 TO WATNGSW4 138.0 KV 520536 CKT 1 b. with stuck breaker near OKEENE 4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. OKEENE 4 138.0 KV 521016 TO DOVERSW4 138.0 KV 520882 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | PATTERS4_504124.0 | a. Apply single-phase fault on a.1. PATTERS4 138.0 KV 507431 TO ASHDWN_W 4 138.0 KV 504124 CKT 1 a.2. LOAD A1 504124 a.3. ASHDWN_W 4 138.0 KV 504124 TO CRAIGJT4 138.0 KV 510890 CKT 1 b. with stuck breaker near PATTERS4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. PATTERS4 138.0 KV 507431 TO SNASHVL4 138.0 KV 507434 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | PECANCK5_515230 | a. Apply single-phase fault on a.1. PECANCK5 161.0 KV 515234 TO AGENCY 5 161.0 KV 515230 CKT 1 b. with stuck breaker near PECANCK5161 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. PECANCK5 161.0 KV 515234 TO 5TRIBES5 161.0 KV 515228 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | PECANCK7_509782 | a. Apply single-phase fault on a.1. PECANCK7 345.0 KV 515235 TO R.S.S.-7 345.0 KV 509782 CKT 1 b. with stuck breaker near PECANCK7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. PECANCK7 345.0 KV 515235 TO MUSKOGE7 345.0 KV 515224 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | RENO_4_514941 | a. Apply single-phase fault on a.1. RENO 4 138.0 KV 514973 TO DUNJEE 4 138.0 KV 514884 CKT 1 a.2. LOAD 1 514884 a.3. DUNJEE 4 138.0 KV 514884 TO HSL 4 138.0 KV 514941 CKT 1 b. with stuck breaker near RENO 4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. RENO 4 138.0 KV 514973 TO NE10TH 4 138.0 KV 514964 CKT 1 c.2. LOAD 1 514964 c.3. NE10TH 4 138.0 KV 514964 TO MIDWAY 4 138.0 KV 514966 CKT 1 c.4. LOAD 1 514966 c.5. MIDWAY 4 138.0 KV 514966 TO HSL 4 138.0 KV 514941 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | SAPLPRD4_509896 | a. Apply single-phase fault on a.1. SAPLPRD4 138.0 KV 509871 TO DENV_WTAP4 138.0 KV 509896 CKT 1 b. with stuck breaker near SAPLPRD4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. SAPLPRD4 138.0 KV 509871 TO OAKSWTP4 138.0 KV 509848 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | SE15TH_4_514941 | a. Apply single-phase fault on a.1. SE15TH 4 138.0 KV 514993 TO HSL 4 138.0 KV 514941 CKT 1 b. with stuck breaker near SE15TH 4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. SE15TH 4 138.0 KV 514993 TO GLENDAL4 138.0 KV 514986 CKT 1 c.2. LOAD 1 514986 c.3. GLENDAL4 138.0 KV 514986 TO TINKER74 138.0 KV 515959 CKT 1 c.4. LOAD 1 515959 c.5. TINKER74 138.0 KV 515959 TO TINKER64 138.0 KV 515806 CKT 1 c.6. LOAD 1 515806 c.7. TINKER64 138.0 KV 515806 TO TINKER54 138.0 KV 514994 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | SEMINOL7_510907 | a. Apply single-phase fault on a.1. SEMINOL7 345.0 KV 515045 TO PITTSB-7 345.0 KV 510907 CKT 1 b. with stuck breaker near SEMINOL7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. SEMINOL7 345.0 KV 515045 TO ARCADIA7 345.0 KV 514908 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | SKYLINE4_514851 | a. Apply single-phase fault on a.1. SKYLINE4 138.0 KV 514850 TO QUAILCK4 138.0 KV 514851 CKT 1 b. with stuck breaker near SKYLINE4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. SKYLINE4 138.0 KV 514850 TO MEMRIAL4 138.0 KV 514835 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | SUGARHL4_507454 | a. Apply single-phase fault on a.1. SUGARHL4 138.0 KV 508080 TO TURK 4 138.0 KV 507454 CKT 1 b. with stuck breaker near SUGARHL4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. SUGARHL4 138.0 KV 508080 TO NWTXARK4 138.0 KV 508071 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | SUNNYSD7_511568 | a. Apply single-phase fault on a.1. SUNNYSD7 345.0 KV 515136 TO TERRYRD7 345.0 KV 511568 CKT 1 b. with stuck breaker near SUNNYSD7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. SUNNYSD7 345.0 KV 515136 TO G17-075-TAP 345.0 KV 560088 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | SW_5TH_4_514922 | a. Apply single-phase fault on a.1. SW 5TH 4 138.0 KV 514920 TO CLASSEN4 138.0 KV 514922 CKT 1 b. with stuck breaker near SW 5TH 4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. SW 5TH 4 138.0 KV 514920 TO MUSTANG4 138.0 KV 514861 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | SW_SHV_7_508809 | a. Apply single-phase fault on a.1. SW SHV 7 345.0 KV 507760 TO LONGWD 7 345.0 KV 508809 CKT 1 b. with stuck breaker near SW SHV 7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. SW SHV 7 345.0 KV 507760 TO DOLHILL7 345.0 KV 500250 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | TNO4_509895 | a. Apply single-phase fault on a.1. T.NO.--4 138.0 KV 509817 TO T.NO.2-4 138.0 KV 509895 CKT 1 b. with stuck breaker near T.NO.--4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. T.NO.--4 138.0 KV 509817 TO CDC-WT 4 138.0 KV 509842 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | TPS4_509800 | a. Apply single-phase fault on a.1. T.P.S.-4 138.0 KV 509788 TO 36LEWIS4 138.0 KV 509800 CKT 1 a.2. LOAD 1 509800 a.3. 36LEWIS4 138.0 KV 509800 TO 52DELTP4 138.0 KV 509776 CKT 1 b. with stuck breaker near T.P.S.-4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. T.P.S.-4 138.0 KV 509788 TO 36&OLY-4 138.0 KV 509724 CKT 1 c.2. LOAD 1 509724 c.3. 36&OLY-4 138.0 KV 509724 TO CARSN-T4 138.0 KV 509739 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | TSE4_509828 | a. Apply single-phase fault on a.1. T.S.E.-4 138.0 KV 509811 TO 21STTAP4 138.0 KV 509828 CKT 1 b. with stuck breaker near T.S.E.-4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. T.S.E.-4 138.0 KV 509811 TO 52DELTP4 138.0 KV 509776 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | TWNLKSW4_520847 | a. Apply single-phase fault on a.1. TWNLKSW4 138.0 KV 521073 TO TWNLKJT4 138.0 KV 520847 CKT 1 b. with stuck breaker near TWNLKSW4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. DOVERSW4 138.0 KV 520882 TO DOVER 4 138.0 KV 520879 CKT 1 c.2. LOAD 1 520879 c.3. DOVER 4 138.0 KV 520879 TO TWNLAKE4 138.0 KV 520540 CKT 1 c.4. LOAD 1 520540 c.5. TWNLAKE4 138.0 KV 520540 TO TWNLKSW4 138.0 KV 521073 CKT Z1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | WESTERN4_514870 | a. Apply single-phase fault on a.1. WESTERN4 138.0 KV 514869 TO STNWAL 4 138.0 KV 514870 CKT 1 b. with stuck breaker near WESTERN4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. WESTERN4 138.0 KV 514869 TO DOUGLTP4 138.0 KV 514868 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | WILKES_7_508809 | a. Apply single-phase fault on a.1. WILKES 7 345.0 KV 508841 TO LONGWD 7 345.0 KV 508809 CKT 1 b. with stuck breaker near WILKES 7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. WILKES 7 345.0 KV 508841 TO WELSH 7 345.0 KV 508359 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25S | Transfer | WWRDEHV7_515852 | a. Apply single-phase fault on a.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 1 b. with stuck breaker near WWRDEHV7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | 21STTAP4_508911 | a. Apply single-phase fault on a.1. 21STTAP4 138.0 KV 509828 TO 509811 CKT 1 b. with stuck breaker near 21STTAP4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. 21STTAP4 138.0 KV 509828 TO MINGO-N4 138.0 KV 509760 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | 36MER_4_515338 | a. Apply single-phase fault on a.1. 36&MER 4 138.0 KV 514888 TO HOBBYLO4 138.0 KV 515338 CKT 1 b. with stuck breaker near 36&MER 4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. 36&MER 4 138.0 KV 514888 TO SW 5TH 4 138.0 KV 514920 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | 52DELTP4_509811 | a. Apply single-phase fault on a.1. 52DELTP4 138.0 KV 509776 TO 36LEWIS4 138.0 KV 509800 CKT 1 a.2. LOAD 1 509800 a.3. 36LEWIS4 138.0 KV 509800 TO T.P.S.-4 138.0 KV 509788 CKT 1 b. with stuck breaker near 52DELTP4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. 52DELTP4 138.0 KV 509776 TO T.S.E.-4 138.0 KV 509811 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | 52DELWT4_509788 | a. Apply single-phase fault on a.1. 52DELWT4 138.0 KV 509814 TO T.P.S.-4 138.0 KV 509788 CKT 1 b. with stuck breaker near 52DELWT4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. R.S.S.-4 138.0 KV 509783 TO 52DELWT4 138.0 KV 509814 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | 7SAREPTA_337562 | a. Apply single-phase fault on a.1. 7SAREPTA% 345.0 KV 337376 TO 7EL DORADO 345.0 KV 337562 CKT 1 b. with stuck breaker near 7SAREPTA%345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. 7SAREPTA% 345.0 KV 337376 TO LONGWD 7 345.0 KV 508809 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | ARCADIA4_514833 | a. Apply single-phase fault on a.1. DANFRTH4 138.0 KV 514833 TO BURGETT4 138.0 KV 514510 CKT 1 a.2. LOAD 1 514510 a.3. BURGETT4 138.0 KV 514510 TO RNDBARN4 138.0 KV 515461 CKT 1 a.4. LOAD 1 515461 a.5. RNDBARN4 138.0 KV 515461 TO ARCADIA4 138.0 KV 514907 CKT 1 b. with stuck breaker near ARCADIA4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. ARCADIA4 138.0 KV 514907 TO JNSKAMO4 138.0 KV 514906 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | ARCADIA7_514880 | a. Apply single-phase fault on a.1. ARCADIA7 345.0 KV 514908 TO NORTWST7 345.0 KV 514880 CKT 1 b. with stuck breaker near ARCADIA7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. ARCADIA7 345.0 KV 514908 TO REDBUD 7 345.0 KV 514909 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | BARNES_4_514994.0 | a. Apply single-phase fault on a.1. BARNES 4 138.0 KV 515003 TO TINKER54 138.0 KV 514994 CKT 1 b. with stuck breaker near BARNES 4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. BARNES 4 138.0 KV 515003 TO DRAPER 4 138.0 KV 514933 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | BECKHAM7_511553 | a. Apply single-phase fault on a.1. BECKHAM7 345.0 KV 516059 TO CHISHOLM7 345.0 KV 511553 CKT 1 b. with stuck breaker near BECKHAM7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. BECKHAM7 345.0 KV 516059 TO BORDER 7 345.0 KV 515458 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | CATOOSA4_509752 | a. Apply single-phase fault on a.1. CATOOSA4 138.0 KV 509790 TO INOLATP4 138.0 KV 509752 CKT 1 b. with stuck breaker near CATOOSA4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. CATOOSA4 138.0 KV 509790 TO LLANETP4 138.0 KV 509804 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | CIMARON4_514853 | a. Apply single-phase fault on a.1. CIMARON4 138.0 KV 514898 TO HAYMAKR4 138.0 KV 514863 CKT 1 a.2. LOAD 1 514863 a.3. HAYMAKR4 138.0 KV 514863 TO DVISION4 138.0 KV 514853 CKT 1 b. with stuck breaker near CIMARON4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. CIMARON4 138.0 KV 514898 TO CZECHAL4 138.0 KV 514894 CKT 1 c.2. LOAD 1 514894 c.3. CZECHAL4 138.0 KV 514894 TO XEROX 4 138.0 KV 514893 CKT 1 c.4. LOAD 1 514893 c.5. XEROX 4 138.0 KV 514893 TO MORGAN 4 138.0 KV 514896 CKT 1 c.6. LOAD 1 514896 c.7. MORGAN 4 138.0 KV 514896 TO MUSTANG4 138.0 KV 514861 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | CLASSEN4_514920.0 | a. Apply single-phase fault on a.1. CLASSEN4 138.0 KV 514922 TO SW 5TH 4 138.0 KV 514920 CKT 1 b. with stuck breaker near CLASSEN4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. CLASSEN4 138.0 KV 514922 TO CROSTWN4 138.0 KV 515851 CKT 1 c.2. LOAD 1 515851 c.3. CROSTWN4 138.0 KV 515851 TO LIGHTCK4 138.0 KV 514923 CKT 1 c.4. LOAD 1 514923 c.5. LIGHTCK4 138.0 KV 514923 TO TROSPER4 138.0 KV 514963 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | DOUGLTP4_514861 | a. Apply single-phase fault on a.1. MUSTANG4 138.0 KV 514861 TO COUNCIL4 138.0 KV 514865 CKT 1 a.2. LOAD 1 514865 a.3. COUNCIL4 138.0 KV 514865 TO WESTOAK4 138.0 KV 514866 CKT 1 a.4. LOAD 1 514866 a.5. MERIDAN4 138.0 KV 514867 TO WESTOAK4 138.0 KV 514866 CKT 1 a.6. LOAD 1 514866 a.7. MERIDAN4 138.0 KV 514867 TO DOUGLTP4 138.0 KV 514868 CKT 1 b. with stuck breaker near DOUGLTP4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. DOUGLTP4 138.0 KV 514868 TO WESTERN4 138.0 KV 514869 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | DOVERSW4_520405 | a. Apply single-phase fault on a.1. DOVERSW4 138.0 KV 520882 TO NKNGFSH4 138.0 KV 520603 CKT 1 a.2. LOAD 1A 520603 a.3. LOAD 1B 520603 a.4. NKNGFSH4 138.0 KV 520603 TO KGFSJCT4 138.0 KV 520405 CKT 1 b. with stuck breaker near DOVERSW4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. DOVERSW4 138.0 KV 520882 TO DOVER 4 138.0 KV 520879 CKT 1 c.2. LOAD 1 520879 c.3. DOVER 4 138.0 KV 520879 TO TWNLAKE4 138.0 KV 520540 CKT 1 c.4. LOAD 1 520540 c.5. TWNLAKE4 138.0 KV 520540 TO TWNLKSW4 138.0 KV 521073 CKT Z1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | DVISION4_514848 | a. Apply single-phase fault on a.1. DVISION4 138.0 KV 514853 TO LAKESID4 138.0 KV 514849 CKT 1 a.2. LOAD 1 514849 a.3. LAKESID4 138.0 KV 514849 TO HEFNER 4 138.0 KV 514848 CKT 1 b. with stuck breaker near DVISION4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. CIMARON4 138.0 KV 514898 TO HAYMAKR4 138.0 KV 514863 CKT 1 c.2. LOAD 1 514863 c.3. HAYMAKR4 138.0 KV 514863 TO DVISION4 138.0 KV 514853 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | FIREWHL_TAP_515422 | a. Apply single-phase fault on a.1. FIREWHL-TAP 345.0 KV 588839 TO C-RIVER7 345.0 KV 515422 CKT 1 b. with stuck breaker near FIREWHL-TAP345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. FIREWHL-TAP 345.0 KV 588839 TO MUSKOGE7 345.0 KV 515224 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | GRACMNT7_514801 | a. Apply single-phase fault on a.1. GRACMNT7 345.0 KV 515800 TO MINCO 7 345.0 KV 514801 CKT 1 b. with stuck breaker near GRACMNT7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. GRACMNT7 345.0 KV 515800 TO G16-091-TAP 345.0 KV 587744 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | HENESEY4_520882.0 | a. Apply single-phase fault on a.1. HENESEY4 138.0 KV 514774 TO DOVERSW4 138.0 KV 520882 CKT 1 b. with stuck breaker near HENESEY4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. HENESEY4 138.0 KV 514774 TO WAUKOMI4 138.0 KV 514710 CKT 1 c.2. LOAD 1 514710 c.3. HENESEY4 138.0 KV 514774 TO WAUKOMI4 138.0 KV 514710 CKT 1 c.4. LOAD 1 514710 c.5. WAUKOMI4 138.0 KV 514710 TO WAUKOTP4 138.0 KV 514711 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | HSL_4_515046 | a. Apply single-phase fault on a.1. HSL 4 138.0 KV 514941 TO HAMMTAP4 138.0 KV 515046 CKT 1 b. with stuck breaker near HSL 4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. HSL 4 138.0 KV 514941 TO JNSKAMO4 138.0 KV 514906 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | JNSKAMO4_514907 | a. Apply single-phase fault on a.1. JNSKAMO4 138.0 KV 514906 TO ARCADIA4 138.0 KV 514907 CKT 1 b. with stuck breaker near JNSKAMO4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. JNSKAMO4 138.0 KV 514906 TO 4MEMORALT 138.0 KV 300136 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | JONESSB4_514835 | a. Apply single-phase fault on a.1. MEMRIAL4 138.0 KV 514835 TO BRYANT 4 138.0 KV 514839 CKT 1 a.2. LOAD 1 514839 a.3. BRYANT 4 138.0 KV 514839 TO ACORN 4 138.0 KV 515459 CKT 1 a.4. LOAD 1 515459 a.5. ACORN 4 138.0 KV 515459 TO JONESSB4 138.0 KV 515480 CKT 1 b. with stuck breaker near JONESSB4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. JONESSB4 138.0 KV 515480 TO CHTWOOD4 138.0 KV 514842 CKT 1 c.2. LOAD 1 514842 c.3. CHTWOOD4 138.0 KV 514842 TO LGARBER4 138.0 KV 515465 CKT 1 c.4. LOAD 1 515465 c.5. LGARBER4 138.0 KV 515465 TO ARCADIA4 138.0 KV 514907 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | KENSH_E_TP4_509829 | a. Apply single-phase fault on a.1. KENSH-E-TP4 138.0 KV 509830 TO FULTONW4 138.0 KV 509829 CKT 1 b. with stuck breaker near KENSH-E-TP4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. KENSH-E-TP4 138.0 KV 509830 TO T.S.E.-4 138.0 KV 509811 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | LLANETP4_509786 | a. Apply single-phase fault on a.1. LLANETP4 138.0 KV 509804 TO BA.N-ST4 138.0 KV 509786 CKT 1 b. with stuck breaker near LLANETP4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. LLANETP4 138.0 KV 509804 TO CATOOSA4 138.0 KV 509790 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | LONGWD_7_508841 | a. Apply single-phase fault on a.1. LONGWD 7 345.0 KV 508809 TO WILKES 7 345.0 KV 508841 CKT 1 b. with stuck breaker near LONGWD 7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. LONGWD 7 345.0 KV 508809 TO SW SHV 7 345.0 KV 507760 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | MEMRIAL4_514837 | a. Apply single-phase fault on a.1. MEMRIAL4 138.0 KV 514835 TO TENESTP4 138.0 KV 514837 CKT 1 b. with stuck breaker near MEMRIAL4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. MEMRIAL4 138.0 KV 514835 TO BRYANT 4 138.0 KV 514839 CKT 1 c.2. LOAD 1 514839 c.3. BRYANT 4 138.0 KV 514839 TO ACORN 4 138.0 KV 515459 CKT 1 c.4. LOAD 1 515459 c.5. ACORN 4 138.0 KV 515459 TO JONESSB4 138.0 KV 515480 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | MINCO_7_514901 | a. Apply single-phase fault on a.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 b. with stuck breaker near MINCO 7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. MINCO 7 345.0 KV 514801 TO NORMHLL7 345.0 KV 516096 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | MUSKOGE7_515302 | a. Apply single-phase fault on a.1. MUSKOGE7 345.0 KV 515224 TO CLARKSV7 345.0 KV 509745 CKT 1 b. with stuck breaker near MUSKOGE7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. MUSKOGE7 345.0 KV 515224 TO FTSMITH7 345.0 KV 515302 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | MUSTANG4_514920 | a. Apply single-phase fault on a.1. MUSTANG4 138.0 KV 514861 TO SW 5TH 4 138.0 KV 514920 CKT 1 b. with stuck breaker near MUSTANG4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. MUSTANG4 138.0 KV 514861 TO COUNCIL4 138.0 KV 514865 CKT 1 c.2. LOAD 1 514865 c.3. COUNCIL4 138.0 KV 514865 TO WESTOAK4 138.0 KV 514866 CKT 1 c.4. LOAD 1 514866 c.5. MERIDAN4 138.0 KV 514867 TO WESTOAK4 138.0 KV 514866 CKT 1 c.6. LOAD 1 514866 c.7. MERIDAN4 138.0 KV 514867 TO DOUGLTP4 138.0 KV 514868 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | NES4_510385 | a. Apply single-phase fault on a.1. N.E.S.-4 138.0 KV 510396 TO RICE CK4 138.0 KV 510385 CKT 1 a.2. LOAD M1 510385 a.3. RICE CK4 138.0 KV 510385 TO BV-SE--4 138.0 KV 510391 CKT 1 b. with stuck breaker near N.E.S.-4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. N.E.S.-4 138.0 KV 510396 TO HAWTHRN4 138.0 KV 510413 CKT 1 c.2. LOAD 1 510413 c.3. HAWTHRN4 138.0 KV 510413 TO CHELSA4 138.0 KV 510410 CKT 1 c.4. LOAD 1 510410 c.5. CHELSA4 138.0 KV 510410 TO ALWUETP4 138.0 KV 510429 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | NNBOSTN4_762431.0 | a. Apply single-phase fault on a.1. NNBOSTN4 138.0 KV 508069 TO G18-003-TAP 138.0 KV 762431 CKT 1 b. with stuck breaker near NNBOSTN4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. NNBOSTN4 138.0 KV 508069 TO 508104 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | NWTXARK4_508049 | a. Apply single-phase fault on a.1. NWTXARK4 138.0 KV 508071 TO NASH 4 138.0 KV 508049 CKT 1 b. with stuck breaker near NWTXARK4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. NWT-BNT4 138.0 KV 508070 TO NWTXARK4 138.0 KV 508071 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | NWT_BNT4_508071 | a. Apply single-phase fault on a.1. NWT-BNT4 138.0 KV 508070 TO NWTXARK4 138.0 KV 508071 CKT 1 b. with stuck breaker near NWT-BNT4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. NWT-BNT4 138.0 KV 508070 TO BANN 4 138.0 KV 508054 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | OKEENE_4_520536.0 | a. Apply single-phase fault on a.1. OKEENE 4 138.0 KV 521016 TO WATNGSW4 138.0 KV 520536 CKT 1 b. with stuck breaker near OKEENE 4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. OKEENE 4 138.0 KV 521016 TO DOVERSW4 138.0 KV 520882 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | PATTERS4_504124.0 | a. Apply single-phase fault on a.1. PATTERS4 138.0 KV 507431 TO ASHDWN_W 4 138.0 KV 504124 CKT 1 a.2. LOAD A1 504124 a.3. ASHDWN_W 4 138.0 KV 504124 TO CRAIGJT4 138.0 KV 510890 CKT 1 b. with stuck breaker near PATTERS4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. PATTERS4 138.0 KV 507431 TO SNASHVL4 138.0 KV 507434 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | PECANCK5_515230 | a. Apply single-phase fault on a.1. PECANCK5 161.0 KV 515234 TO AGENCY 5 161.0 KV 515230 CKT 1 b. with stuck breaker near PECANCK5161 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. PECANCK5 161.0 KV 515234 TO 5TRIBES5 161.0 KV 515228 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | PECANCK7_509782 | a. Apply single-phase fault on a.1. PECANCK7 345.0 KV 515235 TO R.S.S.-7 345.0 KV 509782 CKT 1 b. with stuck breaker near PECANCK7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. PECANCK7 345.0 KV 515235 TO MUSKOGE7 345.0 KV 515224 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | RENO_4_514941 | a. Apply single-phase fault on a.1. RENO 4 138.0 KV 514973 TO DUNJEE 4 138.0 KV 514884 CKT 1 a.2. LOAD 1 514884 a.3. DUNJEE 4 138.0 KV 514884 TO HSL 4 138.0 KV 514941 CKT 1 b. with stuck breaker near RENO 4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. RENO 4 138.0 KV 514973 TO NE10TH 4 138.0 KV 514964 CKT 1 c.2. LOAD 1 514964 c.3. NE10TH 4 138.0 KV 514964 TO MIDWAY 4 138.0 KV 514966 CKT 1 c.4. LOAD 1 514966 c.5. MIDWAY 4 138.0 KV 514966 TO HSL 4 138.0 KV 514941 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | SAPLPRD4_509896 | a. Apply single-phase fault on a.1. SAPLPRD4 138.0 KV 509871 TO DENV_WTAP4 138.0 KV 509896 CKT 1 b. with stuck breaker near SAPLPRD4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. SAPLPRD4 138.0 KV 509871 TO OAKSWTP4 138.0 KV 509848 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | SE15TH_4_514941 | a. Apply single-phase fault on a.1. SE15TH 4 138.0 KV 514993 TO HSL 4 138.0 KV 514941 CKT 1 b. with stuck breaker near SE15TH 4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. SE15TH 4 138.0 KV 514993 TO GLENDAL4 138.0 KV 514986 CKT 1 c.2. LOAD 1 514986 c.3. GLENDAL4 138.0 KV 514986 TO TINKER74 138.0 KV 515959 CKT 1 c.4. LOAD 1 515959 c.5. TINKER74 138.0 KV 515959 TO TINKER64 138.0 KV 515806 CKT 1 c.6. LOAD 1 515806 c.7. TINKER64 138.0 KV 515806 TO TINKER54 138.0 KV 514994 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | SEMINOL7_510907 | a. Apply single-phase fault on a.1. SEMINOL7 345.0 KV 515045 TO PITTSB-7 345.0 KV 510907 CKT 1 b. with stuck breaker near SEMINOL7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. SEMINOL7 345.0 KV 515045 TO ARCADIA7 345.0 KV 514908 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | SKYLINE4_514851 | a. Apply single-phase fault on a.1. SKYLINE4 138.0 KV 514850 TO QUAILCK4 138.0 KV 514851 CKT 1 b. with stuck breaker near SKYLINE4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. SKYLINE4 138.0 KV 514850 TO MEMRIAL4 138.0 KV 514835 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | SUGARHL4_507454 | a. Apply single-phase fault on a.1. SUGARHL4 138.0 KV 508080 TO TURK 4 138.0 KV 507454 CKT 1 b. with stuck breaker near SUGARHL4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. SUGARHL4 138.0 KV 508080 TO NWTXARK4 138.0 KV 508071 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | SUNNYSD7_511568 | a. Apply single-phase fault on a.1. SUNNYSD7 345.0 KV 515136 TO TERRYRD7 345.0 KV 511568 CKT 1 b. with stuck breaker near SUNNYSD7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. SUNNYSD7 345.0 KV 515136 TO G17-075-TAP 345.0 KV 560088 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | SW_5TH_4_514922 | a. Apply single-phase fault on a.1. SW 5TH 4 138.0 KV 514920 TO CLASSEN4 138.0 KV 514922 CKT 1 b. with stuck breaker near SW 5TH 4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. SW 5TH 4 138.0 KV 514920 TO MUSTANG4 138.0 KV 514861 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | SW_SHV_7_508809 | a. Apply single-phase fault on a.1. SW SHV 7 345.0 KV 507760 TO LONGWD 7 345.0 KV 508809 CKT 1 b. with stuck breaker near SW SHV 7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. SW SHV 7 345.0 KV 507760 TO DOLHILL7 345.0 KV 500250 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | TNO4_509895 | a. Apply single-phase fault on a.1. T.NO.--4 138.0 KV 509817 TO T.NO.2-4 138.0 KV 509895 CKT 1 b. with stuck breaker near T.NO.--4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. T.NO.--4 138.0 KV 509817 TO CDC-WT 4 138.0 KV 509842 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | TPS4_509800 | a. Apply single-phase fault on a.1. T.P.S.-4 138.0 KV 509788 TO 36LEWIS4 138.0 KV 509800 CKT 1 a.2. LOAD 1 509800 a.3. 36LEWIS4 138.0 KV 509800 TO 52DELTP4 138.0 KV 509776 CKT 1 b. with stuck breaker near T.P.S.-4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. T.P.S.-4 138.0 KV 509788 TO 36&OLY-4 138.0 KV 509724 CKT 1 c.2. LOAD 1 509724 c.3. 36&OLY-4 138.0 KV 509724 TO CARSN-T4 138.0 KV 509739 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | TSE4_509828 | a. Apply single-phase fault on a.1. T.S.E.-4 138.0 KV 509811 TO 21STTAP4 138.0 KV 509828 CKT 1 b. with stuck breaker near T.S.E.-4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. T.S.E.-4 138.0 KV 509811 TO 52DELTP4 138.0 KV 509776 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | TWNLKSW4_520847 | a. Apply single-phase fault on a.1. TWNLKSW4 138.0 KV 521073 TO TWNLKJT4 138.0 KV 520847 CKT 1 b. with stuck breaker near TWNLKSW4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. DOVERSW4 138.0 KV 520882 TO DOVER 4 138.0 KV 520879 CKT 1 c.2. LOAD 1 520879 c.3. DOVER 4 138.0 KV 520879 TO TWNLAKE4 138.0 KV 520540 CKT 1 c.4. LOAD 1 520540 c.5. TWNLAKE4 138.0 KV 520540 TO TWNLKSW4 138.0 KV 521073 CKT Z1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | WESTERN4_514870 | a. Apply single-phase fault on a.1. WESTERN4 138.0 KV 514869 TO STNWAL 4 138.0 KV 514870 CKT 1 b. with stuck breaker near WESTERN4138 kV for 7cycles c. Clear fault after 10 cycles and trip: c.1. WESTERN4 138.0 KV 514869 TO DOUGLTP4 138.0 KV 514868 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | WILKES_7_508809 | a. Apply single-phase fault on a.1. WILKES 7 345.0 KV 508841 TO LONGWD 7 345.0 KV 508809 CKT 1 b. with stuck breaker near WILKES 7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. WILKES 7 345.0 KV 508841 TO WELSH 7 345.0 KV 508359 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-001 CF | 25W | Transfer | WWRDEHV7_515852 | a. Apply single-phase fault on a.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 1 b. with stuck breaker near WWRDEHV7345 kV for 6cycles c. Clear fault after 10 cycles and trip: c.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | 53CACHE4__ARTVLTP4 | 3 Phase fault on 53CACHE4 (511509) 138 kV Bus a. Apply fault at the 53CACHE4 (511509) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53CACHE4 138.0 KV 511509 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | 7_RIVERS___6__PECOS______6 | 3 Phase fault on 7-RIVERS 6 (528095) 230 kV Bus a. Apply fault at the 7-RIVERS 6 (528095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 7-RIVERS 6 230.0 KV 528095 TO PECOS 6 230.0 KV 528179 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | AMA_SOUTH__6__SWISHER____6 | 3 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 230.0 KV 524415 TO SWISHER 6 230.0 KV 525213 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | AMOCOWASSON6__MUSTANG____6 | 3 Phase fault on AMOCOWASSON6 (526784) 230 kV Bus a. Apply fault at the AMOCOWASSON6 (526784) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCOWASSON6 230.0 KV 526784 TO MUSTANG 6 230.0 KV 527149 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | AMOCOWASSON6__XTO_MAHONEY6 | 3 Phase fault on AMOCOWASSON6 (526784) 230 kV Bus a. Apply fault at the AMOCOWASSON6 (526784) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCOWASSON6 230.0 KV 526784 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | ARTVLTP4__ARTVILL4 | 3 Phase fault on ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTVLTP4 138.0 KV 511537 TO ARTVILL4 138.0 KV 511538 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | BLCKRVR_DST3__CHINA_DRAW_3 | 3 Phase fault on BLCKRVR_DST3 (528206) 115 kV Bus a. Apply fault at the BLCKRVR_DST3 (528206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLCKRVR_DST3 115.0 KV 528206 TO CHINA_DRAW 3 115.0 KV 528222 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | BLUECLDPOI_6__NEEDMORE___6 | 3 Phase fault on BLUECLDPOI 6 (525585) 230 kV Bus a. Apply fault at the BLUECLDPOI 6 (525585) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUECLDPOI 6 230.0 KV 525585 TO NEEDMORE 6 230.0 KV 525586 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Decrease acceleration factor to 0.2.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | BORDER_____7__BECKHAM7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | BORDER_____7__TUCO_INT___7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO TUCO_INT 7 345.0 KV 525832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | BRU_SUB____6__OXYBRU_____6 | 3 Phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRU_SUB 6 230.0 KV 527009 TO OXYBRU 6 230.0 KV 527010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | BRU_SUB____6__XTO_MAHONEY6 | 3 Phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRU_SUB 6 230.0 KV 527009 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | BUCKEYE_TP_3__BUCKEYE____3 | 3 Phase fault on BUCKEYE_TP 3 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3 115.0 KV 528348 TO BUCKEYE 3 115.0 KV 528385 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | BUCKEYE_TP_3__LE_TXACO_TP3 | 3 Phase fault on BUCKEYE_TP 3 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3 115.0 KV 528348 TO LE-TXACO_TP3 115.0 KV 528627 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | BYRD_TP____3__BYRD_______3 | 3 Phase fault on BYRD_TP 3 (528581) 115 kV Bus a. Apply fault at the BYRD_TP 3 (528581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BYRD_TP 3 115.0 KV 528581 TO BYRD 3 115.0 KV 528582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CALLAHAN___3__FLOYD_CNTY_3 | 3 Phase fault on CALLAHAN 3 (525763) 115 kV Bus a. Apply fault at the CALLAHAN 3 (525763) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALLAHAN 3 115.0 KV 525763 TO FLOYD_CNTY 3 115.0 KV 525780 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CARDINAL___3__TARGA______3 | 3 Phase fault on CARDINAL 3 (528596) 115 kV Bus a. Apply fault at the CARDINAL 3 (528596) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARDINAL 3 115.0 KV 528596 TO TARGA 3 115.0 KV 528605 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CARLISLE___3__LP_DOUD_TP_3 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 115.0 KV 526160 TO LP-DOUD_TP 3 115.0 KV 526162 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CARLISLE___3__MURPHY_____3 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 115.0 KV 526160 TO MURPHY 3 115.0 KV 526192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CARLISLE___6__WOLFFORTH__6 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 230.0 KV 526161 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CARLSBAD___3__PECOS______3 | 3 Phase fault on CARLSBAD 3 (528160) 115 kV Bus a. Apply fault at the CARLSBAD 3 (528160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLSBAD 3 115.0 KV 528160 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CHAVES_CNTY6__EDDY_NORTH_6 | 3 Phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY6 230.0 KV 527483 TO EDDY_NORTH 6 230.0 KV 527799 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CHINA_DRAW_3__CD_SVC_HV__3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO CD_SVC_HV 3 115.0 KV 528225 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CHINA_DRAW_3__CHVRN_EDDYS3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO CHVRN_EDDYS3 115.0 KV 528252 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CHINA_DRAW_3__WOOD_DRAW__3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO WOOD_DRAW 3 115.0 KV 528228 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CHISHOLM7__BECKHAM7 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CHISHOLM7__G16_037_TAP | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | COMANC_2__L_E_S__2 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L.E.S.-2 69.0 KV 511466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | COMANC_4__112GORE4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | COMANC_4__COMMTAP4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | COMANC_4__L_E_S__4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | COMMTAP4__OMDUNCN4 | 3 Phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMMTAP4 138.0 KV 511494 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | COOPER_RNCH3__BYRD_TP____3 | 3 Phase fault on COOPER_RNCH3 (528554) 115 kV Bus a. Apply fault at the COOPER_RNCH3 (528554) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_RNCH3 115.0 KV 528554 TO BYRD_TP 3 115.0 KV 528581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | COX________3__HALE_CNTY__3 | 3 Phase fault on COX 3 (525326) 115 kV Bus a. Apply fault at the COX 3 (525326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 115.0 KV 525326 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CROSBY_____3__LUBBCK_EST_3 | 3 Phase fault on CROSBY 3 (525926) 115 kV Bus a. Apply fault at the CROSBY 3 (525926) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSBY 3 115.0 KV 525926 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CROSSROADS_7__EDDY_CNTY__7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 345.0 KV 527656 TO EDDY_CNTY 7 345.0 KV 527802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CUNNIGHM_N_6__POTASH_JCT_6 | 3 Phase fault on CUNNIGHM_N 6 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6 (527865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_N 6 230.0 KV 527865 TO POTASH_JCT 6 230.0 KV 527963 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CUNNIGHM_S_6__HOBBS_INT__6 | 3 Phase fault on CUNNIGHM_S 6 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 230.0 KV 527867 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CUNNINHAM__3__BUCKEYE_TP_3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO BUCKEYE_TP 3 115.0 KV 528348 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CUNNINHAM__3__HOBBS_INT__3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO HOBBS_INT 3 115.0 KV 527891 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CUNNINHAM__3__MADDOX_____3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO MADDOX 3 115.0 KV 528355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CUNNINHAM__3__MONUMNT_TP_3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO MONUMNT_TP 3 115.0 KV 528568 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CUNNINHAM__3__QUAHADA____3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO QUAHADA 3 115.0 KV 528394 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CUSTERMTN__3__PONDEROSA__3 | 3 Phase fault on CUSTERMTN 3 (528239) 115 kV Bus a. Apply fault at the CUSTERMTN 3 (528239) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTERMTN 3 115.0 KV 528239 TO PONDEROSA 3 115.0 KV 528240 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CUSTERMTN__3__WHITTEN____3 | 3 Phase fault on CUSTERMTN 3 (528239) 115 kV Bus a. Apply fault at the CUSTERMTN 3 (528239) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTERMTN 3 115.0 KV 528239 TO WHITTEN 3 115.0 KV 528540 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | DCP_ZIA_TP_3__DCP_ZIA____3 | 3 Phase fault on DCP_ZIA TP 3 (528422) 115 kV Bus a. Apply fault at the DCP_ZIA TP 3 (528422) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DCP_ZIA TP 3 115.0 KV 528422 TO DCP_ZIA 3 115.0 KV 528423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | DCP_ZIA_TP_3__MALJMAR1&2_3 | 3 Phase fault on DCP_ZIA TP 3 (528422) 115 kV Bus a. Apply fault at the DCP_ZIA TP 3 (528422) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ZIA 3 115.0 KV 528420 TO DCP_ZIA TP 3 115.0 KV 528422 CKT 1 b.2. MALJMAR1&2 3 115.0 KV 528406 TO ZIA 3 115.0 KV 528420 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | DRINKARD_TP3__DRINKARD___3 | 3 Phase fault on DRINKARD_TP3 (528533) 115 kV Bus a. Apply fault at the DRINKARD_TP3 (528533) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRINKARD_TP3 115.0 KV 528533 TO DRINKARD 3 115.0 KV 528589 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | DRINKARD___3__NA_ENRICH__3 | 3 Phase fault on DRINKARD 3 (528589) 115 kV Bus a. Apply fault at the DRINKARD 3 (528589) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRINKARD 3 115.0 KV 528589 TO NA_ENRICH 3 115.0 KV 528603 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | DUNCAN_4__DUNCHERTP4 | 3 Phase fault on DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138.0 KV 511453 TO DUNCHERTP4 138.0 KV 511552 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | DUNCAN_4__OMDUNCN4 | 3 Phase fault on DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138.0 KV 511453 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | EAGLE_CREEK3__EDDY_NTH___3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO EDDY_NTH 3 115.0 KV 527798 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | EDDY_CNTY__7__KIOWA______7 | 3 Phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 345.0 KV 527802 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | EDDY_NORTH_6__7_RIVERS___6 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 230.0 KV 527799 TO 7-RIVERS 6 230.0 KV 528095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | EDDY_NORTH_6__CUNNIGHM_N_6 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 230.0 KV 527799 TO CUNNIGHM_N 6 230.0 KV 527865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | EDDY_NTH___3__CV_8_MILE__3 | 3 Phase fault on EDDY_NTH 3 (527798) 115 kV Bus a. Apply fault at the EDDY_NTH 3 (527798) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NTH 3 115.0 KV 527798 TO CV-8_MILE 3 115.0 KV 527809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | EDDY_STH___3__CV_DAYTON_+3 | 3 Phase fault on EDDY_STH 3 (527793) 115 kV Bus a. Apply fault at the EDDY_STH 3 (527793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_STH 3 115.0 KV 527793 TO CV-DAYTON +3 115.0 KV 527821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | EDDY_STH___3__PECOS______3 | 3 Phase fault on EDDY_STH 3 (527793) 115 kV Bus a. Apply fault at the EDDY_STH 3 (527793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_STH 3 115.0 KV 527793 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | ELGINJT4__ELSWORTH___4 | 3 Phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT4 138.0 KV 511486 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | ENRON_TP___3__ENRON______3 | 3 Phase fault on ENRON_TP 3 (528317) 115 kV Bus a. Apply fault at the ENRON_TP 3 (528317) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENRON_TP 3 115.0 KV 528317 TO ENRON 3 115.0 KV 528318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | ENRON_TP___3__LEA_NATIONL3 | 3 Phase fault on ENRON_TP 3 (528317) 115 kV Bus a. Apply fault at the ENRON_TP 3 (528317) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENRON_TP 3 115.0 KV 528317 TO LEA_NATIONL3 115.0 KV 528399 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | EUNICE_____3__CARDINAL___3 | 3 Phase fault on EUNICE 3 (528512) 115 kV Bus a. Apply fault at the EUNICE 3 (528512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUNICE 3 115.0 KV 528512 TO CARDINAL 3 115.0 KV 528596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | EUNICE_____3__DRINKARD_TP3 | 3 Phase fault on EUNICE 3 (528512) 115 kV Bus a. Apply fault at the EUNICE 3 (528512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUNICE 3 115.0 KV 528512 TO DRINKARD_TP3 115.0 KV 528533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | FIESTA_____3__CARLSBAD___3 | 3 Phase fault on FIESTA 3 (528151) 115 kV Bus a. Apply fault at the FIESTA 3 (528151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIESTA 3 115.0 KV 528151 TO CARLSBAD 3 115.0 KV 528160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | FLETCHR4__FLE_TAP4 | 3 Phase fault on FLETCHR4 (511422) 138 kV Bus a. Apply fault at the FLETCHR4 (511422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR4 138.0 KV 511422 TO FLE TAP4 138.0 KV 511423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | FLE_TAP4__G16_097_TAP | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | FLE_TAP4__L_E_S__4 | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | FLOYD_CNTY_3__BLANCO_____3 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 115.0 KV 525780 TO BLANCO 3 115.0 KV 525803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | FLOYD_CNTY_3__TUCO_INT___3 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 115.0 KV 525780 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | G16_091_TAP__GEN_2016_095 | 3 Phase fault on G16-091-TAP (587744) 345 kV Bus a. Apply fault at the G16-091-TAP (587744) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-091-TAP 345.0 KV 587744 TO GEN-2016-095 345.0 KV 587770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | G17_151TAP__G18_015_TAP | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | G17_151TAP__GEN_2017_151 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO GEN-2017-151 345.0 KV 762217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | G17_171_TAP__GEN_2017_171 | 3 Phase fault on G17-171-TAP (760938) 345 kV Bus a. Apply fault at the G17-171-TAP (760938) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-171-TAP 345.0 KV 760938 TO GEN-2017-171 345.0 KV 760939 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | GEN_2016_091__G16_091_TAP | 3 Phase fault on GEN-2016-091 (587740) 345 kV Bus a. Apply fault at the GEN-2016-091 (587740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2016-091 345.0 KV 587740 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | GEN_2018_004__G18_004_TAP | 3 Phase fault on GEN-2018-004 (762438) 115 kV Bus a. Apply fault at the GEN-2018-004 (762438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-004 115.0 KV 762438 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | GEN_2018_015__G18_015_TAP | 3 Phase fault on GEN-2018-015 (762460) 345 kV Bus a. Apply fault at the GEN-2018-015 (762460) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-015 345.0 KV 762460 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | GRACMNT4__ANADARK4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | GRACMNT4__WASHITA4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO WASHITA4 138.0 KV 521089 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | GRACMNT7__G16_037_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | GRACMNT7__G16_091_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | GRACMNT7__GEN_2015_093 | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO GEN-2015-093 345.0 KV 563269 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | GRASSLAND__6__CIRRUS_WND_6 | 3 Phase fault on GRASSLAND 6 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6 (526677) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 6 230.0 KV 526677 TO CIRRUS_WND 6 230.0 KV 526679 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | HALECENTER_2__TUCO_INT___2 | 3 Phase fault on HALECENTER 2 (525738) 69 kV Bus a. Apply fault at the HALECENTER 2 (525738) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALECENTER 2 69.0 KV 525738 TO TUCO_INT 2 69.0 KV 525826 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | HALE_CNTY__3__PLANT_X____3 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 115.0 KV 525454 TO PLANT_X 3 115.0 KV 525480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | HALE_CNTY__3__TUCO_INT___3 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 115.0 KV 525454 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | HIGGEAST___3__HIGG_______3 | 3 Phase fault on HIGGEAST 3 (527286) 115 kV Bus a. Apply fault at the HIGGEAST 3 (527286) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGGEAST 3 115.0 KV 527286 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | HOBBS_INT__3__HIGG_______3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO BENSING 3 115.0 KV 528433 CKT 1 b.2. LOAD 1 528433 b.3. LOAD 1* 528433 b.4. HIGG 3 115.0 KV 527363 TO BENSING 3 115.0 KV 528433 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | HOBBS_INT__3__LE_WEST_SUB3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO LE-WEST_SUB3 115.0 KV 528333 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | HOBBS_INT__3__MADDOX_____3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO MADDOX 3 115.0 KV 528355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | HOBBS_INT__3__MILLEN_TPW_3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO MILLEN_TPW 3 115.0 KV 528434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | HOBBS_INT__6__ANDREWS____6 | 3 Phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 230.0 KV 527894 TO ANDREWS 6 230.0 KV 528604 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | HOBBS_INT__7__KIOWA______7 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | IMC__1_TP__3__IMC__1_____3 | 3 Phase fault on IMC_#1_TP 3 (528035) 115 kV Bus a. Apply fault at the IMC_#1_TP 3 (528035) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMC_#1_TP 3 115.0 KV 528035 TO IMC_#1 3 115.0 KV 528037 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | IMC__1_TP__3__XTO_DI9_TP_3 | 3 Phase fault on IMC_#1_TP 3 (528035) 115 kV Bus a. Apply fault at the IMC_#1_TP 3 (528035) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMC_#1_TP 3 115.0 KV 528035 TO XTO_DI9_TP 3 115.0 KV 528064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | INK_BASIN__6__HOBBS_INT__6 | 3 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 230.0 KV 527028 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | INTREPDW_TP3__IMC__1_TP__3 | 3 Phase fault on INTREPDW_TP3 (527999) 115 kV Bus a. Apply fault at the INTREPDW_TP3 (527999) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INTREPDW_TP3 115.0 KV 527999 TO IMC_#1_TP 3 115.0 KV 528035 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | INTREPDW_TP3__INTREPIDWST3 | 3 Phase fault on INTREPDW_TP3 (527999) 115 kV Bus a. Apply fault at the INTREPDW_TP3 (527999) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INTREPDW_TP3 115.0 KV 527999 TO INTREPIDWST3 115.0 KV 528000 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | JOHNCO_7__SUNNYSD7 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | JOHNSON_DRW3__HIGG_______3 | 3 Phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNSON_DRW3 115.0 KV 527362 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | JOHNSON_DRW3__TAYLOR_____3 | 3 Phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNSON_DRW3 115.0 KV 527362 TO TAYLOR 3 115.0 KV 528413 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | JONES______6__GRASSLAND__6 | 3 Phase fault on JONES 6 (526337) 230 kV Bus a. Apply fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES 6 230.0 KV 526337 TO GRASSLAND 6 230.0 KV 526677 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | KIOWA______7__N_LOVING___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO N_LOVING 7 345.0 KV 528185 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | KIOWA______7__RDRUNNER___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | KRESS_INT__3__HALE_CNTY__3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | KRESS_INT__3__SWISHER____3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO SWISHER 3 115.0 KV 525212 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LAMTON_____3__HALE_CNTY__3 | 3 Phase fault on LAMTON 3 (525414) 115 kV Bus a. Apply fault at the LAMTON 3 (525414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMTON 3 115.0 KV 525414 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LEA_NATIONL3__SUMMIT_3 | 3 Phase fault on LEA_NATIONL3 (528399) 115 kV Bus a. Apply fault at the LEA_NATIONL3 (528399) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEA_NATIONL3 115.0 KV 528399 TO SUMMIT_3 115.0 KV 528404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LEA_ROAD___3__OIL_CENTER_3 | 3 Phase fault on LEA_ROAD 3 (528505) 115 kV Bus a. Apply fault at the LEA_ROAD 3 (528505) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEA_ROAD 3 115.0 KV 528505 TO OIL_CENTER 3 115.0 KV 528552 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LE_SANANDRS2__LE_BUCKEYE_2 | 3 Phase fault on LE-SANANDRS2 (528622) 69 kV Bus a. Apply fault at the LE-SANANDRS2 (528622) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-SANANDRS2 69.0 KV 528622 TO LE-BUCKEYE 2 69.0 KV 528630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LE_SANANDRS2__LE_LEE_____2 | 3 Phase fault on LE-SANANDRS2 (528622) 69 kV Bus a. Apply fault at the LE-SANANDRS2 (528622) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-SANANDRS2 69.0 KV 528622 TO LE-LEE 2 69.0 KV 528634 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LE_SANANDRS2__LE_MHOON___2 | 3 Phase fault on LE-SANANDRS2 (528622) 69 kV Bus a. Apply fault at the LE-SANANDRS2 (528622) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-SANANDRS2 69.0 KV 528622 TO LE-MHOON 2 69.0 KV 528667 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LE_SANANDRS2__LE_VACUUM__2 | 3 Phase fault on LE-SANANDRS2 (528622) 69 kV Bus a. Apply fault at the LE-SANANDRS2 (528622) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-SANANDRS2 69.0 KV 528622 TO LE-VACUUM 2 69.0 KV 528642 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LE_SANANDRS3__LE_TXACO_TP3 | 3 Phase fault on LE-SANANDRS3 (528341) 115 kV Bus a. Apply fault at the LE-SANANDRS3 (528341) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-SANANDRS3 115.0 KV 528341 TO LE-TXACO_TP3 115.0 KV 528627 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LE_TXACO_TP3__LE_TEXACO__3 | 3 Phase fault on LE-TXACO_TP3 (528627) 115 kV Bus a. Apply fault at the LE-TXACO_TP3 (528627) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-TXACO_TP3 115.0 KV 528627 TO LE-TEXACO 3 115.0 KV 528792 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LE_WEST_SUB3__LE_NRTH_INT3 | 3 Phase fault on LE-WEST_SUB3 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3 (528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3 115.0 KV 528333 TO LE-NRTH_INT3 115.0 KV 528334 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LIVSTNRIDGE3__CARDINAL___3 | 3 Phase fault on LIVSTNRIDGE3 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 115.0 KV 527953 TO MEDANOS 3 115.0 KV 527954 CKT 1 b.2. LOAD 1 527954 b.3. MEDANOS 3 115.0 KV 527954 TO SAGE_BRUSH 3 115.0 KV 527955 CKT 1 b.4. LOAD 1 527955 b.5. LOAD 1* 527955 b.6. SAGE_BRUSH 3 115.0 KV 527955 TO CARDINAL 3 115.0 KV 528596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LIVSTNRIDGE3__WIPP_______3 | 3 Phase fault on LIVSTNRIDGE3 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 115.0 KV 527953 TO WIPP 3 115.0 KV 528009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LIVSTNRIDGE3__XTO_DI9_TP_3 | 3 Phase fault on LIVSTNRIDGE3 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 115.0 KV 527953 TO XTO_DI9_TP 3 115.0 KV 528064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LUBBCK_EST_6__JONES______6 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 230.0 KV 526299 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LUBBCK_STH_3__LUBBCK_EST_3 | 3 Phase fault on LUBBCK_STH 3 (526268) 115 kV Bus a. Apply fault at the LUBBCK_STH 3 (526268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 3 115.0 KV 526268 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LUBBCK_STH_6__JONES______6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO JONES 6 230.0 KV 526337 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LUBBCK_STH_6__WOLFFORTH__6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LWSTAP_4__L_E_S__4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LWSTAP_4__RPPAPER4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LWS___S4__LWSTAP_4 | 3 Phase fault on LWS S4 (511431) 138 kV Bus a. Apply fault at the LWS S4 (511431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS S4 138.0 KV 511431 TO LWSTAP 4 138.0 KV 511439 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | L_E_S__2__LGORE_N2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-N2 69.0 KV 511469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | L_E_S__2__LGORE_S2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-S2 69.0 KV 511470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | L_E_S__4__ARTVLTP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 b.2. LOAD 1 511474 b.3. SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | L_E_S__4__COMMTAP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | L_E_S__4__ELGINJT4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | L_E_S__7__G16_091_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | L_E_S__7__G17_171_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | MADDOX_____3__ENRON_TP___3 | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO PEARLE 3 115.0 KV 528392 CKT 1 b.2. LOAD 1 528392 b.3. LOAD 1* 528392 b.4. ENRON_TP 3 115.0 KV 528317 TO PEARLE 3 115.0 KV 528392 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | MADDOX_____3__G18_004_TAP | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | MADDOX_____3__MONUMENT___3 | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO MONUMENT 3 115.0 KV 528491 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection. High voltage issue at G18-004-TAP. | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800. Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | MAPCO______3__JOHNSON_DRW3 | 3 Phase fault on MAPCO 3 (527360) 115 kV Bus a. Apply fault at the MAPCO 3 (527360) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAPCO 3 115.0 KV 527360 TO JOHNSON_DRW3 115.0 KV 527362 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | MILLEN_TPW_3__MILLEN_TPE_3 | 3 Phase fault on MILLEN_TPW 3 (528434) 115 kV Bus a. Apply fault at the MILLEN_TPW 3 (528434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPW 3 115.0 KV 528434 TO MILLEN_TPE 3 115.0 KV 528436 CKT *1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | MILLEN_TPW_3__MILLEN_____3 | 3 Phase fault on MILLEN_TPW 3 (528434) 115 kV Bus a. Apply fault at the MILLEN_TPW 3 (528434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPW 3 115.0 KV 528434 TO MILLEN 3 115.0 KV 528435 CKT *1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | MILLEN_____3__MILLEN_TPE_3 | 3 Phase fault on MILLEN 3 (528435) 115 kV Bus a. Apply fault at the MILLEN 3 (528435) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN 3 115.0 KV 528435 TO MILLEN_TPE 3 115.0 KV 528436 CKT *1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | MINCO__7__CIMARON7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | MINCO__7__GEN_2017_233 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GEN-2017-233 345.0 KV 761250 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8 or reduce to 0.2.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | MINCO__7__GRACMNT7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | MINCO__7__MCNOWND7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MCNOWND7 345.0 KV 515444 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | MINCO__7__MNCWND37 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MNCWND37 345.0 KV 515549 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | MINCO__7__NORMHLL7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | MONUMENT___3__MONUMNT_TP_3 | 3 Phase fault on MONUMENT 3 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3 115.0 KV 528491 TO MONUMNT_TP 3 115.0 KV 528568 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | MONUMENT___3__W_HOBBS____3 | 3 Phase fault on MONUMENT 3 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3 115.0 KV 528491 TO W_HOBBS 3 115.0 KV 528498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | MONUMNT_TP_3__BYRD_TP____3 | 3 Phase fault on MONUMNT_TP 3 (528568) 115 kV Bus a. Apply fault at the MONUMNT_TP 3 (528568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMNT_TP 3 115.0 KV 528568 TO BYRD_TP 3 115.0 KV 528581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | MUSTANG____6__SEMINOLE___6 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6 (527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 230.0 KV 527149 TO SEMINOLE 6 230.0 KV 527276 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | NEEDMORE___6__YOAKUM_____6 | 3 Phase fault on NEEDMORE 6 (525586) 230 kV Bus a. Apply fault at the NEEDMORE 6 (525586) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEEDMORE 6 230.0 KV 525586 TO YOAKUM 6 230.0 KV 526935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | NEWHART____6__PLANT_X____6 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 230.0 KV 525461 TO PLANT_X 6 230.0 KV 525481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | NICHOLS____6__AMA_SOUTH__6 | 3 Phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 230.0 KV 524044 TO AMA_SOUTH 6 230.0 KV 524415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues. Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | NORTH_LOVNG3__AGAVE_PDURO3 | 3 Phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 115.0 KV 528182 TO AGAVE_PDURO3 115.0 KV 528195 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | NORTH_LOVNG3__BLACKRIVER_3 | 3 Phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 115.0 KV 528182 TO BLACKRIVER 3 115.0 KV 528193 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | NORTH_LOVNG3__HOPI_SUB___3 | 3 Phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 115.0 KV 528182 TO HOPI_SUB 3 115.0 KV 528226 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | NORTH_LOVNG3__SOUTH_LOVNG3 | 3 Phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 115.0 KV 528182 TO SOUTH_LOVNG3 115.0 KV 528192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | N_LOVING___7__CHINA_DRAW_7 | 3 Phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 345.0 KV 528185 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | OASIS______6__ROOSEVELT__6 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 230.0 KV 524875 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | OKLEHV24__OKLEHV14 | 3 Phase fault on OKLEHV24 (590001) 138 kV Bus a. Apply fault at the OKLEHV24 (590001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKLEHV24 138.0 KV 590001 TO OKLEHV14 138.0 KV 590003 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | OXY_WSEM_TP3__JOHNSON_DRW3 | 3 Phase fault on OXY_WSEM_TP3 (527325) 115 kV Bus a. Apply fault at the OXY_WSEM_TP3 (527325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OXY_WSEM_TP3 115.0 KV 527325 TO JOHNSON_DRW3 115.0 KV 527362 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | O_K_U__7__G17_151TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | O_K_U__7__G18_015_TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | O_K_U__7__GEN_2017_033 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO GEN-2017-033 345.0 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | O_K_U__7__L_E_S__7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO L.E.S.-7 345.0 KV 511468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | O_K_U__7__OKLAUN_HVDC7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO OKLAUN HVDC7 345.0 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | PCA________3__CARLSBAD___3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO CARLSBAD 3 115.0 KV 528160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | PCA________3__CV_LUSK_TP_3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO CV-LUSK_TP 3 115.0 KV 527948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | PCA________3__POTASH_JCT_3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO POTASH_JCT 3 115.0 KV 527962 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | PCA________3__XTO_BIGEDDY3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO XTO_BIGEDDY3 115.0 KV 528396 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | PHANTOM____3__SOUTH_LOVNG3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO MALAGABEND 3 115.0 KV 528194 CKT 1 b.2. LOAD 1 528194 b.3. SOUTH_LOVNG3 115.0 KV 528192 TO MALAGABEND 3 115.0 KV 528194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | PHANTOM____3__WOLFCAMP_TP3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO BOPCO_PKRLK3 115.0 KV 528020 CKT 1 b.2. LOAD 1 528020 b.3. BOPCO_PKRLK3 115.0 KV 528020 TO WOLFCAMP_TP3 115.0 KV 528235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | PHANTOM____3__WOOD_DRAW__3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO WOOD_DRAW 3 115.0 KV 528228 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | PHANTOM____7__CHINA_DRAW_7 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 345.0 KV 528015 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | PHANTOM____7__RDRUNNER___7 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 345.0 KV 528015 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | PLAINS_INT_3__YOAKUM_____3 | 3 Phase fault on PLAINS_INT 3 (526928) 115 kV Bus a. Apply fault at the PLAINS_INT 3 (526928) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINS_INT 3 115.0 KV 526928 TO YOAKUM 3 115.0 KV 526934 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | PLANT_X____6__G17_146_TAP | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO G17-146-TAP 230.0 KV 760498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | LANOGSU1 trips on voltage protection settings. GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues. Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | PLANT_X____6__SUNDOWN____6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO SUNDOWN 6 230.0 KV 526435 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | LANOGSU1 trips on voltage protection settings. GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues. Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | PLANT_X____6__TOLK_______6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | LANOGSU1 trips on voltage protection settings. GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues. Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | PLSNT_HILL_6__ROOSEVELT__6 | 3 Phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 230.0 KV 524770 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | POTASH_JCT_2__DUVAL__1___2 | 3 Phase fault on POTASH_JCT 2 (527961) 69 kV Bus a. Apply fault at the POTASH_JCT 2 (527961) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 2 69.0 KV 527961 TO DUVAL_#1 2 69.0 KV 527980 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | POTASH_JCT_2__KERMAC_____2 | 3 Phase fault on POTASH_JCT 2 (527961) 69 kV Bus a. Apply fault at the POTASH_JCT 2 (527961) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 2 69.0 KV 527961 TO KERMAC 2 69.0 KV 527996 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | POTASH_JCT_2__MISSCHEM_2_2 | 3 Phase fault on POTASH_JCT 2 (527961) 69 kV Bus a. Apply fault at the POTASH_JCT 2 (527961) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 2 69.0 KV 527961 TO MISSCHEM#2 2 69.0 KV 528022 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | POTASH_JCT_2__NATPOT_TP__2 | 3 Phase fault on POTASH_JCT 2 (527961) 69 kV Bus a. Apply fault at the POTASH_JCT 2 (527961) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 2 69.0 KV 527961 TO NATPOT_TP 2 69.0 KV 528145 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | POTASH_JCT_3__CARLSBAD___3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO CARLSBAD 3 115.0 KV 528160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | POTASH_JCT_3__INTREPDW_TP3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO INTREPDW_TP3 115.0 KV 527999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | POTASH_JCT_3__KIOWA______3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO KIOWA 3 115.0 KV 527966 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | POTASH_JCT_6__PECOS______6 | 3 Phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6 230.0 KV 527963 TO PECOS 6 230.0 KV 528179 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | POTTER_CO__6__NEWHART____6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | PRENTICE___3__YOAKUM_____3 | 3 Phase fault on PRENTICE 3 (526792) 115 kV Bus a. Apply fault at the PRENTICE 3 (526792) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRENTICE 3 115.0 KV 526792 TO YOAKUM 3 115.0 KV 526934 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | QUAHADA____3__DCP_ZIA_TP_3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO DCP_ZIA TP 3 115.0 KV 528422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | QUAHADA____3__LEA_NATIONL3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO LEA_NATIONL3 115.0 KV 528399 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | QUAHADA____3__PCA________3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO XTO_BIGEDDY3 115.0 KV 528396 CKT 1 b.2. LOAD 1 528396 b.3. PCA 3 115.0 KV 527930 TO XTO_BIGEDDY3 115.0 KV 528396 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | RANDALL____6__AMA_SOUTH__6 | 3 Phase fault on RANDALL 6 (524365) 230 kV Bus a. Apply fault at the RANDALL 6 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 230.0 KV 524365 TO AMA_SOUTH 6 230.0 KV 524415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | RDRUNNER___3__AGAVE_RHIL23 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHIL23 115.0 KV 528231 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | RDRUNNER___3__BATTLE_AXE_3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO BATTLE_AXE 3 115.0 KV 528040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | RDRUNNER___3__CUSTERMTN__3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO CUSTERMTN 3 115.0 KV 528239 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | RDRUNNER___3__GEN_2016_121 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO GEN-2016-121 115.0 KV 587990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | RDRUNNER___3__GEN_2018_052 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO GEN-2018-052 115.0 KV 762866 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | RDRUNNER___3__OCHOA______3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHILL3 115.0 KV 528230 CKT 1 b.2. LOAD 1 528230 b.3. AGAVE_RHILL3 115.0 KV 528230 TO OCHOA 3 115.0 KV 528232 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | RED_BLUFF__3__RDRUNNER___3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 115.0 KV 528018 TO RDRUNNER 3 115.0 KV 528025 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | RED_BLUFF__3__WIPP_______3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAND_DUNES 3 115.0 KV 528016 TO RED_BLUFF 3 115.0 KV 528018 CKT 1 b.2. WIPP 3 115.0 KV 528009 TO SAND_DUNES 3 115.0 KV 528016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | RED_BLUFF__3__WOLFCAMP_TP3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 115.0 KV 528018 TO WOLFCAMP_TP3 115.0 KV 528235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | ROOSEVELT__6__TOLK_______6 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 230.0 KV 524909 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | RR_SVC_HV__3__RDRUNNER___3 | 3 Phase fault on RR_SVC_HV 3 (528024) 115 kV Bus a. Apply fault at the RR_SVC_HV 3 (528024) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RR_SVC_HV 3 115.0 KV 528024 TO RDRUNNER 3 115.0 KV 528025 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8. Reclosing was removed.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | RSVLT_CC_E_7__CROSSROADS_7 | 3 Phase fault on RSVLT_CC_E 7 (527655) 345 kV Bus a. Apply fault at the RSVLT_CC_E 7 (527655) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_E 7 345.0 KV 527655 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | RUSHSPR7__GEN_2018_055 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345.0 KV 511571 TO GEN-2018-055 345.0 KV 762900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | RUSSELL____3__HIGG_______3 | 3 Phase fault on RUSSELL 3 (527284) 115 kV Bus a. Apply fault at the RUSSELL 3 (527284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL 3 115.0 KV 527284 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | SAGA_SCOL__7__CROSSROADS_7 | 3 Phase fault on SAGA_SCOL 7 (527610) 345 kV Bus a. Apply fault at the SAGA_SCOL 7 (527610) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAGA_SCOL 7 345.0 KV 527610 TO CROSSROADS 7 345.0 KV 527656 CKT 1 | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | SANGER_SW__3__G18_004_TAP | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | SANGER_SW__3__SW_4J44____3 | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO SW_4J44 3 115.0 KV 528484 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | SANGER_SW__3__W_BENDER___3 | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO OXYPERMIAN 3 115.0 KV 528575 CKT 1 b.2. LOAD 1 528575 b.3. LOAD 2 528575 b.4. OXY_NHU_RCF3 115.0 KV 528574 TO OXYPERMIAN 3 115.0 KV 528575 CKT 1 b.5. LOAD 1 528575 b.6. LOAD 2 528575 b.7. W_BENDER 3 115.0 KV 528449 TO OXY_NHU_RCF3 115.0 KV 528574 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | SN_JUAN_TAP6__CHAVES_CNTY6 | 3 Phase fault on SN_JUAN_TAP6 (524885) 230 kV Bus a. Apply fault at the SN_JUAN_TAP6 (524885) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SN_JUAN_TAP6 230.0 KV 524885 TO CHAVES_CNTY6 230.0 KV 527483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | SP_ABERNTHY2__TUCO_INT2__2 | 3 Phase fault on SP-ABERNTHY2 (525731) 69 kV Bus a. Apply fault at the SP-ABERNTHY2 (525731) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ABERNTHY2 69.0 KV 525731 TO TUCO_INT2 2 69.0 KV 525816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | SUNDOWN____6__WOLFFORTH__6 | 3 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 230.0 KV 526435 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | SUNNYSD7__G17_075_TAP | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G17-075-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | SUNNYSD7__GEN_2017_167 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO GEN-2017-167 345.0 KV 761859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | SWISHER____6__NEWHART____6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | SWISHER____6__TUCO_INT___6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | SW_4J44____3__TAYLOR_____3 | 3 Phase fault on SW_4J44 3 (528484) 115 kV Bus a. Apply fault at the SW_4J44 3 (528484) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OXY_S_HOBBS3 115.0 KV 528480 TO SW_4J44 3 115.0 KV 528484 CKT 1 b.2. S_HOBBS 3 115.0 KV 528477 TO OXY_S_HOBBS3 115.0 KV 528480 CKT 1 b.3. LOAD 1 528480 b.4. LOAD 2 528480 b.5. LOAD 3 528480 b.6. E_SANGER 3 115.0 KV 528470 TO S_HOBBS 3 115.0 KV 528477 CKT 1 b.7. LOAD 1 528477 b.8. LOAD 2 528477 b.9. TAYLOR 3 115.0 KV 528413 TO E_SANGER 3 115.0 KV 528470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | SW_4J44____3__W_HOBBS____3 | 3 Phase fault on SW_4J44 3 (528484) 115 kV Bus a. Apply fault at the SW_4J44 3 (528484) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW_4J44 3 115.0 KV 528484 TO W_HOBBS 3 115.0 KV 528498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | S_JAL______3__DOLLARHIDE_3 | 3 Phase fault on S_JAL 3 (528547) 115 kV Bus a. Apply fault at the S_JAL 3 (528547) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S_JAL 3 115.0 KV 528547 TO DOLLARHIDE 3 115.0 KV 528561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TAYLOR_____3__MILLEN_TPE_3 | 3 Phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 3 115.0 KV 528413 TO NE_HOBBS 3 115.0 KV 528442 CKT 1 b.2. LOAD 1 528442 b.3. MILLEN_TPE 3 115.0 KV 528436 TO NE_HOBBS 3 115.0 KV 528442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TAYLOR_____3__W_BENDER___3 | 3 Phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 3 115.0 KV 528413 TO W_BENDER 3 115.0 KV 528449 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TEAGUE_____3__CARDINAL___3 | 3 Phase fault on TEAGUE 3 (528526) 115 kV Bus a. Apply fault at the TEAGUE 3 (528526) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEAGUE 3 115.0 KV 528526 TO CARDINAL 3 115.0 KV 528596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TEAGUE_____3__S_JAL______3 | 3 Phase fault on TEAGUE 3 (528526) 115 kV Bus a. Apply fault at the TEAGUE 3 (528526) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEAGUE 3 115.0 KV 528526 TO S_JAL 3 115.0 KV 528547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TERRYRD7__G17_171_TAP | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TERRYRD7__RSHSPR1_MPT1 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RSHSPR1_MPT1 345.0 KV 511979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TERRYRD7__RUSHSPR7 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TERRYRD7__SUNNYSD7 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TOLK_______6__GEN_2017_158 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO GEN-2017-158 230.0 KV 762132 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TOLK_______6__LAMB_CNTY__6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO LAMB_CNTY 6 230.0 KV 525637 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | LANOGSU1 trips on voltage protection settings. GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues. Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TOLK_______6__NEEDMORE___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO NEEDMORE 6 230.0 KV 525586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | LANOGSU1 trips on voltage protection settings. GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues. Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TOLK_______6__TUCO_INT___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | LANOGSU1 trips on voltage protection settings. GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues. Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TOLK_______7__CROSSROADS_7 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TUCO_INT___2__LH_WIL&ELN+2 | 3 Phase fault on TUCO_INT 2 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 2 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 69.0 KV 525826 TO LH-WIL&ELN+2 69.0 KV 525853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TUCO_INT___2__SP_NEWDEAL_2 | 3 Phase fault on TUCO_INT 2 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 2 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 69.0 KV 525826 TO SP-NEWDEAL 2 69.0 KV 525885 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TUCO_INT___3__CARLISLE___3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO STANTON_W 3 115.0 KV 526076 CKT 1 b.2. LOAD 1 526076 b.3. STANTON_W 3 115.0 KV 526076 TO INDIANA 3 115.0 KV 526146 CKT 1 b.4. LOAD 1 526146 b.5. LOAD 2 526146 b.6. SP-ERSKINE 3 115.0 KV 526109 TO INDIANA 3 115.0 KV 526146 CKT 1 b.7. LOAD 1 526146 b.8. LOAD 2 526146 b.9. SP-ERSKINE 3 115.0 KV 526109 TO CARLISLE 3 115.0 KV 526160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TUCO_INT___3__LUBBCK_EST_3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TUCO_INT___6__ANTELOPE_1_6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO ANTELOPE_1 6 230.0 KV 525840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TUCO_INT___6__CARLISLE___6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO CARLISLE 6 230.0 KV 526161 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TUCO_INT___6__HALE_WNDCL16 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO HALE_WNDCL16 230.0 KV 525957 CKT 1 | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TUCO_INT___6__JONES______6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TUCO_INT___7__ELK_CT1 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO ELK_CT1 345.0 KV 525850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TUCO_INT___7__G17_151TAP | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TUCO_INT___7__YOAKUM_345 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO YOAKUM_345 345.0 KV 526936 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TWEEDY_____3__EDDY_NTH___3 | 3 Phase fault on TWEEDY 3 (527597) 115 kV Bus a. Apply fault at the TWEEDY 3 (527597) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWEEDY 3 115.0 KV 527597 TO EDDY_NTH 3 115.0 KV 527798 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | WHITTEN____3__LEA_ROAD___3 | 3 Phase fault on WHITTEN 3 (528540) 115 kV Bus a. Apply fault at the WHITTEN 3 (528540) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 3 115.0 KV 528519 TO WHITTEN 3 115.0 KV 528540 CKT 1 b.2. LOAD 1 528540 b.3. LEA_ROAD 3 115.0 KV 528505 TO WARD 3 115.0 KV 528519 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | WHITTEN____3__S_JAL______3 | 3 Phase fault on WHITTEN 3 (528540) 115 kV Bus a. Apply fault at the WHITTEN 3 (528540) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITTEN 3 115.0 KV 528540 TO S_JAL 3 115.0 KV 528547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | WOLFCAMP_TP3__WOLFCAMP___3 | 3 Phase fault on WOLFCAMP_TP3 (528235) 115 kV Bus a. Apply fault at the WOLFCAMP_TP3 (528235) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCAMP_TP3 115.0 KV 528235 TO WOLFCAMP 3 115.0 KV 528236 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | WWRDEHV7__BECKHAM7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | WWRDEHV7__DGRASSE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | WWRDEHV7__G07621119_20 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G07621119-20 345.0 KV 515599 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | WWRDEHV7__G16_003_TAP | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G16-003-TAP 345.0 KV 560071 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | WWRDEHV7__GUTHRIE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GUTHRIE7 345.0 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | WWRDEHV7__TATONGA7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | W_BENDER___3__N_HOBBS____3 | 3 Phase fault on W_BENDER 3 (528449) 115 kV Bus a. Apply fault at the W_BENDER 3 (528449) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_BENDER 3 115.0 KV 528449 TO N_HOBBS 3 115.0 KV 528456 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | W_HOBBS____3__DRINKARD_TP3 | 3 Phase fault on W_HOBBS 3 (528498) 115 kV Bus a. Apply fault at the W_HOBBS 3 (528498) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_HOBBS 3 115.0 KV 528498 TO DRINKARD_TP3 115.0 KV 528533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | XTO_DI9_TP_3__XTO_DI9____3 | 3 Phase fault on XTO_DI9_TP 3 (528064) 115 kV Bus a. Apply fault at the XTO_DI9_TP 3 (528064) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XTO_DI9_TP 3 115.0 KV 528064 TO XTO_DI9 3 115.0 KV 528066 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | XTO_MAHONEY6__GEN_2017_239 | 3 Phase fault on XTO_MAHONEY6 (527011) 230 kV Bus a. Apply fault at the XTO_MAHONEY6 (527011) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XTO_MAHONEY6 230.0 KV 527011 TO GEN-2017-239 230.0 KV 761355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | YOAKUM_345__HOBBS_INT__7 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | YOAKUM_____3__ARCO_TP____3 | 3 Phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 115.0 KV 526934 TO ARCO_TP 3 115.0 KV 527041 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | YOAKUM_____3__LG_PLSHILL_3 | 3 Phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 115.0 KV 526934 TO LG-PLSHILL 3 115.0 KV 527194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | YOAKUM_____6__BRU_SUB____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | YOAKUM_____6__INK_BASIN__6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO INK_BASIN 6 230.0 KV 527028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | YOAKUM_____6__MUSTANG____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO MUSTANG 6 230.0 KV 527149 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | YOAKUM_____6__SUNDOWN____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 b.2. SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | 53CACHE4__ARTVLTP4 | 3 Phase fault on 53CACHE4 (511509) 138 kV Bus a. Apply fault at the 53CACHE4 (511509) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53CACHE4 138.0 KV 511509 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | 7_RIVERS___6__PECOS______6 | 3 Phase fault on 7-RIVERS 6 (528095) 230 kV Bus a. Apply fault at the 7-RIVERS 6 (528095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 7-RIVERS 6 230.0 KV 528095 TO PECOS 6 230.0 KV 528179 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | AMA_SOUTH__6__SWISHER____6 | 3 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 230.0 KV 524415 TO SWISHER 6 230.0 KV 525213 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | AMOCOWASSON6__MUSTANG____6 | 3 Phase fault on AMOCOWASSON6 (526784) 230 kV Bus a. Apply fault at the AMOCOWASSON6 (526784) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCOWASSON6 230.0 KV 526784 TO MUSTANG 6 230.0 KV 527149 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | AMOCOWASSON6__XTO_MAHONEY6 | 3 Phase fault on AMOCOWASSON6 (526784) 230 kV Bus a. Apply fault at the AMOCOWASSON6 (526784) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCOWASSON6 230.0 KV 526784 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | ARTVLTP4__ARTVILL4 | 3 Phase fault on ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTVLTP4 138.0 KV 511537 TO ARTVILL4 138.0 KV 511538 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | BLCKRVR_DST3__CHINA_DRAW_3 | 3 Phase fault on BLCKRVR_DST3 (528206) 115 kV Bus a. Apply fault at the BLCKRVR_DST3 (528206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLCKRVR_DST3 115.0 KV 528206 TO CHINA_DRAW 3 115.0 KV 528222 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | BLUECLDPOI_6__NEEDMORE___6 | 3 Phase fault on BLUECLDPOI 6 (525585) 230 kV Bus a. Apply fault at the BLUECLDPOI 6 (525585) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUECLDPOI 6 230.0 KV 525585 TO NEEDMORE 6 230.0 KV 525586 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Reduce acceleration factor to 0.2.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | BORDER_____7__BECKHAM7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | BORDER_____7__TUCO_INT___7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO TUCO_INT 7 345.0 KV 525832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | BRU_SUB____6__OXYBRU_____6 | 3 Phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRU_SUB 6 230.0 KV 527009 TO OXYBRU 6 230.0 KV 527010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | BRU_SUB____6__XTO_MAHONEY6 | 3 Phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRU_SUB 6 230.0 KV 527009 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | BUCKEYE_TP_3__BUCKEYE____3 | 3 Phase fault on BUCKEYE_TP 3 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3 115.0 KV 528348 TO BUCKEYE 3 115.0 KV 528385 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | BUCKEYE_TP_3__LE_TXACO_TP3 | 3 Phase fault on BUCKEYE_TP 3 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3 115.0 KV 528348 TO LE-TXACO_TP3 115.0 KV 528627 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | BYRD_TP____3__BYRD_______3 | 3 Phase fault on BYRD_TP 3 (528581) 115 kV Bus a. Apply fault at the BYRD_TP 3 (528581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BYRD_TP 3 115.0 KV 528581 TO BYRD 3 115.0 KV 528582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CALLAHAN___3__FLOYD_CNTY_3 | 3 Phase fault on CALLAHAN 3 (525763) 115 kV Bus a. Apply fault at the CALLAHAN 3 (525763) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALLAHAN 3 115.0 KV 525763 TO FLOYD_CNTY 3 115.0 KV 525780 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CARDINAL___3__TARGA______3 | 3 Phase fault on CARDINAL 3 (528596) 115 kV Bus a. Apply fault at the CARDINAL 3 (528596) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARDINAL 3 115.0 KV 528596 TO TARGA 3 115.0 KV 528605 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CARLISLE___3__LP_DOUD_TP_3 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 115.0 KV 526160 TO LP-DOUD_TP 3 115.0 KV 526162 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CARLISLE___3__MURPHY_____3 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 115.0 KV 526160 TO MURPHY 3 115.0 KV 526192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CARLISLE___6__WOLFFORTH__6 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 230.0 KV 526161 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CARLSBAD___3__PECOS______3 | 3 Phase fault on CARLSBAD 3 (528160) 115 kV Bus a. Apply fault at the CARLSBAD 3 (528160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLSBAD 3 115.0 KV 528160 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CHAVES_CNTY6__EDDY_NORTH_6 | 3 Phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY6 230.0 KV 527483 TO EDDY_NORTH 6 230.0 KV 527799 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CHINA_DRAW_3__CD_SVC_HV__3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO CD_SVC_HV 3 115.0 KV 528225 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CHINA_DRAW_3__CHVRN_EDDYS3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO CHVRN_EDDYS3 115.0 KV 528252 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CHINA_DRAW_3__WOOD_DRAW__3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO WOOD_DRAW 3 115.0 KV 528228 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CHISHOLM7__BECKHAM7 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CHISHOLM7__G16_037_TAP | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | COMANC_2__L_E_S__2 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L.E.S.-2 69.0 KV 511466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | COMANC_4__112GORE4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | COMANC_4__COMMTAP4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | COMANC_4__L_E_S__4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | COMMTAP4__OMDUNCN4 | 3 Phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMMTAP4 138.0 KV 511494 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | COOPER_RNCH3__BYRD_TP____3 | 3 Phase fault on COOPER_RNCH3 (528554) 115 kV Bus a. Apply fault at the COOPER_RNCH3 (528554) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_RNCH3 115.0 KV 528554 TO BYRD_TP 3 115.0 KV 528581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | COX________3__HALE_CNTY__3 | 3 Phase fault on COX 3 (525326) 115 kV Bus a. Apply fault at the COX 3 (525326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 115.0 KV 525326 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CROSBY_____3__LUBBCK_EST_3 | 3 Phase fault on CROSBY 3 (525926) 115 kV Bus a. Apply fault at the CROSBY 3 (525926) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSBY 3 115.0 KV 525926 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CROSSROADS_7__EDDY_CNTY__7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 345.0 KV 527656 TO EDDY_CNTY 7 345.0 KV 527802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CUNNIGHM_N_6__POTASH_JCT_6 | 3 Phase fault on CUNNIGHM_N 6 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6 (527865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_N 6 230.0 KV 527865 TO POTASH_JCT 6 230.0 KV 527963 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CUNNIGHM_S_6__HOBBS_INT__6 | 3 Phase fault on CUNNIGHM_S 6 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 230.0 KV 527867 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CUNNINHAM__3__BUCKEYE_TP_3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO BUCKEYE_TP 3 115.0 KV 528348 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CUNNINHAM__3__HOBBS_INT__3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO HOBBS_INT 3 115.0 KV 527891 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CUNNINHAM__3__MADDOX_____3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO MADDOX 3 115.0 KV 528355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CUNNINHAM__3__MONUMNT_TP_3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO MONUMNT_TP 3 115.0 KV 528568 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CUNNINHAM__3__QUAHADA____3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO QUAHADA 3 115.0 KV 528394 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CUSTERMTN__3__PONDEROSA__3 | 3 Phase fault on CUSTERMTN 3 (528239) 115 kV Bus a. Apply fault at the CUSTERMTN 3 (528239) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTERMTN 3 115.0 KV 528239 TO PONDEROSA 3 115.0 KV 528240 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CUSTERMTN__3__WHITTEN____3 | 3 Phase fault on CUSTERMTN 3 (528239) 115 kV Bus a. Apply fault at the CUSTERMTN 3 (528239) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTERMTN 3 115.0 KV 528239 TO WHITTEN 3 115.0 KV 528540 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | DCP_ZIA_TP_3__DCP_ZIA____3 | 3 Phase fault on DCP_ZIA TP 3 (528422) 115 kV Bus a. Apply fault at the DCP_ZIA TP 3 (528422) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DCP_ZIA TP 3 115.0 KV 528422 TO DCP_ZIA 3 115.0 KV 528423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | DCP_ZIA_TP_3__MALJMAR1&2_3 | 3 Phase fault on DCP_ZIA TP 3 (528422) 115 kV Bus a. Apply fault at the DCP_ZIA TP 3 (528422) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ZIA 3 115.0 KV 528420 TO DCP_ZIA TP 3 115.0 KV 528422 CKT 1 b.2. MALJMAR1&2 3 115.0 KV 528406 TO ZIA 3 115.0 KV 528420 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | DRINKARD_TP3__DRINKARD___3 | 3 Phase fault on DRINKARD_TP3 (528533) 115 kV Bus a. Apply fault at the DRINKARD_TP3 (528533) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRINKARD_TP3 115.0 KV 528533 TO DRINKARD 3 115.0 KV 528589 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | DRINKARD___3__NA_ENRICH__3 | 3 Phase fault on DRINKARD 3 (528589) 115 kV Bus a. Apply fault at the DRINKARD 3 (528589) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRINKARD 3 115.0 KV 528589 TO NA_ENRICH 3 115.0 KV 528603 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | DUNCAN_4__DUNCHERTP4 | 3 Phase fault on DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138.0 KV 511453 TO DUNCHERTP4 138.0 KV 511552 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | DUNCAN_4__OMDUNCN4 | 3 Phase fault on DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138.0 KV 511453 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | EAGLE_CREEK3__EDDY_NTH___3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO EDDY_NTH 3 115.0 KV 527798 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | EDDY_CNTY__7__KIOWA______7 | 3 Phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 345.0 KV 527802 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | EDDY_NORTH_6__7_RIVERS___6 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 230.0 KV 527799 TO 7-RIVERS 6 230.0 KV 528095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | EDDY_NORTH_6__CUNNIGHM_N_6 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 230.0 KV 527799 TO CUNNIGHM_N 6 230.0 KV 527865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | EDDY_NTH___3__CV_8_MILE__3 | 3 Phase fault on EDDY_NTH 3 (527798) 115 kV Bus a. Apply fault at the EDDY_NTH 3 (527798) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NTH 3 115.0 KV 527798 TO CV-8_MILE 3 115.0 KV 527809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | EDDY_STH___3__CV_DAYTON_+3 | 3 Phase fault on EDDY_STH 3 (527793) 115 kV Bus a. Apply fault at the EDDY_STH 3 (527793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_STH 3 115.0 KV 527793 TO CV-DAYTON +3 115.0 KV 527821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | EDDY_STH___3__PECOS______3 | 3 Phase fault on EDDY_STH 3 (527793) 115 kV Bus a. Apply fault at the EDDY_STH 3 (527793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_STH 3 115.0 KV 527793 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | ELGINJT4__ELSWORTH___4 | 3 Phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT4 138.0 KV 511486 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | ENRON_TP___3__ENRON______3 | 3 Phase fault on ENRON_TP 3 (528317) 115 kV Bus a. Apply fault at the ENRON_TP 3 (528317) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENRON_TP 3 115.0 KV 528317 TO ENRON 3 115.0 KV 528318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | ENRON_TP___3__LEA_NATIONL3 | 3 Phase fault on ENRON_TP 3 (528317) 115 kV Bus a. Apply fault at the ENRON_TP 3 (528317) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENRON_TP 3 115.0 KV 528317 TO LEA_NATIONL3 115.0 KV 528399 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | EUNICE_____3__CARDINAL___3 | 3 Phase fault on EUNICE 3 (528512) 115 kV Bus a. Apply fault at the EUNICE 3 (528512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUNICE 3 115.0 KV 528512 TO CARDINAL 3 115.0 KV 528596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | EUNICE_____3__DRINKARD_TP3 | 3 Phase fault on EUNICE 3 (528512) 115 kV Bus a. Apply fault at the EUNICE 3 (528512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUNICE 3 115.0 KV 528512 TO DRINKARD_TP3 115.0 KV 528533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | FIESTA_____3__CARLSBAD___3 | 3 Phase fault on FIESTA 3 (528151) 115 kV Bus a. Apply fault at the FIESTA 3 (528151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIESTA 3 115.0 KV 528151 TO CARLSBAD 3 115.0 KV 528160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | FLETCHR4__FLE_TAP4 | 3 Phase fault on FLETCHR4 (511422) 138 kV Bus a. Apply fault at the FLETCHR4 (511422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR4 138.0 KV 511422 TO FLE TAP4 138.0 KV 511423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | FLE_TAP4__G16_097_TAP | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | FLE_TAP4__L_E_S__4 | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | FLOYD_CNTY_3__BLANCO_____3 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 115.0 KV 525780 TO BLANCO 3 115.0 KV 525803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | FLOYD_CNTY_3__TUCO_INT___3 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 115.0 KV 525780 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | G16_091_TAP__GEN_2016_095 | 3 Phase fault on G16-091-TAP (587744) 345 kV Bus a. Apply fault at the G16-091-TAP (587744) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-091-TAP 345.0 KV 587744 TO GEN-2016-095 345.0 KV 587770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | G17_151TAP__G18_015_TAP | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | G17_151TAP__GEN_2017_151 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO GEN-2017-151 345.0 KV 762217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | G17_171_TAP__GEN_2017_171 | 3 Phase fault on G17-171-TAP (760938) 345 kV Bus a. Apply fault at the G17-171-TAP (760938) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-171-TAP 345.0 KV 760938 TO GEN-2017-171 345.0 KV 760939 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | GEN_2016_091__G16_091_TAP | 3 Phase fault on GEN-2016-091 (587740) 345 kV Bus a. Apply fault at the GEN-2016-091 (587740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2016-091 345.0 KV 587740 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | GEN_2018_004__G18_004_TAP | 3 Phase fault on GEN-2018-004 (762438) 115 kV Bus a. Apply fault at the GEN-2018-004 (762438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-004 115.0 KV 762438 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | GEN_2018_015__G18_015_TAP | 3 Phase fault on GEN-2018-015 (762460) 345 kV Bus a. Apply fault at the GEN-2018-015 (762460) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-015 345.0 KV 762460 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | GRACMNT4__ANADARK4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | GRACMNT4__WASHITA4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO WASHITA4 138.0 KV 521089 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | GRACMNT7__G16_037_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | GRACMNT7__G16_091_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | GRACMNT7__GEN_2015_093 | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO GEN-2015-093 345.0 KV 563269 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | GRASSLAND__6__CIRRUS_WND_6 | 3 Phase fault on GRASSLAND 6 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6 (526677) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 6 230.0 KV 526677 TO CIRRUS_WND 6 230.0 KV 526679 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | HALECENTER_2__TUCO_INT___2 | 3 Phase fault on HALECENTER 2 (525738) 69 kV Bus a. Apply fault at the HALECENTER 2 (525738) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALECENTER 2 69.0 KV 525738 TO TUCO_INT 2 69.0 KV 525826 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | HALE_CNTY__3__PLANT_X____3 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 115.0 KV 525454 TO PLANT_X 3 115.0 KV 525480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | HALE_CNTY__3__TUCO_INT___3 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 115.0 KV 525454 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | HIGGEAST___3__HIGG_______3 | 3 Phase fault on HIGGEAST 3 (527286) 115 kV Bus a. Apply fault at the HIGGEAST 3 (527286) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGGEAST 3 115.0 KV 527286 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | HOBBS_INT__3__HIGG_______3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO BENSING 3 115.0 KV 528433 CKT 1 b.2. LOAD 1 528433 b.3. LOAD 1* 528433 b.4. HIGG 3 115.0 KV 527363 TO BENSING 3 115.0 KV 528433 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | HOBBS_INT__3__LE_WEST_SUB3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO LE-WEST_SUB3 115.0 KV 528333 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | HOBBS_INT__3__MADDOX_____3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO MADDOX 3 115.0 KV 528355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | HOBBS_INT__3__MILLEN_TPW_3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO MILLEN_TPW 3 115.0 KV 528434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | HOBBS_INT__6__ANDREWS____6 | 3 Phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 230.0 KV 527894 TO ANDREWS 6 230.0 KV 528604 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | HOBBS_INT__7__KIOWA______7 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | IMC__1_TP__3__IMC__1_____3 | 3 Phase fault on IMC_#1_TP 3 (528035) 115 kV Bus a. Apply fault at the IMC_#1_TP 3 (528035) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMC_#1_TP 3 115.0 KV 528035 TO IMC_#1 3 115.0 KV 528037 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | IMC__1_TP__3__XTO_DI9_TP_3 | 3 Phase fault on IMC_#1_TP 3 (528035) 115 kV Bus a. Apply fault at the IMC_#1_TP 3 (528035) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMC_#1_TP 3 115.0 KV 528035 TO XTO_DI9_TP 3 115.0 KV 528064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | INK_BASIN__6__HOBBS_INT__6 | 3 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 230.0 KV 527028 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | INTREPDW_TP3__IMC__1_TP__3 | 3 Phase fault on INTREPDW_TP3 (527999) 115 kV Bus a. Apply fault at the INTREPDW_TP3 (527999) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INTREPDW_TP3 115.0 KV 527999 TO IMC_#1_TP 3 115.0 KV 528035 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | INTREPDW_TP3__INTREPIDWST3 | 3 Phase fault on INTREPDW_TP3 (527999) 115 kV Bus a. Apply fault at the INTREPDW_TP3 (527999) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INTREPDW_TP3 115.0 KV 527999 TO INTREPIDWST3 115.0 KV 528000 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | JOHNCO_7__SUNNYSD7 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | JOHNSON_DRW3__HIGG_______3 | 3 Phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNSON_DRW3 115.0 KV 527362 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | JOHNSON_DRW3__TAYLOR_____3 | 3 Phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNSON_DRW3 115.0 KV 527362 TO TAYLOR 3 115.0 KV 528413 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | JONES______6__GRASSLAND__6 | 3 Phase fault on JONES 6 (526337) 230 kV Bus a. Apply fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES 6 230.0 KV 526337 TO GRASSLAND 6 230.0 KV 526677 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | KIOWA______7__N_LOVING___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO N_LOVING 7 345.0 KV 528185 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | KIOWA______7__RDRUNNER___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | KRESS_INT__3__HALE_CNTY__3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | KRESS_INT__3__SWISHER____3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO SWISHER 3 115.0 KV 525212 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LAMTON_____3__HALE_CNTY__3 | 3 Phase fault on LAMTON 3 (525414) 115 kV Bus a. Apply fault at the LAMTON 3 (525414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMTON 3 115.0 KV 525414 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LEA_NATIONL3__SUMMIT_3 | 3 Phase fault on LEA_NATIONL3 (528399) 115 kV Bus a. Apply fault at the LEA_NATIONL3 (528399) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEA_NATIONL3 115.0 KV 528399 TO SUMMIT_3 115.0 KV 528404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LEA_ROAD___3__OIL_CENTER_3 | 3 Phase fault on LEA_ROAD 3 (528505) 115 kV Bus a. Apply fault at the LEA_ROAD 3 (528505) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEA_ROAD 3 115.0 KV 528505 TO OIL_CENTER 3 115.0 KV 528552 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LE_SANANDRS2__LE_BUCKEYE_2 | 3 Phase fault on LE-SANANDRS2 (528622) 69 kV Bus a. Apply fault at the LE-SANANDRS2 (528622) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-SANANDRS2 69.0 KV 528622 TO LE-BUCKEYE 2 69.0 KV 528630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LE_SANANDRS2__LE_LEE_____2 | 3 Phase fault on LE-SANANDRS2 (528622) 69 kV Bus a. Apply fault at the LE-SANANDRS2 (528622) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-SANANDRS2 69.0 KV 528622 TO LE-LEE 2 69.0 KV 528634 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LE_SANANDRS2__LE_MHOON___2 | 3 Phase fault on LE-SANANDRS2 (528622) 69 kV Bus a. Apply fault at the LE-SANANDRS2 (528622) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-SANANDRS2 69.0 KV 528622 TO LE-MHOON 2 69.0 KV 528667 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LE_SANANDRS2__LE_VACUUM__2 | 3 Phase fault on LE-SANANDRS2 (528622) 69 kV Bus a. Apply fault at the LE-SANANDRS2 (528622) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-SANANDRS2 69.0 KV 528622 TO LE-VACUUM 2 69.0 KV 528642 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LE_SANANDRS3__LE_TXACO_TP3 | 3 Phase fault on LE-SANANDRS3 (528341) 115 kV Bus a. Apply fault at the LE-SANANDRS3 (528341) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-SANANDRS3 115.0 KV 528341 TO LE-TXACO_TP3 115.0 KV 528627 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LE_TXACO_TP3__LE_TEXACO__3 | 3 Phase fault on LE-TXACO_TP3 (528627) 115 kV Bus a. Apply fault at the LE-TXACO_TP3 (528627) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-TXACO_TP3 115.0 KV 528627 TO LE-TEXACO 3 115.0 KV 528792 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LE_WEST_SUB3__LE_NRTH_INT3 | 3 Phase fault on LE-WEST_SUB3 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3 (528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3 115.0 KV 528333 TO LE-NRTH_INT3 115.0 KV 528334 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LIVSTNRIDGE3__CARDINAL___3 | 3 Phase fault on LIVSTNRIDGE3 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 115.0 KV 527953 TO MEDANOS 3 115.0 KV 527954 CKT 1 b.2. LOAD 1 527954 b.3. MEDANOS 3 115.0 KV 527954 TO SAGE_BRUSH 3 115.0 KV 527955 CKT 1 b.4. LOAD 1 527955 b.5. LOAD 1* 527955 b.6. SAGE_BRUSH 3 115.0 KV 527955 TO CARDINAL 3 115.0 KV 528596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LIVSTNRIDGE3__WIPP_______3 | 3 Phase fault on LIVSTNRIDGE3 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 115.0 KV 527953 TO WIPP 3 115.0 KV 528009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LIVSTNRIDGE3__XTO_DI9_TP_3 | 3 Phase fault on LIVSTNRIDGE3 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 115.0 KV 527953 TO XTO_DI9_TP 3 115.0 KV 528064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LUBBCK_EST_6__JONES______6 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 230.0 KV 526299 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LUBBCK_STH_3__LUBBCK_EST_3 | 3 Phase fault on LUBBCK_STH 3 (526268) 115 kV Bus a. Apply fault at the LUBBCK_STH 3 (526268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 3 115.0 KV 526268 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LUBBCK_STH_6__JONES______6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO JONES 6 230.0 KV 526337 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LUBBCK_STH_6__WOLFFORTH__6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LWSTAP_4__L_E_S__4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LWSTAP_4__RPPAPER4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LWS___S4__LWSTAP_4 | 3 Phase fault on LWS S4 (511431) 138 kV Bus a. Apply fault at the LWS S4 (511431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS S4 138.0 KV 511431 TO LWSTAP 4 138.0 KV 511439 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | L_E_S__2__LGORE_N2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-N2 69.0 KV 511469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | L_E_S__2__LGORE_S2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-S2 69.0 KV 511470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | L_E_S__4__ARTVLTP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 b.2. LOAD 1 511474 b.3. SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | L_E_S__4__COMMTAP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | L_E_S__4__ELGINJT4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | L_E_S__7__G16_091_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | L_E_S__7__G17_171_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | MADDOX_____3__ENRON_TP___3 | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO PEARLE 3 115.0 KV 528392 CKT 1 b.2. LOAD 1 528392 b.3. LOAD 1* 528392 b.4. ENRON_TP 3 115.0 KV 528317 TO PEARLE 3 115.0 KV 528392 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | MADDOX_____3__G18_004_TAP | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | MADDOX_____3__MONUMENT___3 | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO MONUMENT 3 115.0 KV 528491 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | MAPCO______3__JOHNSON_DRW3 | 3 Phase fault on MAPCO 3 (527360) 115 kV Bus a. Apply fault at the MAPCO 3 (527360) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAPCO 3 115.0 KV 527360 TO JOHNSON_DRW3 115.0 KV 527362 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | MILLEN_TPW_3__MILLEN_TPE_3 | 3 Phase fault on MILLEN_TPW 3 (528434) 115 kV Bus a. Apply fault at the MILLEN_TPW 3 (528434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPW 3 115.0 KV 528434 TO MILLEN_TPE 3 115.0 KV 528436 CKT *1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | MILLEN_TPW_3__MILLEN_____3 | 3 Phase fault on MILLEN_TPW 3 (528434) 115 kV Bus a. Apply fault at the MILLEN_TPW 3 (528434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPW 3 115.0 KV 528434 TO MILLEN 3 115.0 KV 528435 CKT *1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | MILLEN_____3__MILLEN_TPE_3 | 3 Phase fault on MILLEN 3 (528435) 115 kV Bus a. Apply fault at the MILLEN 3 (528435) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN 3 115.0 KV 528435 TO MILLEN_TPE 3 115.0 KV 528436 CKT *1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | MINCO__7__CIMARON7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | MINCO__7__GEN_2017_233 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GEN-2017-233 345.0 KV 761250 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | MINCO__7__GRACMNT7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | MINCO__7__MCNOWND7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MCNOWND7 345.0 KV 515444 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | MINCO__7__MNCWND37 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MNCWND37 345.0 KV 515549 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | MINCO__7__NORMHLL7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | MONUMENT___3__MONUMNT_TP_3 | 3 Phase fault on MONUMENT 3 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3 115.0 KV 528491 TO MONUMNT_TP 3 115.0 KV 528568 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | MONUMENT___3__W_HOBBS____3 | 3 Phase fault on MONUMENT 3 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3 115.0 KV 528491 TO W_HOBBS 3 115.0 KV 528498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | MONUMNT_TP_3__BYRD_TP____3 | 3 Phase fault on MONUMNT_TP 3 (528568) 115 kV Bus a. Apply fault at the MONUMNT_TP 3 (528568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMNT_TP 3 115.0 KV 528568 TO BYRD_TP 3 115.0 KV 528581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | MUSTANG____6__SEMINOLE___6 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6 (527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 230.0 KV 527149 TO SEMINOLE 6 230.0 KV 527276 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | NEEDMORE___6__YOAKUM_____6 | 3 Phase fault on NEEDMORE 6 (525586) 230 kV Bus a. Apply fault at the NEEDMORE 6 (525586) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEEDMORE 6 230.0 KV 525586 TO YOAKUM 6 230.0 KV 526935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | NEWHART____6__PLANT_X____6 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 230.0 KV 525461 TO PLANT_X 6 230.0 KV 525481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | NICHOLS____6__AMA_SOUTH__6 | 3 Phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 230.0 KV 524044 TO AMA_SOUTH 6 230.0 KV 524415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8 or reduce to 0.2.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | NORTH_LOVNG3__AGAVE_PDURO3 | 3 Phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 115.0 KV 528182 TO AGAVE_PDURO3 115.0 KV 528195 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | NORTH_LOVNG3__BLACKRIVER_3 | 3 Phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 115.0 KV 528182 TO BLACKRIVER 3 115.0 KV 528193 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | NORTH_LOVNG3__HOPI_SUB___3 | 3 Phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 115.0 KV 528182 TO HOPI_SUB 3 115.0 KV 528226 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | NORTH_LOVNG3__SOUTH_LOVNG3 | 3 Phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 115.0 KV 528182 TO SOUTH_LOVNG3 115.0 KV 528192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | N_LOVING___7__CHINA_DRAW_7 | 3 Phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 345.0 KV 528185 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | OASIS______6__ROOSEVELT__6 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 230.0 KV 524875 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | OKLEHV24__OKLEHV14 | 3 Phase fault on OKLEHV24 (590001) 138 kV Bus a. Apply fault at the OKLEHV24 (590001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKLEHV24 138.0 KV 590001 TO OKLEHV14 138.0 KV 590003 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | OXY_WSEM_TP3__JOHNSON_DRW3 | 3 Phase fault on OXY_WSEM_TP3 (527325) 115 kV Bus a. Apply fault at the OXY_WSEM_TP3 (527325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OXY_WSEM_TP3 115.0 KV 527325 TO JOHNSON_DRW3 115.0 KV 527362 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | O_K_U__7__G17_151TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | O_K_U__7__G18_015_TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | O_K_U__7__GEN_2017_033 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO GEN-2017-033 345.0 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | O_K_U__7__L_E_S__7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO L.E.S.-7 345.0 KV 511468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | O_K_U__7__OKLAUN_HVDC7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO OKLAUN HVDC7 345.0 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | PCA________3__CARLSBAD___3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO CARLSBAD 3 115.0 KV 528160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | PCA________3__CV_LUSK_TP_3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO CV-LUSK_TP 3 115.0 KV 527948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | PCA________3__POTASH_JCT_3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO POTASH_JCT 3 115.0 KV 527962 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | PCA________3__XTO_BIGEDDY3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO XTO_BIGEDDY3 115.0 KV 528396 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | PHANTOM____3__SOUTH_LOVNG3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO MALAGABEND 3 115.0 KV 528194 CKT 1 b.2. LOAD 1 528194 b.3. SOUTH_LOVNG3 115.0 KV 528192 TO MALAGABEND 3 115.0 KV 528194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | PHANTOM____3__WOLFCAMP_TP3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO BOPCO_PKRLK3 115.0 KV 528020 CKT 1 b.2. LOAD 1 528020 b.3. BOPCO_PKRLK3 115.0 KV 528020 TO WOLFCAMP_TP3 115.0 KV 528235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | PHANTOM____3__WOOD_DRAW__3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO WOOD_DRAW 3 115.0 KV 528228 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | PHANTOM____7__CHINA_DRAW_7 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 345.0 KV 528015 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | PHANTOM____7__RDRUNNER___7 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 345.0 KV 528015 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | PLAINS_INT_3__YOAKUM_____3 | 3 Phase fault on PLAINS_INT 3 (526928) 115 kV Bus a. Apply fault at the PLAINS_INT 3 (526928) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINS_INT 3 115.0 KV 526928 TO YOAKUM 3 115.0 KV 526934 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | PLANT_X____6__G17_146_TAP | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO G17-146-TAP 230.0 KV 760498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | PLANT_X____6__SUNDOWN____6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO SUNDOWN 6 230.0 KV 526435 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | LANOGSU1 trips on voltage protection settings. GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues. Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | PLANT_X____6__TOLK_______6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | PLSNT_HILL_6__ROOSEVELT__6 | 3 Phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 230.0 KV 524770 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | POTASH_JCT_2__DUVAL__1___2 | 3 Phase fault on POTASH_JCT 2 (527961) 69 kV Bus a. Apply fault at the POTASH_JCT 2 (527961) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 2 69.0 KV 527961 TO DUVAL_#1 2 69.0 KV 527980 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | POTASH_JCT_2__KERMAC_____2 | 3 Phase fault on POTASH_JCT 2 (527961) 69 kV Bus a. Apply fault at the POTASH_JCT 2 (527961) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 2 69.0 KV 527961 TO KERMAC 2 69.0 KV 527996 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | POTASH_JCT_2__MISSCHEM_2_2 | 3 Phase fault on POTASH_JCT 2 (527961) 69 kV Bus a. Apply fault at the POTASH_JCT 2 (527961) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 2 69.0 KV 527961 TO MISSCHEM#2 2 69.0 KV 528022 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | POTASH_JCT_2__NATPOT_TP__2 | 3 Phase fault on POTASH_JCT 2 (527961) 69 kV Bus a. Apply fault at the POTASH_JCT 2 (527961) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 2 69.0 KV 527961 TO NATPOT_TP 2 69.0 KV 528145 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | POTASH_JCT_3__CARLSBAD___3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO CARLSBAD 3 115.0 KV 528160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | POTASH_JCT_3__INTREPDW_TP3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO INTREPDW_TP3 115.0 KV 527999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | POTASH_JCT_3__KIOWA______3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO KIOWA 3 115.0 KV 527966 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | POTASH_JCT_6__PECOS______6 | 3 Phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6 230.0 KV 527963 TO PECOS 6 230.0 KV 528179 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | POTTER_CO__6__NEWHART____6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | PRENTICE___3__YOAKUM_____3 | 3 Phase fault on PRENTICE 3 (526792) 115 kV Bus a. Apply fault at the PRENTICE 3 (526792) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRENTICE 3 115.0 KV 526792 TO YOAKUM 3 115.0 KV 526934 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | QUAHADA____3__DCP_ZIA_TP_3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO DCP_ZIA TP 3 115.0 KV 528422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | QUAHADA____3__LEA_NATIONL3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO LEA_NATIONL3 115.0 KV 528399 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | QUAHADA____3__PCA________3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO XTO_BIGEDDY3 115.0 KV 528396 CKT 1 b.2. LOAD 1 528396 b.3. PCA 3 115.0 KV 527930 TO XTO_BIGEDDY3 115.0 KV 528396 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | RANDALL____6__AMA_SOUTH__6 | 3 Phase fault on RANDALL 6 (524365) 230 kV Bus a. Apply fault at the RANDALL 6 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 230.0 KV 524365 TO AMA_SOUTH 6 230.0 KV 524415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | RDRUNNER___3__AGAVE_RHIL23 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHIL23 115.0 KV 528231 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | RDRUNNER___3__BATTLE_AXE_3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO BATTLE_AXE 3 115.0 KV 528040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | RDRUNNER___3__CUSTERMTN__3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO CUSTERMTN 3 115.0 KV 528239 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | RDRUNNER___3__GEN_2016_121 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO GEN-2016-121 115.0 KV 587990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | RDRUNNER___3__GEN_2018_052 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO GEN-2018-052 115.0 KV 762866 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | RDRUNNER___3__OCHOA______3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHILL3 115.0 KV 528230 CKT 1 b.2. LOAD 1 528230 b.3. AGAVE_RHILL3 115.0 KV 528230 TO OCHOA 3 115.0 KV 528232 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | RED_BLUFF__3__RDRUNNER___3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 115.0 KV 528018 TO RDRUNNER 3 115.0 KV 528025 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | RED_BLUFF__3__WIPP_______3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAND_DUNES 3 115.0 KV 528016 TO RED_BLUFF 3 115.0 KV 528018 CKT 1 b.2. WIPP 3 115.0 KV 528009 TO SAND_DUNES 3 115.0 KV 528016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | RED_BLUFF__3__WOLFCAMP_TP3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 115.0 KV 528018 TO WOLFCAMP_TP3 115.0 KV 528235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | ROOSEVELT__6__TOLK_______6 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 230.0 KV 524909 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | RR_SVC_HV__3__RDRUNNER___3 | 3 Phase fault on RR_SVC_HV 3 (528024) 115 kV Bus a. Apply fault at the RR_SVC_HV 3 (528024) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RR_SVC_HV 3 115.0 KV 528024 TO RDRUNNER 3 115.0 KV 528025 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8. Reclosing was removed.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | RSVLT_CC_E_7__CROSSROADS_7 | 3 Phase fault on RSVLT_CC_E 7 (527655) 345 kV Bus a. Apply fault at the RSVLT_CC_E 7 (527655) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_E 7 345.0 KV 527655 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | RUSHSPR7__GEN_2018_055 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345.0 KV 511571 TO GEN-2018-055 345.0 KV 762900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | RUSSELL____3__HIGG_______3 | 3 Phase fault on RUSSELL 3 (527284) 115 kV Bus a. Apply fault at the RUSSELL 3 (527284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL 3 115.0 KV 527284 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | SAGA_SCOL__7__CROSSROADS_7 | 3 Phase fault on SAGA_SCOL 7 (527610) 345 kV Bus a. Apply fault at the SAGA_SCOL 7 (527610) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAGA_SCOL 7 345.0 KV 527610 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. Generator Islanded. | Increase acceleration factor to 0.8 or reduce to 0.2. Reclosing was removed.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | SANGER_SW__3__G18_004_TAP | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | SANGER_SW__3__SW_4J44____3 | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO SW_4J44 3 115.0 KV 528484 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | SANGER_SW__3__W_BENDER___3 | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO OXYPERMIAN 3 115.0 KV 528575 CKT 1 b.2. LOAD 1 528575 b.3. LOAD 2 528575 b.4. OXY_NHU_RCF3 115.0 KV 528574 TO OXYPERMIAN 3 115.0 KV 528575 CKT 1 b.5. LOAD 1 528575 b.6. LOAD 2 528575 b.7. W_BENDER 3 115.0 KV 528449 TO OXY_NHU_RCF3 115.0 KV 528574 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | SN_JUAN_TAP6__CHAVES_CNTY6 | 3 Phase fault on SN_JUAN_TAP6 (524885) 230 kV Bus a. Apply fault at the SN_JUAN_TAP6 (524885) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SN_JUAN_TAP6 230.0 KV 524885 TO CHAVES_CNTY6 230.0 KV 527483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | SP_ABERNTHY2__TUCO_INT2__2 | 3 Phase fault on SP-ABERNTHY2 (525731) 69 kV Bus a. Apply fault at the SP-ABERNTHY2 (525731) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ABERNTHY2 69.0 KV 525731 TO TUCO_INT2 2 69.0 KV 525816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | SUNDOWN____6__WOLFFORTH__6 | 3 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 230.0 KV 526435 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | SUNNYSD7__G17_075_TAP | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G17-075-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | SUNNYSD7__GEN_2017_167 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO GEN-2017-167 345.0 KV 761859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | SWISHER____6__NEWHART____6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | SWISHER____6__TUCO_INT___6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | SW_4J44____3__TAYLOR_____3 | 3 Phase fault on SW_4J44 3 (528484) 115 kV Bus a. Apply fault at the SW_4J44 3 (528484) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OXY_S_HOBBS3 115.0 KV 528480 TO SW_4J44 3 115.0 KV 528484 CKT 1 b.2. S_HOBBS 3 115.0 KV 528477 TO OXY_S_HOBBS3 115.0 KV 528480 CKT 1 b.3. LOAD 1 528480 b.4. LOAD 2 528480 b.5. LOAD 3 528480 b.6. E_SANGER 3 115.0 KV 528470 TO S_HOBBS 3 115.0 KV 528477 CKT 1 b.7. LOAD 1 528477 b.8. LOAD 2 528477 b.9. TAYLOR 3 115.0 KV 528413 TO E_SANGER 3 115.0 KV 528470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | SW_4J44____3__W_HOBBS____3 | 3 Phase fault on SW_4J44 3 (528484) 115 kV Bus a. Apply fault at the SW_4J44 3 (528484) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW_4J44 3 115.0 KV 528484 TO W_HOBBS 3 115.0 KV 528498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | S_JAL______3__DOLLARHIDE_3 | 3 Phase fault on S_JAL 3 (528547) 115 kV Bus a. Apply fault at the S_JAL 3 (528547) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S_JAL 3 115.0 KV 528547 TO DOLLARHIDE 3 115.0 KV 528561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TAYLOR_____3__MILLEN_TPE_3 | 3 Phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 3 115.0 KV 528413 TO NE_HOBBS 3 115.0 KV 528442 CKT 1 b.2. LOAD 1 528442 b.3. MILLEN_TPE 3 115.0 KV 528436 TO NE_HOBBS 3 115.0 KV 528442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TAYLOR_____3__W_BENDER___3 | 3 Phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 3 115.0 KV 528413 TO W_BENDER 3 115.0 KV 528449 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TEAGUE_____3__CARDINAL___3 | 3 Phase fault on TEAGUE 3 (528526) 115 kV Bus a. Apply fault at the TEAGUE 3 (528526) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEAGUE 3 115.0 KV 528526 TO CARDINAL 3 115.0 KV 528596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TEAGUE_____3__S_JAL______3 | 3 Phase fault on TEAGUE 3 (528526) 115 kV Bus a. Apply fault at the TEAGUE 3 (528526) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEAGUE 3 115.0 KV 528526 TO S_JAL 3 115.0 KV 528547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TERRYRD7__G17_171_TAP | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TERRYRD7__RSHSPR1_MPT1 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RSHSPR1_MPT1 345.0 KV 511979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8 or reduce to 0.2.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TERRYRD7__RUSHSPR7 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TERRYRD7__SUNNYSD7 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TOLK_______6__GEN_2017_158 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO GEN-2017-158 230.0 KV 762132 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8 or reduce to 0.2.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TOLK_______6__LAMB_CNTY__6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO LAMB_CNTY 6 230.0 KV 525637 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | LANOGSU1 trips on voltage protection settings. GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues. Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TOLK_______6__NEEDMORE___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO NEEDMORE 6 230.0 KV 525586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | LANOGSU1 trips on voltage protection settings. GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues. Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TOLK_______6__TUCO_INT___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | No | Yes | Yes | LANOGSU1 trips on voltage protection settings. GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues. Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TOLK_______7__CROSSROADS_7 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TUCO_INT___2__LH_WIL&ELN+2 | 3 Phase fault on TUCO_INT 2 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 2 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 69.0 KV 525826 TO LH-WIL&ELN+2 69.0 KV 525853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TUCO_INT___2__SP_NEWDEAL_2 | 3 Phase fault on TUCO_INT 2 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 2 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 69.0 KV 525826 TO SP-NEWDEAL 2 69.0 KV 525885 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TUCO_INT___3__CARLISLE___3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO STANTON_W 3 115.0 KV 526076 CKT 1 b.2. LOAD 1 526076 b.3. STANTON_W 3 115.0 KV 526076 TO INDIANA 3 115.0 KV 526146 CKT 1 b.4. LOAD 1 526146 b.5. LOAD 2 526146 b.6. SP-ERSKINE 3 115.0 KV 526109 TO INDIANA 3 115.0 KV 526146 CKT 1 b.7. LOAD 1 526146 b.8. LOAD 2 526146 b.9. SP-ERSKINE 3 115.0 KV 526109 TO CARLISLE 3 115.0 KV 526160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TUCO_INT___3__LUBBCK_EST_3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TUCO_INT___6__ANTELOPE_1_6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO ANTELOPE_1 6 230.0 KV 525840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TUCO_INT___6__CARLISLE___6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO CARLISLE 6 230.0 KV 526161 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TUCO_INT___6__HALE_WNDCL16 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO HALE_WNDCL16 230.0 KV 525957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TUCO_INT___6__JONES______6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TUCO_INT___7__ELK_CT1 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO ELK_CT1 345.0 KV 525850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TUCO_INT___7__G17_151TAP | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TUCO_INT___7__YOAKUM_345 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO YOAKUM_345 345.0 KV 526936 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TWEEDY_____3__EDDY_NTH___3 | 3 Phase fault on TWEEDY 3 (527597) 115 kV Bus a. Apply fault at the TWEEDY 3 (527597) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWEEDY 3 115.0 KV 527597 TO EDDY_NTH 3 115.0 KV 527798 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | WHITTEN____3__LEA_ROAD___3 | 3 Phase fault on WHITTEN 3 (528540) 115 kV Bus a. Apply fault at the WHITTEN 3 (528540) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 3 115.0 KV 528519 TO WHITTEN 3 115.0 KV 528540 CKT 1 b.2. LOAD 1 528540 b.3. LEA_ROAD 3 115.0 KV 528505 TO WARD 3 115.0 KV 528519 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | WHITTEN____3__S_JAL______3 | 3 Phase fault on WHITTEN 3 (528540) 115 kV Bus a. Apply fault at the WHITTEN 3 (528540) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITTEN 3 115.0 KV 528540 TO S_JAL 3 115.0 KV 528547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | WOLFCAMP_TP3__WOLFCAMP___3 | 3 Phase fault on WOLFCAMP_TP3 (528235) 115 kV Bus a. Apply fault at the WOLFCAMP_TP3 (528235) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCAMP_TP3 115.0 KV 528235 TO WOLFCAMP 3 115.0 KV 528236 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | WWRDEHV7__BECKHAM7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | WWRDEHV7__DGRASSE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | WWRDEHV7__G07621119_20 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G07621119-20 345.0 KV 515599 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | WWRDEHV7__G16_003_TAP | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G16-003-TAP 345.0 KV 560071 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | WWRDEHV7__GUTHRIE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GUTHRIE7 345.0 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | WWRDEHV7__TATONGA7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | W_BENDER___3__N_HOBBS____3 | 3 Phase fault on W_BENDER 3 (528449) 115 kV Bus a. Apply fault at the W_BENDER 3 (528449) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_BENDER 3 115.0 KV 528449 TO N_HOBBS 3 115.0 KV 528456 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | W_HOBBS____3__DRINKARD_TP3 | 3 Phase fault on W_HOBBS 3 (528498) 115 kV Bus a. Apply fault at the W_HOBBS 3 (528498) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_HOBBS 3 115.0 KV 528498 TO DRINKARD_TP3 115.0 KV 528533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | XTO_DI9_TP_3__XTO_DI9____3 | 3 Phase fault on XTO_DI9_TP 3 (528064) 115 kV Bus a. Apply fault at the XTO_DI9_TP 3 (528064) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XTO_DI9_TP 3 115.0 KV 528064 TO XTO_DI9 3 115.0 KV 528066 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | XTO_MAHONEY6__GEN_2017_239 | 3 Phase fault on XTO_MAHONEY6 (527011) 230 kV Bus a. Apply fault at the XTO_MAHONEY6 (527011) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XTO_MAHONEY6 230.0 KV 527011 TO GEN-2017-239 230.0 KV 761355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | YOAKUM_345__HOBBS_INT__7 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | YOAKUM_____3__ARCO_TP____3 | 3 Phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 115.0 KV 526934 TO ARCO_TP 3 115.0 KV 527041 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | YOAKUM_____3__LG_PLSHILL_3 | 3 Phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 115.0 KV 526934 TO LG-PLSHILL 3 115.0 KV 527194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | YOAKUM_____6__BRU_SUB____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | YOAKUM_____6__INK_BASIN__6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO INK_BASIN 6 230.0 KV 527028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | YOAKUM_____6__MUSTANG____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO MUSTANG 6 230.0 KV 527149 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | YOAKUM_____6__SUNDOWN____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 b.2. SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | 7_RIVERS___6__528094_0 | 3 Phase fault on 7-RIVERS 6 (528095) 230 kV Bus a. Apply fault at the 7-RIVERS 6( 528095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 7-RIVERS 6 528095 TO 7-RIVERS 3 528094 TO 7-RIVER_TR11 528090 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | AMA_SOUTH__6__524414_0 | 4 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6( 524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 524415 TO AMA_SOUTH 3 524414 TO AMA_SO_TR1 1 524410 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CARLISLE___3__526159_0 | 5 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3( 526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 526160 TO CARLISLE 2 526159 TO CRLSLE_TR2 1 526158 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CARLISLE___6__526160_0 | 6 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6( 526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 526161 TO CARLISLE 3 526160 TO CRLSLE_TR1 1 526157 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CARLSBAD___3__528159_0 | 7 Phase fault on CARLSBAD 3 (528160) 115 kV Bus a. Apply fault at the CARLSBAD 3( 528160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLSBAD 3 528160 TO CARLSBAD 2 528159 TO CRLSBAD_TR21 528158 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CHAVES_CNTY6__527482_0 | 8 Phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6( 527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY6 527483 TO CHAVES_CNTY3 527482 TO CHAVES_TR2 1 527479 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CHINA_DRAW_7__528222_0 | 9 Phase fault on CHINA_DRAW 7 (528223) 345 kV Bus a. Apply fault at the CHINA_DRAW 7( 528223) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHINA_DRAW 7 528223 TO CHINA_DRAW 3 528222 TO CHINA_DRAW 1 528219 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CHISHOLM6__511553_0 | 10 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6( 511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CUNNIGHM_S_6__527864_0 | 11 Phase fault on CUNNIGHM_S 6 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6( 527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 527867 TO CUNNINHAM 3 527864 TO CUNNHM_TR1 1 527863 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | DUNCAN_2__511453_0 | 12 Phase fault on DUNCAN-2 (511452) 69 kV Bus a. Apply fault at the DUNCAN-2( 511452) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-2 511452 TO DUNCAN-4 511453 TO DUNC2-1 511410 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | EDDY_CNTY__7__527799_0 | 13 Phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7( 527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 527802 TO EDDY_NORTH 6 527799 TO EDDY_TR 1 527796 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | EDDY_NORTH_6__527793_0 | 14 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6( 527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 527799 TO EDDY_STH 3 527793 TO EDDY_TR3 1 527795 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | EDDY_NORTH_6__527798_0 | 15 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6( 527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 527799 TO EDDY_NTH 3 527798 TO EDDY_TR2 1 527797 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | ELGINJT2__511486_0 | 16 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2( 511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | FLOYD_CNTY_3__525779_0 | 17 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3( 525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 525780 TO FLOYD_CNTY 2 525779 TO FLOYD_TR2 1 525778 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | GRACMNT4__515800_0 | 18 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4( 515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | GRASSLAND__6__526676_0 | 19 Phase fault on GRASSLAND 6 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6( 526677) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 6 526677 TO GRASSLAND 3 526676 TO GRASLND_TR11 526674 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | HALE_CNTY__3__525453_0 | 20 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3( 525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 525454 TO HALE_CNTY 2 525453 TO HALE_TR2 1 525452 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | HALE_WNDCL16__525931_0 | 21 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16( 525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL11 525931 TO HALE_WD_TR11 525930 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | HALE_WNDCL16__525981_0 | 22 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16( 525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL21 525981 TO HALE_WD_TR21 525980 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | HALE_WNDCL16__525990_0 | 23 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16( 525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL31 525990 TO HALE_WD_TR31 525989 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | HOBBS_INT__6__527891_0 | 24 Phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6( 527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 527894 TO HOBBS_INT 3 527891 TO HOBBS_TR1 1 527890 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | HOBBS_INT__7__527894_0 | 25 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7( 527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 527896 TO HOBBS_INT 6 527894 TO HOBBS_TR3 1 527895 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | INK_BASIN__6__527027_0 | 26 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6( 527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 527028 TO INK_BASIN 3 527027 TO INKBASN_TR 1 527026 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | KIOWA______7__527966_0 | 27 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7( 527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 527965 TO KIOWA 3 527966 TO KIOWA_TR1 1 527964 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LAMB_CNTY__6__525636_0 | 28 Phase fault on LAMB_CNTY 6 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6( 525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 6 525637 TO LAMB_CNTY 3 525636 TO LAMB_TR3 1 525633 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LE_WEST_SUB3__528337_0 | 29 Phase fault on LE-WEST_SUB3 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3( 528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3 528333 TO WC_SEC 1 528337 TO WC_TER 1 528336 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LUBBCK_EST_3__526297_0 | 30 Phase fault on LUBBCK_EST 3 (526298) 115 kV Bus a. Apply fault at the LUBBCK_EST 3( 526298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 3 526298 TO LUBBCK_EST 2 526297 TO LBB_EST TR31 526296 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LUBBCK_EST_6__526298_0 | 31 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6( 526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 526299 TO LUBBCK_EST 3 526298 TO LBB_EST TR11 526294 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LUBBCK_STH_6__526268_0 | 32 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6( 526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 526269 TO LUBBCK_STH 3 526268 TO LBB_STH TR11 526265 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | L_E_S__2__511467_0 | 33 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2( 511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | L_E_S__4__511468_0 | 34 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4( 511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | MUSTANG____6__527146_0 | 35 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6( 527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 527149 TO MUSTANG 3 527146 TO MUSTANG_TR11 527143 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | NEWHART____6__525460_0 | 36 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6( 525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 525461 TO NEWHART 3 525460 TO NEWHART_TR11 525459 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | N_LOVING___7__528182_0 | 37 Phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7( 528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 528185 TO NORTH_LOVNG3 528182 TO N_LOVING TR1 528186 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | OKLAUN_7__590003_0 | 38 Phase fault on OKLAUN 7 (599891) 345 kV Bus a. Apply fault at the OKLAUN 7( 599891) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OKLAUN 7 599891 TO OKLEHV14 590003 TO OK1TERT 590004 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | PCA________3__527929_0 | 39 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3( 527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 527930 TO PCA 2 527929 TO PCA_TR1 1 527928 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | PECOS______6__528178_0 | 40 Phase fault on PECOS 6 (528179) 230 kV Bus a. Apply fault at the PECOS 6( 528179) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECOS 6 528179 TO PECOS 3 528178 TO PECOS_TR1 1 528176 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | PHANTOM____7__528013_0 | 41 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7( 528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 528015 TO PHANTOM 3 528013 TO PHANTOM TR21 528012 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | PLANT_X____6__525480_0 | 42 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6( 525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 525481 TO PLANT_X 3 525480 TO PLANTX_TR1 1 525479 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | No | Yes | Yes | High voltage issue. | Operational steady state fixes (existing caps/taps/gen set points)
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | POTASH_JCT_3__527961_0 | 43 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3( 527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 527962 TO POTASH_JCT 2 527961 TO POTASH_TR3 1 527960 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | POTASH_JCT_6__527962_0 | 44 Phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6( 527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6 527963 TO POTASH_JCT 3 527962 TO POTASH_TR1 1 527958 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | RDRUNNER___7__528025_0 | 45 Phase fault on RDRUNNER 7 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7( 528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7 528027 TO RDRUNNER 3 528025 TO RDRNNER_TR11 528023 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | ROOSEVELT__6__524908_0 | 46 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6( 524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 524909 TO ROOSEVELT 3 524908 TO ROSEVLT_TR11 524907 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | RSHSPR1_COL1__511979_0 | 47 Phase fault on RSHSPR1_COL1 (511978) 34.5 kV Bus a. Apply fault at the RSHSPR1_COL1( 511978) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSHSPR1_COL1 511978 TO RSHSPR1_MPT1 511979 TO RSHSPR1_TER1 511583 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | RUSHSPR7__511965_0 | 48 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7( 511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 511571 TO RUSHSPRW1-1 511965 TO RUSHSPR1-1 511572 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | SUNDOWN____6__526434_0 | 49 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6( 526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 526435 TO SUNDOWN 3 526434 TO SUNDOWN_TR11 526432 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | SUNNYSD4__515136_0 | 50 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4( 515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | SUNNYSD7__515135_0 | 51 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7( 515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | SWISHER____6__525212_0 | 52 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6( 525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 525213 TO SWISHER 3 525212 TO SWISHER_TR11 525211 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TOLK_______7__525531_0 | 53 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7( 525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 525549 TO TOLK 6 525531 TO TOLK_TR 2 525538 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TUCO_INT___3__525816_0 | 54 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3( 525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT2 2 525816 TO TUCO_TR7 1 525814 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TUCO_INT___3__525826_0 | 55 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3( 525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT 2 525826 TO TUCO_TR6 1 525823 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TUCO_INT___6__525828_0 | 56 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6( 525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 525830 TO TUCO_INT 3 525828 TO TUCO_TR4 1 525821 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TUCO_INT___7__525830_0 | 57 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7( 525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 525832 TO TUCO_INT 6 525830 TO TUCO_TR2 1 525825 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | WOLFFORTH__6__526524_0 | 58 Phase fault on WOLFFORTH 6 (526525) 230 kV Bus a. Apply fault at the WOLFFORTH 6( 526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFFORTH 6 526525 TO WOLFFORTH 3 526524 TO WOLFRTH_TR11 526522 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | WWRDEHV4__515375_0 | 59 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4( 515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8 or reduce to 0.2.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | YOAKUM_345__526935_0 | 60 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345( 526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 526936 TO YOAKUM 6 526935 TO YOAKUM_TR1 526937 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | YOAKUM_____6__526934_0 | 61 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6( 526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 526935 TO YOAKUM 3 526934 TO YOAKUM_TR2 1 526932 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | 7_RIVERS___6__528094_0 | 3 Phase fault on 7-RIVERS 6 (528095) 230 kV Bus a. Apply fault at the 7-RIVERS 6( 528095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 7-RIVERS 6 528095 TO 7-RIVERS 3 528094 TO 7-RIVER_TR11 528090 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | AMA_SOUTH__6__524414_0 | 4 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6( 524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 524415 TO AMA_SOUTH 3 524414 TO AMA_SO_TR1 1 524410 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CARLISLE___3__526159_0 | 5 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3( 526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 526160 TO CARLISLE 2 526159 TO CRLSLE_TR2 1 526158 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CARLISLE___6__526160_0 | 6 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6( 526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 526161 TO CARLISLE 3 526160 TO CRLSLE_TR1 1 526157 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CARLSBAD___3__528159_0 | 7 Phase fault on CARLSBAD 3 (528160) 115 kV Bus a. Apply fault at the CARLSBAD 3( 528160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLSBAD 3 528160 TO CARLSBAD 2 528159 TO CRLSBAD_TR21 528158 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CHAVES_CNTY6__527482_0 | 8 Phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6( 527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY6 527483 TO CHAVES_CNTY3 527482 TO CHAVES_TR2 1 527479 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CHINA_DRAW_7__528222_0 | 9 Phase fault on CHINA_DRAW 7 (528223) 345 kV Bus a. Apply fault at the CHINA_DRAW 7( 528223) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHINA_DRAW 7 528223 TO CHINA_DRAW 3 528222 TO CHINA_DRAW 1 528219 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CHISHOLM6__511553_0 | 10 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6( 511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CUNNIGHM_S_6__527864_0 | 11 Phase fault on CUNNIGHM_S 6 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6( 527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 527867 TO CUNNINHAM 3 527864 TO CUNNHM_TR1 1 527863 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | DUNCAN_2__511453_0 | 12 Phase fault on DUNCAN-2 (511452) 69 kV Bus a. Apply fault at the DUNCAN-2( 511452) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-2 511452 TO DUNCAN-4 511453 TO DUNC2-1 511410 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | EDDY_CNTY__7__527799_0 | 13 Phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7( 527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 527802 TO EDDY_NORTH 6 527799 TO EDDY_TR 1 527796 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | EDDY_NORTH_6__527793_0 | 14 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6( 527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 527799 TO EDDY_STH 3 527793 TO EDDY_TR3 1 527795 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | EDDY_NORTH_6__527798_0 | 15 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6( 527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 527799 TO EDDY_NTH 3 527798 TO EDDY_TR2 1 527797 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | ELGINJT2__511486_0 | 16 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2( 511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | FLOYD_CNTY_3__525779_0 | 17 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3( 525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 525780 TO FLOYD_CNTY 2 525779 TO FLOYD_TR2 1 525778 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | GRACMNT4__515800_0 | 18 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4( 515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | GRASSLAND__6__526676_0 | 19 Phase fault on GRASSLAND 6 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6( 526677) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 6 526677 TO GRASSLAND 3 526676 TO GRASLND_TR11 526674 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | HALE_CNTY__3__525453_0 | 20 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3( 525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 525454 TO HALE_CNTY 2 525453 TO HALE_TR2 1 525452 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | HALE_WNDCL16__525931_0 | 21 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16( 525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL11 525931 TO HALE_WD_TR11 525930 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | HALE_WNDCL16__525981_0 | 22 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16( 525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL21 525981 TO HALE_WD_TR21 525980 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | HALE_WNDCL16__525990_0 | 23 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16( 525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL31 525990 TO HALE_WD_TR31 525989 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | HOBBS_INT__6__527891_0 | 24 Phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6( 527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 527894 TO HOBBS_INT 3 527891 TO HOBBS_TR1 1 527890 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | HOBBS_INT__7__527894_0 | 25 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7( 527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 527896 TO HOBBS_INT 6 527894 TO HOBBS_TR3 1 527895 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | INK_BASIN__6__527027_0 | 26 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6( 527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 527028 TO INK_BASIN 3 527027 TO INKBASN_TR 1 527026 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | KIOWA______7__527966_0 | 27 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7( 527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 527965 TO KIOWA 3 527966 TO KIOWA_TR1 1 527964 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LAMB_CNTY__6__525636_0 | 28 Phase fault on LAMB_CNTY 6 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6( 525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 6 525637 TO LAMB_CNTY 3 525636 TO LAMB_TR3 1 525633 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LE_WEST_SUB3__528337_0 | 29 Phase fault on LE-WEST_SUB3 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3( 528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3 528333 TO WC_SEC 1 528337 TO WC_TER 1 528336 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LUBBCK_EST_3__526297_0 | 30 Phase fault on LUBBCK_EST 3 (526298) 115 kV Bus a. Apply fault at the LUBBCK_EST 3( 526298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 3 526298 TO LUBBCK_EST 2 526297 TO LBB_EST TR31 526296 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LUBBCK_EST_6__526298_0 | 31 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6( 526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 526299 TO LUBBCK_EST 3 526298 TO LBB_EST TR11 526294 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LUBBCK_STH_6__526268_0 | 32 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6( 526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 526269 TO LUBBCK_STH 3 526268 TO LBB_STH TR11 526265 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | L_E_S__2__511467_0 | 33 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2( 511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | L_E_S__4__511468_0 | 34 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4( 511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | MUSTANG____6__527146_0 | 35 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6( 527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 527149 TO MUSTANG 3 527146 TO MUSTANG_TR11 527143 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | NEWHART____6__525460_0 | 36 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6( 525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 525461 TO NEWHART 3 525460 TO NEWHART_TR11 525459 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | N_LOVING___7__528182_0 | 37 Phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7( 528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 528185 TO NORTH_LOVNG3 528182 TO N_LOVING TR1 528186 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | OKLAUN_7__590003_0 | 38 Phase fault on OKLAUN 7 (599891) 345 kV Bus a. Apply fault at the OKLAUN 7( 599891) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OKLAUN 7 599891 TO OKLEHV14 590003 TO OK1TERT 590004 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | PCA________3__527929_0 | 39 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3( 527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 527930 TO PCA 2 527929 TO PCA_TR1 1 527928 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | PECOS______6__528178_0 | 40 Phase fault on PECOS 6 (528179) 230 kV Bus a. Apply fault at the PECOS 6( 528179) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECOS 6 528179 TO PECOS 3 528178 TO PECOS_TR1 1 528176 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | PHANTOM____7__528013_0 | 41 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7( 528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 528015 TO PHANTOM 3 528013 TO PHANTOM TR21 528012 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | PLANT_X____6__525480_0 | 42 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6( 525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 525481 TO PLANT_X 3 525480 TO PLANTX_TR1 1 525479 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | No | Yes | Yes | GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | POTASH_JCT_3__527961_0 | 43 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3( 527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 527962 TO POTASH_JCT 2 527961 TO POTASH_TR3 1 527960 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | POTASH_JCT_6__527962_0 | 44 Phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6( 527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6 527963 TO POTASH_JCT 3 527962 TO POTASH_TR1 1 527958 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | RDRUNNER___7__528025_0 | 45 Phase fault on RDRUNNER 7 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7( 528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7 528027 TO RDRUNNER 3 528025 TO RDRNNER_TR11 528023 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | ROOSEVELT__6__524908_0 | 46 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6( 524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 524909 TO ROOSEVELT 3 524908 TO ROSEVLT_TR11 524907 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | No | Yes | Yes | GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | RSHSPR1_COL1__511979_0 | 47 Phase fault on RSHSPR1_COL1 (511978) 34.5 kV Bus a. Apply fault at the RSHSPR1_COL1( 511978) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSHSPR1_COL1 511978 TO RSHSPR1_MPT1 511979 TO RSHSPR1_TER1 511583 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | RUSHSPR7__511965_0 | 48 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7( 511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 511571 TO RUSHSPRW1-1 511965 TO RUSHSPR1-1 511572 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | SUNDOWN____6__526434_0 | 49 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6( 526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 526435 TO SUNDOWN 3 526434 TO SUNDOWN_TR11 526432 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | SUNNYSD4__515136_0 | 50 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4( 515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | SUNNYSD7__515135_0 | 51 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7( 515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | SWISHER____6__525212_0 | 52 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6( 525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 525213 TO SWISHER 3 525212 TO SWISHER_TR11 525211 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TOLK_______7__525531_0 | 53 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7( 525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 525549 TO TOLK 6 525531 TO TOLK_TR 2 525538 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TUCO_INT___3__525816_0 | 54 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3( 525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT2 2 525816 TO TUCO_TR7 1 525814 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TUCO_INT___3__525826_0 | 55 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3( 525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT 2 525826 TO TUCO_TR6 1 525823 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TUCO_INT___6__525828_0 | 56 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6( 525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 525830 TO TUCO_INT 3 525828 TO TUCO_TR4 1 525821 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TUCO_INT___7__525830_0 | 57 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7( 525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 525832 TO TUCO_INT 6 525830 TO TUCO_TR2 1 525825 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | WOLFFORTH__6__526524_0 | 58 Phase fault on WOLFFORTH 6 (526525) 230 kV Bus a. Apply fault at the WOLFFORTH 6( 526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFFORTH 6 526525 TO WOLFFORTH 3 526524 TO WOLFRTH_TR11 526522 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | WWRDEHV4__515375_0 | 59 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4( 515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | YOAKUM_345__526935_0 | 60 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345( 526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 526936 TO YOAKUM 6 526935 TO YOAKUM_TR1 526937 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | YOAKUM_____6__526934_0 | 61 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6( 526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 526935 TO YOAKUM 3 526934 TO YOAKUM_TR2 1 526932 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_111_P4_2_CHINA_DRAW | Apply single-phase fault on LINE 528223 TO 528015 CKT 1, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and DISCONNECT 528219 and DISCONNECT 528219 and DISCONNECT 523823 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_113_P4_2_CHINA_DRAW | Apply single-phase fault on and DISCONNECT 528219, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528223 TO 528185 CKT 1 and LINE 528223 TO 528015 CKT 1 and DISCONNECT 528219 and DISCONNECT 523823 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_114_P4_2_EDDY_CNTY | Apply single-phase fault on LINE 527802 TO 527965 CKT 1, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and DISCONNECT 527796 and DISCONNECT 527796 and DISCONNECT 527802 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_115_P4_2_EDDY_CNTY | Apply single-phase fault on and DISCONNECT 527796, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and LINE 527802 TO 527965 CKT 1 and DISCONNECT 527796 and DISCONNECT 527802 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_120_P4_3_KIOWA | Apply single-phase fault on and DISCONNECT 527964, near KIOWA 7 for 5 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus . Clear Fault after 16 cycles and trip LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_122_P4_2_N_LOVING | Apply single-phase fault on LINE 528185 TO 528223 CKT 1, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528186 and DISCONNECT 528185 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_124_P4_2_N_LOVING | Apply single-phase fault on and DISCONNECT 528186, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 528223 CKT 1 and LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528185 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_126_P4_2_ROADRUNNER | Apply single-phase fault on LINE 528027 TO 528015 CKT 1, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528023 and DISCONNECT 528027 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_128_P4_2_ROADRUNNER | Apply single-phase fault on and DISCONNECT 528023, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 528015 CKT 1 and LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528027 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_129_P4_2_YOAKUM | Apply single-phase fault on LINE 526936 TO 525832 CKT 1, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764866 CKT 1 and DISCONNECT 526937 and DISCONNECT 526937 and DISCONNECT 526936 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_131_P4_2_YOAKUM | Apply single-phase fault on and DISCONNECT 526937, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764945 CKT 1 and LINE 526936 TO 527896 CKT 1 and DISCONNECT 526937 and DISCONNECT 526936 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_132_P4_3_TUCO | Apply single-phase fault on and DISCONNECT 525824, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 560022 TO 525832 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_133_P4_1_MUSTANG | Apply single-phase fault on and DISCONNECT 527162, near MUSTANG 3 for 5 cycles with stuck breaker at MUSTANG 3 (527146) 115 kV Bus . Clear Fault after 11 cycles and trip LINE 527202 TO 527146 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_135_P4_3_NICHOLS | Apply single-phase fault on and DISCONNECT 524041, near NICHOLS 6 for 5 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524023 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_137_P4_3_YOAKUM | Apply single-phase fault on and DISCONNECT 526931, near YOAKUM 6 for 5 cycles with stuck breaker at YOAKUM 6 (526935) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525586 TO 526935 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_141_P4_3_TUCO_INT | Apply single-phase fault on and DISCONNECT 525825, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 525832 TO 560022 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_142_P4_3_HITCHLAND | Apply single-phase fault on and DISCONNECT 523091, near HITCHLAND 7 for 5 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523091 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-100 and LANOGSU1 trip on voltage protection settings | Disabling voltage protection settings for GEN-2017-100 and LANOGSU1 prevents trips. There are no stability constraints when these generators trip offline or when the protection settings are disabled to prevent them from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_143_P4_3_WHEELER | Apply single-phase fault on WHEELER 523777 TO WHEELER 523776 TO WHEELER 523774 CKT 1 and DISCONNECT 523774, near WHEELER 6 for 5 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523777 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_148_P4_5_BUSHLAND | Apply single-phase fault on LINE 524267 TO 524290 CKT 1 and DISCONNECT 524263 and DISCONNECT 524285 and DISCONNECT 524287 and LINE 524267 TO 523959 CKT 1, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 16 cycles and trip LINE 524267 TO 524623 CKT 1 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_145_P4_4_BUSHLAND | Apply single-phase fault on and Drop Shunt at Bus 524267, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524267 and DISCONNECT 524285 and DISCONNECT 524287 and DISCONNECT 524263 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_146_P4_4_SWISHER | Apply single-phase fault on and Drop Shunt at Bus 525213, near SWISHER 6 for 5 cycles with stuck breaker at SWISHER 6 (525213) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525213 TO 525830 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_147_P4_4_TUCO_INT | Apply single-phase fault on and Drop Shunt at Bus 525830, near TUCO_INT 6 for 5 cycles with stuck breaker at TUCO_INT 6 (525830) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 525819 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_149_P4_1_HARRINGTON_G1 | Apply single-phase fault on LINE 523977 TO 524010 CKT 1 and LINE 523977 TO 524163 CKT 1 and LINE 523977 TO 524044 CKT 1 and DISCONNECT 523977 and DISCONNECT 523971, near HARRNG_WST 6 for 16 cycles with stuck breaker at HARRNG_WST 6 (523977) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_150_P4_1_HARRINGTON_G2 | Apply single-phase fault on LINE 523978 TO 524365 CKT 1 and LINE 523978 TO 524044 CKT 2 and DISCONNECT 523978 and DISCONNECT 523972, near HARRNG_MID 6 for 16 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_151_P4_1_HARRINGTON_G3 | Apply single-phase fault on LINE 523979 TO 523267 CKT 1 and LINE 523979 TO 523959 CKT 1 and DISCONNECT 523979 and DISCONNECT 523973, near HARRNG_EST 6 for 16 cycles with stuck breaker at HARRNG_EST 6 (523979) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_152_P4_1_JONES_G1 | Apply single-phase fault on and DISCONNECT 526331, near JONES 6 for 18 cycles with stuck breaker at JONES 6 (526337) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_153_P4_6_HARRINGTON_M | Apply single-phase fault on and DISCONNECT 523978 and trip GENERATOR 1 523972 and drop LOAD S1 523972 and DISCONNECT 523972, near HARRNG_MID 6 for 5 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_154_P4_6_MOORE_EAST | Apply single-phase fault on and DISCONNECT 523308 and trip GENERATOR 1 523297 and trip GENERATOR 3 523301 and drop LOAD F1 523297 and drop LOAD 1 523301 and drop LOAD A3 523301 and DISCONNECT 523294 and DISCONNECT 523295 and DISCONNECT 523296 and DISCONNECT 523297 and DISCONNECT 523301 and DISCONNECT 523302, near MOORE_E 3 for 5 cycles with stuck breaker at MOORE_E 3 (523308) 115 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_108_P4_2_CARPENTER | Apply single-phase fault on LINE 523823 TO 523853 CKT 1 and DISCONNECT 523823, near CARPENTER 7 for 21 cycles with stuck breaker at CARPENTER 7 (523823) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_109_P4_2_CROSSROADS | Apply single-phase fault on LINE 527802 TO 527656 CKT 1 and LINE 525549 TO 527656 CKT 1 and DISCONNECT 527655 and DISCONNECT 527653 and DISCONNECT 527651 and DISCONNECT 527652 and DISCONNECT 527654 and trip GENERATOR 1 527605 and trip GENERATOR 1 527607 and trip GENERATOR 1 527614 and trip GENERATOR 1 527615 and trip GENERATOR 1 527617 and trip GENERATOR 1 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629 and DISCONNECT 527656 and DISCONNECT 527658 and DISCONNECT 527659 and DISCONNECT 527660 and DISCONNECT 527661 and DISCONNECT 527662 and DISCONNECT 527663 and DISCONNECT 527666 and DISCONNECT 527667 and DISCONNECT 577120 and DISCONNECT 577121, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_110_P4_2_CROSSROADS | Apply single-phase fault on and LINE 527656 TO 525549 CKT 1 and LINE 527656 TO 527610 CKT 1 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_117_P4_2_FINNEY | Apply single-phase fault on LINE 531449 TO 523853 CKT 1 LINE 523823 TO 523853 CKT 1 and DISCONNECT 523853 and DISCONNECT 599950 and DISCONNECT 599951 and DISCONNECT 523118 and DISCONNECT 523114 and DISCONNECT 523115 and DISCONNECT 523116 and DISCONNECT 523117 and trip GENERATOR 1 523061 and trip GENERATOR 1 523062 and DISCONNECT 523061 and DISCONNECT 523062 and DISCONNECT 523063 and DISCONNECT 523064, near FINNEY 7 for 21 cycles with stuck breaker at FINNEY 7 (523853) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_118_P4_2_HITCHLAND | Apply single-phase fault on LINE 523097 TO 515554 CKT 2 and DISCONNECT 523112 and DISCONNECT 523111 and DISCONNECT 523109 and DISCONNECT 523107 and DISCONNECT 523110, near HITCHLAND 7 for 21 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_119_P4_2_HOBBS_INT | Apply single-phase fault on LINE 527896 TO 527965 CKT 1 and LINE 527896 TO 764866 CKT 1 and DISCONNECT 527895 and DISCONNECT 527896, near HOBBS_INT 7 for 21 cycles with stuck breaker at HOBBS_INT 7 (527896) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_125_P4_2_POTTERCO | Apply single-phase fault on LINE 523097 TO 523961 CKT 1 and DISCONNECT 523957 and DISCONNECT 523957 and DISCONNECT 523961 and DISCONNECT 524296 and DISCONNECT 524299 and DISCONNECT 524298 and DISCONNECT 524294 and DISCONNECT 524295 and DISCONNECT 524297, near POTTER_CO 7 for 21 cycles with stuck breaker at POTTER_CO 7 (523961) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_134_P4_2_NICHOLS | Apply single-phase fault on LINE 523978 TO 524044 CKT 2 and LINE 523551 TO 524044 CKT 1, near NICHOLS 6 for 21 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_136_P4_2_POTTERCO | Apply single-phase fault on LINE 524267 TO 523959 CKT 1 and LINE 524010 TO 523959 CKT 1, near POTTER_CO 6 for 21 cycles with stuck breaker at POTTER_CO 6 (523959) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_138_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 560022 CKT 1 and DISCONNECT 525824, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_139_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 560022 CKT 1 and DISCONNECT 525825, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_140_P4_2_WHEELER | Apply single-phase fault on LINE 523777 TO 511541 CKT &1 and DISCONNECT 523777 and DISCONNECT 523774, near WHEELER 6 for 21 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_121_P4_2_KIOWA | Apply single-phase fault on LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964, near KIOWA 7 for 20 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_111_P4_2_CHINA_DRAW | Apply single-phase fault on LINE 528223 TO 528015 CKT 1, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and DISCONNECT 528219 and DISCONNECT 528219 and DISCONNECT 523823 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_113_P4_2_CHINA_DRAW | Apply single-phase fault on and DISCONNECT 528219, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528223 TO 528185 CKT 1 and LINE 528223 TO 528015 CKT 1 and DISCONNECT 528219 and DISCONNECT 523823 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_114_P4_2_EDDY_CNTY | Apply single-phase fault on LINE 527802 TO 527965 CKT 1, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and DISCONNECT 527796 and DISCONNECT 527796 and DISCONNECT 527802 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_115_P4_2_EDDY_CNTY | Apply single-phase fault on and DISCONNECT 527796, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and LINE 527802 TO 527965 CKT 1 and DISCONNECT 527796 and DISCONNECT 527802 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_120_P4_3_KIOWA | Apply single-phase fault on and DISCONNECT 527964, near KIOWA 7 for 5 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus . Clear Fault after 16 cycles and trip LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_122_P4_2_N_LOVING | Apply single-phase fault on LINE 528185 TO 528223 CKT 1, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528186 and DISCONNECT 528185 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_124_P4_2_N_LOVING | Apply single-phase fault on and DISCONNECT 528186, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 528223 CKT 1 and LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528185 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_126_P4_2_ROADRUNNER | Apply single-phase fault on LINE 528027 TO 528015 CKT 1, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528023 and DISCONNECT 528027 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_128_P4_2_ROADRUNNER | Apply single-phase fault on and DISCONNECT 528023, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 528015 CKT 1 and LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528027 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_129_P4_2_YOAKUM | Apply single-phase fault on LINE 526936 TO 525832 CKT 1, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764866 CKT 1 and DISCONNECT 526937 and DISCONNECT 526937 and DISCONNECT 526936 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_131_P4_2_YOAKUM | Apply single-phase fault on and DISCONNECT 526937, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764945 CKT 1 and LINE 526936 TO 527896 CKT 1 and DISCONNECT 526937 and DISCONNECT 526936 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_132_P4_3_TUCO | Apply single-phase fault on and DISCONNECT 525824, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 560022 TO 525832 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_133_P4_1_MUSTANG | Apply single-phase fault on and DISCONNECT 527162, near MUSTANG 3 for 5 cycles with stuck breaker at MUSTANG 3 (527146) 115 kV Bus . Clear Fault after 11 cycles and trip LINE 527202 TO 527146 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_135_P4_3_NICHOLS | Apply single-phase fault on and DISCONNECT 524041, near NICHOLS 6 for 5 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524023 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_137_P4_3_YOAKUM | Apply single-phase fault on and DISCONNECT 526931, near YOAKUM 6 for 5 cycles with stuck breaker at YOAKUM 6 (526935) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525586 TO 526935 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_141_P4_3_TUCO_INT | Apply single-phase fault on and DISCONNECT 525825, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 525832 TO 560022 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_142_P4_3_HITCHLAND | Apply single-phase fault on and DISCONNECT 523091, near HITCHLAND 7 for 5 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523091 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-100 trips on voltage protection settings | Disabling voltage protection settings for GEN-2017-100 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_143_P4_3_WHEELER | Apply single-phase fault on WHEELER 523777 TO WHEELER 523776 TO WHEELER 523774 CKT 1 and DISCONNECT 523774, near WHEELER 6 for 5 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523777 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_148_P4_5_BUSHLAND | Apply single-phase fault on LINE 524267 TO 524290 CKT 1 and DISCONNECT 524263 and DISCONNECT 524285 and DISCONNECT 524287 and LINE 524267 TO 523959 CKT 1, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 16 cycles and trip LINE 524267 TO 524623 CKT 1 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_145_P4_4_BUSHLAND | Apply single-phase fault on and Drop Shunt at Bus 524267, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524267 and DISCONNECT 524285 and DISCONNECT 524287 and DISCONNECT 524263 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_146_P4_4_SWISHER | Apply single-phase fault on and Drop Shunt at Bus 525213, near SWISHER 6 for 5 cycles with stuck breaker at SWISHER 6 (525213) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525213 TO 525830 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_147_P4_4_TUCO_INT | Apply single-phase fault on and Drop Shunt at Bus 525830, near TUCO_INT 6 for 5 cycles with stuck breaker at TUCO_INT 6 (525830) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 525819 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_149_P4_1_HARRINGTON_G1 | Apply single-phase fault on LINE 523977 TO 524010 CKT 1 and LINE 523977 TO 524163 CKT 1 and LINE 523977 TO 524044 CKT 1 and DISCONNECT 523977 and DISCONNECT 523971, near HARRNG_WST 6 for 16 cycles with stuck breaker at HARRNG_WST 6 (523977) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_150_P4_1_HARRINGTON_G2 | Apply single-phase fault on LINE 523978 TO 524365 CKT 1 and LINE 523978 TO 524044 CKT 2 and DISCONNECT 523978 and DISCONNECT 523972, near HARRNG_MID 6 for 16 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_151_P4_1_HARRINGTON_G3 | Apply single-phase fault on LINE 523979 TO 523267 CKT 1 and LINE 523979 TO 523959 CKT 1 and DISCONNECT 523979 and DISCONNECT 523973, near HARRNG_EST 6 for 16 cycles with stuck breaker at HARRNG_EST 6 (523979) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_152_P4_1_JONES_G1 | Apply single-phase fault on and DISCONNECT 526331, near JONES 6 for 18 cycles with stuck breaker at JONES 6 (526337) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_153_P4_6_HARRINGTON_M | Apply single-phase fault on and DISCONNECT 523978 and trip GENERATOR 1 523972 and drop LOAD S1 523972 and DISCONNECT 523972, near HARRNG_MID 6 for 5 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_154_P4_6_MOORE_EAST | Apply single-phase fault on and DISCONNECT 523308 and trip GENERATOR 1 523297 and trip GENERATOR 3 523301 and drop LOAD F1 523297 and drop LOAD 1 523301 and drop LOAD A3 523301 and DISCONNECT 523294 and DISCONNECT 523295 and DISCONNECT 523296 and DISCONNECT 523297 and DISCONNECT 523301 and DISCONNECT 523302, near MOORE_E 3 for 5 cycles with stuck breaker at MOORE_E 3 (523308) 115 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_108_P4_2_CARPENTER | Apply single-phase fault on LINE 523823 TO 523853 CKT 1 and DISCONNECT 523823, near CARPENTER 7 for 21 cycles with stuck breaker at CARPENTER 7 (523823) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_109_P4_2_CROSSROADS | Apply single-phase fault on LINE 527802 TO 527656 CKT 1 and LINE 525549 TO 527656 CKT 1 and DISCONNECT 527655 and DISCONNECT 527653 and DISCONNECT 527651 and DISCONNECT 527652 and DISCONNECT 527654 and trip GENERATOR 1 527605 and trip GENERATOR 1 527607 and trip GENERATOR 1 527614 and trip GENERATOR 1 527615 and trip GENERATOR 1 527617 and trip GENERATOR 1 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629 and DISCONNECT 527656 and DISCONNECT 527658 and DISCONNECT 527659 and DISCONNECT 527660 and DISCONNECT 527661 and DISCONNECT 527662 and DISCONNECT 527663 and DISCONNECT 527666 and DISCONNECT 527667 and DISCONNECT 577120 and DISCONNECT 577121, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_110_P4_2_CROSSROADS | Apply single-phase fault on and LINE 527656 TO 525549 CKT 1 and LINE 527656 TO 527610 CKT 1 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_117_P4_2_FINNEY | Apply single-phase fault on LINE 531449 TO 523853 CKT 1 LINE 523823 TO 523853 CKT 1 and DISCONNECT 523853 and DISCONNECT 599950 and DISCONNECT 599951 and DISCONNECT 523118 and DISCONNECT 523114 and DISCONNECT 523115 and DISCONNECT 523116 and DISCONNECT 523117 and trip GENERATOR 1 523061 and trip GENERATOR 1 523062 and DISCONNECT 523061 and DISCONNECT 523062 and DISCONNECT 523063 and DISCONNECT 523064, near FINNEY 7 for 21 cycles with stuck breaker at FINNEY 7 (523853) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_118_P4_2_HITCHLAND | Apply single-phase fault on LINE 523097 TO 515554 CKT 2 and DISCONNECT 523112 and DISCONNECT 523111 and DISCONNECT 523109 and DISCONNECT 523107 and DISCONNECT 523110, near HITCHLAND 7 for 21 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_119_P4_2_HOBBS_INT | Apply single-phase fault on LINE 527896 TO 527965 CKT 1 and LINE 527896 TO 764866 CKT 1 and DISCONNECT 527895 and DISCONNECT 527896, near HOBBS_INT 7 for 21 cycles with stuck breaker at HOBBS_INT 7 (527896) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_125_P4_2_POTTERCO | Apply single-phase fault on LINE 523097 TO 523961 CKT 1 and DISCONNECT 523957 and DISCONNECT 523957 and DISCONNECT 523961 and DISCONNECT 524296 and DISCONNECT 524299 and DISCONNECT 524298 and DISCONNECT 524294 and DISCONNECT 524295 and DISCONNECT 524297, near POTTER_CO 7 for 21 cycles with stuck breaker at POTTER_CO 7 (523961) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_134_P4_2_NICHOLS | Apply single-phase fault on LINE 523978 TO 524044 CKT 2 and LINE 523551 TO 524044 CKT 1, near NICHOLS 6 for 21 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_136_P4_2_POTTERCO | Apply single-phase fault on LINE 524267 TO 523959 CKT 1 and LINE 524010 TO 523959 CKT 1, near POTTER_CO 6 for 21 cycles with stuck breaker at POTTER_CO 6 (523959) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_138_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 560022 CKT 1 and DISCONNECT 525824, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_139_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 560022 CKT 1 and DISCONNECT 525825, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_140_P4_2_WHEELER | Apply single-phase fault on LINE 523777 TO 511541 CKT &1 and DISCONNECT 523777 and DISCONNECT 523774, near WHEELER 6 for 21 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_121_P4_2_KIOWA | Apply single-phase fault on LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964, near KIOWA 7 for 20 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | BORDER7_345kV_515458 | a. Apply single-phase fault on: a.1. BORDER7 345KV 515458 TO TUCO_INT7 345KV 525832 CKT 1, b.with stuck breaker near BORDER 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1.BORDER7 345KV 515458 TO BECKHAM7 345KV 516059 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CUNNIGHM_N_6_115kV_527865 | a. Apply single-phase fault on: a.1. CUNNIGHMN6 115KV 527865 TO POTASHJCT6 115KV 527963 CKT 1, b.with stuck breaker near CUNNIGHM_N 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.CUNNIGHMN6 115KV 527865 TO CUNNIGHMS6 115KV 527867 CKT *1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CUNNIGHM_S_6_115kV_527867 | a. Apply single-phase fault on: a.1. CUNNIGHMN6 115KV 527867 TO HOBBSINT6 115KV 527894 CKT 1, b.with stuck breaker near CUNNIGHM_S 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.CUNNIGHMN6 115KV 527865 TO CUNNIGHMS6 115KV 527867 CKT *1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | Cunningham_115kV_527864 | a. Apply single-phase fault on: a.1. Cunningham 115KV 527864 TO Monument TP 115KV 528568 CKT 1, b.with stuck breaker near CUNNINHAM 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.Cunningham 115KV 527864 TO Quahada 115KV 528394 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | CUSTERMTN_115kV_528239 | a. Apply single-phase fault on: a.1. CUSTERMTN 115KV 528239 TO WHITTEN 115KV 528540 CKT 1, b.with stuck breaker near CUSTERMTN 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.CUSTERMTN 115KV 528239 TO RDRUNNER 115KV 528025 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | ENRON_TP3_115kV_528317 | a. Apply single-phase fault on: a.1. Maddox 115KV 528355 TO PEARLE3 115KV 528392 CKT 1 a.2. ENRONTP3 115KV 528317 TO PEARLE3 115KV 528392 CKT 1, b.with stuck breaker near ENRON_TP 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.ENRONTP3 115KV 528317 TO LEANATIONL3 115KV 528399 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | KIOWA_345kV_527965 | a. Apply single-phase fault on: a.1. KIOWA 345KV 527965 TO HOBBSINT 345KV 527896 CKT 1, b.with stuck breaker near KIOWA 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1.KIOWA 345KV 527965 TO NLOVING 345KV 528185 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LEA_NATIONL3_115kV_528399 | a. Apply single-phase fault on: a.1. LEANATIONL3 115KV 528399 TO ENRONTP3 115KV 528317 CKT 1, b.with stuck breaker near LEA_NATIONL3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.QUAHADA3 115KV 528394 TO LEANATIONL3 115KV 528399 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LES_345kV_511468 | a. Apply single-phase fault on: a.1. LES7 345KV 511468 TO G17171TAP 345.0 KV 760938 CKT 1, b.with stuck breaker near L.E.S.-7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1.OKU7 345KV 511456 TO LES7 345KV 511468 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | Maddox_115kV_528355 | a. Apply single-phase fault on: a.1. Maddox 115KV 528355 TO PEARLE3 115KV 528392 CKT 1 a.2. ENRONTP3 115KV 528317 TO PEARLE3 115KV 528392 CKT 1, b.with stuck breaker near MADDOX 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.Maddox 115KV 528355 TO Monument 115KV 528491 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | MONUMENT_115kV_528491 | a. Apply single-phase fault on: a.1. WHOBBS3 115KV 528498 TO MONUMENT3 115KV 528491 CKT 1, b.with stuck breaker near MONUMENT 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.MONUMENT3 115KV 528491 TO MADDOX3 115KV 528355 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | OKU7_345kV_511456 | a. Apply single-phase fault on: a.1. OKU7 345KV 511456 TO LES7 345.0 KV 511468 CKT 1, b.with stuck breaker near O.K.U.-7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1.OKU7 345KV 511456 TO G18015TAP 345KV 762467 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | PHANTOM_345kV_528015 | a. Apply single-phase fault on: a.1. PHANTOM 345KV 528015 TO CHINADRAW 345KV 528223 CKT 1, b.with stuck breaker near RDRUNNER 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1.RDRUNNER 345KV 528027 TO PHANTOM 345KV 528015 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | Rdrunner_115kV_528025 | a. Apply single-phase fault on: a.1. RDRUNNER 115KV 528025 TO AGAVERHILL 115KV 528230 CKT 1, b.with stuck breaker near RDRUNNER 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.RDRUNNER 115KV 528025 TO REDBLUFF 115KV 528018 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | RDRUNNER_345kV_528027 | a. Apply single-phase fault on: a.1. RDRUNNER 345KV 528027 TO KIOWA 345KV 527965 CKT 1, b.with stuck breaker near RDRUNNER 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1.RDRUNNER 345KV 528027 TO PHANTOM 345KV 528015 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | REDBLUFF_115kV_528018 | a. Apply single-phase fault on: a.1. REDBLUFF 115KV 528018 TO WOLFCAMPTP3 115KV 528235 CKT 1, b.with stuck breaker near RED_BLUFF 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.RDRUNNER 115KV 528025 TO REDBLUFF 115KV 528018 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | SANGERSW3_115kV_528463 | a. Apply single-phase fault on: a.1. WBENDER 115KV 528449 TO OXYNHURCF3 115KV 528574 CKT 1 a.2. OXYPERMIAN3 115KV 528575 TO OXYNHURCF3 115KV 528574 CKT 1 a.3. OXYPERMIAN3 115KV 528575 TO SANGERSW3 115KV 528463 CKT 1, b.with stuck breaker near SANGER_SW 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.SANGERSW3 115KV 528463 TO G18004TAP 115KV 762442 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TUCOINT6_230kV_525830 | a. Apply single-phase fault on: a.1. TUCOINT6 230.0 KV 525830 TO SWISHER6 230.0 KV 525213 CKT 1, b.with stuck breaker near TUCO_INT 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.TUCOINT6 230.0 KV 525830 TO CARLISLE6 230.0 KV 526161 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | TUCOINT7_345kV_525832 | a. Apply single-phase fault on: a.1. BORDER7 345KV 515458 TO TUCOINT7 345KV 525832 CKT 1, b.with stuck breaker near TUCO_INT 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1.TUCOINT7 345KV 525832 TO YOAKUM_345 345KV 526936 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | WBENDER_115kV_528449 | a. Apply single-phase fault on: a.1. WBENDER 115KV 528449 TO OXYNHURCF3 115KV 528574 CKT 1 a.2. OXYPERMIAN3 115KV 528575 TO OXYNHURCF3 115KV 528574 CKT 1 a.3. OXYPERMIAN3 115KV 528575 TO SANGERSW3 115KV 528463 CKT 1, b.with stuck breaker near W_BENDER 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.WBENDER 115KV 528449 TO NHOBBS3 115KV 528456 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | W_HOBBS_115kV_528498 | a. Apply single-phase fault on: a.1. WHOBBS3 115KV 528498 TO MONUMENT3 115KV 528491 CKT 1, b.with stuck breaker near W_HOBBS 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.WHOBBS3 115KV 528498 TO DRINKARDTP3 115KV 528533 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | BORDER7_345kV_515458 | a. Apply single-phase fault on: a.1. BORDER7 345KV 515458 TO TUCO_INT7 345KV 525832 CKT 1, b.with stuck breaker near BORDER 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1.BORDER7 345KV 515458 TO BECKHAM7 345KV 516059 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CUNNIGHM_N_6_115kV_527865 | a. Apply single-phase fault on: a.1. CUNNIGHMN6 115KV 527865 TO POTASHJCT6 115KV 527963 CKT 1, b.with stuck breaker near CUNNIGHM_N 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.CUNNIGHMN6 115KV 527865 TO CUNNIGHMS6 115KV 527867 CKT *1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CUNNIGHM_S_6_115kV_527867 | a. Apply single-phase fault on: a.1. CUNNIGHMN6 115KV 527867 TO HOBBSINT6 115KV 527894 CKT 1, b.with stuck breaker near CUNNIGHM_S 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.CUNNIGHMN6 115KV 527865 TO CUNNIGHMS6 115KV 527867 CKT *1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | Cunningham_115kV_527864 | a. Apply single-phase fault on: a.1. Cunningham 115KV 527864 TO Monument TP 115KV 528568 CKT 1, b.with stuck breaker near CUNNINHAM 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.Cunningham 115KV 527864 TO Quahada 115KV 528394 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | CUSTERMTN_115kV_528239 | a. Apply single-phase fault on: a.1. CUSTERMTN 115KV 528239 TO WHITTEN 115KV 528540 CKT 1, b.with stuck breaker near CUSTERMTN 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.CUSTERMTN 115KV 528239 TO RDRUNNER 115KV 528025 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | ENRON_TP3_115kV_528317 | a. Apply single-phase fault on: a.1. Maddox 115KV 528355 TO PEARLE3 115KV 528392 CKT 1 a.2. ENRONTP3 115KV 528317 TO PEARLE3 115KV 528392 CKT 1, b.with stuck breaker near ENRON_TP 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.ENRONTP3 115KV 528317 TO LEANATIONL3 115KV 528399 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | KIOWA_345kV_527965 | a. Apply single-phase fault on: a.1. KIOWA 345KV 527965 TO HOBBSINT 345KV 527896 CKT 1, b.with stuck breaker near KIOWA 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1.KIOWA 345KV 527965 TO NLOVING 345KV 528185 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LEA_NATIONL3_115kV_528399 | a. Apply single-phase fault on: a.1. LEANATIONL3 115KV 528399 TO ENRONTP3 115KV 528317 CKT 1, b.with stuck breaker near LEA_NATIONL3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.QUAHADA3 115KV 528394 TO LEANATIONL3 115KV 528399 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LES_345kV_511468 | a. Apply single-phase fault on: a.1. LES7 345KV 511468 TO G17171TAP 345.0 KV 760938 CKT 1, b.with stuck breaker near L.E.S.-7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1.OKU7 345KV 511456 TO LES7 345KV 511468 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | Maddox_115kV_528355 | a. Apply single-phase fault on: a.1. Maddox 115KV 528355 TO PEARLE3 115KV 528392 CKT 1 a.2. ENRONTP3 115KV 528317 TO PEARLE3 115KV 528392 CKT 1, b.with stuck breaker near MADDOX 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.Maddox 115KV 528355 TO Monument 115KV 528491 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | MONUMENT_115kV_528491 | a. Apply single-phase fault on: a.1. WHOBBS3 115KV 528498 TO MONUMENT3 115KV 528491 CKT 1, b.with stuck breaker near MONUMENT 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.MONUMENT3 115KV 528491 TO MADDOX3 115KV 528355 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | OKU7_345kV_511456 | a. Apply single-phase fault on: a.1. OKU7 345KV 511456 TO LES7 345.0 KV 511468 CKT 1, b.with stuck breaker near O.K.U.-7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1.OKU7 345KV 511456 TO G18015TAP 345KV 762467 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | PHANTOM_345kV_528015 | a. Apply single-phase fault on: a.1. PHANTOM 345KV 528015 TO CHINADRAW 345KV 528223 CKT 1, b.with stuck breaker near RDRUNNER 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1.RDRUNNER 345KV 528027 TO PHANTOM 345KV 528015 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | Rdrunner_115kV_528025 | a. Apply single-phase fault on: a.1. RDRUNNER 115KV 528025 TO AGAVERHILL 115KV 528230 CKT 1, b.with stuck breaker near RDRUNNER 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.RDRUNNER 115KV 528025 TO REDBLUFF 115KV 528018 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | RDRUNNER_345kV_528027 | a. Apply single-phase fault on: a.1. RDRUNNER 345KV 528027 TO KIOWA 345KV 527965 CKT 1, b.with stuck breaker near RDRUNNER 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1.RDRUNNER 345KV 528027 TO PHANTOM 345KV 528015 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | REDBLUFF_115kV_528018 | a. Apply single-phase fault on: a.1. REDBLUFF 115KV 528018 TO WOLFCAMPTP3 115KV 528235 CKT 1, b.with stuck breaker near RED_BLUFF 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.RDRUNNER 115KV 528025 TO REDBLUFF 115KV 528018 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | SANGERSW3_115kV_528463 | a. Apply single-phase fault on: a.1. WBENDER 115KV 528449 TO OXYNHURCF3 115KV 528574 CKT 1 a.2. OXYPERMIAN3 115KV 528575 TO OXYNHURCF3 115KV 528574 CKT 1 a.3. OXYPERMIAN3 115KV 528575 TO SANGERSW3 115KV 528463 CKT 1, b.with stuck breaker near SANGER_SW 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.SANGERSW3 115KV 528463 TO G18004TAP 115KV 762442 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TUCOINT6_230kV_525830 | a. Apply single-phase fault on: a.1. TUCOINT6 230.0 KV 525830 TO SWISHER6 230.0 KV 525213 CKT 1, b.with stuck breaker near TUCO_INT 6 230 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.TUCOINT6 230.0 KV 525830 TO CARLISLE6 230.0 KV 526161 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | TUCOINT7_345kV_525832 | a. Apply single-phase fault on: a.1. BORDER7 345KV 515458 TO TUCOINT7 345KV 525832 CKT 1, b.with stuck breaker near TUCO_INT 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1.TUCOINT7 345KV 525832 TO YOAKUM_345 345KV 526936 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | WBENDER_115kV_528449 | a. Apply single-phase fault on: a.1. WBENDER 115KV 528449 TO OXYNHURCF3 115KV 528574 CKT 1 a.2. OXYPERMIAN3 115KV 528575 TO OXYNHURCF3 115KV 528574 CKT 1 a.3. OXYPERMIAN3 115KV 528575 TO SANGERSW3 115KV 528463 CKT 1, b.with stuck breaker near W_BENDER 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.WBENDER 115KV 528449 TO NHOBBS3 115KV 528456 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | W_HOBBS_115kV_528498 | a. Apply single-phase fault on: a.1. WHOBBS3 115KV 528498 TO MONUMENT3 115KV 528491 CKT 1, b.with stuck breaker near W_HOBBS 3 115 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1.WHOBBS3 115KV 528498 TO DRINKARDTP3 115KV 528533 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_89_P2_2_PLANT_X6 | Apply single-phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 5 cycles and trip the faulted elements: b.1. DISCONNECT 525481 b.2.GENERATOR 1 525494 b.3. LOAD S1 525494 b.4. DISCONNECT 525479 b.5. DISCONNECT 525494 | P2_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_90_P2_2_GRASSLAND6 | Apply single-phase fault on GRASSLAND 6 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6 (526677) 230 kV Bus b. Clear fault after 5 cycles and trip the faulted elements: b.1. DISCONNECT 526677 b.2. GENERATOR 1 526678 b.3. LOAD A1 599125 b.4. DISCONNECT 526674 b.5. DISCONNECT 526678 b.6. DISCONNECT 526679 b.7. DISCONNECT 599125 b.8. DISCONNECT 599126 | P2_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_91_P2_2_CUNNIGHM_N6 | Apply single-phase fault on CUNNIGHM_N 6 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6 (527865) 230 kV Bus b. Clear fault after 5 cycles and trip the faulted elements: b.1. DISCONNECT 527865 b.2. GENERATOR 1 527883 b.3. LOAD S1 527883 b.4. DISCONNECT 527883 | P2_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_89_P2_2_PLANT_X6 | Apply single-phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 5 cycles and trip the faulted elements: b.1. DISCONNECT 525481 b.2.GENERATOR 1 525494 b.3. LOAD S1 525494 b.4. DISCONNECT 525479 b.5. DISCONNECT 525494 | P2_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_90_P2_2_GRASSLAND6 | Apply single-phase fault on GRASSLAND 6 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6 (526677) 230 kV Bus b. Clear fault after 5 cycles and trip the faulted elements: b.1. DISCONNECT 526677 b.2. GENERATOR 1 526678 b.3. LOAD A1 599125 b.4. DISCONNECT 526674 b.5. DISCONNECT 526678 b.6. DISCONNECT 526679 b.7. DISCONNECT 599125 b.8. DISCONNECT 599126 | P2_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_91_P2_2_CUNNIGHM_N6 | Apply single-phase fault on CUNNIGHM_N 6 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6 (527865) 230 kV Bus b. Clear fault after 5 cycles and trip the faulted elements: b.1. DISCONNECT 527865 b.2. GENERATOR 1 527883 b.3. LOAD S1 527883 b.4. DISCONNECT 527883 | P2_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_163_P5_5_CUNNINGHAM | Single phase fault with stuck relay near CUNNIGHM_N 6 (527865) 230 kV bus a. Apply fault at the CUNNIGHM_N 6 (527865) 230 kV bus b. Run fault for 19.32 cycles and trip the faulted elements b.1. LINE 527867 TO 527894 CKT 1 c. Run fault for 6.06 cycles and trip the faulted elements c.1. LINE 527865 TO 527963 CKT 1 d. Run fault for 17.1 cycles and trip the faulted elements d.1. GENERATOR 1 527883 d.2. DISCONNECT 527883 d.3. LINE 527865 TO 527883 CKT 1 e. Run fault for 13.2 cycles and trip the faulted elements e.1. LINE 527865 TO 527799 CKT 1 f. Run fault for 2.22 cycles and trip the faulted elements f.1. GENERATOR 1 527882 f.2. DISCONNECT 527882 f.3. LINE 527867 TO 527882 CKT 1 g. Run fault for 66.12 cycles and trip the faulted elements g.1. DISCONNECT 527863 g.2. DISCONNECT 527865 g.3. DISCONNECT 527867 h. Clear fault at CUNNIGHM_N 6 (527865) 230 kV bus | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_164_P5_5_BUSHLAND | Single phase fault with stuck relay near BUSHLAND 6 (524267) 230 kV bus a. Apply fault at the BUSHLAND 6 (524267) 230 kV bus b. Run fault for 5 cycles and trip the faulted elements b.1. DISCONNECT 524263 b.2. LINE 524267 TO 524623 CKT 1 b.3. LINE 524267 TO 524290 CKT 1 b.4 GENERATOR 1 524285 b.5. GENERATOR 1 524287 c. Run fault for 32 cycles and trip the faulted elements c.1. LINE 524267 TO 523959 CKT 1 d. Clear fault at the BUSHLAND 6 (524267) 230 kV bus and trip the faulted elements d.1. LOAD A1 524285 d.2. DISCONNECT 524267 d.3. DISCONNECT 524275 d.4. DISCONNECT 524276 d.5. DISCONNECT 524285 d.6. DISCONNECT 524287 d.7. DISCONNECT 524289 d.8. DISCONNECT 524290 | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_165_P5_5_BUSHLAND | Single phase fault with stuck relay near BUSHLAND 6 (524267) 230 kV bus a. Apply fault at the BUSHLAND 6 (524267) 230 kV bus b. Run fault for 5 cycles and trip the faulted elements b.1. DISCONNECT 524263 b.2. LINE 524267 TO 523959 CKT 1 b.3. LINE 524267 TO 524290 CKT 1 b.4. GENERATOR 1 524285 b.5. GENERATOR 1 524287 c. Run fault for 32 cycles and trip the faulted elements c.1. LINE 524267 TO 524623 CKT 1 d. Clear fault at the BUSHLAND 6 (524267) 230 kV bus and trip the faulted elements d.1. LOAD A1 524285 d.2. DISCONNECT 524267 d.3. DISCONNECT 524275 d.4. DISCONNECT 524276 d.5. DISCONNECT 524285 d.6. DISCONNECT 524287 d.7. DISCONNECT 524289 d.8. DISCONNECT 524290 | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_166_P5_5_GRASSLAND | Single phase fault with stuck relay near GRASSLAND 6 (526677) 230 kV bus a. Apply fault at the GRASSLAND 6 (526677) 230 kV bus b. Run fault for 34.38 cycles and trip the faulted elements b.1. LINE 526677 TO 526337 CKT 1 c. Run fault for 54.9 cycles and trip the faulted elements c.1. LINE 526676 TO 526656 CKT 1 d. Clear fault at the GRASSLAND 6 (526677) 230 kV bus and trip the faulted elements d.1. GENERATOR 1 526678 d.2. LOAD 1 526513 d.3. LOAD 1 526569 d.4. LOAD 1 526576 d.5. LOAD 1 526583 d.6. LOAD 1 526592 d.7. LOAD 1 526622 d.8. LOAD 2 526622 d.9. LOAD 3 526622 d.10. LOAD 1 526814 d.11. LOAD A1 599125 d.12 DISCONNECT 526513 d.13. DISCONNECT 526569 d.14. DISCONNECT 526576 d.15. DISCONNECT 526583 d.16. DISCONNECT 526592 d.17. DISCONNECT 526622 d.18.DISCONNECT 526674 d.19. DISCONNECT 526676 d.20. DISCONNECT 526677 d.21. DISCONNECT 526678 d.22. DISCONNECT 526679 d.23. DISCONNECT 526691 d.24. DISCONNECT 526692 d.25. DISCONNECT 526693 d.26. DISCONNECT 526694 d.27. DISCONNECT 526799 d.28. DISCONNECT 526814 d.29. DISCONNECT 526821 d.30. DISCONNECT 599125 d.31. DISCONNECT 599126 | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_167_P5_3_LAMB | Single phase fault with stuck relay near LAMB_CNTY 3 (525636) 115 kV bus a. Apply fault at the LAMB_CNTY 3 (525636) 115 kV bus b. Run fault for 39 cycles and trip the faulted elements b.1. LINE 525636 TO 526020 CKT 1 c. Run fault for 15.48 cycles and trip the faulted elements c.1. LINE 525480 TO 525636 CKT 1 d. Run fault for 46.32 cycles and trip the faulted elements d.1. LINE 525637 TO 525531 CKT 1 d. Clear fault at the LAMB_CNTY 3 (525636) 115 kV bus and trip the faulted elements d.1. LOAD 1 525592 d.2. LOAD 1 525599 d.3. LOAD 2 525599 d.4. LOAD 1 525606 d.5. LOAD 1 525613 d.6. LOAD 1 525620 d.7. LOAD 2 525620 d.8. LOAD 1 525650 d.9. LOAD 1 525664 d.10. LOAD 2 525664 d.11. LOAD 1 525671 d.12. LOAD 1 525678 d.13. LOAD 1 525687 d.14. LOAD 1 525694 d.15. LOAD 1 525701 d.16. LOAD 2 525701 d.17. LOAD 1 525703 d.18. LOAD 1 525708 d.19. LOAD 1 525717 d.20. DISCONNECT 525592 d.21. DISCONNECT 525599 d.22. DISCONNECT 525606 d.23. DISCONNECT 525613 d.24. DISCONNECT 525620 d.25. DISCONNECT 525631 d.26. DISCONNECT 525632 d.27. DISCONNECT 525633 d.28. DISCONNECT 525635 d.29. DISCONNECT 525636 d.30. DISCONNECT 525637 d.31. DISCONNECT 525650 d.32. DISCONNECT 525657 d.32. DISCONNECT 525664 d.33. DISCONNECT 525671 d.34. DISCONNECT 525678 d.35. DISCONNECT 525687 d.36. DISCONNECT 525694 d.37. DISCONNECT 525697 d.38. DISCONNECT 525701 d.39. DISCONNECT 525703 d.40. DISCONNECT 525708 d.41. DISCONNECT 525717 | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_168_P5_5_LAMB | Single phase fault with stuck relay near LAMB_CNTY 3 (525636) 115 kV bus a. Apply fault at the LAMB_CNTY 3 (525636) 115 kV bus b. Run fault for 39 cycles and trip the faulted elements b.1. LINE 525636 TO 526020 CKT 1 c. Run fault for 14.88 cycles and trip the faulted elements c.1. DISCONNECT 525633 d. Run fault for 0.6 cycles and trip the faulted elements d.1. LINE 525636 TO 525480 CKT 1 e. Clear fault at the LAMB_CNTY 3 (525636) 115 kV bus and trip the faulted elements e.1. LOAD 1 525592 e.2. LOAD 1 525599 e.3. LOAD 2 525599 e.4. LOAD 1 525606 e.5. LOAD 1 525613 e.6. LOAD 1 525620 e.7. LOAD 2 525620 e.8. LOAD 1 525650 e.9. LOAD 1 525664 e.10. LOAD 2 525664 e.11. LOAD 1 525671 e.12. LOAD 1 525678 e.13. LOAD 1 525687 e.14. LOAD 1 525694 e.15. LOAD 1 525701 e.16. LOAD 2 525701 e.17. LOAD 1 525703 e.18. LOAD 1 525708 e.19. LOAD 1 525717 e.20. DISCONNECT 525592 e.21. DISCONNECT 525599 e.22. DISCONNECT 525606 e.23. DISCONNECT 525613 e.24. DISCONNECT 525620 e.25. DISCONNECT 525631 e.26. DISCONNECT 525632 e.27. DISCONNECT 525635 e.28. DISCONNECT 525636 e.29. DISCONNECT 525650 e.30. DISCONNECT 525657 e.31. DISCONNECT 525664 e.32. DISCONNECT 525671 e.33. DISCONNECT 525678 e.34. DISCONNECT 525687 e.35. DISCONNECT 525694 e.36. DISCONNECT 525697 e.37. DISCONNECT 525701 e.38. DISCONNECT 525703 e.39. DISCONNECT 525708 e.40. DISCONNECT 525717 | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_169_P5_2_LUBBOCK_STH | Single phase fault with stuck relay near LUBBCK_STH 6 (526269) 230 kV bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV bus b. Run fault for 4.38 cycles and trip the faulted elements b.1. LINE 526269 TO 526525 CKT 1 c. Run fault for 40.2 cycles and trip the faulted elements c.1. LINE 526268 TO 526213 CKT 1 d. Run fault for 130.44 cycles and trip the faulted elements d.1. LINE 526268 TO 526298 CKT 1 e. Run fault for 60.3 cycles and trip the faulted elements e.1. LINE 526269 TO 526337 CKT 1 e.2. LINE 526269 TO 526337 CKT 2 f. Run fault for 63.6 cycles and trip the faulted elements f.1. DISCONNECT 526264 g. Run fault for 0.78 cycles and trip the faulted elements g.1. LINE 526602 TO 526656 CKT 1 h. Clear fault at the LUBBCK_STH 6 (526269) 230 kV bus and trip the faulted elements h.1. LOAD 1 526205 h.2. LOAD 1 526228 h.3. LOAD 1 526249 h.4. LOAD 1 526602 h.5. DISCONNECT 526205 h.6. DISCONNECT 526228 h.7. DISCONNECT 526249 h.8. DISCONNECT 526256 h.9. DISCONNECT 526265 h.10. DISCONNECT 526266 h.11. DISCONNECT 526267 h.12. DISCONNECT 526268 h.13. DISCONNECT 526269 h.14. DISCONNECT 526602 | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_170_P5_2_MOORE | Single phase fault with stuck relay near RB-S&S 3 (523315) 115 kV bus a. Apply fault at the RB-S&S 3 (523315) 115 kV bus b. Run fault for 4.02 cycles and trip the faulted elements b.1. LINE 523315 TO 523318 CKT 1 c. Run fault for 8.28 cycles and trip the faulted elements c.1. LINE 523216 TO 523246 CKT 1 d. Run fault for 48.9 cycles and trip the faulted elements d.1. DISCONNECT 523302 e. Run fault for 10.62 cycles and trip the faulted elements e.1. LINE 523235 TO 523228 CKT 1 f. Run fault for 3.18 cycles and trip the faulted elements f.1. LINE 523176 TO 523175 CKT 1 g. Run fault for 35.1 cycles and trip the faulted elements g.1. LINE 523352 TO 523377 CKT 1 h. Clear fault at the RB-S&S 3 (523315) 115 kV bus and trip the faulted elements h.1. GENERATOR 1 523252 h.2. GENERATOR 1 523254 h.3. GENERATOR 1 523277 h.4. GENERATOR 1 523297 h.5. GENERATOR 3 523301 h.6. LOAD 1 523176 h.7. LOAD 1 523177 h.8. LOAD 1 523216 h.9. LOAD 1 523217 h.10. LOAD 1 523237 h.11. LOAD 1 523240 h.12. LOAD F1 523252 h.13. LOAD F1 523254 h.14. LOAD 1 523255 h.15. LOAD 2 523255 h.16. LOAD D1 523255 h.17. LOAD D2 523255 h.18. LOAD 1 523277 h.19. LOAD A1 523277 h.20. LOAD F1 523297 h.21. LOAD 1 523301 h.22. LOAD A3 523301 h.23. LOAD 1 523315 h.24. LOAD 1 523359 h.25. LOAD D1 523359 h.26. LOAD 1 523366 h.27. DISCONNECT 523176 h.28. DISCONNECT 523177 h.29. DISCONNECT 523216 h.30. DISCONNECT 523217 h.31. DISCONNECT 523235 h.32. DISCONNECT 523237 h.33. DISCONNECT 523240 h.34. DISCONNECT 523251 h.35. DISCONNECT 523252 h.36. DISCONNECT 523253 h.37. DISCONNECT 523254 h.38. DISCONNECT 523255 h.39. DISCONNECT 523256 h.40. DISCONNECT 523277 h.41. DISCONNECT 523294 h.42. DISCONNECT 523295 h.43. DISCONNECT 523296 h.44. DISCONNECT 523297 h.45. DISCONNECT 523301 h.46. DISCONNECT 523304 h.47. DISCONNECT 523308 h.47. DISCONNECT 523315 h.48. DISCONNECT 523352 h.49. DISCONNECT 523359 h.50. DISCONNECT 523366 | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_171_P5_5_OASIS | Single phase fault with stuck relay near OASIS 3 (524874) 115 kV bus a. Apply fault at the OASIS 3 (524874) 115 kV bus b. Run fault for 19.2 cycles and trip the faulted elements b.1. LINE 524874 TO 524924 CKT 1 c. Run fault for 0.18 cycles and trip the faulted elements c.1. LINE 524764 TO 524822 CKT 1 d. Run fault for 10.8 cycles and trip the faulted elements d.1. LINE 524784 TO 524808 CKT 1 e. Run fault for 14.04 cycles and trip the faulted elements e.1. LINE 524875 TO 524909 CKT 1 f. Run fault for 49.08 cycles and trip the faulted elements f.1. DISCONNECT 524872 g. Clear fault at the OASIS 3 (524874) 115 kV bus and trip the faulted elements g.1. LOAD 1 524784 g.2. LOAD 1 524794 g.3. LOAD 1 524797 g.4. LOAD 1 524801 g.5. LOAD 1 524863 g.6. DISCONNECT 524764 g.7. DISCONNECT 524784 g.8. DISCONNECT 524790 g.9. DISCONNECT 524794 g.10. DISCONNECT 524797 g.11. DISCONNECT 524801 g.12. DISCONNECT 524863 | P5_Member | Yes | Yes | Yes | Yes | No | Yes | Yes | GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_172_P5_5_POTASH | Single phase fault with stuck relay near POTASH_JCT 3 (527962) 115 kV bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV bus b. Run fault for 19.02 cycles and trip the faulted elements b.1. LINE 527962 TO 527930 CKT 1 c. Run fault for 0.18 cycles and trip the faulted elements c.1. LINE 528064 TO 527953 CKT 1 d. Run fault for 15.3 cycles and trip the faulted elements d.1. LINE 527962 TO 528160 CKT 1 e. Run fault for 4.08 cycles and trip the faulted elements e.1. DISCONNECT 527958 f. Run fault for 14.94 cycles and trip the faulted elements f.1. LINE 528145 TO 527929 CKT 1 g. Clear fault at POTASH_JCT 3 (527962) 115 kV bus | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_173_P5_5_7_RIVERS | Single phase fault with stuck relay near 7-RIVERS 3 (528094) 115 kV bus a. Apply fault at the 7-RIVERS 3 (528094) 115 kV bus b. Run fault for 19.38 cycles and trip the faulted elements b.1. LINE 528094 TO 527711 CKT 1 b.2. LINE 528070 TO 528178 CKT 1 b.3. LINE 527786 TO 528116 CKT 1 c. Run fault for 20.4 cycles and trip the faulted elements c.1. LINE 528095 TO 528179 CKT 1 d. Run fault for 136.92 cycles and trip the faulted elements d.1. LINE 528095 TO 527799 CKT 1 e. Clear fault at the 7-RIVERS 3 (528094) 115 kV bus and trip the faulted elements e.1. LOAD 1 528003 e.2. LOAD 1 528076 e.3. LOAD 1 528079 e.4. LOAD 1 528109 e.5. LOAD 1 528116 e.6. DISCONNECT 528003 e.7. DISCONNECT 528070 e.7. DISCONNECT 528076 e.8. DISCONNECT 528079 e.9. DISCONNECT 528090 e.10. DISCONNECT 528091 e.11. DISCONNECT 528093 e.12. DISCONNECT 528094 e.13. DISCONNECT 528095 e.14. DISCONNECT 528109 e.15. DISCONNECT 528116 | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_174_P5_5_YOAKUM | Single phase fault with stuck relay near YOAKUM 3 (526934) 115 kV bus a. Apply fault at the YOAKUM 3 (526934) 115 kV bus b. Run fault for 19.5 cycles and trip the faulted elements b.1. LINE 526934 TO 527194 CKT 1 c. Run fault for 1.5 cycles and trip the faulted elements c.1. LINE 526934 TO 526928 CKT 1 d. Run fault for 8.4 cycles and trip the faulted elements d.1. LINE 526792 TO 526736 CKT 1 e. Run fault for 24.6 cycles and trip the faulted elements e.1. DISCONNECT 527122 e.2. LINE 527130 TO 527136 CKT @1 f. Run fault for 3.72 cycles and trip the faulted elements f.1. GENERATOR 1 527162 f.2. DISCONNECT 527162 g. Run fault for 0.18 cycles and trip the faulted elements g.1. LINE 527051 TO 527062 CKT 1 h. Run fault for 0.12 cycles and trip the faulted elements h.1. GENERATOR 1 527161 h.2. DISCONNECT 527161 h.3. GENERATOR 1 527163 i. Run fault for 0.96 cycles and trip the faulted elements i.1. DISCONNECT 526932 i.2. DISCONNECT 526931 j. Clear fault at the YOAKUM 3 (526934) 115 kV bus and trip the faulted elements j.1. LOAD 1 526792 j.2. LOAD D1 526792 j.3. LOAD 1 527018 j.4. LOAD 1 527047 j.5. LOAD 1 527056 j.6. DISCONNECT 526792 j.7. DISCONNECT 526934 j.8. DISCONNECT 527018 j.9. DISCONNECT 527041 j.10. DISCONNECT 527047 j.11. DISCONNECT 527051 j.12.DISCONNECT 527056 | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_175_P5_5_CARLISLE | Single phase fault with stuck relay near CARLISLE 3 (526160) 115 kV bus a. Apply fault at the CARLISLE 3 (526160) 115 kV bus b. Run fault for 19.38 cycles and trip the faulted elements b.1. LINE 526109 TO 526146 CKT 1 c. Run fault for 14.64 cycles and trip the faulted elements c.1. LINE 526475 TO 526481 CKT 1 d. Run fault for 13.08 cycles and trip the faulted elements d.1. DISCONNECT 526157 e. Run fault for 12.78 cycles and trip the faulted elements e.1. LINE 526160 TO 526192 CKT 1 f. Clear fault at the CARLISLE 3 (526160) 115 kV bus and trip the faulted elements f.1. LOAD 1 526109 f.2. LOAD 1 526160 f.3. LOAD D2 526160 f.4. LOAD 1 526176 f.5. LOAD 1 526221 f.6. LOAD 1 526483 f.7. DISCONNECT 526109 f.8. DISCONNECT 526130 f.9. DISCONNECT 526158 f.10. DISCONNECT 526159 f.11. DISCONNECT 526160 f.12. DISCONNECT 526162 f.13. DISCONNECT 526176 f.14. DISCONNECT 526184 f.15. DISCONNECT 526221 f.16. DISCONNECT 526481 f.17. DISCONNECT 526483 | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_176_P5_2_ALLEN | Single phase fault with stuck relay near ALLEN 3 (526213) 115 kV bus a. Apply fault at the ALLEN 3 (526213) 115 kV bus b. Run fault for 3.42 cycles and trip the faulted elements b.1. LINE 526243 TO 526199 CKT 1 c. Run fault for 53.4 cycles and trip the faulted elements c.1. LINE 526213 TO 526268 CKT 1 d. Clear fault at the ALLEN 3 (526213) 115 kV bus and trip the faulted elements d.1. LOAD 1 526213 d.2. LOAD 2 526213 d.3. LOAD 1 526236 d.4. LOAD 1 526243 d.5. DISCONNECT 526213 d.6. DISCONNECT 526236 d.7. DISCONNECT 526243 | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_177_P5_2_ALLEN | Single phase fault with stuck relay near ALLEN 3 (526213) 115 kV bus a. Apply fault at the ALLEN 3 (526213) 115 kV bus b. Run fault for 5.52 cycles and trip the faulted elements b.1. LINE 526213 TO 526268 CKT 1 c. Run fault for 55.68 cycles and trip the faulted elements c.1. LINE 526243 TO 526199 CKT 1 d. Clear fault at the ALLEN 3 (526213) 115 kV bus and trip the faulted elements d.1. LOAD 1 526213 d.2. LOAD 2 526213 d.3. LOAD 1 526236 d.4. LOAD 1 526243 d.5. DISCONNECT 526213 d.6. DISCONNECT 526236 d.7. DISCONNECT 526243 | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_178_P5_2_ALLEN | Single phase fault with stuck relay near ALLEN 3 (526213) 115 kV bus a. Apply fault at the ALLEN 3 (526213) 115 kV bus b. Run fault for 48.3 cycles and trip the faulted elements b.1. LINE 526213 TO 526268 CKT 1 c. Run fault for 6.72 cycles and trip the faulted elements c.1. LINE 526243 TO 526199 CKT 1 d. Clear fault at the ALLEN 3 (526213) 115 kV bus and trip the faulted elements d.1. LOAD 1 526213 d.2. LOAD 2 526213 d.3. LOAD 1 526236 d.4. LOAD 1 526243 d.5. DISCONNECT 526213 d.6. DISCONNECT 526236 d.7. DISCONNECT 526243 | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_179_P5_2_HARRNG_EST | Single phase fault with stuck relay near HARRNG_EST 6 (523979) 230 kV bus a. Apply fault at the HARRNG_EST 6 (523979) 230 kV bus b. Run fault for 20 cycles and trip the faulted elements b.1. DISCONNECT 523979 b.2. GENERATOR 1 523973 b.3. DISCONNECT 523973 c. Clear fault at HARRNG_EST 6 (523979) 230 kV bus | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_180_P5_2_WOLFFORTH | Single phase fault with stuck relay near WOLFFORTH 3 (526524) 115 kV bus a. Apply fault at the WOLFFORTH 3 (526524) 115 kV bus b. Run fault for 10 cycles and trip the faulted elements b.1. LINE 526162 TO 526160 CKT 1 b.2. DISCONNECT 526522 c. Run fault for 22 cycles and trip the faulted elements c.1. LINE 526524 TO 526736 CKT 1 d. Clear fault at the WOLFFORTH 3 (526524) 115 kV bus and trip the faulted elements d.1. LOAD 1 526176 d.2. LOAD 1 526475 d.3. LOAD 1 526483 d.4. DISCONNECT 526162 d.5. DISCONNECT 526176 d.6. DISCONNECT 526475 d.7. DISCONNECT 526481 d.8. DISCONNECT 526483 d.9. DISCONNECT 526524 | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25S | Transfer | LT__SPS_All_181_P5_3_LAMB | Single phase fault with stuck relay near LAMB_CNTY 3 (525636) 115 kV bus a. Apply fault at the LAMB_CNTY 3 (525636) 115 kV bus b. Run fault for 39 cycles and trip the faulted elements b.1. LINE 525636 TO 526020 CKT 1 c. Run fault for 15.48 cycles and trip the faulted elements c.1. LINE 525636 TO 525480 CKT 1 d. Run fault for 46.32 cycles and trip the faulted elements d.1. LINE 525637 TO 525531 CKT 1 e. Clear fault at the LAMB_CNTY 3 (525636) 115 kV bus and trip the faulted elements e.1. LOAD 1 525592 e.2. LOAD 1 525599 e.3. LOAD 2 525599 e.4. LOAD 1 525606 e.5. LOAD 1 525613 e.6. LOAD 1 525620 e.7. LOAD 2 525620 e.8. LOAD 1 525650 e.9. LOAD 1 525664 e.10. LOAD 2 525664 e.11. LOAD 1 525671 e.12. LOAD 1 525678 e.13. LOAD 1 525687 e.14. LOAD 1 525694 e.15. LOAD 1 525701 e.16. LOAD 2 525701 e.17. LOAD 1 525703 e.18. LOAD 1 525708 e.19. LOAD 1 525717 e.20. DISCONNECT 525592 e.21. DISCONNECT 525599 e.22. DISCONNECT 525606 e.23. DISCONNECT 525613 e.24. DISCONNECT 525620 e.25. DISCONNECT 525631 e.26. DISCONNECT 525632 e.27. DISCONNECT 525633 e.28. DISCONNECT 525635 e.29. DISCONNECT 525636 e.30. DISCONNECT 525637 e.31. DISCONNECT 525650 e.32. DISCONNECT 525657 e.33. DISCONNECT 525664 e.34. DISCONNECT 525671 e.35. DISCONNECT 525678 e.36. DISCONNECT 525687 e.37. DISCONNECT 525694 e.38. DISCONNECT 525697 e.39. DISCONNECT 525701 e.40. DISCONNECT 525703 e.41. DISCONNECT 525708 e.42. DISCONNECT 525717 | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_163_P5_5_CUNNINGHAM | Single phase fault with stuck relay near CUNNIGHM_N 6 (527865) 230 kV bus a. Apply fault at the CUNNIGHM_N 6 (527865) 230 kV bus b. Run fault for 19.32 cycles and trip the faulted elements b.1. LINE 527867 TO 527894 CKT 1 c. Run fault for 6.06 cycles and trip the faulted elements c.1. LINE 527865 TO 527963 CKT 1 d. Run fault for 17.1 cycles and trip the faulted elements d.1. GENERATOR 1 527883 d.2. DISCONNECT 527883 d.3. LINE 527865 TO 527883 CKT 1 e. Run fault for 13.2 cycles and trip the faulted elements e.1. LINE 527865 TO 527799 CKT 1 f. Run fault for 2.22 cycles and trip the faulted elements f.1. GENERATOR 1 527882 f.2. DISCONNECT 527882 f.3. LINE 527867 TO 527882 CKT 1 g. Run fault for 66.12 cycles and trip the faulted elements g.1. DISCONNECT 527863 g.2. DISCONNECT 527865 g.3. DISCONNECT 527867 h. Clear fault at CUNNIGHM_N 6 (527865) 230 kV bus | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_164_P5_5_BUSHLAND | Single phase fault with stuck relay near BUSHLAND 6 (524267) 230 kV bus a. Apply fault at the BUSHLAND 6 (524267) 230 kV bus b. Run fault for 5 cycles and trip the faulted elements b.1. DISCONNECT 524263 b.2. LINE 524267 TO 524623 CKT 1 b.3. LINE 524267 TO 524290 CKT 1 b.4 GENERATOR 1 524285 b.5. GENERATOR 1 524287 c. Run fault for 32 cycles and trip the faulted elements c.1. LINE 524267 TO 523959 CKT 1 d. Clear fault at the BUSHLAND 6 (524267) 230 kV bus and trip the faulted elements d.1. LOAD A1 524285 d.2. DISCONNECT 524267 d.3. DISCONNECT 524275 d.4. DISCONNECT 524276 d.5. DISCONNECT 524285 d.6. DISCONNECT 524287 d.7. DISCONNECT 524289 d.8. DISCONNECT 524290 | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_165_P5_5_BUSHLAND | Single phase fault with stuck relay near BUSHLAND 6 (524267) 230 kV bus a. Apply fault at the BUSHLAND 6 (524267) 230 kV bus b. Run fault for 5 cycles and trip the faulted elements b.1. DISCONNECT 524263 b.2. LINE 524267 TO 523959 CKT 1 b.3. LINE 524267 TO 524290 CKT 1 b.4. GENERATOR 1 524285 b.5. GENERATOR 1 524287 c. Run fault for 32 cycles and trip the faulted elements c.1. LINE 524267 TO 524623 CKT 1 d. Clear fault at the BUSHLAND 6 (524267) 230 kV bus and trip the faulted elements d.1. LOAD A1 524285 d.2. DISCONNECT 524267 d.3. DISCONNECT 524275 d.4. DISCONNECT 524276 d.5. DISCONNECT 524285 d.6. DISCONNECT 524287 d.7. DISCONNECT 524289 d.8. DISCONNECT 524290 | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_166_P5_5_GRASSLAND | Single phase fault with stuck relay near GRASSLAND 6 (526677) 230 kV bus a. Apply fault at the GRASSLAND 6 (526677) 230 kV bus b. Run fault for 34.38 cycles and trip the faulted elements b.1. LINE 526677 TO 526337 CKT 1 c. Run fault for 54.9 cycles and trip the faulted elements c.1. LINE 526676 TO 526656 CKT 1 d. Clear fault at the GRASSLAND 6 (526677) 230 kV bus and trip the faulted elements d.1. GENERATOR 1 526678 d.2. LOAD 1 526513 d.3. LOAD 1 526569 d.4. LOAD 1 526576 d.5. LOAD 1 526583 d.6. LOAD 1 526592 d.7. LOAD 1 526622 d.8. LOAD 2 526622 d.9. LOAD 3 526622 d.10. LOAD 1 526814 d.11. LOAD A1 599125 d.12 DISCONNECT 526513 d.13. DISCONNECT 526569 d.14. DISCONNECT 526576 d.15. DISCONNECT 526583 d.16. DISCONNECT 526592 d.17. DISCONNECT 526622 d.18.DISCONNECT 526674 d.19. DISCONNECT 526676 d.20. DISCONNECT 526677 d.21. DISCONNECT 526678 d.22. DISCONNECT 526679 d.23. DISCONNECT 526691 d.24. DISCONNECT 526692 d.25. DISCONNECT 526693 d.26. DISCONNECT 526694 d.27. DISCONNECT 526799 d.28. DISCONNECT 526814 d.29. DISCONNECT 526821 d.30. DISCONNECT 599125 d.31. DISCONNECT 599126 | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_167_P5_3_LAMB | Single phase fault with stuck relay near LAMB_CNTY 3 (525636) 115 kV bus a. Apply fault at the LAMB_CNTY 3 (525636) 115 kV bus b. Run fault for 39 cycles and trip the faulted elements b.1. LINE 525636 TO 526020 CKT 1 c. Run fault for 15.48 cycles and trip the faulted elements c.1. LINE 525480 TO 525636 CKT 1 d. Run fault for 46.32 cycles and trip the faulted elements d.1. LINE 525637 TO 525531 CKT 1 d. Clear fault at the LAMB_CNTY 3 (525636) 115 kV bus and trip the faulted elements d.1. LOAD 1 525592 d.2. LOAD 1 525599 d.3. LOAD 2 525599 d.4. LOAD 1 525606 d.5. LOAD 1 525613 d.6. LOAD 1 525620 d.7. LOAD 2 525620 d.8. LOAD 1 525650 d.9. LOAD 1 525664 d.10. LOAD 2 525664 d.11. LOAD 1 525671 d.12. LOAD 1 525678 d.13. LOAD 1 525687 d.14. LOAD 1 525694 d.15. LOAD 1 525701 d.16. LOAD 2 525701 d.17. LOAD 1 525703 d.18. LOAD 1 525708 d.19. LOAD 1 525717 d.20. DISCONNECT 525592 d.21. DISCONNECT 525599 d.22. DISCONNECT 525606 d.23. DISCONNECT 525613 d.24. DISCONNECT 525620 d.25. DISCONNECT 525631 d.26. DISCONNECT 525632 d.27. DISCONNECT 525633 d.28. DISCONNECT 525635 d.29. DISCONNECT 525636 d.30. DISCONNECT 525637 d.31. DISCONNECT 525650 d.32. DISCONNECT 525657 d.32. DISCONNECT 525664 d.33. DISCONNECT 525671 d.34. DISCONNECT 525678 d.35. DISCONNECT 525687 d.36. DISCONNECT 525694 d.37. DISCONNECT 525697 d.38. DISCONNECT 525701 d.39. DISCONNECT 525703 d.40. DISCONNECT 525708 d.41. DISCONNECT 525717 | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_168_P5_5_LAMB | Single phase fault with stuck relay near LAMB_CNTY 3 (525636) 115 kV bus a. Apply fault at the LAMB_CNTY 3 (525636) 115 kV bus b. Run fault for 39 cycles and trip the faulted elements b.1. LINE 525636 TO 526020 CKT 1 c. Run fault for 14.88 cycles and trip the faulted elements c.1. DISCONNECT 525633 d. Run fault for 0.6 cycles and trip the faulted elements d.1. LINE 525636 TO 525480 CKT 1 e. Clear fault at the LAMB_CNTY 3 (525636) 115 kV bus and trip the faulted elements e.1. LOAD 1 525592 e.2. LOAD 1 525599 e.3. LOAD 2 525599 e.4. LOAD 1 525606 e.5. LOAD 1 525613 e.6. LOAD 1 525620 e.7. LOAD 2 525620 e.8. LOAD 1 525650 e.9. LOAD 1 525664 e.10. LOAD 2 525664 e.11. LOAD 1 525671 e.12. LOAD 1 525678 e.13. LOAD 1 525687 e.14. LOAD 1 525694 e.15. LOAD 1 525701 e.16. LOAD 2 525701 e.17. LOAD 1 525703 e.18. LOAD 1 525708 e.19. LOAD 1 525717 e.20. DISCONNECT 525592 e.21. DISCONNECT 525599 e.22. DISCONNECT 525606 e.23. DISCONNECT 525613 e.24. DISCONNECT 525620 e.25. DISCONNECT 525631 e.26. DISCONNECT 525632 e.27. DISCONNECT 525635 e.28. DISCONNECT 525636 e.29. DISCONNECT 525650 e.30. DISCONNECT 525657 e.31. DISCONNECT 525664 e.32. DISCONNECT 525671 e.33. DISCONNECT 525678 e.34. DISCONNECT 525687 e.35. DISCONNECT 525694 e.36. DISCONNECT 525697 e.37. DISCONNECT 525701 e.38. DISCONNECT 525703 e.39. DISCONNECT 525708 e.40. DISCONNECT 525717 | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_169_P5_2_LUBBOCK_STH | Single phase fault with stuck relay near LUBBCK_STH 6 (526269) 230 kV bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV bus b. Run fault for 4.38 cycles and trip the faulted elements b.1. LINE 526269 TO 526525 CKT 1 c. Run fault for 40.2 cycles and trip the faulted elements c.1. LINE 526268 TO 526213 CKT 1 d. Run fault for 130.44 cycles and trip the faulted elements d.1. LINE 526268 TO 526298 CKT 1 e. Run fault for 60.3 cycles and trip the faulted elements e.1. LINE 526269 TO 526337 CKT 1 e.2. LINE 526269 TO 526337 CKT 2 f. Run fault for 63.6 cycles and trip the faulted elements f.1. DISCONNECT 526264 g. Run fault for 0.78 cycles and trip the faulted elements g.1. LINE 526602 TO 526656 CKT 1 h. Clear fault at the LUBBCK_STH 6 (526269) 230 kV bus and trip the faulted elements h.1. LOAD 1 526205 h.2. LOAD 1 526228 h.3. LOAD 1 526249 h.4. LOAD 1 526602 h.5. DISCONNECT 526205 h.6. DISCONNECT 526228 h.7. DISCONNECT 526249 h.8. DISCONNECT 526256 h.9. DISCONNECT 526265 h.10. DISCONNECT 526266 h.11. DISCONNECT 526267 h.12. DISCONNECT 526268 h.13. DISCONNECT 526269 h.14. DISCONNECT 526602 | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_170_P5_2_MOORE | Single phase fault with stuck relay near RB-S&S 3 (523315) 115 kV bus a. Apply fault at the RB-S&S 3 (523315) 115 kV bus b. Run fault for 4.02 cycles and trip the faulted elements b.1. LINE 523315 TO 523318 CKT 1 c. Run fault for 8.28 cycles and trip the faulted elements c.1. LINE 523216 TO 523246 CKT 1 d. Run fault for 48.9 cycles and trip the faulted elements d.1. DISCONNECT 523302 e. Run fault for 10.62 cycles and trip the faulted elements e.1. LINE 523235 TO 523228 CKT 1 f. Run fault for 3.18 cycles and trip the faulted elements f.1. LINE 523176 TO 523175 CKT 1 g. Run fault for 35.1 cycles and trip the faulted elements g.1. LINE 523352 TO 523377 CKT 1 h. Clear fault at the RB-S&S 3 (523315) 115 kV bus and trip the faulted elements h.1. GENERATOR 1 523252 h.2. GENERATOR 1 523254 h.3. GENERATOR 1 523277 h.4. GENERATOR 1 523297 h.5. GENERATOR 3 523301 h.6. LOAD 1 523176 h.7. LOAD 1 523177 h.8. LOAD 1 523216 h.9. LOAD 1 523217 h.10. LOAD 1 523237 h.11. LOAD 1 523240 h.12. LOAD F1 523252 h.13. LOAD F1 523254 h.14. LOAD 1 523255 h.15. LOAD 2 523255 h.16. LOAD D1 523255 h.17. LOAD D2 523255 h.18. LOAD 1 523277 h.19. LOAD A1 523277 h.20. LOAD F1 523297 h.21. LOAD 1 523301 h.22. LOAD A3 523301 h.23. LOAD 1 523315 h.24. LOAD 1 523359 h.25. LOAD D1 523359 h.26. LOAD 1 523366 h.27. DISCONNECT 523176 h.28. DISCONNECT 523177 h.29. DISCONNECT 523216 h.30. DISCONNECT 523217 h.31. DISCONNECT 523235 h.32. DISCONNECT 523237 h.33. DISCONNECT 523240 h.34. DISCONNECT 523251 h.35. DISCONNECT 523252 h.36. DISCONNECT 523253 h.37. DISCONNECT 523254 h.38. DISCONNECT 523255 h.39. DISCONNECT 523256 h.40. DISCONNECT 523277 h.41. DISCONNECT 523294 h.42. DISCONNECT 523295 h.43. DISCONNECT 523296 h.44. DISCONNECT 523297 h.45. DISCONNECT 523301 h.46. DISCONNECT 523304 h.47. DISCONNECT 523308 h.47. DISCONNECT 523315 h.48. DISCONNECT 523352 h.49. DISCONNECT 523359 h.50. DISCONNECT 523366 | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_171_P5_5_OASIS | Single phase fault with stuck relay near OASIS 3 (524874) 115 kV bus a. Apply fault at the OASIS 3 (524874) 115 kV bus b. Run fault for 19.2 cycles and trip the faulted elements b.1. LINE 524874 TO 524924 CKT 1 c. Run fault for 0.18 cycles and trip the faulted elements c.1. LINE 524764 TO 524822 CKT 1 d. Run fault for 10.8 cycles and trip the faulted elements d.1. LINE 524784 TO 524808 CKT 1 e. Run fault for 14.04 cycles and trip the faulted elements e.1. LINE 524875 TO 524909 CKT 1 f. Run fault for 49.08 cycles and trip the faulted elements f.1. DISCONNECT 524872 g. Clear fault at the OASIS 3 (524874) 115 kV bus and trip the faulted elements g.1. LOAD 1 524784 g.2. LOAD 1 524794 g.3. LOAD 1 524797 g.4. LOAD 1 524801 g.5. LOAD 1 524863 g.6. DISCONNECT 524764 g.7. DISCONNECT 524784 g.8. DISCONNECT 524790 g.9. DISCONNECT 524794 g.10. DISCONNECT 524797 g.11. DISCONNECT 524801 g.12. DISCONNECT 524863 | P5_Member | Yes | Yes | Yes | Yes | No | Yes | Yes | GEN-2001-036 trips on Voltage protection settings. High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points) prevents GEN-2001-036 from tripping and fixes high voltage issues.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_172_P5_5_POTASH | Single phase fault with stuck relay near POTASH_JCT 3 (527962) 115 kV bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV bus b. Run fault for 19.02 cycles and trip the faulted elements b.1. LINE 527962 TO 527930 CKT 1 c. Run fault for 0.18 cycles and trip the faulted elements c.1. LINE 528064 TO 527953 CKT 1 d. Run fault for 15.3 cycles and trip the faulted elements d.1. LINE 527962 TO 528160 CKT 1 e. Run fault for 4.08 cycles and trip the faulted elements e.1. DISCONNECT 527958 f. Run fault for 14.94 cycles and trip the faulted elements f.1. LINE 528145 TO 527929 CKT 1 g. Clear fault at POTASH_JCT 3 (527962) 115 kV bus | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_173_P5_5_7_RIVERS | Single phase fault with stuck relay near 7-RIVERS 3 (528094) 115 kV bus a. Apply fault at the 7-RIVERS 3 (528094) 115 kV bus b. Run fault for 19.38 cycles and trip the faulted elements b.1. LINE 528094 TO 527711 CKT 1 b.2. LINE 528070 TO 528178 CKT 1 b.3. LINE 527786 TO 528116 CKT 1 c. Run fault for 20.4 cycles and trip the faulted elements c.1. LINE 528095 TO 528179 CKT 1 d. Run fault for 136.92 cycles and trip the faulted elements d.1. LINE 528095 TO 527799 CKT 1 e. Clear fault at the 7-RIVERS 3 (528094) 115 kV bus and trip the faulted elements e.1. LOAD 1 528003 e.2. LOAD 1 528076 e.3. LOAD 1 528079 e.4. LOAD 1 528109 e.5. LOAD 1 528116 e.6. DISCONNECT 528003 e.7. DISCONNECT 528070 e.7. DISCONNECT 528076 e.8. DISCONNECT 528079 e.9. DISCONNECT 528090 e.10. DISCONNECT 528091 e.11. DISCONNECT 528093 e.12. DISCONNECT 528094 e.13. DISCONNECT 528095 e.14. DISCONNECT 528109 e.15. DISCONNECT 528116 | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_174_P5_5_YOAKUM | Single phase fault with stuck relay near YOAKUM 3 (526934) 115 kV bus a. Apply fault at the YOAKUM 3 (526934) 115 kV bus b. Run fault for 19.5 cycles and trip the faulted elements b.1. LINE 526934 TO 527194 CKT 1 c. Run fault for 1.5 cycles and trip the faulted elements c.1. LINE 526934 TO 526928 CKT 1 d. Run fault for 8.4 cycles and trip the faulted elements d.1. LINE 526792 TO 526736 CKT 1 e. Run fault for 24.6 cycles and trip the faulted elements e.1. DISCONNECT 527122 e.2. LINE 527130 TO 527136 CKT @1 f. Run fault for 3.72 cycles and trip the faulted elements f.1. GENERATOR 1 527162 f.2. DISCONNECT 527162 g. Run fault for 0.18 cycles and trip the faulted elements g.1. LINE 527051 TO 527062 CKT 1 h. Run fault for 0.12 cycles and trip the faulted elements h.1. GENERATOR 1 527161 h.2. DISCONNECT 527161 h.3. GENERATOR 1 527163 i. Run fault for 0.96 cycles and trip the faulted elements i.1. DISCONNECT 526932 i.2. DISCONNECT 526931 j. Clear fault at the YOAKUM 3 (526934) 115 kV bus and trip the faulted elements j.1. LOAD 1 526792 j.2. LOAD D1 526792 j.3. LOAD 1 527018 j.4. LOAD 1 527047 j.5. LOAD 1 527056 j.6. DISCONNECT 526792 j.7. DISCONNECT 526934 j.8. DISCONNECT 527018 j.9. DISCONNECT 527041 j.10. DISCONNECT 527047 j.11. DISCONNECT 527051 j.12.DISCONNECT 527056 | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_175_P5_5_CARLISLE | Single phase fault with stuck relay near CARLISLE 3 (526160) 115 kV bus a. Apply fault at the CARLISLE 3 (526160) 115 kV bus b. Run fault for 19.38 cycles and trip the faulted elements b.1. LINE 526109 TO 526146 CKT 1 c. Run fault for 14.64 cycles and trip the faulted elements c.1. LINE 526475 TO 526481 CKT 1 d. Run fault for 13.08 cycles and trip the faulted elements d.1. DISCONNECT 526157 e. Run fault for 12.78 cycles and trip the faulted elements e.1. LINE 526160 TO 526192 CKT 1 f. Clear fault at the CARLISLE 3 (526160) 115 kV bus and trip the faulted elements f.1. LOAD 1 526109 f.2. LOAD 1 526160 f.3. LOAD D2 526160 f.4. LOAD 1 526176 f.5. LOAD 1 526221 f.6. LOAD 1 526483 f.7. DISCONNECT 526109 f.8. DISCONNECT 526130 f.9. DISCONNECT 526158 f.10. DISCONNECT 526159 f.11. DISCONNECT 526160 f.12. DISCONNECT 526162 f.13. DISCONNECT 526176 f.14. DISCONNECT 526184 f.15. DISCONNECT 526221 f.16. DISCONNECT 526481 f.17. DISCONNECT 526483 | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_176_P5_2_ALLEN | Single phase fault with stuck relay near ALLEN 3 (526213) 115 kV bus a. Apply fault at the ALLEN 3 (526213) 115 kV bus b. Run fault for 3.42 cycles and trip the faulted elements b.1. LINE 526243 TO 526199 CKT 1 c. Run fault for 53.4 cycles and trip the faulted elements c.1. LINE 526213 TO 526268 CKT 1 d. Clear fault at the ALLEN 3 (526213) 115 kV bus and trip the faulted elements d.1. LOAD 1 526213 d.2. LOAD 2 526213 d.3. LOAD 1 526236 d.4. LOAD 1 526243 d.5. DISCONNECT 526213 d.6. DISCONNECT 526236 d.7. DISCONNECT 526243 | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_177_P5_2_ALLEN | Single phase fault with stuck relay near ALLEN 3 (526213) 115 kV bus a. Apply fault at the ALLEN 3 (526213) 115 kV bus b. Run fault for 5.52 cycles and trip the faulted elements b.1. LINE 526213 TO 526268 CKT 1 c. Run fault for 55.68 cycles and trip the faulted elements c.1. LINE 526243 TO 526199 CKT 1 d. Clear fault at the ALLEN 3 (526213) 115 kV bus and trip the faulted elements d.1. LOAD 1 526213 d.2. LOAD 2 526213 d.3. LOAD 1 526236 d.4. LOAD 1 526243 d.5. DISCONNECT 526213 d.6. DISCONNECT 526236 d.7. DISCONNECT 526243 | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_178_P5_2_ALLEN | Single phase fault with stuck relay near ALLEN 3 (526213) 115 kV bus a. Apply fault at the ALLEN 3 (526213) 115 kV bus b. Run fault for 48.3 cycles and trip the faulted elements b.1. LINE 526213 TO 526268 CKT 1 c. Run fault for 6.72 cycles and trip the faulted elements c.1. LINE 526243 TO 526199 CKT 1 d. Clear fault at the ALLEN 3 (526213) 115 kV bus and trip the faulted elements d.1. LOAD 1 526213 d.2. LOAD 2 526213 d.3. LOAD 1 526236 d.4. LOAD 1 526243 d.5. DISCONNECT 526213 d.6. DISCONNECT 526236 d.7. DISCONNECT 526243 | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_179_P5_2_HARRNG_EST | Single phase fault with stuck relay near HARRNG_EST 6 (523979) 230 kV bus a. Apply fault at the HARRNG_EST 6 (523979) 230 kV bus b. Run fault for 20 cycles and trip the faulted elements b.1. DISCONNECT 523979 b.2. GENERATOR 1 523973 b.3. DISCONNECT 523973 c. Clear fault at HARRNG_EST 6 (523979) 230 kV bus | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_180_P5_2_WOLFFORTH | Single phase fault with stuck relay near WOLFFORTH 3 (526524) 115 kV bus a. Apply fault at the WOLFFORTH 3 (526524) 115 kV bus b. Run fault for 10 cycles and trip the faulted elements b.1. LINE 526162 TO 526160 CKT 1 b.2. DISCONNECT 526522 c. Run fault for 22 cycles and trip the faulted elements c.1. LINE 526524 TO 526736 CKT 1 d. Clear fault at the WOLFFORTH 3 (526524) 115 kV bus and trip the faulted elements d.1. LOAD 1 526176 d.2. LOAD 1 526475 d.3. LOAD 1 526483 d.4. DISCONNECT 526162 d.5. DISCONNECT 526176 d.6. DISCONNECT 526475 d.7. DISCONNECT 526481 d.8. DISCONNECT 526483 d.9. DISCONNECT 526524 | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 | 25W | Transfer | LT__SPS_All_181_P5_3_LAMB | Single phase fault with stuck relay near LAMB_CNTY 3 (525636) 115 kV bus a. Apply fault at the LAMB_CNTY 3 (525636) 115 kV bus b. Run fault for 39 cycles and trip the faulted elements b.1. LINE 525636 TO 526020 CKT 1 c. Run fault for 15.48 cycles and trip the faulted elements c.1. LINE 525636 TO 525480 CKT 1 d. Run fault for 46.32 cycles and trip the faulted elements d.1. LINE 525637 TO 525531 CKT 1 e. Clear fault at the LAMB_CNTY 3 (525636) 115 kV bus and trip the faulted elements e.1. LOAD 1 525592 e.2. LOAD 1 525599 e.3. LOAD 2 525599 e.4. LOAD 1 525606 e.5. LOAD 1 525613 e.6. LOAD 1 525620 e.7. LOAD 2 525620 e.8. LOAD 1 525650 e.9. LOAD 1 525664 e.10. LOAD 2 525664 e.11. LOAD 1 525671 e.12. LOAD 1 525678 e.13. LOAD 1 525687 e.14. LOAD 1 525694 e.15. LOAD 1 525701 e.16. LOAD 2 525701 e.17. LOAD 1 525703 e.18. LOAD 1 525708 e.19. LOAD 1 525717 e.20. DISCONNECT 525592 e.21. DISCONNECT 525599 e.22. DISCONNECT 525606 e.23. DISCONNECT 525613 e.24. DISCONNECT 525620 e.25. DISCONNECT 525631 e.26. DISCONNECT 525632 e.27. DISCONNECT 525633 e.28. DISCONNECT 525635 e.29. DISCONNECT 525636 e.30. DISCONNECT 525637 e.31. DISCONNECT 525650 e.32. DISCONNECT 525657 e.33. DISCONNECT 525664 e.34. DISCONNECT 525671 e.35. DISCONNECT 525678 e.36. DISCONNECT 525687 e.37. DISCONNECT 525694 e.38. DISCONNECT 525697 e.39. DISCONNECT 525701 e.40. DISCONNECT 525703 e.41. DISCONNECT 525708 e.42. DISCONNECT 525717 | P5_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | 53CACHE4__ARTVLTP4 | 3 Phase fault on 53CACHE4 (511509) 138 kV Bus a. Apply fault at the 53CACHE4 (511509) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53CACHE4 138.0 KV 511509 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | 7_RIVERS___6__PECOS______6 | 3 Phase fault on 7-RIVERS 6 (528095) 230 kV Bus a. Apply fault at the 7-RIVERS 6 (528095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 7-RIVERS 6 230.0 KV 528095 TO PECOS 6 230.0 KV 528179 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | AMA_SOUTH__6__SWISHER____6 | 3 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 230.0 KV 524415 TO SWISHER 6 230.0 KV 525213 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | AMOCOWASSON6__MUSTANG____6 | 3 Phase fault on AMOCOWASSON6 (526784) 230 kV Bus a. Apply fault at the AMOCOWASSON6 (526784) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCOWASSON6 230.0 KV 526784 TO MUSTANG 6 230.0 KV 527149 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | AMOCOWASSON6__XTO_MAHONEY6 | 3 Phase fault on AMOCOWASSON6 (526784) 230 kV Bus a. Apply fault at the AMOCOWASSON6 (526784) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCOWASSON6 230.0 KV 526784 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | ARTVLTP4__ARTVILL4 | 3 Phase fault on ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTVLTP4 138.0 KV 511537 TO ARTVILL4 138.0 KV 511538 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | BLCKRVR_DST3__CHINA_DRAW_3 | 3 Phase fault on BLCKRVR_DST3 (528206) 115 kV Bus a. Apply fault at the BLCKRVR_DST3 (528206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLCKRVR_DST3 115.0 KV 528206 TO CHINA_DRAW 3 115.0 KV 528222 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | BLUECLDPOI_6__NEEDMORE___6 | 3 Phase fault on BLUECLDPOI 6 (525585) 230 kV Bus a. Apply fault at the BLUECLDPOI 6 (525585) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUECLDPOI 6 230.0 KV 525585 TO NEEDMORE 6 230.0 KV 525586 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Decrease acceleration factor to 0.2.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | BORDER_____7__BECKHAM7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | BORDER_____7__TUCO_INT___7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO TUCO_INT 7 345.0 KV 525832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | BRU_SUB____6__OXYBRU_____6 | 3 Phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRU_SUB 6 230.0 KV 527009 TO OXYBRU 6 230.0 KV 527010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | BRU_SUB____6__XTO_MAHONEY6 | 3 Phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRU_SUB 6 230.0 KV 527009 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | BUCKEYE_TP_3__BUCKEYE____3 | 3 Phase fault on BUCKEYE_TP 3 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3 115.0 KV 528348 TO BUCKEYE 3 115.0 KV 528385 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | BUCKEYE_TP_3__LE_TXACO_TP3 | 3 Phase fault on BUCKEYE_TP 3 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3 115.0 KV 528348 TO LE-TXACO_TP3 115.0 KV 528627 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | BYRD_TP____3__BYRD_______3 | 3 Phase fault on BYRD_TP 3 (528581) 115 kV Bus a. Apply fault at the BYRD_TP 3 (528581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BYRD_TP 3 115.0 KV 528581 TO BYRD 3 115.0 KV 528582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CALLAHAN___3__FLOYD_CNTY_3 | 3 Phase fault on CALLAHAN 3 (525763) 115 kV Bus a. Apply fault at the CALLAHAN 3 (525763) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALLAHAN 3 115.0 KV 525763 TO FLOYD_CNTY 3 115.0 KV 525780 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CARDINAL___3__TARGA______3 | 3 Phase fault on CARDINAL 3 (528596) 115 kV Bus a. Apply fault at the CARDINAL 3 (528596) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARDINAL 3 115.0 KV 528596 TO TARGA 3 115.0 KV 528605 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CARLISLE___3__LP_DOUD_TP_3 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 115.0 KV 526160 TO LP-DOUD_TP 3 115.0 KV 526162 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CARLISLE___3__MURPHY_____3 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 115.0 KV 526160 TO MURPHY 3 115.0 KV 526192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CARLISLE___6__WOLFFORTH__6 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 230.0 KV 526161 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CARLSBAD___3__PECOS______3 | 3 Phase fault on CARLSBAD 3 (528160) 115 kV Bus a. Apply fault at the CARLSBAD 3 (528160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLSBAD 3 115.0 KV 528160 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CHAVES_CNTY6__EDDY_NORTH_6 | 3 Phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY6 230.0 KV 527483 TO EDDY_NORTH 6 230.0 KV 527799 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CHINA_DRAW_3__CD_SVC_HV__3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO CD_SVC_HV 3 115.0 KV 528225 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CHINA_DRAW_3__CHVRN_EDDYS3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO CHVRN_EDDYS3 115.0 KV 528252 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CHINA_DRAW_3__WOOD_DRAW__3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO WOOD_DRAW 3 115.0 KV 528228 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CHISHOLM7__BECKHAM7 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CHISHOLM7__G16_037_TAP | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes. | Increase acceleration factor to 0.8.
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | COMANC_2__L_E_S__2 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L.E.S.-2 69.0 KV 511466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | COMANC_4__112GORE4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | COMANC_4__COMMTAP4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | COMANC_4__L_E_S__4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | COMMTAP4__OMDUNCN4 | 3 Phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMMTAP4 138.0 KV 511494 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | COOPER_RNCH3__BYRD_TP____3 | 3 Phase fault on COOPER_RNCH3 (528554) 115 kV Bus a. Apply fault at the COOPER_RNCH3 (528554) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_RNCH3 115.0 KV 528554 TO BYRD_TP 3 115.0 KV 528581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | COX________3__HALE_CNTY__3 | 3 Phase fault on COX 3 (525326) 115 kV Bus a. Apply fault at the COX 3 (525326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 115.0 KV 525326 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CROSBY_____3__LUBBCK_EST_3 | 3 Phase fault on CROSBY 3 (525926) 115 kV Bus a. Apply fault at the CROSBY 3 (525926) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSBY 3 115.0 KV 525926 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CROSSROADS_7__EDDY_CNTY__7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 345.0 KV 527656 TO EDDY_CNTY 7 345.0 KV 527802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CUNNIGHM_N_6__POTASH_JCT_6 | 3 Phase fault on CUNNIGHM_N 6 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6 (527865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_N 6 230.0 KV 527865 TO POTASH_JCT 6 230.0 KV 527963 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CUNNIGHM_S_6__HOBBS_INT__6 | 3 Phase fault on CUNNIGHM_S 6 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 230.0 KV 527867 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CUNNINHAM__3__BUCKEYE_TP_3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO BUCKEYE_TP 3 115.0 KV 528348 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CUNNINHAM__3__HOBBS_INT__3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO HOBBS_INT 3 115.0 KV 527891 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CUNNINHAM__3__MADDOX_____3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO MADDOX 3 115.0 KV 528355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-001 CF | 25S | Transfer | CUNNINHAM__3__MONUMNT_TP_3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO MONUMNT_TP 3 115.0 KV 528568 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cylces, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes