## Executive Summary
Executive Summary: DISIS-2018-001 Phase 1 of Power Flow
Pursuant to the Southwest Power Pool (SPP) Open Access Transmission Tariff (OATT), SPP has conducted this Definitive Interconnection System Impact Study (DISIS) for generation interconnection requests received during the DISIS Queue Cluster Window which closed on March 31, 2018. The primary objective of this DISIS is to identify the system constraints, transient instabilities, and over-dutied equipment associated with connecting the generation to the area transmission system. The Impact Study and other subsequent Interconnection Studies are designed to identify required Transmission Owner Interconnection Facilities, Network Upgrades and other Direct Assignment Facilities needed to inject power into the grid at each specific point of interconnection. The study analysis for the generation interconnection requests included in this DISIS are displayed in this workbook. This workbook provides a convenient method to sort and analyze required study data. The DISIS Manual Version 1.6 posted on http://opsportal.spp.org/Studies/Gen contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gistudies@spp.org for more information about the study process. DISIS-2018-001 includes study requests in the following cluster groups: (00NR, 01 - North, 02 - Nebraska, 03 - Central, 04 - Southeast, 05 - Southwest)
DISIS Manual Version 1.6
https://opsportal.spp.org/documents/studies/DISIS%20Manual.pdf
This DISIS analyzes the impact of interconnecting new generation for total of:
9,011.59 MW
The minimum cost of interconnecting all requests included in this DISIS is estimated at:
Network Upgrade Costs: $222,172,040.21 Interconnection Costs: $429,077,175.00
Models Used in Study
2021 ITP Series
Winter: 2026
Summer: 2023, 2026
Light: 2026
By: SPP Generator Interconnection Department
Published: August 9, 2022
Costs for Solar/Battery Requests were allocated using the 26SP (summer peak) model.
Costs for Wind Requests were allocated using the 26L (light load) model.
Short Circuit Ratio calculation is provided per group. A value of "N/A" means the request was offline for that scenario.
Assigned Upgrade Costs include the new cumulative impact criteria from BP7250.
Network Upgrades assigned in DISIS-2017-002 Phase 1 are included as Contingent Upgrades. Refer to 'Upgrade Summary' tab for list of Contingent Upgrades included in the analysis.

## Revision History
Revision History
Date | Author | Change Description
4475400% | SPP | Phase 1 Draft Posting
4476100% | SPP | Phase 1 Final Posting
4478200% | SPP | Phase 1 Final Posting with Interconnection Cost Estimate Updates

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details
4476100% | Upgrades and Cost | 4 | Requests | Updated fuel types, LOIS amounts, and limiting elements
4476100% | Upgrades and Cost | 5 | Constraints Summary | Upgrade constraints based on TO feedback
4476100% | Upgrades and Cost | 6 | Assigned Upgraded Costs | Removed mitigaiton assigned due to updated line ratings
4476100% | Upgrades and Cost | 7 | Upgrade Summary | Removed mitigaiton assigned due to updated line ratings
4478200% | Upgrades and Cost | 6 | Assigned Upgraded Costs | Updated Interconnection Cost Estimates due to updated costs provided by Transmission Owner

## Requests
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | LOIS Amount | Limiting Element | Service | Area | POI | Status
ASGI-2017-013 | 01 NORTH | 20 | DIS-18-1 | Wind | 40 | 40 | None | ER | WAPA | Wolsey 69kV Substation | DISIS STAGE
GEN-2018-007 | 01 NORTH | 20 | DIS-18-1 | Solar | 150 | 125.9 | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 | ER/NR | WAPA | Summit 115kV Substation | DISIS STAGE
GEN-2018-010 | 01 NORTH | 20 | DIS-18-1 | Battery | 74.1 | 74.1 | None | ER/NR | WAPA | Neset 230kV Substation | DISIS STAGE
GEN-2018-008 | 01 NORTH | 20 | DIS-18-1 | Wind | 252 | 252 | None | ER/NR | WAPA | Groton-Leland Olds 345kV Line | DISIS STAGE
GEN-2018-039 | 01 NORTH | 20 | DIS-18-1 | Solar | 72 | 72 | None | ER/NR | WAPA | Edgeley 115kV substation | DISIS STAGE
GEN-2018-012 | 02 NEBRASKA | 20 | DIS-18-1 | Wind | 74.1 | 60.27 | 640325 REDWILO3 345 762808 G18-045-TAP 345 1 | ER/NR | NPPD | Antelope - Hoskins 345kV line | DISIS STAGE
GEN-2018-025 | 02 NEBRASKA | 20 | DIS-18-1 | Battery | 200 | 200 | None | ER | OPPD | Fort Calhoun 345kV Substation | DISIS STAGE
GEN-2018-033 | 02 NEBRASKA | 20 | DIS-18-1 | Battery | 200 | 200 | None | ER | OPPD | Cass County 345kV Substation | DISIS STAGE
GEN-2018-036 | 02 NEBRASKA | 20 | DIS-18-1 | Battery | 200 | 87.35 | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 | ER | WAPA | Stegall 230kV Substation | DISIS STAGE
GEN-2018-037 | 02 NEBRASKA | 20 | DIS-18-1 | Battery | 100 | 100 | None | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV | DISIS STAGE
GEN-2018-043 | 02 NEBRASKA | 20 | DIS-18-1 | Solar | 500 | 343.98 | 646209 S1209 5 161 646231 S1231 5 161 1 | ER/NR | OPPD | Ft. Calhoun - Raun 345 kV Line Break | DISIS STAGE
GEN-2018-044 | 02 NEBRASKA | 20 | DIS-18-1 | Solar | 500 | 343.98 | 646209 S1209 5 161 646231 S1231 5 161 1 | ER/NR | OPPD | Fort Calhoun 345kV Substation | DISIS STAGE
GEN-2018-045 | 02 NEBRASKA | 20 | DIS-18-1 | Solar | 550 | 447.36 | 640325 REDWILO3 345 762808 G18-045-TAP 345 1 | ER/NR | NPPD | Gentleman â€“ Red Willow 345kV Line Break | DISIS STAGE
GEN-2018-046 | 02 NEBRASKA | 20 | DIS-18-1 | Wind | 400 | 325.35 | 640325 REDWILO3 345 762808 G18-045-TAP 345 1 | ER/NR | NPPD | Gerald Gentleman-Red Willow 345kV line break | DISIS STAGE
GEN-2018-056 | 02 NEBRASKA | 20 | DIS-18-1 | Solar | 102.6 | 83.45 | 640325 REDWILO3 345 762808 G18-045-TAP 345 1 | ER/NR | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | DISIS STAGE
GEN-2018-060 | 02 NEBRASKA | 20 | DIS-18-1 | Wind | 50 | 50 | None | ER/NR | NPPD | Axtell-Post Rock 345 kV | DISIS STAGE
ASGI-2018-003 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | 0 | Non-converged | ER | KCPL | AP City 69kV Substation | DISIS STAGE
ASGI-2018-006 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | 0 | Non-converged | ER | KCPL | Metz 69kV Substation | DISIS STAGE
ASGI-2018-007 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | 0 | Non-converged | ER | KCPL | Salisbury 161kV Substation | DISIS STAGE
ASGI-2018-010 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | 0 | Non-converged | ER | KCPL | Pleasant Valley 161kV Substation | DISIS STAGE
ASGI-2018-011 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | 0 | Non-converged | ER | KCPL | South Ottawa 161kV Substation | DISIS STAGE
GEN-2018-009 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 150 | 150 | None | ER/NR | SUNC | Cimarron 115kV Substation | DISIS STAGE
GEN-2018-013 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 74.1 | 11.83 | 532775 87TH 7 345 542977 CRAIG 7 345 1 | ER/NR | WERE | Abilene Energy Center-Northview 115kV Line | DISIS STAGE
GEN-2018-014 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 74.1 | 0 | Non-converged | ER/NR | KCPL | Holt County 345kV Substation | DISIS STAGE
GEN-2018-022 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 300 | 0 | Non-converged | ER/NR | KCPL | Mullen Creek 345kV Substation | DISIS STAGE
GEN-2018-030 | 03 CENTRAL | 20 | DIS-18-1 | Battery | 200 | 200 | None | ER | SPS | Lamar-Finney 345kV Substation | DISIS STAGE
GEN-2018-031 | 03 CENTRAL | 20 | DIS-18-1 | Battery | 50 | 0 | Non-converged | ER | KCPL | Blue Valley 161kV Substation | DISIS STAGE
GEN-2018-032 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 310 | 0 | Non-converged | ER | WERE | Neosho 345kV Substation | DISIS STAGE
GEN-2018-038 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 203.4 | 0 | Non-converged | ER/NR | KCPL | Sibley 345kV substation | DISIS STAGE
GEN-2018-040 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 100 | 0 | Non-converged | ER/NR | KCPL | Sibley - Overton 345kV Line Break | DISIS STAGE
GEN-2018-041 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 400 | 0 | Non-converged | ER/NR | KCPL | Sibley - Overton 345kV Line Break | DISIS STAGE
GEN-2018-042 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 300 | 0 | Non-converged | ER/NR | KCPL | Sibley - Overton 345kV Line Break | DISIS STAGE
GEN-2018-049 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 120 | 120 | None | ER/NR | SUNC | Thistle 345kV Substation | DISIS STAGE
GEN-2018-053 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 100 | 15.96 | 532775 87TH 7 345 542977 CRAIG 7 345 1 | ER/NR | WERE | Kelly 161kV Substation | DISIS STAGE
GEN-2018-054 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 120 | 0 | Non-converged | ER/NR | KCPL | KC South - N. Raymore 161kV Line | DISIS STAGE
GEN-2018-057 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 203.4 | 203.4 | None | ER/NR | WERE | Gordon Evans 138kV | DISIS STAGE
GEN-2018-058 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 252 | 0 | Non-converged | ER/NR | WERE | Stranger Creek 345kV | DISIS STAGE
GEN-2018-059 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 252 | 0 | Non-converged | ER/NR | WERE | Stranger Creek 345kV | DISIS STAGE
GEN-2018-061 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 50 | 7.98 | 532775 87TH 7 345 542977 CRAIG 7 345 1 | ER/NR | WERE | Kelly 161kV Substation | DISIS STAGE
GEN-2018-062 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 75.6 | 0 | Non-converged | ER/NR | KACY | Nearman 161kV substation | DISIS STAGE
GEN-2018-003 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 150 | 111.98 | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 | ER/NR | AEPW | North Boston-Bann 138kV Line | DISIS STAGE
GEN-2018-011 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery | 74.1 | 74.1 | None | ER/NR | WFEC | Dover 138 kV Switching Station | DISIS STAGE
GEN-2018-021 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 74.1 | 74.1 | None | ER/NR | AEPW | Chisholm-Gracemont 345kV Line | DISIS STAGE
GEN-2018-024 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery | 100 | 100 | None | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | DISIS STAGE
GEN-2018-026 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery | 100 | 100 | None | ER | OKGE | Mustang 138kV Substation | DISIS STAGE
GEN-2018-027 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery | 100 | 53.8242 | 509776 52DELTP4 138 509800 36LEWIS4 138 1 | ER | OKGE | Tulsa Power Station 38kV Substation | DISIS STAGE
GEN-2018-028 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery | 200 | 200 | None | ER | OKGE | Tulsa North 138kV Substation | DISIS STAGE
GEN-2018-029 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery | 100 | 100 | None | ER | OKGE | Horseshoe Lake 138kV Substation | DISIS STAGE
GEN-2018-048 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 300 | 300 | None | ER/NR | OKGE | Pecan Creek 345kV Substation | DISIS STAGE
GEN-2018-050 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 200 | 200 | None | ER/NR | AEPW | Longwood 345kV Substation | DISIS STAGE
GEN-2018-055 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 252 | 252 | None | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | DISIS STAGE
GEN-2018-004 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 74.99 | 74.99 | None | ER | SPS | T14 Circuit 115kV line | DISIS STAGE
GEN-2018-015 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 252 | 252 | None | ER/NR | SPS | Tuco-Oklaunion 345kV Line | DISIS STAGE
GEN-2018-051 | 05 SOUTHWEST | 20 | DIS-18-1 | Battery | 35 | 35 | None | ER/NR | OKGE | Pecan Creek 345kV | DISIS STAGE
GEN-2018-052 | 05 SOUTHWEST | 20 | DIS-18-1 | Battery | 70 | 70 | None | ER/NR | SPS | Roadrunner 115kV Substation | DISIS STAGE
GEN-2007-043 | 04 SOUTHEAST | 2 | ICS1 | Wind | 200 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 04 SOUTHEAST | 2 | ICS1 | Wind | 0.3 |  |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-018 | 03 CENTRAL | 2 | ICS1 | Wind | 250 |  |  | ER | SPS | Finney 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | 03 CENTRAL | 2 | ICS1 | Wind | 68.8 |  |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-006GIA-27 | 04 SOUTHEAST | 8 | PQ | Wind | 150 |  |  | ER | AECI | Remington 138kV
GEN-2006-002 | 04 SOUTHEAST | 8 | PQ | Wind | 1.8 |  |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 05 SOUTHWEST | 8 | PQ | Wind | 290 |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039M | 03 CENTRAL | 8 | PQ | Wind | 1 |  |  | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 03 CENTRAL | 8 | PQ | Wind | 3 |  |  | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 CENTRAL | 8 | PQ | Wind | 1 |  |  | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-021N | 02 NEBRASKA | 8 | PQ | Wind | 15 |  |  | ER | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
NPPDBuffaloCountySolar | 02 NEBRASKA | 8 | PQ | Solar | 10 |  |  | ER | NPPD | Kearney Northeast
NPPDBurtCountyWind | 02 NEBRASKA | 8 | PQ | Wind | 20 |  |  | ER | NPPD | Tekamah & Oakland 115kV
GEN-2008-051 | 05 SOUTHWEST | 3 | DIS-09-1 | Wind | 1 |  |  | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 200.1 |  |  | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 0.4 |  |  | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 13.13 |  |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 358.8 |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-022 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 21.65 |  |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 59.2 |  |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-040 | 04 SOUTHEAST | 5 | DIS-10-2 | Wind | 1.8 |  |  | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 0.3 |  |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-010 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 100.8 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 175 |  |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 165.6 |  |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 299 |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-054 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 2 |  |  | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-037 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 6.6 |  |  | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 04 SOUTHEAST | 8 | DIS-12-1 | Wind | 40.8 |  |  | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-006 | 03 CENTRAL | 8 | DIS-12-1 | Steam | 22.5 |  |  | ER | SUNC | Tap Hugoton - Rolla 69kV
GEN-2012-033 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 0.72 |  |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 SOUTHWEST | 9 | DIS-12-2 | Wind | 18.15 |  |  | ER | SPS | FE-Clovis Interchange 115kV
GEN-2012-024 | 03 CENTRAL | 9 | DIS-12-2 | Wind | 1.8 |  |  | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-002 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 |  |  | ER | SPS | FE Tucumcari 115kV
ASGI-2013-003 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 |  |  | ER | SPS | FE Clovis 115kV
GEN-2013-008 | 02 NEBRASKA | 10 | DIS-13-1 | Wind | 1.2 |  |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-002 | 02 NEBRASKA | 10 | DIS-13-1 | Wind | 50.6 |  |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2013-005 | 05 SOUTHWEST | 11 | DIS-13-2 | Wind | 1.65 |  |  | ER | SPS | FE Clovis 115kV
GEN-2013-019 | 02 NEBRASKA | 11 | DIS-13-2 | Wind | 73.6 |  |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-005 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 5.67 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-002 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 10.53 |  |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 CENTRAL | 12 | DIS-14-1 | Wind | 200.6 |  |  | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-004 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 3.96 |  |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 0.11 |  |  | ER/NR | LES | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-057 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 249.9 |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 1 |  |  | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 249.35 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-040 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 44 |  |  | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 30 |  |  | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-025 | 03 CENTRAL | 13 | DIS-14-2 | Wind | 2.42 |  |  | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-021 | 03 CENTRAL | 13 | DIS-14-2 | Wind | 300 |  |  | ER/NR | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 10.22 |  |  | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 SOUTHEAST | 14 | DIS-15-1 | Solar | 120 |  |  | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-024 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 11.73 |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 13.44 |  |  | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-001 | 03 CENTRAL | 14 | DIS-15-1 | Thermal | 6.13 |  |  | ER | SUNC | Ninnescah 115kV
GEN-2015-005 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 200.11 |  |  | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-023 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 300.72 |  |  | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-045 | 04 SOUTHEAST | 15 | DIS-15-2 | Battery | 20 |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-092 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 250 |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-048 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 200 |  |  | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-057 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 100.65 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-047 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 2.17 |  |  | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-062 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 4.5 |  |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-093 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 250 |  |  | ER | OKGE | Gracemont 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-063 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 0.75 |  |  | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-055 | 04 SOUTHEAST | 15 | DIS-15-2 | Solar | 40 |  |  | ER | WFEC | Erick 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-090 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 11.73 |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-069 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 0.75 |  |  | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 300 |  |  | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-066 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 248.4 |  |  | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-088 | 02 NEBRASKA | 15 | DIS-15-2 | Wind | 300 |  |  | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 5 |  |  | ER/NR | WAPA | Nelson 115kV
GEN-2007-020IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 16 |  |  | ER/NR | BEPC-SPP | Nelson 115kV
GEN-2005-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 |  |  | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2006-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 |  |  | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2009-026IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 3.5 |  |  | ER/NR | BEPC-SPP | Dickenson-Heskett 230kV
GEN-2009-018IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 |  |  | ER | BEPC-SPP | Groton 115kV
GEN-2007-017IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 202 |  |  | ER/NR | OPPD | Ft Thompson-Grand Island 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-018IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 198 |  |  | ER/NR | OPPD | Ft Thompson-Grand Island 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 34 |  |  | ER/NR | BEPC-SPP | Wessington Springs 230kV
GEN-2006-002IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 2 |  |  | ER/NR | WAPA | Wessington Springs 230kV
MPC02100 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.75 |  |  | ER | OTP | Center - Mandan 230 kV
GEN-2006-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 |  |  | ER/NR | XEL | Marshall 115kV
GEN-2014-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Gas | 11.72 |  |  | ER/NR | BEPC-SPP | Williston 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-020AIS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.4 |  |  | ER/NR | WAPA | Tripp Junction 115kV
ASGI-2016-005NWE205 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.2 |  |  | ER | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.2 |  |  | ER | WAPA | Kimball 69kV
GEN-2016-051 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 9.8 |  |  | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-009 | 03 CENTRAL | 16 | DIS-16-1 | Steam Turbine | 29 |  |  | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-071 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200.1 |  |  | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-036 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 303.6 |  |  | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
PQOKGEMustang | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 287 |  |  | ER | OKGE | MUSTANG4
GEN-2016-030 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 100 |  |  | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-032 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 |  |  | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 |  |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 |  |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 1.5 |  |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-082 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 200 |  |  | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-095 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 176 |  |  | ER | WFEC | Tap Mooreland - Knob Hill 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-061 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.7 |  |  | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-020 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 150 |  |  | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-070 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 5.3 |  |  | ER | SPS | Martin 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-004 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 10 |  |  | ER | SPS | Palo Duro 115kV
GEN-2016-016 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 78.2 |  |  | ER | MIDW | North Kinsley 115 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-073 | 03 CENTRAL | 16 | DIS-16-1 | WIND | 220 |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-003 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 248.4 |  |  | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-046 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 299 |  |  | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-050 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 250.7 |  |  | ER | NPPD | Axtell â€“ Post Rock 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-063 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 |  |  | ER/NR | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-021 | 02 NEBRASKA | 16 | DIS-16-1 | WIND | 300 |  |  | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-043 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 230 |  |  | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-007 | 01 NORTH | 16 | DIS-16-1 | Wind | 100.05 |  |  | ER | WAPA | Valley City 115 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-075 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 50 |  |  | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA PENDING
GEN-2016-004 | 01 NORTH | 16 | DIS-16-1 | Wind | 202 |  |  | ER/NR | WAPA | Basin Electric 230 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-133 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-134 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-137 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-138 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-139 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-141 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-142 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-145 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-146 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-132 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 6.12 |  |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-128 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 176 |  |  | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-131 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 2.5 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 172.5 |  |  | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-102 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 150.9 |  |  | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-118 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 288 |  |  | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-010 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 90 |  |  | ER | SPS | TEXAS_CNTY 3
GEN-2016-177 | 05 SOUTHWEST | 17 | DIS-16-2 | Gas Turbine | 17 |  |  | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-121 | 05 SOUTHWEST | 17 | DIS-16-2 | Solar | 110 |  |  | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-160 | 03 CENTRAL | 17 | DIS-16-2 | Battery | 20 |  |  | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-149 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-174 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-176 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-162 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 252 |  |  | ER | WERE | Benton 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-163 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 252 |  |  | ER | WERE | Benton 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-153 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 134 |  |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-115 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 300 |  |  | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-157 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 252 |  |  | ER | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-158 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 252 |  |  | ER | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-091 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 303.6 |  |  | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-095 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 200 |  |  | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA PENDING
GEN-2016-094 | 01 NORTH | 17 | DIS-16-2 | Wind | 200 |  |  | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-097 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 |  |  | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA PENDING
GEN-2016-119 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 600 |  |  | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-111 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-167 | 04 SOUTHEAST | 17 | DIS-16-2 | Solar | 73.5 |  |  | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-074 | 02 NEBRASKA | 17 | DIS-16-2 | Wind | 200 |  |  | ER | NPPD | Sweetwater 345kV | IA PENDING
GEN-2016-087 | 01 NORTH | 17 | DIS-16-2 | Wind | 98.9 |  |  | ER | WAPA | Bismark-Glenham 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-036 | 01 NORTH | 17 | DIS-16-2 | Wind | 44.6 |  |  | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-147 | 02 NEBRASKA | 17 | DIS-16-2 | Solar | 40 |  |  | ER | NPPD | Sidney 115 kV Sub | IA PENDING
GEN-2016-130 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 |  |  | ER | WAPA | Leland Olds 345 kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2017-006GIA-53 | 03 CENTRAL | 16.5 | Dis-16-2-PQ | Wind | 238 |  |  | ER/NR | AECI | 5MARYVL
GEN-2017-076 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 52.2 |  |  | ER | AEPW | Chamber Springs 161kV sub | FACILITY STUDY STAGE
GEN-2017-057 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 |  |  | ER | AEPW | Hosston 69kV | FACILITY STUDY STAGE
GEN-2017-074 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 |  |  | ER | AEPW | Pryor Junction 138kV sub | FACILITY STUDY STAGE
GEN-2017-033 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 200 |  |  | ER/NR | AEPW | Oklaunion 345 kV sub | FACILITY STUDY STAGE
GEN-2017-073 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 |  |  | ER | GRDA | Dry Gulch 161kV sub | FACILITY STUDY STAGE
GEN-2017-061 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 101.5 |  |  | ER/NR | GRDA | GRDA1 to CLARMR 5 161kV line | FACILITY STUDY STAGE
GEN-2017-071 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 |  |  | ER | OKGE | Greenwood 138kV sub | FACILITY STUDY STAGE
GEN-2017-072 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 52.2 |  |  | ER | OKGE | Greenwood 138kV sub | FACILITY STUDY STAGE
GEN-2017-027 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 140 |  |  | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | FACILITY STUDY STAGE
GEN-2017-023 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 85 |  |  | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | FACILITY STUDY STAGE
GEN-2017-100 | 05 SOUTHWEST | 18 | DIS-17-1 | Solar | 102.6 |  |  | ER/NR | SPS | Texas County 115kV | FACILITY STUDY STAGE
GEN-2017-047 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 102 |  |  | ER/NR | SPS | Cole 115kV | FACILITY STUDY STAGE
GEN-2017-086 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 150 |  |  | ER | WERE | Viola 345kV | FACILITY STUDY STAGE
GEN-2017-068 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 103.5 |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | FACILITY STUDY STAGE
GEN-2017-018 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 189 |  |  | ER/NR | SUNC | Thistle 345 kV sub | FACILITY STUDY STAGE
GEN-2017-011 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 151.8 |  |  | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | FACILITY STUDY STAGE
GEN-2016-037 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 300 |  |  | ER | AEPW | Chisholm-Gracemont 345kV | FACILITY STUDY STAGE
GEN-2017-075 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 |  |  | ER | OKGE | Hugo-Sunnyside 345 kV | FACILITY STUDY STAGE
GEN-2017-004 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 201.6 |  |  | ER | SUNC | Elm Creek - Summit 345 kV | FACILITY STUDY STAGE
GEN-2017-005 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 190 |  |  | ER | WERE | Marmaton - Litchfield 161 kV | FACILITY STUDY STAGE
GEN-2017-021 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 200 |  |  | ER/NR | SUNC | Post Rock - Spearville 345 kV | FACILITY STUDY STAGE
GEN-2017-099 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 150 |  |  | ER/NR | SUNC | Post Rock - Spearville 345 kV | FACILITY STUDY STAGE
GEN-2017-022 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 65 |  |  | ER/NR | WERE | Altoona- NE Parson 138kV | FACILITY STUDY STAGE
GEN-2017-032 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 200 |  |  | ER | SPS | Finney - Lamar 345 kV | FACILITY STUDY STAGE
GEN-2017-036 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 100 |  |  | ER | WFEC | Snyder - Cache 138 kV | FACILITY STUDY STAGE
GEN-2017-040 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200.1 |  |  | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | FACILITY STUDY STAGE
GEN-2017-092 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 |  |  | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | FACILITY STUDY STAGE
GEN-2017-077 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 |  |  | ER | AEPW | Explorer Claremore Tap EXCLART4 | FACILITY STUDY STAGE
GEN-2017-094 | 01 NORTH | 18 | DIS-17-1 | Wind | 200 |  |  | ER | WAPA | Fort Thompson-Huron 230 kV | FACILITY STUDY STAGE
GEN-2017-097 | 01 NORTH | 18 | DIS-17-1 | Solar | 128 |  |  | ER | WAPA | Underwood 115 kV Sub | FACILITY STUDY STAGE
GEN-2017-048 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 |  |  | ER | WAPA | Neset 230 kV Substation | FACILITY STUDY STAGE
GEN-2017-014 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 |  |  | ER | WAPA | Philip Tap 230 kV | FACILITY STUDY STAGE
GEN-2017-010 | 01 NORTH | 18 | DIS-17-1 | Wind | 200.1 |  |  | ER | WAPA | Rhame 230 kV Sub | FACILITY STUDY STAGE
BEPCNDPW1 | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 5 |  |  | ER | BEPC-SPP | NELSON 7
GEN-2017-140 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 160 |  |  | ER/NR | AEPW | Clarksville 345kV Switching Station | DISIS STAGE
GEN-2017-141 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 241.7 |  |  | ER/NR | AEPW | Clarksville 345kV Switching Station | DISIS STAGE
GEN-2017-213 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar/Battery | 300 |  |  | ER | AEPW | Clarksville 345kV Substation | DISIS STAGE
GEN-2017-156 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 234 |  |  | ER/NR | AEPW | Pittsburg 345kV Substation | DISIS STAGE
GEN-2017-157 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 202 |  |  | ER/NR | AEPW | Pittsburg 345kV Substation | DISIS STAGE
GEN-2017-164 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 |  |  | ER/NR | OKGE | Woodring 345kV Substation | DISIS STAGE
GEN-2017-178 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery | 52 |  |  | ER/NR | OKGE | Woodring 345kV Substation | DISIS STAGE
GEN-2017-150 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 |  |  | ER/NR | OKGE | Minco 345kV | DISIS STAGE
GEN-2017-233 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 215 |  |  | ER/NR | OKGE | Minco 345kV | DISIS STAGE
GEN-2017-149 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 258 |  |  | ER/NR | OKGE | Johnson County 345kV Substation | DISIS STAGE
GEN-2017-154 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 255 |  |  | ER/NR | OKGE | Johnson County 345kV Substation | DISIS STAGE
GEN-2017-152 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 252 |  |  | ER/NR | OKGE | McClain 138kV | DISIS STAGE
GEN-2017-153 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 253 |  |  | ER/NR | OKGE | McClain 138kV | DISIS STAGE
GEN-2017-168 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 |  |  | ER/NR | OKGE | McClain 138kV | DISIS STAGE
GEN-2017-169 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery | 52 |  |  | ER/NR | OKGE | McClain 138kV | DISIS STAGE
GEN-2017-132 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 400 |  |  | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-133 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 200 |  |  | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-134 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 250 |  |  | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-137 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 295 |  |  | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-240 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 202 |  |  | ER/NR | OKGE | Bristow 138kV Substation | DISIS STAGE
GEN-2017-166 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 |  |  | ER/NR | OKGE | Sunnyside 345kV | DISIS STAGE
GEN-2017-167 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery | 52 |  |  | ER/NR | OKGE | Sunnyside 345kV | DISIS STAGE
GEN-2017-232 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 52.2 |  |  | ER/NR | OKGE | Brown 138kV Substation | DISIS STAGE
GEN-2017-155 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 300 |  |  | ER/NR | OKGE | Muskogee 345kV Substation | DISIS STAGE
GEN-2017-231 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 |  |  | ER/NR | OKGE | Branch 161kV Substation | DISIS STAGE
GEN-2017-203 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar/Battery | 210 |  |  | ER | OKGE | Renfrow 345kV Substation | DISIS STAGE
GEN-2017-230 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 |  |  | ER/NR | OKGE | Tryon 138kV Substation | DISIS STAGE
GEN-2017-117 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery | 19.8 |  |  | ER/NR | WFEC | El Reno SW 138kV | DISIS STAGE
GEN-2017-176 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar/Wind | 300 |  |  | ER/NR | SPS | Newhart 230kV Substation | DISIS STAGE
GEN-2017-217 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 300 |  |  | ER/NR | SPS | Plant X 230kV Substation | DISIS STAGE
GEN-2017-158 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 265 |  |  | ER | SPS | Tolk 230kV Substation | DISIS STAGE
GEN-2017-239 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 300 |  |  | ER | SPS | Mahoney 230kV Substation | DISIS STAGE
GEN-2017-187 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 150 |  |  | ER | SPS | Sulphur Springs 115kV Substation | DISIS STAGE
GEN-2017-102 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 67.5 |  |  | ER | SPS | Crossroads 345kV | DISIS STAGE
GEN-2017-123 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 180 |  |  | ER/NR | WERE | Stranger Creek 345kV | DISIS STAGE
GEN-2017-125 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 252 |  |  | ER/NR | WERE | Swissvale 345kV | DISIS STAGE
GEN-2017-128 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 202 |  |  | ER/NR | WERE | Swissvale 345kV | DISIS STAGE
GEN-2017-142 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 170 |  |  | ER/NR | WERE | Swissvale 345kV Station | DISIS STAGE
GEN-2017-191 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 |  |  | ER/NR | WERE | Swissvale 345kV | DISIS STAGE
GEN-2017-192 | 03 CENTRAL | 19 | DIS-17-2 | Battery | 52 |  |  | ER/NR | WERE | Swissvale 345kV | DISIS STAGE
GEN-2017-220 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 |  |  | ER/NR | WERE | Buffalo Flats 345kV Substation | DISIS STAGE
GEN-2017-221 | 03 CENTRAL | 19 | DIS-17-2 | Battery | 152 |  |  | ER/NR | WERE | Buffalo Flats 345kV Substation | DISIS STAGE
GEN-2017-193 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 |  |  | ER/NR | WERE | Tecumseh 230kV Substation | DISIS STAGE
GEN-2017-194 | 03 CENTRAL | 19 | DIS-17-2 | Battery | 52 |  |  | ER/NR | WERE | Tecumseh 230kV Substation | DISIS STAGE
GEN-2017-121 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 200 |  |  | ER/NR | WERE | Sumner 138kV | DISIS STAGE
GEN-2017-179 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 222 |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | DISIS STAGE
GEN-2017-226 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | DISIS STAGE
GEN-2017-227 | 03 CENTRAL | 19 | DIS-17-2 | Battery | 201.6 |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | DISIS STAGE
GEN-2017-119 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 180 |  |  | ER | SUNC | Elm Creek 345kV substation | DISIS STAGE
GEN-2017-186 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 100 |  |  | ER | KCPL | KC South-N. Raymore 161 kV | DISIS STAGE
ASGI-2017-014 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 40 |  |  | ER/NR | KCPL | Post Oak 69 kV
GEN-2017-115 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 244 |  |  | ER | KCPL | Holt County 345 kV | DISIS STAGE
GEN-2017-195 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 500.4 |  |  | ER/NR | KCPL | West Gardner 345kV | DISIS STAGE
GEN-2017-196 | 03 CENTRAL | 19 | DIS-17-2 | Battery | 128 |  |  | ER/NR | KCPL | West Gardner 345kV | DISIS STAGE
GEN-2017-147 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 252 |  |  | ER/NR | KCPL | Stilwell 345kV | DISIS STAGE
GEN-2017-228 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 302.4 |  |  | ER/NR | KCPL | Stilwell 345kV Substation | DISIS STAGE
GEN-2017-229 | 03 CENTRAL | 19 | DIS-17-2 | Battery | 76 |  |  | ER/NR | KCPL | Stilwell 345kV Substation | DISIS STAGE
GEN-2017-224 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 302.4 |  |  | ER/NR | KCPL | Craig 345kV Substation | DISIS STAGE
GEN-2017-225 | 03 CENTRAL | 19 | DIS-17-2 | Battery | 76 |  |  | ER/NR | KCPL | Craig 345kV Substation | DISIS STAGE
GEN-2017-188 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 130 |  |  | ER | EMDE | Asbury 161 kV | DISIS STAGE
GEN-2017-148 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 202 |  |  | ER/NR | EMDE | Joplin 161kV sub | DISIS STAGE
GEN-2017-131 | 03 CENTRAL | 19 | DIS-17-2 | Battery | 29.6 |  |  | ER/NR | WERE | Altoona- NE Parson 138kV | DISIS STAGE
GEN-2017-201 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 250 |  |  | ER/NR | NPPD | Hoskins 345kV Substation | DISIS STAGE
GEN-2017-210 | 02 NEBRASKA | 19 | DIS-17-2 | Solar/Battery | 310 |  |  | ER | NPPD | McCool 345kV Substation | DISIS STAGE
GEN-2017-144 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 200 |  |  | ER | WAPA | Holt County 345kV | DISIS STAGE
GEN-2017-181 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 300 |  |  | ER/NR | NPPD | Tobias 345kV Substation | DISIS STAGE
GEN-2017-182 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 128 |  |  | ER/NR | NPPD | Tobias 345kV Substation | DISIS STAGE
GEN-2017-198 | 02 NEBRASKA | 19 | DIS-17-2 | Battery | 11.64 |  |  | ER | OPPD | Jones St. No 1201 69kV substation | DISIS STAGE
GEN-2017-113 | 01 NORTH | 19 | DIS-17-2 | Wind | 119 |  |  | ER | WAPA | Martin 115kV | DISIS STAGE
GEN-2017-222 | 01 NORTH | 19 | DIS-17-2 | Wind | 180 |  |  | ER | WAPA | Denison 230kV Substation | DISIS STAGE
GEN-2017-237 | 01 NORTH | 19 | DIS-17-2 | Wind | 150 |  |  | ER | WAPA | Snake Butte 115kV Substation | DISIS STAGE
GEN-2017-214 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 |  |  | ER/NR | WAPA | Logan 230kV Substation | DISIS STAGE
GEN-2017-215 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 |  |  | ER/NR | WAPA | Logan 230kV Substation | DISIS STAGE
GEN-2017-216 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 |  |  | ER/NR | WAPA | Logan 230kV Substation | DISIS STAGE
GEN-2017-235 | 01 NORTH | 19 | DIS-17-2 | Wind | 50 |  |  | ER/NR | WAPA | Logan 230kV Substation | DISIS STAGE
GEN-2017-236 | 01 NORTH | 19 | DIS-17-2 | Wind | 50 |  |  | ER/NR | WAPA | Logan 230kV Substation | DISIS STAGE
GEN-2017-199 | 01 NORTH | 19 | DIS-17-2 | Battery | 202 |  |  | ER/NR | WAPA | Groton 345kV Substation | DISIS STAGE
GEN-2017-200 | 01 NORTH | 19 | DIS-17-2 | Wind | 302 |  |  | ER/NR | WAPA | Groton 345kV Substation | DISIS STAGE
GEN-2017-120 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 260 |  |  | ER | WERE | Abilene Energy Center-Northview 115kV | DISIS STAGE
GEN-2017-114 | 01 NORTH | 19 | DIS-17-2 | Wind | 450 |  |  | ER | WAPA | Chappelle Creek - Leland Olds 345kV | DISIS STAGE
GEN-2017-146 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 151.8 |  |  | ER | SPS | Deaf Smith-Plant X 230kV | DISIS STAGE
GEN-2017-209 | 03 CENTRAL | 19 | DIS-17-2 | Solar/Battery | 300 |  |  | ER | KCPL | LaCygne - Neosho 345kV | DISIS STAGE
GEN-2017-171 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 150 |  |  | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | DISIS STAGE
GEN-2017-172 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 |  |  | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | DISIS STAGE
GEN-2017-173 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 |  |  | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | DISIS STAGE
GEN-2017-108 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 |  |  | ER/NR | KCPL | Stillwell - Clinton 161kV Line | DISIS STAGE
GEN-2017-183 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 400 |  |  | ER/NR | KCPL | Nashua-St. Joe 345kV | DISIS STAGE
GEN-2017-184 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 |  |  | ER/NR | KCPL | Nashua-St. Joe 345kV | DISIS STAGE
GEN-2017-202 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 200 |  |  | ER/NR | SWPA | New Madrid - Sikeston 161kV | DISIS STAGE
GEN-2017-116 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 192.5 |  |  | ER | SPS | Oasis - Pleasant Hill 230kV | DISIS STAGE
GEN-2017-234 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 115 |  |  | ER | NPPD | Spalding to North Loup 115kV | DISIS STAGE
GEN-2017-111 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 152 |  |  | ER | KCPL | Clinton â€“ Stilwell 161 kV Line Tap | DISIS STAGE
GEN-2017-112 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 200 |  |  | ER | KCPL | Clinton â€“ Stilwell 161 kV Line Tap | DISIS STAGE
GEN-2017-105 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 75 |  |  | ER/NR | OPPD | Tekamah - Raun 161 kV Line | DISIS STAGE
GEN-2017-218 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 600 |  |  | ER/NR | SPS | Tolk-Plant X 230kV Line | DISIS STAGE
GEN-2017-151 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 300 |  |  | ER | SPS | TUCO-Oklaunion 345kV | DISIS STAGE
GEN-2017-175 | 01 NORTH | 19 | DIS-17-2 | Wind | 300 |  |  | ER | WAPA | Vfodnes-Utica Jct. 230kV | DISIS STAGE
GEN-2017-185 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 200 |  |  | ER/NR | OKGE | Viola - Hunters 345kV | DISIS STAGE
GIA-83 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 1031 |  |  | ER/NR | AECI | McCredie 345 kV
GIA-84 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 200.62 |  |  | ER | AECI | New Madrid 345 kV
GIA-85 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar/Battery | 436 |  |  | ER/NR | AECI | Morgan 345 kV | DISIS STAGE
GIA-86 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 103.68 |  |  | ER/NR | AECI | Thomas Hill 69 kV
GIA-88 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 92.09 |  |  | ER/NR | AECI | Eudora 69 kV
GIA-90 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 108 |  |  | ER/NR | AECI | Montgomery City 161 kV
GIA-91 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 104.4 |  |  | ER/NR | AECI | Sedalia 69 kV
GIA-92 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 170 |  |  | ER/NR | AECI | Harrisburg - Higbee 161 kV
GIA-93 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 100 |  |  | ER/NR | AECI | Palmyra 161 kV
J926 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 101.28 |  |  | ER | XEL | Pine Lake - Apple River 161 kV Line
J801 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 74 |  |  | ER | DPC | Crystal Cave-Rock Elm 161kV line tap | DISIS STAGE
J545 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 110 |  |  | ER | XEL | Buffalo 115kV Substation
J874 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 150 |  |  | ER/NR | XEL | Fenton - Chanarambie 115kV Line | DISIS STAGE
J803 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 32.5 |  |  | ER | XEL | Tracy 69 kV line | DISIS STAGE
J722 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 200 |  |  | ER | OTP | Big Stone South 230kV Substation
IR24 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 56 |  |  | ER/NR | ALTW | New 69kV substation near Prescott REC
IR32 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 56 |  |  | ER/NR | ALTW | Murray Junction 69 kV substation
J836 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 200 |  |  | ER | ALTW | Ledyard 345kV Substation
J877 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Solar | 250 |  |  | ER/NR | MEC | Obrien - Kossuth 345kV Line (J529 & J590 New Substation) | DISIS STAGE
J897 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 190 |  |  | ER | GRE | Prairie - Ramsey 230 kV line
J898 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 100 |  |  | ER | DPC | Rice - Beaver Creek 161kV line tap
GIA-94 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 225 |  |  | ER/NR | AECI | Jasper-Morgan 345 kV
GIA-95 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 252 |  |  | ER/NR | AECI | Jasper-Morgan 345 kV
J1205 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 125 |  |  | ER | CLEC | Centennial - West Bay 138 kV | IA PENDING
J1208 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  | ER/NR | AMIL | Muddy - Crab Orchard 138kV Line | IA PENDING
J1209 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  | ER/NR | AMIL | Muddy - Crab Orchard 138kV Line | IA PENDING
J1221 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | GRE | Wing River- Riverton 230kV line | IA PENDING
J1231 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 125 |  |  | ER/NR | BREC | Barkley - Caldwell 161kV Line | IA PENDING
J1241 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 165 |  |  | ER/NR | AMIL | West Mt Vernon - Xenia 345kV Line | IA PENDING
J1268 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | AMMO | Pike - Troy 161kV Line | IA PENDING
J1270 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 200 |  |  | ER | MEC | Kossuth - O'Brien 345 kV Line Tap | IA PENDING
J1281 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 75 |  |  | ER/NR | EES-EAI | Crossett - Monticello East 115 kV | IA PENDING
J1298 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | ALTW | Hayward - Murphy Creek 161kV Line | IA PENDING
J1303 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 95 |  |  | ER/NR | SIPC | Campbell Hill - Jackson 161kV Line | IA PENDING
J1306 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | AMIL | Commodore-Jordan 345kV Line | IA PENDING
J1352 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | AMMO | Spencer Creek - Montgomery 345kV Line | IA PENDING
J1365 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 169.4 |  |  | ER | ALTW | Traer 161-kV Substation | IA PENDING
J1373 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 95 |  |  | ER/NR | EES-EAI | Griffithville - Searcy Price 115 kV Line Tap | IA PENDING
J1395 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | XEL | Hawks Nest Lake - Lyon County 345 kV Line Tap | IA PENDING
J1413 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 235 |  |  | ER/NR | ALTW | Hazleton - Mitchell County 345 kV Line tap | IA PENDING
J1438 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | ALTW | Windsor - Hazelton 161kV Line | IA PENDING
J1442 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 105 |  |  | ER | EES | Rich (SHECO) - Livingston 138 kV | IA PENDING
J1456 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 300 |  |  | ER/NR | OTP | Harvey - Underwood 230 kV Line Tap | IA PENDING
J1474 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 180 |  |  | ER/NR | XEL | Pine Lake - Eagle Point 115kV Line | IA PENDING
J1488 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 500 |  |  | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | IA PENDING
J1490 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 1000 |  |  | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | IA PENDING
MPC03600 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER | OTP | Frontier-Wahpeton 230 kV Line | IA PENDING
MPC03700 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER | OTP | Frontier-Wahpeton 230 kV Line | IA PENDING
MPC03800 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 |  |  | ER/NR | OTP | Center-Prairie 345 kV Line
MPC03900 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 151.2 |  |  | ER/NR | OTP | Center-Prairie 345 kV Line
J1215 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 155 |  |  | ER/NR | EES-EAI | Stuttgart Ricuskey - Woodward 230 kV | IA PENDING
J1315 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 600 |  |  | ER | XEL | Lyon County - Cedar Mountain 345 kV Line Tap | IA PENDING
GIA-96 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 101.32 |  |  | ER | AECI | Stroud 138kV | IA PENDING
J1030 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER | EES | Poco - Menard 138 kV | IA PENDING
J1239 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER | EES | Rilla 115 kV | IA PENDING
J1436 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER | EES | Oak Ridge 115 kV | IA PENDING
J1258 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Battery | 50 |  |  | ER/NR | EES-EAI | KEO EHV 500 kV Substation | IA PENDING
J1415 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 250 |  |  | ER/NR | EES-EAI | KEO EHV 500 kV Substation | IA PENDING
J1060 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 450 |  |  | ER/NR | EES-EAI | West Memphis - Keo 500 kV | IA PENDING
J1125 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 135 |  |  | ER/NR | EES-EAI | Wynne South - Wynne East AECC 161 kV | IA PENDING
J1434 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | EES-EAI | J907 230kV Sub, Brinkley East - Aubrey 230 kV Line | IA PENDING
J1402 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Battery | 0 |  |  | ER/NR | EES-EAI | Cash - Newport AB161kV Line | IA PENDING
J1155 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | EES-EAI | Driver 230 kV | IA PENDING
J1007 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 180 |  |  | ER/NR | EES-EAI | Marion - Marked Tree 161 kV | IA PENDING
J1437 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Wind | 180 |  |  | ER/NR | EES-EAI | AECC Dry Creek 161 kV | IA PENDING
J1191 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 64 |  |  | ER/NR | CWLD | Bolstad 69 kV Substation | IA PENDING
J1025 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 290 |  |  | ER/NR | AMMO | Zachary - Maywood 345 kV Line Tap | IA PENDING
J1182 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 |  |  | ER/NR | AMMO | Zachary Substation 345 kV Bus | IA PENDING
J994 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | AMMO | Guthrie 161 kV Substation | IA PENDING
J1107 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | AMMO | Kelso - Lutesville 345 kV Line Tap | IA PENDING
J1145 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 |  |  | ER/NR | AMMO | Overton - (McCrede) - Montgomery 345 kV Line Tap | IA PENDING
J1087 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | AMMO | Miner - Kelso 161 kV Line Tap | IA PENDING
J1299 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 149 |  |  | ER/NR | AMMO | Miner - Kelso 161kV Line | IA PENDING
J976 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 300 |  |  | ER/NR | AMMO | Montgomery - Enon 345kV Line Tap | IA PENDING
J987 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | AMMO | Montgomery 161kV Substation | IA PENDING
J1034 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 225 |  |  | ER/NR | AMMO | Stoddard - Morley 161kV Line Tap | IA PENDING
J1213 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Hydro | 60 |  |  | ER/NR | AMMO | Taum Sauk 138kV Switchyard, Bus 1 & 2 | IA PENDING
J1026 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 380 |  |  | ER/NR | AMMO | Maywood - Spencer Creek 345 kV Line Tap | IA PENDING
J956 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | AMMO | Spencer Creek 345kV Substation | IA PENDING
J1311 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | AMIL | Fayetteville Bee Hollow Road 138 kV Substation | IA PENDING
J1216 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 185 |  |  | ER/NR | AMIL | Ashley 138 kV Substation | IA PENDING
J1202 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar/Battery | 68.4 |  |  | ER/NR | AMIL | Baldwin Plant 345kV Switchyard - Baldwin Unit 2 | IA PENDING
J1424 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER | CLEC | Cooper - Penton Road 230 kV | IA PENDING
J1072 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | XEL | Adams 345 kV Substation | IA PENDING
J967 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 150 |  |  | ER | XEL | Adams 345kV Substation | IA PENDING
J1169 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER | XEL | Grant 115 kV Substation | IA PENDING
J1312 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER/NR | XEL | Grant 115 kV Substation | IA PENDING
J1445 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | XEL | Mayhew Lake 115kV Substation | IA PENDING
J1045 | 01 NORTH | 19.5 | DIS-18-1-PQ | Battery | 20 |  |  | ER/NR | XEL | Fenton - Chanarambie 115kV Line Tap | IA PENDING
J1092 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | XEL | Three Lakes 115 kV Substation | IA PENDING
J1124 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | XEL | Byron 345kV Substation | IA PENDING
J1426 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | XEL | Benton County 115kV Substation | IA PENDING
J1485 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 |  |  | ER | OTP | Astoria 345 kV Substation (J493/J510) | IA PENDING
J1132 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER | ALTW | Creston East 69 kV Substation | IA PENDING
J1359 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Gas | 95 |  |  | ER/NR | ALTW | Oakridge 69 kV Substation | IA PENDING
J1164 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  | ER | ALTW | Magnolia 161 kV Substation | IA PENDING
J1325 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  | ER/NR | ALTW | Magnolia 161 kV substation | IA PENDING
J1181 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 200 |  |  | ER | ALTW | Hazleton - Mitchell county 345 kV line | IA PENDING
J1444 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | ALTW | Duane Arnold 345kV Substation | IA PENDING
J1313 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | ALTW | 161kV bus at Karma substation | IA PENDING
J1174 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 165 |  |  | ER/NR | ALTW | Ledyard - Colby 345 kV Line Tap | IA PENDING
J1175 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 165 |  |  | ER | ALTW | Ledyard - Colby 345kV Line Tap | IA PENDING
J1050 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 225 |  |  | ER/NR | ALTW | Doud Tap 161 kV Substation | IA PENDING
J982 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 300 |  |  | ER | MEC | Obrien County - Kossuth 345 kV Line Tap | IA PENDING
MPC04000 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 300 |  |  | ER/NR | OTP | Square Butte 230 kV Substation
J1040 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 |  |  | ER/NR | MDU | Wishek Junction 230 kV Substation | IA PENDING
J1314 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | DPC | Apple River 161 kV Substation | IA PENDING
GIA-97 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 354.801 |  |  | ER/NR | AECI | New Madrid - Essex 345kV | IA PENDING
GIA-98 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 253.26 |  |  | ER/NR | AECI | New Madrid - St Francis 345kV | IA PENDING

## Constraints Summary
Group | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
03ALL | ERIS | Non-Converge | Non-Converge | 23SP, 26L, 26SP, 26WP | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV: | [7 empty] | Holt to Atchison 345 kV New Line Build (DISIS-2018-001)
03ALL | ERIS | Non-Converge | Non-Converge | 23SP, 26L, 26SP, 26WP | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1 | [7 empty] | Holt to Atchison 345 kV New Line Build (DISIS-2018-001)
03ALL | ERIS | Non-Converge | Non-Converge | 23SP, 26L, 26SP, 26WP | P12:345:GMO-OPPD:S3458-HOLT:::EHV: | [7 empty] | Holt to Atchison 345 kV New Line Build (DISIS-2018-001)
03ALL | ERIS | Non-Converge | Non-Converge | 23SP, 26L, 26SP, 26WP | P14:345:GMO-OPPD:S3458 REACTOR:::EHV: | [7 empty] | Holt to Atchison 345 kV New Line Build (DISIS-2018-001)
03ALL | ERIS | Non-Converge | Non-Converge | 23SP, 26L, 26SP, 26WP | P22:345:GMO-OPPD:S3458-HOLT:::EHV: | [7 empty] | Holt to Atchison 345 kV New Line Build (DISIS-2018-001)
03ALL | ERIS | Non-Converge | Non-Converge | 23SP, 26L, 26SP, 26WP | P23:345:OPPD:S3458-HOLT:::EHV: | [7 empty] | Holt to Atchison 345 kV New Line Build (DISIS-2018-001)
03ALL | ERIS | Non-Converge | Non-Converge | 23SP, 26L, 26SP, 26WP | P45:345:OPPD:S3455-S3761&T3:::EHV: | [7 empty] | Holt to Atchison 345 kV New Line Build (DISIS-2018-001)
03ALL | ERIS | Non-Converge | Non-Converge | 26L | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | [7 empty] | In-Line Reactor Adjustments
03ALL | ERIS | Non-Converge | Non-Converge | 23SP, 26SP | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | [7 empty] | In-Line Reactor Adjustments
03ALL | ERIS | Non-Converge | Non-Converge | 23SP, 26SP | P23:345:SUNC:HLC_BRK188:::EHV: | [7 empty] | In-Line Reactor Adjustments
03ALL | ERIS | Non-Converge | Non-Converge | 23SP, 26SP | P23:345:SUNC:HLC_BRK282:::EHV: | [7 empty] | In-Line Reactor Adjustments
03ALL | ERIS | Non-Converge | Non-Converge | 26L | P42:345:SPS:HITCHLAND:1R15:SLG:EHV: | [7 empty] | In-Line Reactor Adjustments
01ALL | ERIS | Thermal | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 | 23SP, 26SP, 26WP | 652455 ROBERTSCTY7 115 652522 SUMMIT-7 115 1 |  | 110 | 29.43 | 112.66 |  |  |  | Summit to Watertown 115 kV Rebuild (DISIS-2018-001)
02ALL | ERIS | Thermal | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 | 23SP, 26SP, 26WP | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z |  | 320 | 90.01 | 117.11 |  |  |  | Ogalala to Sidney TS 230 kV Rebuild (DISIS-2018-001)
02ALL | ERIS | Thermal | 640325 REDWILO3 345 762808 G18-045-TAP 345 1 | 23SP, 26WP | 640252 KEYSTON3 345 640325 REDWILO3 345 1 |  | 956 | 76.11 | 108.68 |  |  |  | Red Willow to GEN-2018-045 Tap 345 kV Rebuild (DISIS-2018-001)
02ALL | ERIS | Thermal | 659134 SIDNEY___TS4 230 659210 SIDNEY__-MB4 230 1 | 23SP | 640252 KEYSTON3 345 659425 SD.LS-KS-MB3 345 1 |  | 478 | 76.74 | 100.62 |  |  |  | Sidney TS to Sidney MB 230 kV Rebuild (DISIS-2018-001)
03ALL | ERIS | Thermal | 532772 STRANGR7 345 532775 87TH 7 345 1 | 23SP, 26SP, 26WP | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE |  | 1329 | 104.04 | 110.9 |  |  |  | Stranger to 87th St. 345 kV New Line Build (DISIS-2018-001)
03ALL | ERIS | Thermal | 532775 87TH 7 345 542977 CRAIG 7 345 1 | 23SP, 26SP, 26WP | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE |  | 1195 | 109.42 | 117.47 |  |  |  | Craig to 87th St. 345 kV Rebuild (DISIS-2018-001)
03ALL | ERIS | Thermal | 533244 JARBALO3 115 533249 LEC U4 3 115 1 | 26WP | P23:345:WERE:STRA_345-100:: |  | 118 | 79.9 | 105.72 |  |  |  | Stranger to 87th St. 345 kV New Line Build (DISIS-2018-001)
03ALL | ERIS | Thermal | 533370 NORTHST3 115 533371 NORTHVW3 115 1 | 23SP, 26SP, 26WP | P12:115:WERE:NVIE-SUMM_115:: |  | 68 | 106.97 | 131.99 |  |  |  | North St. to Northview 115 kV Ckt 1 Rebuild (DISIS-2018-001)
03ALL | ERIS | Thermal | 533370 NORTHST3 115 533371 NORTHVW3 115 2 | 23SP, 26SP, 26WP | P12:115:WERE:NVIE-SUMM_115:: |  | 68 | 106.97 | 131.99 |  |  |  | North St. to Northview 115 kV Ckt 2 Rebuild (DISIS-2018-001)
03ALL | ERIS | Thermal | 533370 NORTHST3 115 533376 SALINA 3 115 1 | 23SP, 26SP, 26WP | P12:115:WERE:NVIE-SUMM_115:: |  | 68 | 99.64 | 124.62 |  |  |  | North St. to Salina Main 115 kV Ckt 1 Rebuild (DISIS-2018-001)
03ALL | ERIS | Thermal | 533370 NORTHST3 115 533376 SALINA 3 115 2 | 23SP, 26SP, 26WP | P12:115:WERE:NVIE-SUMM_115:: |  | 68 | 99.64 | 124.62 |  |  |  | North St. to Salina Main 115 kV Ckt 2 Rebuild (DISIS-2018-001)
03ALL | ERIS | Thermal | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 | 23SP, 26SP, 26WP | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL |  | 440 | 60.58 | 139.23 |  |  |  | Sibley 345/161 kV New Transformer Build (DISIS-2018-001)
03ALL | ERIS | Thermal | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 | 23SP, 26SP, 26WP | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL |  | 418 | 56.52 | 147.41 |  |  |  | Sibley to Sibley 161 kV New Line Build (DISIS-2018-001)
03ALL | ERIS | Thermal | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 | 23SP, 26SP, 26WP | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 2 |  | 418 | 82.16 | 120.57 |  |  |  | Sibley to Sibley 161 kV Ckt 1 Rebuild (DISIS-2018-001)
04ALL | ERIS | Thermal | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 | 23SP, 26SP, 26WP | P23:345:AEPW:WELSH CB 11990 NBTB |  | 153 |  | 122.58 |  |  |  | N North Boston to GEN-2018-003-TAP 138 kV Rebuild (DISIS-2018-001)
04ALL | ERIS | Thermal | 509776 52DELTP4 138 509800 36LEWIS4 138 1 | 23SP, 26SP | 509783 R.S.S.-4 138 509849 ORU ETP4 138 1 |  | 278 |  | 116.29 |  |  |  | Delaware Tap to 36th&Lewis 138 kV Rebuild (DISIS-2018-001)
04ALL | ERIS | Thermal | 509776 52DELTP4 138 509811 T.S.E.-4 138 1 | 23SP, 26SP | 509783 R.S.S.-4 138 509849 ORU ETP4 138 1 |  | 278 |  | 103.55 |  |  |  | Delaware Tap to Tulsa SE 138 kV Rebuild (DISIS-2018-001)
04ALL | ERIS | Thermal | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 23SP | System Intact |  | 349 |  | 104.29 |  |  |  | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
04ALL | ERIS | Thermal | 515800 GRACMNT7 345 997832 GRACMNT3 _1 138 1 | 23SP | P42:345:OKGE:SB_CION7384:::: |  | 478 |  | 108.6 |  |  |  | None - FBD Modeling Issue at Minco - To Be Addressed in Phase 2
00NR | NRIS | Thermal | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 26SP | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1 |  | 426 | 88.41 | 102.86 |  |  |  | Crossroads to Yoakum 345 kV New Line (DISIS-2017-002)
00NR | NRIS | Thermal | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 | 23SP, 26SP, 26WP | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL |  | 281 | 20.23 | 115.66 |  |  |  | Sibley 345 kV Substation Reconfiguration (DISIS-2018-001)
00NR | NRIS | Thermal | 646209 S1209 5 161 646231 S1231 5 161 1 | 23SP, 26SP | P12:161:OPPD:S1209-S1231 CKT 2:::HV: |  | 238 | 87.48 | 106.21 |  |  |  | S1209 to S1231 161 kV Rebuild (DISIS-2018-001)

## Assigned Upgrade Costs
Gen Number | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF %
GEN-2018-043 | 00NR | TBD | NRIS | S1209 to S1231 161 kV Rebuild (DISIS-2018-001) | Current Study | Rebuild the existing S1209 to S1231 161 kV 3.27 mile line | 1487373.06 | 46.5% | 3198792 | 0.03877
GEN-2018-044 | 00NR | TBD | NRIS | S1209 to S1231 161 kV Rebuild (DISIS-2018-001) | Current Study | Rebuild the existing S1209 to S1231 161 kV 3.27 mile line | 1711418.94 | 53.5% | 3198792 | 0.04461
GEN-2018-015 | 00NR | TBD | NRIS | Crossroads to Yoakum 345 kV New Line (DISIS-2017-002) | Contingent | Build approximately 72 miles of new 345 kV line from Crossroads to Yoakum | 0 | 0% | 107970840 | 0.0284
GEN-2018-014 | 00NR | TBD | NRIS | Sibley 345 kV Substation Reconfiguration (DISIS-2018-001) | Current Study | Reconfigure the Sibley 345 kV substation to add a double breaker between the Sibley to Hawthorn 345 kV and Sibley to Pleasant Hill 345 kV lines | 220718.62 | 2.519% | 9213876 | 0.12525
GEN-2018-022 | 00NR | TBD | NRIS | Sibley 345 kV Substation Reconfiguration (DISIS-2018-001) | Current Study | Reconfigure the Sibley 345 kV substation to add a double breaker between the Sibley to Hawthorn 345 kV and Sibley to Pleasant Hill 345 kV lines | 894525.15 | 5.053% | 9213876 | 0.12538
GEN-2018-038 | 00NR | TBD | NRIS | Sibley 345 kV Substation Reconfiguration (DISIS-2018-001) | Current Study | Reconfigure the Sibley 345 kV substation to add a double breaker between the Sibley to Hawthorn 345 kV and Sibley to Pleasant Hill 345 kV lines | 1448886.31 | 16.54% | 9213876 | 0.29953
GEN-2018-040 | 00NR | TBD | NRIS | Sibley 345 kV Substation Reconfiguration (DISIS-2018-001) | Current Study | Reconfigure the Sibley 345 kV substation to add a double breaker between the Sibley to Hawthorn 345 kV and Sibley to Pleasant Hill 345 kV lines | 831218.24 | 9.486% | 9213876 | 0.34952
GEN-2018-041 | 00NR | TBD | NRIS | Sibley 345 kV Substation Reconfiguration (DISIS-2018-001) | Current Study | Reconfigure the Sibley 345 kV substation to add a double breaker between the Sibley to Hawthorn 345 kV and Sibley to Pleasant Hill 345 kV lines | 3324872.96 | 37.95% | 9213876 | 0.34952
GEN-2018-042 | 00NR | TBD | NRIS | Sibley 345 kV Substation Reconfiguration (DISIS-2018-001) | Current Study | Reconfigure the Sibley 345 kV substation to add a double breaker between the Sibley to Hawthorn 345 kV and Sibley to Pleasant Hill 345 kV lines | 2493654.72 | 28.46% | 9213876 | 0.34952
GEN-2018-007 | 01 - North | TBD | ERIS | Summit to Watertown 115 kV Rebuild (DISIS-2018-001) | Current Study | Rebuild the existing Summit to Watertown 115 kV 30.7 mile line | 1500000 | 100% | 1500000 | 0.49275
GEN-2018-003 | 04 - Southeast | 156178 |  | North Boston-Bann 138kV GEN-2018-003 Interconnection (TOIF) (AEPW) | Interconnection | Facilitate the interconnection of GEN-2018-003 | 1337068 | 100% | 1337068 | 1
GEN-2018-003 | 04 - Southeast | 156179 |  | North Boston-Bann 138kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-003 | 8857127 | 100% | 8857127 | 1
GEN-2018-004 | 05 - Southwest | 156242 |  | T14 Circuit 115kV GEN-2018-004 Interconnection (TOIF) | Interconnection | Facilitate the interconnection of GEN-2018-004 | 1107176 | 100% | 1107176 | 1
GEN-2018-004 | 05 - Southwest | 156243 |  | T14 Circuit 115kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-004 | 10430297 | 100% | 10430297 | 1
GEN-2018-007 | 01 - North | 156238 |  | Summit 115kV Substation GEN-2018-007 Interconnection (TOIF) (WAPA) | Interconnection | Facilitate the interconnection of GEN-2018-007 | 1565000 | 100% | 1565000 | 1
GEN-2018-007 | 01 - North | 156239 |  | Summit 115kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-007 | 1565000 | 100% | 1565000 | 1
GEN-2018-008 | 01 - North | 156037 |  | Groton-Leland Olds 345kV GEN-2018-008 Interconnection (TOIF) (BEPC) | Interconnection | Facilitate the interconnection of GEN-2018-008 | 2334054 | 100% | 2334054 | 1
GEN-2018-008 | 01 - North | 156038 |  | Groton-Leland Olds 345kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-008 | 20903079 | 100% | 20903079 | 1
GEN-2018-036 | 02 - Nebraska | TBD | ERIS | Ogalala to Sidney TS 230 kV Rebuild (DISIS-2018-001) | Current Study | Rebuild the existing Ogalala to Sidney TS 230 kV 68.9 mile line | 60829594.65 | 100% | 60829594.65 | 0.20286
GEN-2018-036 | 02 - Nebraska | TBD | ERIS | Sidney TS to Sidney MB 230 kV Rebuild (DISIS-2018-001) | Current Study | Rebuild the existing Sidney TS to Sidney MB 230 kV 4.0 mile line | 3534036 | 100% | 3534036 | 0.22359
GEN-2018-012 | 02 - Nebraska | TBD | ERIS | Red Willow to GEN-2018-045 Tap 345 kV Rebuild (DISIS-2018-001) | Current Study | Rebuild the Red Willow to GEN-2018-045 TAP 345 kV 56.0 mile line | 811911.03 | 1.266% | 64123197.32 | 0.06862
GEN-2018-036 | 02 - Nebraska | TBD | ERIS | Red Willow to GEN-2018-045 Tap 345 kV Rebuild (DISIS-2018-001) | Current Study | Rebuild the Red Willow to GEN-2018-045 TAP 345 kV 56.0 mile line | 4067585.22 | 6.343% | 64123197.32 | 0.12737
GEN-2018-045 | 02 - Nebraska | TBD | ERIS | Red Willow to GEN-2018-045 Tap 345 kV Rebuild (DISIS-2018-001) | Current Study | Rebuild the Red Willow to GEN-2018-045 TAP 345 kV 56.0 mile line | 33386325.61 | 52.07% | 64123197.32 | 0.38016
GEN-2018-046 | 02 - Nebraska | TBD | ERIS | Red Willow to GEN-2018-045 Tap 345 kV Rebuild (DISIS-2018-001) | Current Study | Rebuild the Red Willow to GEN-2018-045 TAP 345 kV 56.0 mile line | 24662908.96 | 38.46% | 64123197.32 | 0.38614
GEN-2018-056 | 02 - Nebraska | TBD | ERIS | Red Willow to GEN-2018-045 Tap 345 kV Rebuild (DISIS-2018-001) | Current Study | Rebuild the Red Willow to GEN-2018-045 TAP 345 kV 56.0 mile line | 1194466.5 | 1.863% | 64123197.32 | 0.07291
GEN-2018-009 | 03 - Central | 155901 |  | Cimarron 115kV Substation GEN-2018-009 Interconnection (TOIF) (SUNC) | Interconnection | Facilitate the interconnection of GEN-2018-009 | 500000 | 100% | 500000 | 1
GEN-2018-009 | 03 - Central | 155902 |  | Cimarron 115kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-009 | 4000000 | 100% | 4000000 | 1
GEN-2018-010 | 01 - North | 156176 |  | Neset 230kV Substation GEN-2018-010 Interconnection (TOIF) (BEPC) | Interconnection | Facilitate the interconnection of GEN-2018-010 | 120000 | 100% | 120000 | 1
GEN-2018-010 | 01 - North | 156177 |  | Neset 230kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-010 | 0 | 100% | 0 | 1
GEN-2018-011 | 04 - Southeast | 155903 |  | Dover 138 kV Switching Station GEN-2018-011 Interconnection (TOIF) (WFEC) | Interconnection | Facilitate the interconnection of GEN-2018-011 | 1479500 | 100% | 1479500 | 1
GEN-2018-011 | 04 - Southeast | 155904 |  | Dover 138 kV Switching Station Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-011 | 0 | 100% | 0 | 1
GEN-2018-012 | 02 - Nebraska | 155889 |  | Antelope - Hoskins 345kV GEN-2018-012 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2018-012 | 1500000 | 100% | 1500000 | 1
GEN-2018-012 | 02 - Nebraska | 155890 |  | Antelope - Hoskins 345kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-012 | 5500000 | 100% | 5500000 | 1
GEN-2018-013 | 03 - Central | 155729 |  | Abilene Energy Center-Northview 115kV GEN-2018-013 Interconnection (TOIF) (EKC) | Interconnection | Sharing a POI substation with a prior-queued GEN-2017-120 request | 744761 | 100% | 744761 | 1
GEN-2018-013 | 03 - Central | 155730 |  | Abilene Energy Center-Northview 115kV Line Tap (DISIS-2018-001) | Interconnection | Sharing a POI substation with a prior-queued GEN-2017-120 request | 1234682 | 100% | 1234682 | 1
GEN-2018-014 | 03 - Central | 156039 |  | Holt County 345kV Substation GEN-2018-014 Interconnection (TOIF) (TMO) | Interconnection | Sharing a gen-tie line with a prior-queued GEN-2017-115 request | 0 | 100% | 0 | 1
GEN-2018-014 | 03 - Central | 156040 |  | Holt County 345kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Sharing a gen-tie line with a prior-queued GEN-2017-115 request | 0 | 100% | 0 | 1
GEN-2018-015 | 05 - Southwest | 156219 |  | Tuco-Oklaunion 345kV GEN-2018-015 Interconnection (TOIF) (SWPS) | Interconnection | Facilitate the interconnection of GEN-2018-015 | 1860250 | 100% | 1860250 | 1
GEN-2018-015 | 05 - Southwest | 156220 |  | Tuco-Oklaunion 345kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-015 | 18641931 | 100% | 18641931 | 1
GEN-2018-021 | 04 - Southeast | 155899 |  | Chisholm-Gracemont 345kV GEN-2018-021 Interconnection (TOIF) (AEP) | Interconnection | Sharing a gen-tie line with a prior-queued GEN-2016-037 request | 0 | 100% | 0 | 1
GEN-2018-021 | 04 - Southeast | 155900 |  | Chisholm-Gracemont 345kV Line Tap (DISIS-2018-001) | Interconnection | Sharing a gen-tie line with a prior-queued GEN-2016-037 request | 0 | 100% | 0 | 1
GEN-2018-022 | 03 - Central | 156168 |  | Mullen Creek 345kV Substation GEN-2018-022 Interconnection (TOIF) (EMW) | Interconnection | Facilitate the interconnection of GEN-2018-022 | 1900000 | 100% | 1900000 | 1
GEN-2018-022 | 03 - Central | 156169 |  | Mullen Creek 345kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-022 | 5800000 | 100% | 5800000 | 1
GEN-2018-024 | 04 - Southeast | 155895 |  | Canadian River-Muskogee and Muskogee-Seminole 345kV GEN-2018-024 Interconnection (TOIF) (OGE) | Interconnection | Facilitate the interconnection of GEN-2018-024 | 1500000 | 100% | 1500000 | 1
GEN-2018-024 | 04 - Southeast | 155896 |  | Canadian River-Muskogee and Muskogee-Seminole 345kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-024 | 2500000 | 100% | 2500000 | 1
GEN-2018-025 | 02 - Nebraska | 155907 |  | Fort Calhoun 345kV Substation GEN-2018-025 Interconnection (TOIF) (OPPD) | Interconnection | Facilitate the interconnection of GEN-2018-025 | 0 | 100% | 0 | 1
GEN-2018-025 | 02 - Nebraska | 156027 |  | Fort Calhoun 345kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-025 | 863310.5714 | 28.57% | 3021587 | 1
ASGI-2018-003 | 03 - Central | TBD | ERIS | Rock Creek to Atchison 345 kV New Line Build (DISIS-2018-001) | Current Study | Build a new 345 kV line from Rock Creek to Atchison (Evergy/MEC) (14.0 miles) | 33666.98 | 0.1604% | 20994330 | 0.02183
ASGI-2018-006 | 03 - Central | TBD | ERIS | Rock Creek to Atchison 345 kV New Line Build (DISIS-2018-001) | Current Study | Build a new 345 kV line from Rock Creek to Atchison (Evergy/MEC) (14.0 miles) | 31384.48 | 0.1495% | 20994330 | 0.02035
ASGI-2018-007 | 03 - Central | TBD | ERIS | Rock Creek to Atchison 345 kV New Line Build (DISIS-2018-001) | Current Study | Build a new 345 kV line from Rock Creek to Atchison (Evergy/MEC) (14.0 miles) | 14466.16 | 0.06891% | 20994330 | 0.00938
ASGI-2018-010 | 03 - Central | TBD | ERIS | Rock Creek to Atchison 345 kV New Line Build (DISIS-2018-001) | Current Study | Build a new 345 kV line from Rock Creek to Atchison (Evergy/MEC) (14.0 miles) | 53222.52 | 0.2535% | 20994330 | 0.01972
ASGI-2018-011 | 03 - Central | TBD | ERIS | Rock Creek to Atchison 345 kV New Line Build (DISIS-2018-001) | Current Study | Build a new 345 kV line from Rock Creek to Atchison (Evergy/MEC) (14.0 miles) | 55354.66 | 0.2637% | 20994330 | 0.02051
GEN-2018-014 | 03 - Central | TBD | ERIS | Rock Creek to Atchison 345 kV New Line Build (DISIS-2018-001) | Current Study | Build a new 345 kV line from Rock Creek to Atchison (Evergy/MEC) (14.0 miles) | 3132860.7 | 14.92% | 20994330 | 0.54828
GEN-2018-022 | 03 - Central | TBD | ERIS | Rock Creek to Atchison 345 kV New Line Build (DISIS-2018-001) | Current Study | Build a new 345 kV line from Rock Creek to Atchison (Evergy/MEC) (14.0 miles) | 10829263.58 | 51.58% | 20994330 | 0.46812
GEN-2018-031 | 03 - Central | TBD | ERIS | Rock Creek to Atchison 345 kV New Line Build (DISIS-2018-001) | Current Study | Build a new 345 kV line from Rock Creek to Atchison (Evergy/MEC) (14.0 miles) | 122144.99 | 0.5818% | 20994330 | 0.03168
GEN-2018-032 | 03 - Central | TBD | ERIS | Rock Creek to Atchison 345 kV New Line Build (DISIS-2018-001) | Current Study | Build a new 345 kV line from Rock Creek to Atchison (Evergy/MEC) (14.0 miles) | 385342.76 | 1.835% | 20994330 | 0.01612
GEN-2018-038 | 03 - Central | TBD | ERIS | Rock Creek to Atchison 345 kV New Line Build (DISIS-2018-001) | Current Study | Build a new 345 kV line from Rock Creek to Atchison (Evergy/MEC) (14.0 miles) | 1097289.49 | 5.227% | 20994330 | 0.06996
GEN-2018-040 | 03 - Central | TBD | ERIS | Rock Creek to Atchison 345 kV New Line Build (DISIS-2018-001) | Current Study | Build a new 345 kV line from Rock Creek to Atchison (Evergy/MEC) (14.0 miles) | 579880.25 | 2.762% | 20994330 | 0.0752
GEN-2018-041 | 03 - Central | TBD | ERIS | Rock Creek to Atchison 345 kV New Line Build (DISIS-2018-001) | Current Study | Build a new 345 kV line from Rock Creek to Atchison (Evergy/MEC) (14.0 miles) | 2319520.98 | 11.05% | 20994330 | 0.0752
GEN-2018-042 | 03 - Central | TBD | ERIS | Rock Creek to Atchison 345 kV New Line Build (DISIS-2018-001) | Current Study | Build a new 345 kV line from Rock Creek to Atchison (Evergy/MEC) (14.0 miles) | 1739640.74 | 8.286% | 20994330 | 0.0752
GEN-2018-054 | 03 - Central | TBD | ERIS | Rock Creek to Atchison 345 kV New Line Build (DISIS-2018-001) | Current Study | Build a new 345 kV line from Rock Creek to Atchison (Evergy/MEC) (14.0 miles) | 300550.7 | 1.432% | 20994330 | 0.03248
GEN-2018-058 | 03 - Central | TBD | ERIS | Rock Creek to Atchison 345 kV New Line Build (DISIS-2018-001) | Current Study | Build a new 345 kV line from Rock Creek to Atchison (Evergy/MEC) (14.0 miles) | 84724.2 | 0.4036% | 20994330 | 0.00436
GEN-2018-059 | 03 - Central | TBD | ERIS | Rock Creek to Atchison 345 kV New Line Build (DISIS-2018-001) | Current Study | Build a new 345 kV line from Rock Creek to Atchison (Evergy/MEC) (14.0 miles) | 84724.2 | 0.4036% | 20994330 | 0.00436
GEN-2018-062 | 03 - Central | TBD | ERIS | Rock Creek to Atchison 345 kV New Line Build (DISIS-2018-001) | Current Study | Build a new 345 kV line from Rock Creek to Atchison (Evergy/MEC) (14.0 miles) | 130292.61 | 0.6206% | 20994330 | 0.02235
GEN-2018-014 | 03 - Central | TBD | ERIS | Sibley to Sibley 161 kV New Line Build (DISIS-2018-001) | Current Study | Build a second 161 kV line from Sibley to Sibley (1.19 miles) | 16959.18 | 1.363% | 1244434.17 | 0.01737
GEN-2018-022 | 03 - Central | TBD | ERIS | Sibley to Sibley 161 kV New Line Build (DISIS-2018-001) | Current Study | Build a second 161 kV line from Sibley to Sibley (1.19 miles) | 116015.54 | 9.323% | 1244434.17 | 0.02935
GEN-2018-038 | 03 - Central | TBD | ERIS | Sibley to Sibley 161 kV New Line Build (DISIS-2018-001) | Current Study | Build a second 161 kV line from Sibley to Sibley (1.19 miles) | 228766.35 | 18.38% | 1244434.17 | 0.08536
GEN-2018-040 | 03 - Central | TBD | ERIS | Sibley to Sibley 161 kV New Line Build (DISIS-2018-001) | Current Study | Build a second 161 kV line from Sibley to Sibley (1.19 miles) | 110336.64 | 8.866% | 1244434.17 | 0.08374
GEN-2018-041 | 03 - Central | TBD | ERIS | Sibley to Sibley 161 kV New Line Build (DISIS-2018-001) | Current Study | Build a second 161 kV line from Sibley to Sibley (1.19 miles) | 441346.55 | 35.47% | 1244434.17 | 0.08374
GEN-2018-042 | 03 - Central | TBD | ERIS | Sibley to Sibley 161 kV New Line Build (DISIS-2018-001) | Current Study | Build a second 161 kV line from Sibley to Sibley (1.19 miles) | 331009.91 | 26.6% | 1244434.17 | 0.08374
GEN-2018-058 | 03 - Central | TBD | ERIS | Stranger to 87th St. 345 kV New Line Build (DISIS-2018-001) | Current Study | Build a second 345 kV line from Stranger to 87th St. (24.83 miles) | 18617471.93 | 50% | 37234943.85 | 0.18447
GEN-2018-059 | 03 - Central | TBD | ERIS | Stranger to 87th St. 345 kV New Line Build (DISIS-2018-001) | Current Study | Build a second 345 kV line from Stranger to 87th St. (24.83 miles) | 18617471.92 | 50% | 37234943.85 | 0.18447
GEN-2018-014 | 03 - Central | TBD | ERIS | Sibley 345/161 kV New Transformer Build (DISIS-2018-001) | Current Study | Build a second 345/161 kV transformer at Sibley | 113153.05 | 1.363% | 8302968 | 0.01737
GEN-2018-022 | 03 - Central | TBD | ERIS | Sibley 345/161 kV New Transformer Build (DISIS-2018-001) | Current Study | Build a second 345/161 kV transformer at Sibley | 774065.28 | 9.323% | 8302968 | 0.02935
GEN-2018-038 | 03 - Central | TBD | ERIS | Sibley 345/161 kV New Transformer Build (DISIS-2018-001) | Current Study | Build a second 345/161 kV transformer at Sibley | 1526348.07 | 18.38% | 8302968 | 0.08536
GEN-2018-040 | 03 - Central | TBD | ERIS | Sibley 345/161 kV New Transformer Build (DISIS-2018-001) | Current Study | Build a second 345/161 kV transformer at Sibley | 736175.2 | 8.866% | 8302968 | 0.08374
GEN-2018-041 | 03 - Central | TBD | ERIS | Sibley 345/161 kV New Transformer Build (DISIS-2018-001) | Current Study | Build a second 345/161 kV transformer at Sibley | 2944700.8 | 35.47% | 8302968 | 0.08374
GEN-2018-042 | 03 - Central | TBD | ERIS | Sibley 345/161 kV New Transformer Build (DISIS-2018-001) | Current Study | Build a second 345/161 kV transformer at Sibley | 2208525.6 | 26.6% | 8302968 | 0.08374
GEN-2018-013 | 03 - Central | TBD | ERIS | Craig to 87th St. 345 kV Rebuild (DISIS-2018-001) | Current Study | Rebuild the existing Craig to 87th St. 345 kV 5.1 mile line | 113927.61 | 1.952% | 5836664.4 | 0.05125
GEN-2018-053 | 03 - Central | TBD | ERIS | Craig to 87th St. 345 kV Rebuild (DISIS-2018-001) | Current Study | Rebuild the existing Craig to 87th St. 345 kV 5.1 mile line | 340616.59 | 5.836% | 5836664.4 | 0.11354
GEN-2018-058 | 03 - Central | TBD | ERIS | Craig to 87th St. 345 kV Rebuild (DISIS-2018-001) | Current Study | Rebuild the existing Craig to 87th St. 345 kV 5.1 mile line | 2605905.95 | 44.65% | 5836664.4 | 0.3447
GEN-2018-059 | 03 - Central | TBD | ERIS | Craig to 87th St. 345 kV Rebuild (DISIS-2018-001) | Current Study | Rebuild the existing Craig to 87th St. 345 kV 5.1 mile line | 2605905.95 | 44.65% | 5836664.4 | 0.3447
GEN-2018-061 | 03 - Central | TBD | ERIS | Craig to 87th St. 345 kV Rebuild (DISIS-2018-001) | Current Study | Rebuild the existing Craig to 87th St. 345 kV 5.1 mile line | 170308.3 | 2.918% | 5836664.4 | 0.11354
GEN-2018-022 | 03 - Central | TBD | ERIS | Sibley to Sibley 161 kV Ckt 1 Rebuild (DISIS-2018-001) | Current Study | Rebuild the existing Sibley to Sibley 161 kV Ckt 1 1.19 mile line | 110024.34 | 9.452% | 1164086.56 | 0.02935
GEN-2018-038 | 03 - Central | TBD | ERIS | Sibley to Sibley 161 kV Ckt 1 Rebuild (DISIS-2018-001) | Current Study | Rebuild the existing Sibley to Sibley 161 kV Ckt 1 1.19 mile line | 216952.56 | 18.64% | 1164086.56 | 0.08536
GEN-2018-040 | 03 - Central | TBD | ERIS | Sibley to Sibley 161 kV Ckt 1 Rebuild (DISIS-2018-001) | Current Study | Rebuild the existing Sibley to Sibley 161 kV Ckt 1 1.19 mile line | 104638.71 | 8.989% | 1164086.56 | 0.08374
GEN-2018-041 | 03 - Central | TBD | ERIS | Sibley to Sibley 161 kV Ckt 1 Rebuild (DISIS-2018-001) | Current Study | Rebuild the existing Sibley to Sibley 161 kV Ckt 1 1.19 mile line | 418554.83 | 35.96% | 1164086.56 | 0.08374
GEN-2018-042 | 03 - Central | TBD | ERIS | Sibley to Sibley 161 kV Ckt 1 Rebuild (DISIS-2018-001) | Current Study | Rebuild the existing Sibley to Sibley 161 kV Ckt 1 1.19 mile line | 313916.12 | 26.97% | 1164086.56 | 0.08374
GEN-2018-026 | 04 - Southeast | 156170 |  | Mustang 138kV Substation GEN-2018-026 Interconnection (TOIF) (OKGE) | Interconnection | Facilitate the interconnection of GEN-2018-026 | 750000 | 100% | 750000 | 1
GEN-2018-026 | 04 - Southeast | 156171 |  | Mustang 138kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-026 | 2000000 | 100% | 2000000 | 1
GEN-2018-027 | 04 - Southeast | 156223 |  | Tulsa Power Station 38kV Substation GEN-2018-027 Interconnection (TOIF) (AEP) | Interconnection | Facilitate the interconnection of GEN-2018-027 | 1337068 | 100% | 1337068 | 1
GEN-2018-027 | 04 - Southeast | 156224 |  | Tulsa Power Station 38kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-027 | 9174000 | 100% | 9174000 | 1
GEN-2018-028 | 04 - Southeast | 156221 |  | Tulsa North 138kV Substation GEN-2018-028 Interconnection (TOIF) (AEP) | Interconnection | Facilitate the interconnection of GEN-2018-028 | 1337068 | 100% | 1337068 | 1
GEN-2018-028 | 04 - Southeast | 156222 |  | Tulsa North 138kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-028 | 5324780 | 100% | 5324780 | 1
GEN-2018-029 | 04 - Southeast | 156041 |  | Horseshoe Lake 138kV Substation GEN-2018-029 Interconnection (TOIF) (OKGE) | Interconnection | Facilitate the interconnection of GEN-2018-029 | 3500000 | 100% | 3500000 | 1
GEN-2018-029 | 04 - Southeast | 156042 |  | Horseshoe Lake 138kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-029 | 750000 | 100% | 750000 | 1
GEN-2018-030 | 03 - Central | 156162 |  | Lamar-Finney 345kV Substation GEN-2018-030 Interconnection (TOIF) (SWPS) | Interconnection | Facilitate the interconnection of GEN-2018-030 | 1975117 | 100% | 1975117 | 1
GEN-2018-030 | 03 - Central | 156163 |  | Lamar-Finney 345kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-030 | 1152973 | 100% | 1152973 | 1
GEN-2018-031 | 03 - Central | 155893 |  | Blue Valley 161kV Substation GEN-2018-031 Interconnection (TOIF) (INDN) | Interconnection | Facilitate the interconnection of GEN-2018-031 | 1500000 | 100% | 1500000 | 1
GEN-2018-031 | 03 - Central | 155894 |  | Blue Valley 161kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-031 | 4500000 | 100% | 4500000 | 1
GEN-2018-032 | 03 - Central | 156174 |  | Neosho 345kV Substation GEN-2018-032 Interconnection (TOIF) (EKC) | Interconnection | Facilitate the interconnection of GEN-2018-032 | 1158673 | 100% | 1158673 | 1
GEN-2018-032 | 03 - Central | 156175 |  | Neosho 345kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-032 | 2287131 | 100% | 2287131 | 1
GEN-2018-033 | 02 - Nebraska | 155897 |  | Cass County 345kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-033 | 2292537 | 100% | 2292537 | 1
GEN-2018-033 | 02 - Nebraska | 155898 |  | Cass County 345kV Substation Interconnection Expansion GEN-2018-033 Interconnection (TOIF) (OPPD) | Interconnection | Facilitate the interconnection of GEN-2018-033 | 1662072 | 100% | 1662072 | 1
GEN-2018-036 | 02 - Nebraska | 156233 |  | Stegall 230kV Substation GEN-2018-036 Interconnection (TOIF) (WAPA) | Interconnection | Facilitate the interconnection of GEN-2018-036 | 3571000 | 100% | 3571000 | 1
GEN-2018-036 | 02 - Nebraska | 156234 |  | Stegall 230kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-036 | 3571000 | 100% | 3571000 | 1
GEN-2018-037 | 02 - Nebraska | 156166 |  | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-037 | 1722352 | 100% | 1722352 | 1
GEN-2018-037 | 02 - Nebraska | 156167 |  | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV GEN-2018-037 Interconnection (TOIF) (OPPD) | Interconnection | Facilitate the interconnection of GEN-2018-037 | 10260510 | 100% | 10260510 | 1
GEN-2018-038 | 03 - Central | 156231 |  | Sibley 345kV Substation GEN-2018-038 Interconnection (TOIF) (EMW) | Interconnection | Facilitate the interconnection of GEN-2018-038 | 1900000 | 100% | 1900000 | 1
GEN-2018-038 | 03 - Central | 156232 |  | Sibley 345kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-038 | 32671020 | 100% | 32671020 | 1
GEN-2018-039 | 01 - North | 155905 |  | Edgeley 115kV Substation GEN-2018-039 Interconnection (TOIF) (WAPA) | Interconnection | Facilitate the interconnection of GEN-2018-039 | 1709000 | 100% | 1709000 | 1
GEN-2018-039 | 01 - North | 155906 |  | Edgeley 115kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-039 | 1709000 | 100% | 1709000 | 1
GEN-2018-040 | 03 - Central | 156227 |  | Sibley - Overton 345kV GEN-2018-040 Interconnection (TOIF) (EM) | Interconnection | Facilitate the interconnection of GEN-2018-040 | 2012890 | 100% | 2012890 | 1
GEN-2018-040 | 03 - Central | 156230 |  | Sibley - Overton 345kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-040 | 1665712.5 | 12.5% | 13325700 | 1
GEN-2018-041 | 03 - Central | 156228 |  | Sibley - Overton 345kV GEN-2018-041 Interconnection (TOIF) (EM) | Interconnection | Facilitate the interconnection of GEN-2018-041 | 2012890 | 100% | 2012890 | 1
GEN-2018-041 | 03 - Central | 156230 |  | Sibley - Overton 345kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-041 | 6662850 | 50% | 13325700 | 1
GEN-2018-042 | 03 - Central | 156229 |  | Sibley - Overton 345kV GEN-2018-042 Interconnection (TOIF) (EM) | Interconnection | Facilitate the interconnection of GEN-2018-042 | 2012890 | 100% | 2012890 | 1
GEN-2018-042 | 03 - Central | 156230 |  | Sibley - Overton 345kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-042 | 4997137.5 | 37.5% | 13325700 | 1
GEN-2018-043 | 02 - Nebraska | 156030 |  | Ft. Calhoun - Raun 345 kV GEN-2018-043 Interconnection (TOIF) (OPPD) | Interconnection | Facilitate the interconnection of GEN-2018-043 | 8894071 | 100% | 8894071 | 1
GEN-2018-043 | 02 - Nebraska | 156031 |  | Ft. Calhoun - Raun 345 kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-043 | 0 | 100% | 0 | 1
GEN-2018-044 | 02 - Nebraska | 155908 |  | Fort Calhoun 345kV Substation GEN-2018-044 Interconnection (TOIF) (OPPD) | Interconnection | Facilitate the interconnection of GEN-2018-044 | 0 | 100% | 0 | 1
GEN-2018-044 | 02 - Nebraska | 156027 |  | Fort Calhoun 345kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-044 | 2158276.4286 | 71.43% | 3021587 | 1
GEN-2018-045 | 02 - Nebraska | 156032 |  | Gerald Gentlemen - Red Willow 345kV GEN-2018-45 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2018-045 | 1500000 | 100% | 1500000 | 1
GEN-2018-045 | 02 - Nebraska | 156034 |  | Gerald Gentlemen - Red Willow 345kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-045 | 80994736.8421 | 57.89% | 139900000 | 1
GEN-2018-046 | 02 - Nebraska | 156033 |  | Gerald Gentlemen - Red Willow 345kV GEN-2018-46 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2018-046 | 1500000 | 100% | 1500000 | 1
GEN-2018-046 | 02 - Nebraska | 156034 |  | Gerald Gentlemen - Red Willow 345kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-046 | 58905263.1579 | 42.11% | 139900000 | 1
GEN-2018-027 | 04 - Southeast | TBD | ERIS | Delaware Tap to Tulsa SE 138 kV Rebuild (DISIS-2018-001) | Current Study | Rebuild the existing Delaware Tap to Tulsa SE 138 kV 2.09 mile line | 2391887.96 | 100% | 2391887.96 | 1
GEN-2018-027 | 04 - Southeast | TBD | ERIS | Delaware Tap to 36th&Lewis 138 kV Rebuild (DISIS-2018-001) | Current Study | Rebuild the existing Delaware Tap to 36th&Lewis 138 kV 0.97 mile line | 935234.23 | 100% | 935234.23 | 0.29095
GEN-2018-003 | 04 - Southeast | TBD | ERIS | N North Boston to GEN-2018-003-TAP 138 kV Rebuild (DISIS-2018-001) | Current Study | Rebuild the existing N North Boston to GEN-2018-003-TAP 138 kV 1.73 mile line | 1667995.07 | 100% | 1667995.07 | 0.1573
GEN-2018-021 | 04 - Southeast | 81717 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. | 0 | 100% | 0 | 0.003929
GEN-2018-048 | 04 - Southeast | 156180 |  | Pecan Creek 345kV Substation GEN-2018-048 Interconnection (TOIF) (OGE) | Interconnection | Facilitate the interconnection of GEN-2018-048 | 1500000 | 100% | 1500000 | 1
GEN-2018-048 | 04 - Southeast | 156182 |  | Pecan Creek 345kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-048 | 8955223.8806 | 89.55% | 10000000 | 1
GEN-2018-049 | 03 - Central | 156246 |  | Thistle 345kV Substation GEN-2018-049 Interconnection (TOIF) (ITCGP) | Interconnection | Facilitate the interconnection of GEN-2018-049 | 857280 | 100% | 857280 | 1
GEN-2018-049 | 03 - Central | 156247 |  | Thistle 345kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-049 | 3000000 | 100% | 3000000 | 1
GEN-2018-050 | 04 - Southeast | 156164 |  | Longwood 345kV Substation GEN-2018-050 Interconnection (TOIF) (AEPW) | Interconnection | Facilitate the interconnection of GEN-2018-050 | 1541013 | 100% | 1541013 | 1
GEN-2018-050 | 04 - Southeast | 156165 |  | Longwood 345kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-050 | 8130655 | 100% | 8130655 | 1
GEN-2018-051 | 05 - Southwest | 156182 |  | Pecan Creek 345kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-051 | 1044776.1194 | 10.45% | 10000000 | 1
GEN-2018-051 | 05 - Southwest | 156181 |  | Pecan Creek 345kV Substation GEN-2018-051 Interconnection (TOIF) (OGE) | Interconnection | Facilitate the interconnection of GEN-2018-051 | 1500000 | 100% | 1500000 | 1
GEN-2018-052 | 05 - Southwest | 156183 |  | Roadrunner 115kV Substation GEN-2018-052 Interconnection (TOIF) (SWPS) | Interconnection | Facilitate the interconnection of GEN-2018-052 | 1128837 | 100% | 1128837 | 1
GEN-2018-052 | 05 - Southwest | 156184 |  | Roadrunner 115kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-052 | 1039552 | 100% | 1039552 | 1
GEN-2018-053 | 03 - Central | 156045 |  | Kelly 161kV Substation GEN-2018-053 Interconnection (TOIF) (EKC) | Interconnection | Facilitate the interconnection of GEN-2018-053 | 842712 | 100% | 842712 | 1
GEN-2018-053 | 03 - Central | 156047 |  | Kelly 161kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-053 | 5836541.3333 | 66.67% | 8754812 | 1
GEN-2018-054 | 03 - Central | 156043 |  | KC South - N. Raymore 161kV GEN-2018-054 Interconnection (TOIF) (EMW) | Interconnection | Facilitate the interconnection of GEN-2018-054 | 631242 | 100% | 631242 | 1
GEN-2018-054 | 03 - Central | 156044 |  | KC South - N. Raymore 161kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-054 | 6577588 | 100% | 6577588 | 1
GEN-2018-055 | 04 - Southeast | 156244 |  | Terry Road 345kV Substation (TOIF) (AEP) | Interconnection | Facilitate the interconnection of GEN-2018-055 | 733380 | 100% | 733380 | 1
GEN-2018-055 | 04 - Southeast | 156245 |  | Terry Road 345kV Substation Interconnection Expansion | Interconnection | Facilitate the interconnection of GEN-2018-055 | 50000 | 100% | 50000 | 1
GEN-2018-056 | 02 - Nebraska | 156028 |  | Fort Thompson-Grand Island (Grand Prairie) 345kV GEN-2018-056 Interconnection (TOIF) (WAPA) | Interconnection | Facilitate the interconnection of GEN-2018-056 | 2898000 | 100% | 2898000 | 1
GEN-2018-056 | 02 - Nebraska | 156029 |  | Fort Thompson-Grand Island (Grand Prairie) 345kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-056 | 2898000 | 100% | 2898000 | 1
GEN-2018-057 | 03 - Central | 156035 |  | Gordon Evans 138kV Substation GEN-2018-057 Interconnection (TOIF) (EKC) | Interconnection | Facilitate the interconnection of GEN-2018-057 | 744762 | 100% | 744762 | 1
GEN-2018-057 | 03 - Central | 156036 |  | Gordon Evans 138kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-057 | 1234682 | 100% | 1234682 | 1
GEN-2018-058 | 03 - Central | 156235 |  | Stranger Creek 345kV GEN-2018-058 Interconnection (TOIF) (EKC) | Interconnection | Facilitate the interconnection of GEN-2018-058 | 979960 | 100% | 979960 | 1
GEN-2018-058 | 03 - Central | 156237 |  | Stranger Creek 345kV Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-058 | 385675 | 50% | 771350 | 1
GEN-2018-059 | 03 - Central | 156236 |  | Stranger Creek 345kV GEN-2018-059 Interconnection (TOIF) (EKC) | Interconnection | Facilitate the interconnection of GEN-2018-059 | 979960 | 100% | 979960 | 1
GEN-2018-059 | 03 - Central | 156237 |  | Stranger Creek 345kV Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-059 | 385675 | 50% | 771350 | 1
GEN-2018-060 | 02 - Nebraska | 155891 |  | Axtell-Post Rock 345 kV GEN-2018-060 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2018-060 | 1500000 | 100% | 1500000 | 1
GEN-2018-060 | 02 - Nebraska | 155892 |  | Axtell-Post Rock 345 kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-060 | 50000 | 100% | 50000 | 1
GEN-2018-061 | 03 - Central | 156046 |  | Kelly 161kV Substation GEN-2018-061 Interconnection (TOIF) (EKC) | Interconnection | Facilitate the interconnection of GEN-2018-061 | 842712 | 100% | 842712 | 1
GEN-2018-061 | 03 - Central | 156047 |  | Kelly 161kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-061 | 2918270.6667 | 33.33% | 8754812 | 1
GEN-2018-062 | 03 - Central | 156172 |  | Nearman 161kV Substation GEN-2018-062 Interconnection (TOIF) (KACY) | Interconnection | Facilitate the interconnection of GEN-2018-062 | 510232 | 100% | 510232 | 1
GEN-2018-062 | 03 - Central | 156173 |  | Nearman 161kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-062 | 2005192 | 100% | 2005192 | 1
Total | [6 empty] | 429077175 |  | 429077175

## Upgrade Summary
Upgrade Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time (months) | Total Upgrade Cost
Current Study | 01 - North | DISIS-2018-001 P1 | ERIS | Summit to Watertown 115 kV Structure Replacements (DISIS-2018-001) | TBD | Replace structures on the existing Summit to Watertown 115 kV 30.7 mile line | WAPA | 36 | 1500000
Current Study | 02 - Nebraska | DISIS-2018-001 P1 | ERIS | Red Willow to GEN-2018-045 Tap 345 kV Rebuild (DISIS-2018-001) | TBD | Rebuild the Red Willow to GEN-2018-045 TAP 345 kV 56.0 mile line | NPPD | 36 | 64123197.32
Current Study | 02 - Nebraska | DISIS-2018-001 P1 | ERIS | Ogalala to Sidney TS 230 kV Rebuild (DISIS-2018-001) | TBD | Rebuild the existing Ogalala to Sidney TS 230 kV 68.9 mile line | NPPD/BEPC | 36 | 60829594.65
Current Study | 02 - Nebraska | DISIS-2018-001 P1 | ERIS | Sidney TS to Sidney MB 230 kV Rebuild (DISIS-2018-001) | TBD | Rebuild the existing Sidney TS to Sidney MB 230 kV 4.0 mile line | BEPC | 36 | 3534036
Current Study | 03 - Central | DISIS-2018-001 P1 | ERIS | Rock Creek to Atchison 345 kV New Line Build (DISIS-2018-001) | TBD | Build a new 345 kV line from Rock Creek to Atchison (Evergy/MEC) (14.0 miles) | Evergy/MEC | 36 | 20994330
Current Study | 03 - Central | DISIS-2018-001 P1 | ERIS | Sibley 345/161 kV New Transformer Build (DISIS-2018-001) | TBD | Build a second 345/161 kV transformer at Sibley | Evergy | 36 | 8302968
Current Study | 03 - Central | DISIS-2018-001 P1 | ERIS | Sibley to Sibley 161 kV New Line Build (DISIS-2018-001) | TBD | Build a second 161 kV line from Sibley to Sibley (1.19 miles) | Evergy | 36 | 1244434.17
Current Study | 03 - Central | DISIS-2018-001 P1 | ERIS | Stranger to 87th St. 345 kV New Line Build (DISIS-2018-001) | TBD | Build a second 345 kV line from Stranger to 87th St. (24.83 miles) | WERE | 36 | 37234943.85
Current Study | 03 - Central | DISIS-2018-001 P1 | ERIS | Craig to 87th St. 345 kV Rebuild (DISIS-2018-001) | TBD | Rebuild the existing Craig to 87th St. 345 kV 5.1 mile line | WERE | 36 | 5836664.4
Current Study | 03 - Central | DISIS-2018-001 P1 | ERIS | Sibley to Sibley 161 kV Ckt 1 Rebuild (DISIS-2018-001) | TBD | Rebuild the existing Sibley to Sibley 161 kV Ckt 1 1.19 mile line | WERE | 36 | 1164086.56
Contingent | 04 - Southeast | DISIS-2018-001 P1 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | 81717 | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. | AEPW | 36 | 0
Current Study | 04 - Southeast | DISIS-2018-001 P1 | ERIS | N North Boston to GEN-2018-003-TAP 138 kV Rebuild (DISIS-2018-001) | TBD | Rebuild the existing N North Boston to GEN-2018-003-TAP 138 kV 1.73 mile line | AEPW | 36 | 1667995.07
Current Study | 04 - Southeast | DISIS-2018-001 P1 | ERIS | Delaware Tap to 36th&Lewis 138 kV Rebuild (DISIS-2018-001) | TBD | Rebuild the existing Delaware Tap to 36th&Lewis 138 kV 0.97 mile line | AEPW | 36 | 935234.23
Current Study | 04 - Southeast | DISIS-2018-001 P1 | ERIS | Delaware Tap to Tulsa SE 138 kV Rebuild (DISIS-2018-001) | TBD | Rebuild the existing Delaware Tap to Tulsa SE 138 kV 2.09 mile line | AEPW | 36 | 2391887.96
Current Study | 00NR | DISIS-2018-001 P1 | NRIS | Sibley 345 kV Substation Reconfiguration (DISIS-2018-001) | TBD | Reconfigure the Sibley 345 kV substation to add a double breaker between the Sibley to Hawthorn 345 kV and Sibley to Pleasant Hill 345 kV lines | Evergy | 36 | 9213876
Current Study | 00NR | DISIS-2018-001 P1 | NRIS | S1209 to S1231 161 kV Rebuild (DISIS-2018-001) | TBD | Rebuild the existing S1209 to S1231 161 kV 3.27 mile line | OPPD | 36 | 3198792
Contingent | 04 - Southeast | DISIS-2017-002-P2 | ERIS | Crossroads to Yoakum 345 kV New Line (DISIS-2017-002) | TBD | Build approximately 72 miles of new 345 kV line from Crossroads to Yoakum | SPS | 36 | 107970840
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Gentleman to Cherry County and Cherry County to Holt new 345 kV line | NTC 200220 | Build approximately 76 miles of new 345kV line from Gentleman to Cherry County and 146 miles from Cherry County to Holt | NPPD | 36 | 332910090
Contingent | 01 - North/02 - Nebraska | DISIS-2017-002-P1 | ERIS | Antelope to Holt County 345kV New Line (DISIS-2017-001) (NPPD) | 122699 | Build approximately 20 miles of new 345kV line from Antelope to Holt County | NPPD | 36 | 70000000
Contingent | 01 - North/03 - Central | DISIS-2017-002-P1 | ERIS | Wolf Creek to Blackberry 345 kV New Line Build (DISIS-2017-001) | 122598 | Build approximately 105 miles of new 345kV line from Wolfcreek to Blackberry | WERE | 36 | 128965170
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Neosho to Riv 4525 161 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Neosho to Riv 4525 161 kV 28.41 mile line to achieve a minimum summer/emergency rating of 557MVA | WERE | 36 | 27791343.84
Contingent | 00NR | DISIS-2017-002-P1 | NRIS | Barr Butte to Grenora 115 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Barr Butte to Grenora 115 kV 1.96 mile line to achieve a minimum summer/emergency rating of 155 MVA | WAPA | 36 | 1393246.4
Contingent | 00NR | DISIS-2017-002-P1 | NRIS | County Line to Tecumseh Hill 115 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing County Line to Tecumseh Hill 115 kV 5.32 mile line to achieve a minimum summer/emergency rating of 115 MVA | WERE | 36 | 3781668.8
Contingent | 00NR | DISIS-2017-002-P1 | NRIS | Groton to Bristol 115 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Groton to Bristol 115 kV 21.3 mile line to achieve a minimum summer/emergency rating of 125 MVA | WAPA | 36 | 15140892
Contingent | 00NR | DISIS-2017-002-P1 | NRIS | Midwest to Franklin 138 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Midwest to Franklin 138 kV 1.27 mile line to achieve a minimum winter/emergency rating of 315 MVA | OKGE/WFEC | 36 | 1224481.93
Contingent | 00NR | DISIS-2017-002-P1 | NRIS | Nashua and Roanridge 161 kV Terminal Upgrades (DISIS-2017-002) | TBD | Upgrade terminal equipment at Nashua and Roanridge 161kV to achieve a minimum Summer N/E=311/351 MVA and Winter N/E=371/403 MVA (line conductor limit) | KCPL | 36 | 1132970
Contingent | 00NR | DISIS-2017-002-P1 | NRIS | Nashua to Liberty 161 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Nashua to Liberty 161 kV 7.04 mile line to achieve a minimum winter/emergency rating of 195 MVA | KCPL | 36 | 6886696.96
Contingent | 00NR | DISIS-2017-002-P1 | NRIS | Replace Freemont 115/69 kV transformer (DISIS-2017-002) | TBD | Replace Freemont 115/69 kV transformer to achieve a minimum winter/emergency rating of 60 MVA | OPPD/NPPD | 36 | 2777743
Contingent | 00NR | DISIS-2017-002-P1 | NRIS | Replace Hoskins 230/115 kV transformer. (DISIS-2017-002) | TBD | Replace Hoskins 230/115 kV transformer to achieve a minimum summer/emergency rating of 190 MVA | NPPD | 36 | 6621188
Contingent | 00NR | DISIS-2017-002-P1 | NRIS | Snake Butte to Grenora 115 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Snake Butte to Grenora 115 kV 33.43 mile line to achieve a minimum summer/emergency rating of 195 MVA | WAPA | 36 | 23763381.2
Contingent | 00NR | DISIS-2017-002-P1 | NRIS | Stateline to Judson 115 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Stateline to Judson 115 kV 13.48 mile line to achieve a minimum summer/emergency rating of 135 MVA | WAPA | 36 | 9582123.2
Contingent | 00NR | DISIS-2017-002-P1 | NRIS | Stateline to Mont 115 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Stateline to Mont 115 kV 8.4 mile line to achieve a minimum summer/emergency rating of 300 MVA | WAPA | 36 | 5971056
Contingent | 00NR | DISIS-2017-002-P1 | NRIS | Stateline to Pioneer 115 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Stateline to Pioneer 115 kV 1.0 mile line to achieve a minimum summer/emergency rating of 265 MVA | WAPA | 36 | 710840
Contingent | 00NR | DISIS-2017-002-P1 | NRIS | Stilwell and Redel 161 kV Terminal Upgrades (DISIS-2017-002) | TBD | Upgrade terminal equipment at Stilwell and Redel 161kV to achieve a minimum Summer N/E=311/351 MVA and Winter N/E=366/400 MVA (line conductor limit) | KCPL | 36 | 1132970
Contingent | 00NR | DISIS-2017-002-P1 | NRIS | Tecumseh Hill to G17-105-Tap 161 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Tecumseh Hill to G17-105-Tap 161 kV 3.0 mile line to achieve a minimum winter/emergency rating of 250 MVA | OPPD | 36 | 2934672
Contingent | 00NR/01 - North | DISIS-2017-002-P1 | NRIS | Barr Butte to Strndahl 115 kV Rebuild (DISIS-2017-002) (WAPA) | TBD | Rebuild the existing Barr Butte to Strndahl 115 kV 12.21 mile line to achieve minimum light/emergency rating of 126 MVA | WAPA | 36 | 8679356.4
Contingent | 00NR/01 - North | DISIS-2017-002-P1 | NRIS | Mont to Strndahl 115 kV Rebuild (DISIS-2017-002) (WAPA) | TBD | Rebuild the existing Mont to Strndahl 115 kV 11.97 mile line to achieve a minimum summer/emergency rating of 270 MVA | WAPA | 36 | 8508754.8
Contingent | 00NR/01 - North | DISIS-2017-002-P1 | NRIS | Richland to Lewis 115 kV Rebuild (DISIS-2017-002) (WAPA) | TBD | Rebuild the existing Richland to Lewis 115 kV 2.76 mile line to achieve a minimum summer/emergency rating of 145 MVA | WAPA | 36 | 1961918.4
Contingent | 00NR/01 - North | DISIS-2017-002-P1 | NRIS | Summit to Bristol 115 kV Rebuild (DISIS-2017-002) (WAPA) | TBD | Rebuild the existing Summit to Bristol 115 kV 32.56 mile line to achieve a minimum summer/emergency rating of 125 MVA | WAPA | 36 | 23144950.4
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Anta to Exira 161kV Rebuild (DISIS-2017-002) (WAPA) | TBD | Rebuild the existing Anta to Exira 161kV 5.16 mile line to achieve minimum summer/emergency rating of 333 MVA | WAPA | 36 | 5047635.84
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Belfield 345/230kV Transformer Upgrade (DISIS-2017-002) (WAPA) | TBD | Rebuild existing Belfield Transformer | WAPA | 36 | 8302968
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Belfield to Dickinson 230kV Rebuild (DISIS-2017-002) (WAPA) | TBD | Rebuild the existing Belfield to Dickinson 230kV 15.19 mile line to achieve minimum summer/emergency rating of 668 MVA | WAPA | 36 | 13420501.71
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Belfield to Medora 230kV Rebuild (DISIS-2017-002) (WAPA) | TBD | Rebuild the existing Belfield to Medora 230kV 22.68 mile line to achieve minimum summer/emergency rating of 359 MVA | WAPA | 36 | 20037984.12
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Campbell to Glenham 230kV Rebuild (DISIS-2017-002) (WAPA) | TBD | Rebuild the existing Campbell to Glenham 230kV 15.04 mile line to achieve minimum summer rating of 350 MVA | WAPA | 36 | 13287975.36
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Columbus to Meadow Grove 230kV Rebuild (DISIS-2017-002) (NPPD) | TBD | Rebuild the existing Columbus to Meadow Grove 230kV 44.14 mile line to achieve minimum summer rating of 704 MVA | NPPD | 36 | 38998087.26
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Crocker to Groton 345kV New Line Build (DISIS-2017-002) | TBD | Build approximately 24.29 miles of new 345kV double circuit line from Crocker to Groton | BEPC | 36 | 36425162.55
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Dawson to GEN 2017-109 Tap 230kV Rebuild (DISIS-2017-002) (WAPA) | TBD | Rebuild the existing Dawson to GEN 2017-109 Tap 230kV 20 mile line to achieve minimum summer/emergency rating of 784 MVA | WAPA | 36 | 17670180
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Dawson to Lewis 115kV Rebuild (DISIS-2017-002) (WAPA) | TBD | Rebuild the existing Dawson to Lewis 115kV 48.91 mile line to achieve minimum Light/emergency rating of 139 MVA | WAPA | 36 | 34767184.4
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Dawson to Mingusville 230kV Rebuild (DISIS-2017-002) (WAPA) | TBD | Rebuild the existing Dawson to Mingusville 230kV 29.42 mile line to achieve minimum summer/emergency rating of 406 MVA | WAPA | 36 | 25992834.78
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Ft Randall 230kV Reactive Support (DISIS-2017-002) | TBD | Install +300 MVAR capacitor bank(s) at Ft Randal 230kV | WAPA | 36 | 5682900
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Grand Prairie 345kV Reactive Support (DISIS-2017-002) | TBD | Install +350 MVAR capacitor bank(s) at Grand Prairie 345kV | WAPA | 36 | 8690850
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Ft Randall to Meadow 230kV New Line Build (DISIS-2017-002) | TBD | Build approximately 84.17 miles of new 230kV line from Ft Randall to Meadow Grove | NPPD | 36 | 97442430.62
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Ft Thompson Substation 345kV Upgrade (DISIS-2017-002) (WAPA) | TBD | Ft Thompson Substation 345kV Upgrade | WAPA | 36 | 18427752
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Ft Thompson to Broadland 345kV New Line Build (DISIS-2017-002) | TBD | Build approximately 56 miles of new 345kV line from Ft Thompson to Broadland | WAPA | 36 | 83977320
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Ft Thompson to Ft Randall 230 kV New Line Build (DISIS-2017-002) | TBD | Build approximately 87.32 miles of new 230kV line from Ft Thompson to Ft Randall | WAPA | 36 | 90669967.52
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Ft Thompson to Wessington 230kV New Line Build (DISIS-2017-002) | TBD | Build approximately 46 miles of new 230kV line from Ft Thompson to Wessington | WAPA | 36 | 53253556
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Ft. Randall to Glenham 345kV New Line Build (DISIS-2017-002) | TBD | Build new 345kV line from Ft. Randall to Glenham along existing 115kV transmission path. Add 345/115kV transformers at existing stations. | WAPA | 36 | 633735528.45
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Gavins Pt. to Yankton Jct. 115kV Rebuild (DISIS-2017-002) (WAPA) | TBD | Rebuild the existing Gavins Pt. to Yankton Jct. 115kV 4.03 mile line to achieve minimum summer rating of 165 MVA | WAPA | 36 | 2864685.2
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Grand Island to Sweetwater 345kV New Line Build (DISIS-2017-002) | TBD | Build approximately 63.14 miles of new 345kV line from Grand Island to Sweetwater | NPPD | 36 | 94684428.3
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Groton to Antelope Valley 345kV New Line Build (DISIS-2017-002) | TBD | Build approximately 212.54 miles of new 345kV line from Groton to Antelope Valley | BEPC | 36 | 318723921.3
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Hanlon 230 kV Reactive Support (DISIS-2017-002) | TBD | Install +100 MVAR capacitor bank(s) at Hanlon 230kV | WAPA | 36 | 1894300
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Harmony to St. Francis 115kV Rebuild (DISIS-2017-002) (NPPD) | TBD | Rebuild the existing Harmony to St. Francis 115kV 25.73 mile line to achieve minimum summer rating of 210 MVA | NPPD | 36 | 18289913.2
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Harmony to Valentine 115kV Rebuild (DISIS-2017-002) (NPPD) | TBD | Rebuild the existing Harmony to Valentine 115kV 6.31 mile line to achieve minimum summer rating of 123 MVA | NPPD | 36 | 4485400.4
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Hartington to Gavins 115kV Pt. Rebuild (DISIS-2017-002) (WAPA) | TBD | Rebuild the existing Hartington to Gavins 115kV 20.37 mile Pt. line to achieve minimum summer rating of 143 MVA | WAPA | 36 | 14479810.8
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Holt County to Grand Prairie 345kV Double Circuit Rebuild (DISIS-2017-002) (WAPA) | TBD | Rebuild the Holt County to Grand Prairie 345kV 33.35 mile lines to achieve minimum summer/emergency rating of 1792 MVA | WAPA | 36 | 38167207.4
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Keystone to Red Willow 345kV New Line Build (DISIS-2017-002) | TBD | Build approximately 110 miles of new 345kV line from Keystone to Red Willow | NPPD | 36 | 164955450
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Leland Olds to G17-114 Tap 345kV New Line (DISIS-2017-002) | TBD | Build approximately 176.76 miles of new 345kV line from Leland Olds to G17-114 Tap | WAPA | 36 | 265068412.2
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | G17-114 Tap to Chappelle Creek 345kV New Line (DISIS-2017-002) | TBD | Build approximately 45 miles of new 345kV line from G17-114 Tap to Chappelle Creek | WAPA | 36 | 67481775
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Chappelle Creek to Ft Thompson 345kV New Line (DISIS-2017-002) | TBD | Build approximately 36 miles of new 345kV line from Chappelle Creek to Ft Thompson | WAPA | 36 | 44987850
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Ft Thompson to Grand Prairie 345kV New Line (DISIS-2017-002) | TBD | Build approximately 123.95 miles of new 345kV line from Ft Thompson to Grand Prairie | WAPA | 36 | 185874800.25
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Grand Prairie to Holt County 345kV New Line (DISIS-2017-002) | TBD | Build approximately 33.35 miles of new 345kV line from Grand Prairie to Holt County | WAPA | 36 | 50011493.25
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Holt County to Grand Island 345kV New Line (DISIS-2017-002) | TBD | Build approximately 82.3 miles of new 345kV line from Holt County to Grand Island | WAPA | 36 | 123416668.5
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Mingo 345kV Reactive Support (DISIS-2017-002) (SUNC) | TBD | Install +350 MVAR capacitor bank(s) Mingo (SUNC) | SUNC | 36 | 8690850
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | O'Neill to Spencer 115kV Rebuild (DISIS-2017-002) (WAPA) | TBD | Rebuild the existing O'Neill to Spencer 115kV 25 mile line to achieve minimum summer rating of 256 MVA | WAPA | 36 | 17771000
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Post Rock to Red Willow 345kV New Line Build (DISIS-2017-002) | TBD | Build approximately 170 miles of new 345kV line from Post Rock to Red Willow | NPPD | 36 | 254931150
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Raun to S3451 345kV Rebuild (DISIS-2017-002) (OPPD) | TBD | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve minimum winter rating of 1079 MVA | OPPD | 36 | 73427527.04
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Red Willow 345kV Reactive Support (DISIS-2017-002) (NPPD) | TBD | Install +350 MVAR capacitor bank(s) at Red Willow (NPPD) | NPPD | 36 | 8690850
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Sioux City 345kV Reactive support (WAPA) | TBD | Install +350 MVAR capacitor bank(s) at Sioux City 345kV | WAPA | 36 | 8690850
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Sioux falls to Pahoja 230kV Rebuild (DISIS-2017-002) (WAPA) | TBD | Rebuild the existing Sioux falls to Pahoja 230kV 20.19 mile line to achieve minimum summer rating of 405 MVA | WAPA | 36 | 17838046.71
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Spencer to Ft. Randall 115kV Rebuild (DISIS-2017-002) (WAPA) | TBD | Rebuild the existing Spencer to Ft. Randall 115kV 20 mile line to achieve minimum summer rating of 270 MVA | WAPA | 36 | 14216800
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Split Rock to White 345kV New Line Build (DISIS-2017-002) (WAPA) | TBD | Build a 59 mile second circuit 345kV line from Split Rock to White | WAPA | 36 | 88476105
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | St. Francis to Mission 115kV Rebuild (DISIS-2017-002) (NPPD) | TBD | Rebuild the existing St. Francis to Mission 115kV 19.49 mile line to achieve minimum summer rating of 227 MVA | NPPD | 36 | 13854271.6
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Utica Jct. to Rasmussen 230kV Rebuild (DISIS-2017-002) (WAPA) | TBD | Rebuild the existing Utica Jct. to Rasmussen 230kV 45.67 mile line to achieve minimum summer/emergency rating of 637 MVA | WAPA | 36 | 40349856.03
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | WAPA 345 kV mitigation | TBD | Tap the Antelope to Broadland 345kV line (165 miles from Antelope 345kV) and Leland Olds to Ft Thompson 345kV double circuit line (45 miles from Leland Olds 345kV) and create a new substation (Westfield 345kV),Tap the Leland Olds to Groton 345kV double circuit line (130 miles from Leland Olds) and create a new substation (Fredonia 345kV), New 345kV Double circuit from Westfield to Fredonia | WAPA | 36 | 104337279
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Watertown 345 kV Reactive Support (DISIS-2017-002) | TBD | Install +300 MVAR capacitor bank(s) at Watertown 345kV | WAPA | 36 | 7449300
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Watertown to Crocker 345kV New Line Build (DISIS-2017-002) | TBD | Build approximately 46 miles of new 345kV line from Watertown to Crocker | BEPC | 36 | 68981370
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Wayside 230kV Reactive Support (DISIS-2017-002) | TBD | Install +200 MVAR capacitor bank(s) at Wayside 230kV | WAPA | 36 | 3788600
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Westfield to Broadland 345kV Rebuild (DISIS-2017-002) (BEPC-SPP) | TBD | Rebuild the existing Westfield to Broadland 345kV 133.84 mile line to achieve minimum summer rating of 600 MVA | BEPC | 36 | 153172384.96
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | White to Watertown 345kV New Line Build (DISIS-2017-002) | TBD | Build approximately 44.4 miles of new 345kV second circuit from White to Watertown | WAPA | 36 | 66582018
Contingent | 01 - North | DISIS-2017-002-P1 | ERIS | Williston to Judson 115kV Rebuild (DISIS-2017-002) (BEPC-SPP) | TBD | Rebuild the existing Williston to Judson 115 kV 2.15 mile line to achieve a minimum summer/emergency rating of 260 MVA | WAPA | 36 | 1528306
Contingent | 02 - Nebraska | DISIS-2017-002-P1 | ERIS | JCT205 to S901 69kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing JCT205 to S901 69kV 1.07 mile line to achieve a minimum summer/emergency rating of 112 MVA | OPPD | 36 | 972575.43
Contingent | 02 - Nebraska | DISIS-2017-002-P1 | ERIS | JCT205 to S910 69kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing JCT205 to S910 69kV 2.890 mile line to achieve a minimum summer/emergency rating of 112 MVA | OPPD | 36 | 2626862.61
Contingent | 02 - Nebraska | DISIS-2017-002-P1 | ERIS | Moore to Tobias 345kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Moore to Tobias 345kV 26.470 mile line to achieve a minimum winter/emergency rating of 1792 MVA | NPPD | 36 | 30293432.68
Contingent | 02 - Nebraska | DISIS-2017-002-P1 | ERIS | N.Loup to Loup City 115kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing N.Loup to Loup City 115kV 20.550 mile line to achieve a minimum light load/emergency rating of 239 MVA | NPPD | 36 | 14607762
Contingent | 02 - Nebraska/03 - Central | DISIS-2017-002-P1 | ERIS | Moore to Monolith 345kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Moore to Monolith 345kV 0.75 mile line to achieve a minimum summer/emergency rating of 1792MVA | NPPD | 36 | 858333
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Asbury Plant to CJ 161 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Asbury Plant to CJ 161 kV 12.3 mile line to achieve a minimum summer/emergency rating of 557MVA | EMDE | 36 | 12032155.2
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Asbury Plant to Purcell Switch 161kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Asbury Plant to Purcell Switch 161kV 11.94 mile line to achieve a minimum winter/emergency rating of 557 MVA | EMDE | 36 | 21196000
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Benton to Rose Hill 345 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Benton to Rose Hill 345 kV 15.48 mile line to achieve a minimum summer/emergency rating of 1792MVA | WERE | 36 | 17715993.12
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Butler to Midian 138 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Butler to Midian 138 kV 1 mile line to achieve a minimum summer/emergency rating of 286MVA | WERE | 36 | 964159
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Carthag to Car 395 161 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Carthag to Car 395 161 kV 4.14 mile line to achieve a minimum summer/emergency rating of 557MVA and upgrade equipment within SWPA's Carthage substation including the main and transfer bus | SWPA/EMDE | 36 | 4049847.36
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Carthage to Purcell Switch 161kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Carthage to Purcell Switch 161kV 7.89 mile line to achieve a minimum winter/emergency rating of 557 MVA | EMDE | 36 | 10856000
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | CJ to Joplin Fir Road 161kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing CJ to Fir Road 161kV 3.26 mile line to achieve a minimum winter/emergency rating of 557 MVA | EMDE | 36 | 3409122.18
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Clinton to GEN-2017-108 Tap 161 kV Circuit #1 Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Clinton to GEN-2017-108 Tap 161 kV 11.74 mile line (circuit #1) to achieve a minimum summer/emergency rating of 837 MVA | AECI/KCPL | 36 | 11484349.76
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Clinton to GEN-2017-108 Tap 161 kV New Line Build Circuit #2 (DISIS-2017-002) | TBD | Build a second 161kV circuit from GEN-2017-108 Tap to Clinton (11.74 miles) | AECI/KCPL | 36 | 12277022.82
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Craig to Lenexa 161 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Craig to Lenexa 161 kV 2.95 mile line to achieve a minimum summer/emergency rating of 557MVA | KCPL | 36 | 2885760.8
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Craig to Pflumm 161 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Craig to Pflumm 161 kV 4.41 mile line to achieve a minimum summer/emergency rating of 557MVA | KCPL | 36 | 4313967.84
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | GEN-2017-108 Tap to GEN-2017-111 Tap 161 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing GEN-2017-108 Tap to GEN-2017-111 Tap 161 kV 12 mile line to achieve a minimum summer/emergency rating of 557 MVA | KCPL | 36 | 11738688
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Hawthorne 345kV Reactive Support (DISIS-2017-002) | TBD | Build a new 300 MVAR capacitor at Hawthorne 345 kV. | KCPL | 36 | 7449300
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Hickman 161 kV Terminal Upgrades (DISIS-2017-002) | TBD | Upgrade terminal equipment at Hickman 161kV to achieve a minimum Summer N/E=311/334 MVA and Winter N/E=334/334 MVA (1200A terminal equipment limit) | KCPL | 36 | 566485
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Kildare to New Kirk 138 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Kildare to New Kirk 138 kV 0.58 mile line to achieve a minimum summer/emergency rating of 200MVA | OKGE | 36 | 559212.22
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Kildare to White Eagle 138 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Kildare to White Eagle 138 kV 11.22 mile line to achieve a minimum summer/emergency rating of 359MVA | OKGE | 36 | 10817863.98
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | LA Russell 161kV Reactive Support (DISIS-2017-002) | TBD | Build a new 150 MVAR capacitor at LA Russell Energy Center 161 kV. | EMDE | 36 | 3616350
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Marmaton 161 kV Terminal Upgrades (DISIS-2017-002) | TBD | Upgrade terminal equipment at Marmaton 161kV to achieve a minimum Summer N/E=335/335 MVA and Winter N/E=335/335 MVA (1200A switch limit) | WERE | 36 | 566485
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Marmountain West to Neosho 161 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Marmountain West to Neosho 161 kV 30.09 mile line to achieve a minimum summer/emergency rating of 557MVA | WERE | 36 | 29434760.16
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Midlothian to Creswln 138 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Midlothian to Creswln 138 kV 9.08 mile line to achieve a minimum summer/emergency rating of 286MVA | OKGE | 36 | 8754563.72
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Midlothian to Peck 138 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Midlothian to Peck 138 kV 3.49 mile line to achieve a minimum summer/emergency rating of 286MVA | OKGE | 36 | 3364914.91
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Nashua 345kV New Transformer Build (DISIS-2017-002) | TBD | Build a new 345/161kV transformer at Nashua | KCPL | 36 | 8302968
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Neo Spa to Neo 184 161 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Neo Spa to Neo 184 161 kV 1.7 mile line to achieve a minimum summer/emergency rating of 557MVA and upgrade equipment within SWPA's Neosho substation including the main and transfer bus | SWPA/EMDE | 36 | 1662980.8
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Neo Spa to Tip 292 161 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Neo Spa to Tip 292 161 kV 10.6 mile line to achieve a minimum summer/emergency rating of 557MVA and upgrade equipment within SWPA's Neosho substation including the main and transfer bus | SWPA/EMDE | 36 | 10369174.4
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Newkirk to Newkirk 138 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Newkirk to Newkirk 138 kV 3.89 mile line to achieve a minimum summer/emergency rating of 286MVA | OKGE | 36 | 3750578.51
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Newkirk to Peckhmt 138 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Newkirk to Peckhmt 138 kV 1.46 mile line to achieve a minimum summer/emergency rating of 286MVA | OKGE | 36 | 1407672.14
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Oronogo Jct. to Joplin Fir Road 161kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Oronogo Jct. to Fir Road 161kV 2.86 mile line to achieve a minimum winter/emergency rating of 557 MVA | EMDE | 36 | 4600000
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Overton to Sibley 345 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Overton to Sibley 345 kV 88.64 mile line to achieve a minimum summer/emergency rating of 1792MVA | KCPL | 36 | 101443516.16
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Pflumm to Overland Park 161 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Pflumm to Overland Park 161 kV 3.55 mile line to achieve a minimum summer/emergency rating of 557MVA | GMO | 36 | 3472695.2
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Pleasant Hill 161 kV Terminal Upgrades (DISIS-2017-002) | TBD | Upgrade terminal equipment at Pleasant Hill 161kV to achieve a minimum Summer N/E=956/956 MVA and Winter N/E=956/956 MVA (1600A terminal equipment limit) | GMO | 36 | 566485
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Renfrow to GEN-2017-185 Tap 345 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Renfrow to GEN-2017-185 Tap 345 kV 22.26 mile line to achieve a minimum summer/emergency rating of 1792MVA | OKGE | 36 | 25475323.44
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Sedalia to Sedalia Tap 161 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Sedalia to Sedalia Tap 161 kV 3.57 mile line to achieve a minimum summer/emergency rating of 557 MVA | KCPL | 36 | 3492259.68
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Shwnmsn to Lenexa 161 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Shwnmsn to Lenexa 161 kV 3.91 mile line to achieve a minimum summer/emergency rating of 557MVA | KCPL | 36 | 3824855.84
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Stilwell to GEN-2017-111 Tap 161 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Stilwell to GEN-2017-111 Tap 161 kV 40 mile line to achieve a minimum summer/emergency rating of 557 MVA | KCPL | 36 | 39128960
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Swissvale to West Gardner 345 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Swissvale to West Gardner 345 kV 32.93 mile line to achieve a minimum summer/emergency rating of 1792MVA | WERE | 36 | 49381663.35
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Swissvale Transformer #3 Build (DISIS-2017-002) | TBD | Build a new 345/230kV transformer at Swissvale | WERE | 36 | 8302968
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Tecumseh Hill 345kV New Transformer Build (DISIS-2017-002) | TBD | Build a new 230/115kV transformer at Tecumseh Hill | WERE | 36 | 6621188
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Woodring to Redington 345 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Woodring to Redington 345 kV 19.2 mile line to achieve a minimum summer/emergency rating of 1792MVA | OKGE | 36 | 21973324.8
Contingent | 03 - Central | DISIS-2017-002-P1 | ERIS | Warrensburg to Warrensburg East 69 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Warrensburg to Warrensburg East 69 kV 3.23 mile line to achieve a minimum summer/emergency rating of 71MVA | GMO | 36 | 2935905.27
Contingent | 03 - Central/04 - Southeast | DISIS-2017-002-P1 | ERIS | Benton 345kV Reactive Support (DISIS-2017-002) | TBD | Build a new 300 MVAR capacitor at Benton 345 kV. | WERE | 36 | 7449300
Contingent | 03 - Central/04 - Southeast | DISIS-2017-002-P1 | ERIS | Clark County 345kV Reactive Support (DISIS-2017-002) | TBD | Build a new 300 MVAR capacitor at Clark County 345 kV. | SUNC | 36 | 7449300
Contingent | 03 - Central/04 - Southeast | DISIS-2017-002-P1 | ERIS | Delaware 345kV Reactive Support (DISIS-2017-002) | TBD | Build a new 300 MVAR capacitor at Delaware 345 kV. | AEPW | 36 | 7449300
Contingent | 03 - Central/04 - Southeast | DISIS-2017-002-P1 | ERIS | G16-063-Tap to Hugo 345kV New Line Build (Circuit 2) (DISIS-2017-002) | TBD | Build a second 74.0 mile 345kV line from G16-063-Tap to Hugo with a summer emergency rating of 1195 MVA | OKGE | 36 | 110970030
Contingent | 03 - Central/04 - Southeast | DISIS-2017-002-P1 | ERIS | Geary 345kV Reactive Support (DISIS-2017-002) | TBD | Build a new 300 MVAR capacitor at Geary 345 kV. | WERE | 36 | 7449300
Contingent | 03 - Central/04 - Southeast | DISIS-2017-002-P1 | ERIS | GEN-2017-152-Tap 345kV Reactive Support (DISIS-2017-002) | TBD | Build a new 200 MVAR capacitor at GEN-2017-152-tap 345 kV. | OKGE | 36 | 4966200
Contingent | 03 - Central/04 - Southeast | DISIS-2017-002-P1 | ERIS | Hugo to Valiant 345kV CKT2 New Line Build (DISIS-2017-002) | TBD | Build a second 17.88 mile 345 kV line from Hugo to Valiant. | AEPW/WFEC | 36 | 26812758.6
Contingent | 03 - Central/04 - Southeast | DISIS-2017-002-P1 | ERIS | Hunters to Renfrow 345kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Hunters to Renfro 345 kV 20.45 mile line to achieve a minimum summer/emergency rating of 2008MVA | OKGE | 36 | 23403879.8
Contingent | 03 - Central/04 - Southeast | DISIS-2017-002-P1 | ERIS | LaCygne 345kV Reactive Support (DISIS-2017-002) | TBD | Build a new 300 MVAR capacitor at LaCygne 345 kV. | KCPL | 36 | 7449300
Contingent | 03 - Central/04 - Southeast | DISIS-2017-002-P1 | ERIS | Renfrow to Rose Hill 345kV New Line Build (DISIS-2017-002) | TBD | Build a new 65.0 mile 345 kV line from Renfrow to Rose Hill. | WERE/OKGE | 36 | 97473675
Contingent | 03 - Central/04 - Southeast | DISIS-2017-002-P1 | ERIS | Renfrow to Viola 345kV New Line Build (Circuit 2) (DISIS-2017-002) | TBD | Build a second 32.26 mile 345kV line from Renfrow to Viola with a summer emergency rating of 1076 MVA | OKGE | 36 | 48376934.7
Contingent | 03 - Central/04 - Southeast | DISIS-2017-002-P1 | ERIS | Reno 345kV Reactive Support (DISIS-2017-002) | TBD | Build a new 300 MVAR capacitor at Reno 345 kV. | WERE | 36 | 7449300
Contingent | 03 - Central/04 - Southeast | DISIS-2017-002-P1 | ERIS | Rose Hill 345kV Reactive Support (DISIS-2017-002) | TBD | Build a new 300 MVAR capacitor at Rose Hill 345kV. | WERE | 36 | 7449300
Contingent | 03 - Central/04 - Southeast | DISIS-2017-002-P1 | ERIS | Sooner 345kV Reactive Support (DISIS-2017-002) | TBD | Build a new 300 MVAR capacitor at Sooner 345kV. | OKGE | 36 | 7449300
Contingent | 03 - Central/04 - Southeast | DISIS-2017-002-P1 | ERIS | Sooner to GEN-2016-119 Tap 345 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Sooner to GEN-2016-119 Tap 345 kV 27 mile line to achieve a minimum summer/emergency rating of 1792MVA | OKGE | 36 | 30899988
Contingent | 03 - Central/04 - Southeast | DISIS-2017-002-P1 | ERIS | Sunnyside to G16-063-Tap 345kV CKT2 New Line Build (DISIS-2017-002) | TBD | Build a second 49.5 mile 345 kV line from Sunnyside to G16-063-Tap. | OKGE | 36 | 74229952.5
Contingent | 03 - Central/04 - Southeast | DISIS-2017-002-P1 | ERIS | Thistle 345kV Reactive Support (DISIS-2017-002) | TBD | Build a new 400 MVAR capacitor at Thistle 345kV. | SUNC | 36 | 9932400
Contingent | 03 - Central/04 - Southeast | DISIS-2017-002-P1 | ERIS | Valiant to Ft. Smith 345kV New Line Build (DISIS-2017-002) | TBD | Build a new 77.75 mile 345 kV line from Valiant to Ft. Smith. | AEPW/OKGE | 36 | 116593511.25
Contingent | 03 - Central/04 - Southeast | DISIS-2017-002-P1 | ERIS | Viola 345kV Reactive Support (DISIS-2017-002) | TBD | Build a new 300 MVAR capacitor at Viola 345kV. | WERE | 36 | 7449300
Contingent | 03 - Central/04 - Southeast | DISIS-2017-002-P1 | ERIS | Viola to Wichita 345kV New Line Build (Circuit 2) (DISIS-2017-002) | TBD | Build a second 37.04 mile 345kV line from Viola to Wichita with a summer emergency rating of 1076 MVA | OKGE | 36 | 55544998.8
Contingent | 03 - Central/04 - Southeast | DISIS-2017-002-P1 | ERIS | Wichita 345kV Reactive Support (DISIS-2017-002) | TBD | Build a new 300 MVAR capacitor at Wichita 345kV. | WERE | 36 | 7449300
Contingent | 03 - Central/04 - Southeast | DISIS-2017-002-P1 | ERIS | Wichita to Morris 345kV New Line Build (DISIS-2017-002) | TBD | Build a new 52.93 mile 345 kV line from Wichita to Morris. | WERE | 36 | 79373563.35
Contingent | 03 - Central/04 - Southeast | DISIS-2017-002-P1 | ERIS | Wolf Creek 345kV Reactive Support (DISIS-2017-002) | TBD | Build a new 300 MVAR capacitor at Wolf Creek 345 kV. | WERE | 36 | 7449300
Contingent | 03 - Central/04 - Southeast | DISIS-2017-002-P1 | ERIS | Wolf Creek to West Gardner 345kV New Line Build (DISIS-2017-002) | TBD | Build a new 60 mile 345 kV line from Wolf Creek to West Gardner with a minimum summer/emergency rating of 1792 MVA | WERE/KCPL | 36 | 89975700
Contingent | 03 - Central/04 - Southeast | DISIS-2017-002-P1 | ERIS | Woodring to Hunters 345 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Woodring to Hunters 345 kV 20.38 mile line to achieve a minimum summer/emergency rating of 2008MVA | OKGE | 36 | 23323768.72
Contingent | 03 - Central/04 - Southeast/05 - Southwest | DISIS-2017-002-P1 | ERIS | Ft Smith 500/345kV New Transformer Build (DISIS-2017-002) | TBD | Install a 500/345kV transformer at Ft Smith (600 MVA) | OKGE | 36 | 13803180
Contingent | 03 - Central/04 - Southeast/05 - Southwest | DISIS-2017-002-P1 | ERIS | Ft Smith to Muskogee 500kV New Line Build (DISIS-2017-002) | TBD | Build a new 69 mile 500kV line from Ft Smith to Muskogee | OKGE | 36 | 140520915
Contingent | 03 - Central/04 - Southeast/05 - Southwest | DISIS-2017-002-P1 | ERIS | Mingo 500/345kV New Transformer Build (DISIS-2017-002) | TBD | Install a 500/345kV transformer at Mingo (600 MVA) | SUNC | 36 | 13803180
Contingent | 03 - Central/04 - Southeast/05 - Southwest | DISIS-2017-002-P1 | ERIS | Mingo to Red Willow 500kV New Line Build (DISIS-2017-002) | TBD | Build a 500kV circuit from Mingo to Red Willow (SUNC)(86.4 miles) | SUNC | 36 | 176160277.5
Contingent | 03 - Central/04 - Southeast/05 - Southwest | DISIS-2017-002-P1 | ERIS | Muskogee 500/345kV New Transformer Build (DISIS-2017-002) | TBD | Install a 500/345kV transformer at Muskogee (600 MVA) | OKGE | 36 | 13803180
Contingent | 03 - Central/04 - Southeast/05 - Southwest | DISIS-2017-002-P1 | ERIS | Muskogee to Seminole 500kV New Line Build (DISIS-2017-002) | TBD | Build a 500kV circuit from Muskogee to Seminole (OKGE)(120 miles) | OKGE | 36 | 244384200
Contingent | 03 - Central/04 - Southeast/05 - Southwest | DISIS-2017-002-P1 | ERIS | Muskogee to Wekiewa 500kV New Line Build (DISIS-2017-002) | TBD | Build a 500kV circuit from Muskogee to Wekiewa (OKGE/AEPW)(72 miles) | OKGE/AEPW | 36 | 146630520
Contingent | 03 - Central/04 - Southeast/05 - Southwest | DISIS-2017-002-P1 | ERIS | Post Rock 500/345kV New Transformer Build (DISIS-2017-002) | TBD | Install a 500/345kV transformer at Post Rock (600 MVA) | ITC GP | 36 | 13803180
Contingent | 03 - Central/04 - Southeast/05 - Southwest | DISIS-2017-002-P1 | ERIS | Post Rock to Setab 500kV New Line Build (DISIS-2017-002) | TBD | Build a 500kV circuit from Post Rock to Setab (MIDW/SUNC)(46.8 miles) | MIDW/SUNC | 36 | 95717145
Contingent | 03 - Central/04 - Southeast/05 - Southwest | DISIS-2017-002-P1 | ERIS | Red Willow 500/345kV New Transformer Build (DISIS-2017-002) | TBD | Install a 500/345kV transformer at Red Willow (600 MVA) | SUNC | 36 | 13803180
Contingent | 03 - Central/04 - Southeast/05 - Southwest | DISIS-2017-002-P1 | ERIS | Red Willow to Sweetwater 500kV New Line Build (DISIS-2017-002) | TBD | Build a 500kV circuit from Red Willow to Sweetwater (SUNC/NPPD)(163.2 miles) | SUNC/NPPD | 36 | 331955205
Contingent | 03 - Central/04 - Southeast/05 - Southwest | DISIS-2017-002-P1 | ERIS | Reno 500/345kV New Transformer Build (DISIS-2017-002) | TBD | Install a 500/345kV transformer at Reno (600 MVA) | WERE | 36 | 13803180
Contingent | 03 - Central/04 - Southeast/05 - Southwest | DISIS-2017-002-P1 | ERIS | Reno to Post Rock 500kV New Line Build (DISIS-2017-002) | TBD | Build a 500kV circuit from Reno to Post Rock (WERE/MIDW)(122.4 miles) | WERE/ITC GP | 36 | 248457270
Contingent | 03 - Central/04 - Southeast/05 - Southwest | DISIS-2017-002-P1 | ERIS | Seminole 500/345kV New Transformer Build (DISIS-2017-002) | TBD | Install a 500/345kV transformer at Seminole (600 MVA) | OKGE | 36 | 13803180
Contingent | 03 - Central/04 - Southeast/05 - Southwest | DISIS-2017-002-P1 | ERIS | Setab 500/345kV New Transformer Build (DISIS-2017-002) | TBD | Install a 500/345kV transformer at Setab (600 MVA) | SUNC | 36 | 13803180
Contingent | 03 - Central/04 - Southeast/05 - Southwest | DISIS-2017-002-P1 | ERIS | Setab to Mingo 500kV New Line Build (DISIS-2017-002) | TBD | Build a 500kV circuit from Setab to Mingo (SUNC)(68.4 miles) | SUNC | 36 | 138484380
Contingent | 03 - Central/04 - Southeast/05 - Southwest | DISIS-2017-002-P1 | ERIS | Sooner 500/345kV New Transformer Build (DISIS-2017-002) | TBD | Install a 500/345kV transformer at Sooner (600 MVA) | OKGE | 36 | 13803180
Contingent | 03 - Central/04 - Southeast/05 - Southwest | DISIS-2017-002-P1 | ERIS | Sooner to Viola 500kV New Line Build (DISIS-2017-002) | TBD | Build a 500kV circuit from Sooner to Viola (OKGE/WERE)(84 miles) | OKGE/WERE | 36 | 171068940
Contingent | 03 - Central/04 - Southeast/05 - Southwest | DISIS-2017-002-P1 | ERIS | Sweetwater 500/345kV New Transformer Build (DISIS-2017-002) | TBD | Install a 500/345kV transformer at Sweetwater (600 MVA) | NPPD | 36 | 13803180
Contingent | 03 - Central/04 - Southeast/05 - Southwest | DISIS-2017-002-P1 | ERIS | Viola 500/345kV New Transformer Build (DISIS-2017-002) | TBD | Install a 500/345kV transformer at Viola (600 MVA) | WERE | 36 | 13803180
Contingent | 03 - Central/04 - Southeast/05 - Southwest | DISIS-2017-002-P1 | ERIS | Viola to Reno 500kV New Line Build (DISIS-2017-002) | TBD | Build a 500kV circuit from Viola to Reno (WERE)(64.8 miles) | WERE | 36 | 132374775
Contingent | 03 - Central/04 - Southeast/05 - Southwest | DISIS-2017-002-P1 | ERIS | Wekiewa 500/345kV New Transformer Build (DISIS-2017-002) | TBD | Install a 500/345kV transformer at Wekiewa (600 MVA) | AEP | 36 | 13803180
Contingent | 03 - Central/04 - Southeast/05 - Southwest | DISIS-2017-002-P1 | ERIS | Wekiewa to Sooner 500kV New Line Build (DISIS-2017-002) | TBD | Build a 500kV circuit from Wekiewa to Sooner (OKGE/AEPW)(60 miles) | OKGE/AEPW | 36 | 122192100
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | Broken Arrow North Street Tap to Oneta 138 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Broken Arrow North Street Tap to Oneta 138kV 4.31 mile line to achieve a minimum summer/emergency rating of 335 MVA | AEPW | 36 | 4155525.29
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | Brown to South Brown 138 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Brown to South Brown 138kV 0.12 mile line to achieve a minimum winter/emergency rating of 195 MVA | SWPA/OKGE | 36 | 115699.08
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | Buffalo to West 69 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Buffalo to West 69 kV 21.78 mile line to achieve a minimum summer/emergency rating of 55 MVA | WFEC | 36 | 19796909.22
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | Catoosa to Lynne Lane Tap 138 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Catoosa to Lynne Lane Tap 138kV 1.80 mile line to achieve a minimum summer/emergency rating of 230 MVA | AEPW | 36 | 1735486.2
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | Degrasse to Moorland 138 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Degrasse to Moorland 138 kV 38.45 mile line to achieve a minimum summer/emergency rating of 240 MVA | OKGE/WFEC | 36 | 37071913.55
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | Delaware to Neosho 345 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Delaware to Neosho 345kV 48.02 mile line to achieve a minimum winter/emergency rating of 970 MVA | AEPW/WERE | 36 | 54956200.88
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | Delaware to Opensky 345kV New Line Build (DISIS-2017-002) | TBD | Build a new 95 mile 345 kV line from Delaware to Opensky. | AEPW/OKGE | 36 | 142461525
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | Delaware to Rose Hill 345kV New Line Build (DISIS-2017-002) | TBD | Build a new 65 mile 345 kV line from Delaware to Rose Hill. | AEPW/WERE | 36 | 97473675
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | Fort Supply CKT 1 138/69kV Transformer Replacement (DISIS-2017-002) | TBD | Replace Fort Supply CKT1 transformer with 90 MVA transformer or add an additional transformer at FTSPLY 138/69 kV | WFEC | 36 | 3128743
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | Fort Supply CKT 2 138/69kV Transformer Replacement (DISIS-2017-002) | TBD | Replace Fort Supply CKT 2 transformer with 90 MVA transformer or add an additional transformer at FTSPLY 138/69 kV | WFEC | 36 | 3128743
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | Fort Supply to Fargo JCT 69 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Fort Supply to Fargo JCT 69 kV 12.20 mile line to achieve a minimum spring/emergency rating of 135 MVA | WFEC | 36 | 11089177.8
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | Fort Supply to Fort Supply 69 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Fort Supply to Fort Supply 69 kV 2.80 mile line to achieve a minimum spring/emergency rating of 135 MVA | WFEC | 36 | 2545057.2
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | G17-185-Tap to Viola 345kV CKT2 New Line Build (DISIS-2017-002) | TBD | Build a second 10.0 mile 345 kV line from G17-185-Tap to Viola. | OKGE/WERE | 36 | 14995950
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | Iodine to Moorland 138 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Iodine to Moorland 138 kV 10.72 mile line to achieve a minimum spring/emergency rating of 150 MVA | WFEC | 36 | 10335784.48
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | McClain to Pleasant Valley 138 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing McClain to Pleasant Valley 138 kV 6.78 mile line to achieve a minimum spring/emergency rating of 800 MVA | OKGE | 36 | 6536998.02
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | Northwest Texarkana to Wilkes 345kV New Line Build (DISIS-2017-002) | TBD | Build a new 60 mile 345 kV line from Northwest Texarkana to Wilkes. | AEPW | 36 | 89975700
Contingent | 04 - Southeast | DISIS-2017-002-P1 | NRIS | Penn to Santa Fe 138 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Penn to Santa Fe 138 kV 2.02 mile line to achieve a minimum summer/emergency rating of 215 MVA | OKGE | 36 | 1947601.18
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | Pittsburg to Valiant 345kV CKT2 New Line Build (DISIS-2017-002) | TBD | Build a second 70.2 mile 345 kV line from Pittsburg to Valiant. | AEPW | 36 | 105271569
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | Pleasant Valley to Hollywood 138 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Pleasant Valley to Hollywood 138 kV 3.22 mile line to achieve a minimum summer/emergency rating of 490 MVA | OKGE | 36 | 3104591.98
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | Pleasant Valley to Turner 138 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Pleasant Valley to Turner 138 kV 1.89 mile line to achieve a minimum spring/emergency rating of 360 MVA | OKGE | 36 | 1822260.51
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | Renfrow to G17-185-Tap 345kV CKT2 New Line Build (DISIS-2017-002) | TBD | Build a second 22.26 mile 345 kV line from Renfrow to G17-185-Tap. | OKGE | 36 | 33380984.7
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | Replace Woodward transformer CKT 1 (DISIS-2017-002) | TBD | Replace Woodward transformer CKT1 with 590 MVA transformer or add an additional transformer at Woodward 345/138 kV | OKGE | 36 | 8302968
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | Replace Woodward transformer CKT 2 (DISIS-2017-002) | TBD | Replace Woodward transformer CKT2 with 590 MVA transformer or add an additional transformer at Woodward 345/138 kV | OKGE | 36 | 8302968
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | Replace WWDPST to Woodward 138/138 kV transformer (DISIS-2017-002) | TBD | Rebuild the existing WWDPST to Woodward 138/138 kV transformer to achieve a minimum spring/emergency rating of 440 MVA | OKGE | 36 | 3128743
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | Sogate to Turner 138 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Sogate to Turner 138 kV 2.6 mile line to achieve a minimum spring/emergency rating of 365 MVA | OKGE | 36 | 2506813.4
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | Sooner to Pintail 345 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Sooner to Pintail 345 kV 24.07 mile line to achieve a minimum spring/emergency rating of 1460 MVA | OKGE | 36 | 27546767.08
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | SW134TP4 to McClain 138 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing SW134TP4 to McClain 138 kV 4.99 mile line to achieve a minimum summer/emergency rating of 495 MVA | OKGE | 36 | 4811153.41
Contingent | 04 - Southeast | DISIS-2017-002-P1 | NRIS | SW134TP4 to McClain 138 kV Rebuild (NRIS) (DISIS-2017-002) | TBD | Rebuild the existing SW134TP4 to McClain 138 kV 4.99 mile line to achieve a minimum summer/emergency rating of 895 MVA | OKGE | 36 | 4811153.41
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | SW134TP4 to Sogate 138 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing SW134TP4 to Sogate 138 kV 1.74 mile line to achieve a minimum spring/emergency rating of 380 MVA | OKGE | 36 | 1677636.66
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | SW134TP4 to Westmore 138 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing SW134TP4 to Westmore 138 kV 0.77 mile line to achieve a minimum summer/emergency rating of 665 MVA | OKGE | 36 | 742402.43
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | Tupelo to Brown 138 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Tupelo to Brown 138kV 36.9 mile line to achieve a minimum spring/emergency rating of 110 MVA | SWPA | 36 | 35577467.1
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | Valiant to Lydia 345kV CKT2 New Line Build (DISIS-2017-002) | TBD | Build a second 43.29 mile 345 kV line from Valiant to Lydia. | AEPW | 36 | 64917467.55
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | Valiant to Turk 345kV New Line Build (DISIS-2017-002) | TBD | Build a new 84.0 mile 345 kV line from Valiant to Turk. | AEPW | 36 | 125965980
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | West Gardner to Craig 345 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing West Gardner to Craig 345 kV 16.19 mile line to achieve a minimum summer/emergency rating of 1350 MVA | KCPL | 36 | 18528548.36
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | Woodring to Fargo JCT 69 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Woodring to Fargo JCT 69 kV 2.70 mile line to achieve a minimum spring/emergency rating of 130 MVA | WFEC | 36 | 2454162.3
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | Woodring to Pintail 345 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Woodring to Pintail 345kV 19.15 mile line to achieve a minimum spring/emergency rating of 1235 MVA | OKGE | 36 | 21916102.6
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | Woodward to Windfarm 138 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Woodward to Windfarm 138kV 12.07 mile line to achieve a minimum spring/emergency rating of 290 MVA | OKGE | 36 | 11637399.13
Contingent | 04 - Southeast | DISIS-2017-002-P1 | ERIS | Woodward to WWDPST 138 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Woodward to WWDPST 138 kV 4.40 mile line to achieve a minimum spring/emergency rating of 450 MVA | OKGE | 36 | 4242299.6
Contingent | 04 - Southeast/05 - Southwest | DISIS-2017-002-P1 | ERIS | Ft Smith 500/345kV Transformer Replacement (DISIS-2017-002) | TBD | Replace Ft. Smith transformer with 1035 MVA transformer or add an additional transformer at Ft. Smith 500/345 kV | OKGE | 36 | 13803180
Contingent | 04 - Southeast/05 - Southwest | DISIS-2017-002-P1 | ERIS | Holcomb to Setab 345 kV Rebuild (DISIS-2017-002) | TBD | Rebuild the existing Holcomb to Setab 345 kV 39.66 mile line to achieve a minimum summer/emergency rating of 1792 MVA | SUNC | 36 | 45388649.04
Contingent | 05 - Southwest | DISIS-2017-002-P1 | ERIS | Beaver to Woodward 345kV New Line Build (DISIS-2017-002) | TBD | Build approximately 60 miles of new 345kV line from Beaver to Woodward | OKGE | 36 | 89975700
Contingent | 05 - Southwest | DISIS-2017-002-P1 | ERIS | ELKCTY 230/138kV Transformer Replacement (DISIS-2017-002) | TBD | Add 315 MVA transformer at ELKCTY | AEPW | 36 | 6621188
Contingent | 05 - Southwest | DISIS-2017-002-P1 | ERIS | Hitchland 230/115kV Transformer Replacement (DISIS-2017-002) | TBD | Add 400 MVA transformer at Hitchland | SPS | 36 | 8302968
Contingent | 05 - Southwest | DISIS-2017-002-P1 | ERIS | Potter County 345/230kV Transformer Replacement (DISIS-2017-002) | TBD | Add 625 MVA transformer at Potter County | SPS | 36 | 8302968
Contingent | 05 - Southwest | DISIS-2017-002-P1 | ERIS | Rebuild Asarco to Nichols 115 kV to 195 MVA | TBD | Rebuild the existing Asarco to Nichols 115 kV 0.21 mile line to achieve a minimum light load/emergency rating of 239 MVA | SPS | 36 | 149276.4
Contingent | 05 - Southwest | DISIS-2017-002-P1 | ERIS | Rebuild Clarksville to Muskogee 345 kV (DISIS-2017-002) | TBD | Rebuild the existing Clarksville to Muskogee 345 kV 21.380 mile line to achieve a minimum summer/emergency rating of 1792 MVA | AEPW/OKGE | 36 | 24468212.72
Contingent | 05 - Southwest | DISIS-2017-002-P1 | ERIS | Rebuild Pittsburg to Seminole 345kV to 995 MVA | TBD | Rebuild the existing Pittsburg to Seminole 345kV 51.27 mile line to achieve a minimum light load/emergency rating of 1792 MVA | AEPW/OKGE | 36 | 58675643.88
Contingent | 05 - Southwest | DISIS-2017-002-P1 | ERIS | Rebuild Seagraves to Sulpher 115 kV to 165 MVA | TBD | Rebuild the existing Seagraves to Sulpher 115 kV 12.53 mile line to achieve a minimum light load/emergency rating of 239 MVA | SPS | 36 | 8906825.2
Contingent | 05 - Southwest | DISIS-2017-002-P1 | ERIS | Rebuild Terry County to Sulpher 115 kV to 165 MVA | TBD | Rebuild the existing Terry County to Sulpher 115 kV 23.1 mile line to achieve a minimum light load/emergency rating of 239 MVA | SPS | 36 | 16420404
Contingent | 05 - Southwest | DISIS-2017-002-P1 | ERIS | Rebuild Texas County to Hitchland 115 kV to 195 MVA | TBD | Rebuild the existing Texas County to Hitchland 115 kV 13.04 mile line to achieve a minimum light load/emergency rating of 239 MVA | SPS | 36 | 9269353.6
Contingent | 05 - Southwest | DISIS-2017-002-P1 | ERIS | Tolk 345/230kV Transformer Replacement (DISIS-2017-002) | TBD | Replace Tolk transformer with 1010 MVA transformer (x3) | SPS | 36 | 24908904
Interconnection | 01 - North | DISIS-2018-001 P1 | ERIS | Summit 115kV Substation GEN-2018-007 Interconnection (TOIF) (WAPA) | 156238 | Facilitate the interconnection of GEN-2018-007 | WAPA | TBD | 1565000
Interconnection | 01 - North | DISIS-2018-001 P1 | ERIS | Summit 115kV Substation Interconnection Expansion (DISIS-2018-001) | 156239 | Facilitate the interconnection of GEN-2018-007 | WAPA | TBD | 1565000
Interconnection | 01 - North | DISIS-2018-001 P1 | ERIS | Groton-Leland Olds 345kV GEN-2018-008 Interconnection (TOIF) (BEPC) | 156037 | Facilitate the interconnection of GEN-2018-008 | BEPC | 24 | 2334054
Interconnection | 01 - North | DISIS-2018-001 P1 | ERIS | Groton-Leland Olds 345kV Line Tap (DISIS-2018-001) | 156038 | Facilitate the interconnection of GEN-2018-008 | BEPC | 24 | 20903079
Interconnection | 01 - North | DISIS-2018-001 P1 | ERIS | Neset 230kV Substation GEN-2018-010 Interconnection (TOIF) (BEPC) | 156176 | Facilitate the interconnection of GEN-2018-010 | BEPC | 3 | 120000
Interconnection | 01 - North | DISIS-2018-001 P1 | ERIS | Neset 230kV Substation Interconnection Expansion (DISIS-2018-001) | 156177 | Facilitate the interconnection of GEN-2018-010 | BEPC | 0 | 0
Interconnection | 01 - North | DISIS-2018-001 P1 | ERIS | Edgeley 115kV Substation GEN-2018-039 Interconnection (TOIF) (WAPA) | 155905 | Facilitate the interconnection of GEN-2018-039 | WAPA | TBD | 1709000
Interconnection | 01 - North | DISIS-2018-001 P1 | ERIS | Edgeley 115kV Substation Interconnection Expansion (DISIS-2018-001) | 155906 | Facilitate the interconnection of GEN-2018-039 | WAPA | TBD | 1709000
Interconnection | 02 - Nebraska | DISIS-2018-001 P1 | ERIS | Antelope - Hoskins 345kV GEN-2018-012 Interconnection (TOIF) (NPPD) | 155889 | Facilitate the interconnection of GEN-2018-012 | NPPD | TBD | 1500000
Interconnection | 02 - Nebraska | DISIS-2018-001 P1 | ERIS | Antelope - Hoskins 345kV Line Tap (DISIS-2018-001) | 155890 | Facilitate the interconnection of GEN-2018-012 | NPPD | TBD | 5500000
Interconnection | 02 - Nebraska | DISIS-2018-001 P1 | ERIS | Fort Calhoun 345kV Substation GEN-2018-025 Interconnection (TOIF) (OPPD) | 155907 | Facilitate the interconnection of GEN-2018-025 | OPPD | 0 | 0
Interconnection | 02 - Nebraska | DISIS-2018-001 P1 | ERIS | Fort Calhoun 345kV Substation Interconnection Expansion (DISIS-2018-001) | 156027 | Facilitate the interconnection of GEN-2018-025 and GEN-2018-044 | OPPD | 24 | 3021587
Interconnection | 02 - Nebraska | DISIS-2018-001 P1 | ERIS | Cass County 345kV Substation Interconnection Expansion (DISIS-2018-001) | 155897 | Facilitate the interconnection of GEN-2018-033 | OPPD | 24 | 2292537
Interconnection | 02 - Nebraska | DISIS-2018-001 P1 | ERIS | Cass County 345kV Substation Interconnection Expansion GEN-2018-033 Interconnection (TOIF) (OPPD) | 155898 | Facilitate the interconnection of GEN-2018-033 | OPPD | 24 | 1662072
Interconnection | 02 - Nebraska | DISIS-2018-001 P1 | ERIS | Stegall 230kV Substation GEN-2018-036 Interconnection (TOIF) (WAPA) | 156233 | Facilitate the interconnection of GEN-2018-036 | WAPA | TBD | 3571000
Interconnection | 02 - Nebraska | DISIS-2018-001 P1 | ERIS | Stegall 230kV Substation Interconnection Expansion (DISIS-2018-001) | 156234 | Facilitate the interconnection of GEN-2018-036 | WAPA | TBD | 3571000
Interconnection | 02 - Nebraska | DISIS-2018-001 P1 | ERIS | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV (DISIS-2018-001) | 156166 | Facilitate the interconnection of GEN-2018-037 | OPPD | 24 | 1722352
Interconnection | 02 - Nebraska | DISIS-2018-001 P1 | ERIS | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV GEN-2018-037 Interconnection (TOIF) (OPPD) | 156167 | Facilitate the interconnection of GEN-2018-037 | OPPD | 24 | 10260510
Interconnection | 02 - Nebraska | DISIS-2018-001 P1 | ERIS | Ft. Calhoun - Raun 345 kV GEN-2018-043 Interconnection (TOIF) (OPPD) | 156030 | Facilitate the interconnection of GEN-2018-043 | OPPD | 30 | 8894071
Interconnection | 02 - Nebraska | DISIS-2018-001 P1 | ERIS | Ft. Calhoun - Raun 345 kV Line Tap (DISIS-2018-001) | 156031 | Facilitate the interconnection of GEN-2018-043 | OPPD | 0 | 0
Interconnection | 02 - Nebraska | DISIS-2018-001 P1 | ERIS | Fort Calhoun 345kV Substation GEN-2018-044 Interconnection (TOIF) (OPPD) | 155908 | Facilitate the interconnection of GEN-2018-044 | OPPD | 0 | 0
Interconnection | 02 - Nebraska | DISIS-2018-001 P1 | ERIS | Gerald Gentlemen - Red Willow 345kV GEN-2018-45 Interconnection (TOIF) (NPPD) | 156032 | Facilitate the interconnection of GEN-2018-045 | NPPD | TBD | 1500000
Interconnection | 02 - Nebraska | DISIS-2018-001 P1 | ERIS | Gerald Gentlemen - Red Willow 345kV Line Tap (DISIS-2018-001) | 156034 | Facilitate the interconnection of GEN-2018-045 and GEN-2018-046 | NPPD | TBD | 139900000
Interconnection | 02 - Nebraska | DISIS-2018-001 P1 | ERIS | Gerald Gentlemen - Red Willow 345kV GEN-2018-46 Interconnection (TOIF) (NPPD) | 156033 | Facilitate the interconnection of GEN-2018-046 | NPPD | TBD | 1500000
Interconnection | 02 - Nebraska | DISIS-2018-001 P1 | ERIS | Fort Thompson-Grand Island (Grand Prairie) 345kV GEN-2018-056 Interconnection (TOIF) (WAPA) | 156028 | Facilitate the interconnection of GEN-2018-056 | WAPA | TBD | 2898000
Interconnection | 02 - Nebraska | DISIS-2018-001 P1 | ERIS | Fort Thompson-Grand Island (Grand Prairie) 345kV Line Tap (DISIS-2018-001) | 156029 | Facilitate the interconnection of GEN-2018-056 | WAPA | TBD | 2898000
Interconnection | 02 - Nebraska | DISIS-2018-001 P1 | ERIS | Axtell-Post Rock 345 kV GEN-2018-060 Interconnection (TOIF) (NPPD) | 155891 | Facilitate the interconnection of GEN-2018-060 | NPPD | TBD | 1500000
Interconnection | 02 - Nebraska | DISIS-2018-001 P1 | ERIS | Axtell-Post Rock 345 kV Line Tap (DISIS-2018-001) | 155892 | Facilitate the interconnection of GEN-2018-060 | NPPD | TBD | 50000
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Cimarron 115kV Substation GEN-2018-009 Interconnection (TOIF) (SUNC) | 155901 | Facilitate the interconnection of GEN-2018-009 | SEPC | 33 | 500000
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Cimarron 115kV Substation Interconnection Expansion (DISIS-2018-001) | 155902 | Facilitate the interconnection of GEN-2018-009 | SEPC | 33 | 4000000
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Abilene Energy Center-Northview 115kV GEN-2018-013 Interconnection (TOIF) (EKC) | 155729 | Facilitate the interconnection of GEN-2018-013 | WERE | 24 | 842712
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Abilene Energy Center-Northview 115kV Line Tap (DISIS-2018-001) | 155730 | Facilitate the interconnection of GEN-2018-013 | WERE | 24 | 10605703
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Holt County 345kV Substation GEN-2018-014 Interconnection (TOIF) (TMO) | 156039 | Facilitate the interconnection of GEN-2018-014 | WERE | 0 | 0
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Holt County 345kV Substation Interconnection Expansion (DISIS-2018-001) | 156040 | Facilitate the interconnection of GEN-2018-014 | WERE | 48 | 0
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Mullen Creek 345kV Substation GEN-2018-022 Interconnection (TOIF) (EMW) | 156168 | Facilitate the interconnection of GEN-2018-022 | WERE | 36 | 1900000
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Mullen Creek 345kV Substation Interconnection Expansion (DISIS-2018-001) | 156169 | Facilitate the interconnection of GEN-2018-022 | WERE | 36 | 5800000
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Lamar-Finney 345kV Substation GEN-2018-030 Interconnection (TOIF) (SWPS) | 156162 | Facilitate the interconnection of GEN-2018-030 | SPS | 32 | 1975117
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Lamar-Finney 345kV Substation Interconnection Expansion (DISIS-2018-001) | 156163 | Facilitate the interconnection of GEN-2018-030 | SPS | 32 | 1152973
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Blue Valley 161kV Substation GEN-2018-031 Interconnection (TOIF) (INDN) | 155893 | Facilitate the interconnection of GEN-2018-031 | INDN | 24 | 1500000
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Blue Valley 161kV Substation Interconnection Expansion (DISIS-2018-001) | 155894 | Facilitate the interconnection of GEN-2018-031 | INDN | 36 | 4500000
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Neosho 345kV Substation GEN-2018-032 Interconnection (TOIF) (EKC) | 156174 | Facilitate the interconnection of GEN-2018-032 | WERE | 36 | 1158673
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Neosho 345kV Substation Interconnection Expansion (DISIS-2018-001) | 156175 | Facilitate the interconnection of GEN-2018-032 | WERE | 36 | 2287131
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Sibley 345kV Substation GEN-2018-038 Interconnection (TOIF) (EMW) | 156231 | Facilitate the interconnection of GEN-2018-038 | WERE | 48 | 1900000
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Sibley 345kV Substation Interconnection Expansion (DISIS-2018-001) | 156232 | Facilitate the interconnection of GEN-2018-038 | WERE | 48 | 32671020
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Sibley - Overton 345kV GEN-2018-040 Interconnection (TOIF) (EM) | 156227 | Facilitate the interconnection of GEN-2018-040 | WERE | 48 | 2012890
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Sibley - Overton 345kV Line Tap (DISIS-2018-001) | 156230 | Facilitate the interconnection of GEN-2018-040, GEN-2018-041, and GEN-2018-042 | WERE | 48 | 13325700
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Sibley - Overton 345kV GEN-2018-041 Interconnection (TOIF) (EM) | 156228 | Facilitate the interconnection of GEN-2018-041 | WERE | 48 | 2012890
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Sibley - Overton 345kV GEN-2018-042 Interconnection (TOIF) (EM) | 156229 | Facilitate the interconnection of GEN-2018-042 | WERE | 48 | 2012890
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Thistle 345kV Substation GEN-2018-049 Interconnection (TOIF) (ITCGP) | 156246 | Facilitate the interconnection of GEN-2018-049 | ITCGP | TBD | 857280
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Thistle 345kV Substation Interconnection Expansion (DISIS-2018-001) | 156247 | Facilitate the interconnection of GEN-2018-049 | ITCGP | TBD | 3000000
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Kelly 161kV Substation GEN-2018-053 Interconnection (TOIF) (EKC) | 156045 | Facilitate the interconnection of GEN-2018-053 | WERE | 24 | 842712
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Kelly 161kV Substation Interconnection Expansion (DISIS-2018-001) | 156047 | Facilitate the interconnection of GEN-2018-053 and GEN-2018-061 | WERE | 24 | 8754812
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | KC South - N. Raymore 161kV GEN-2018-054 Interconnection (TOIF) (EMW) | 156043 | Facilitate the interconnection of GEN-2018-054 | WERE | 42 | 631242
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | KC South - N. Raymore 161kV Line Tap (DISIS-2018-001) | 156044 | Facilitate the interconnection of GEN-2018-054 | WERE | 42 | 6577588
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Gordon Evans 138kV Substation GEN-2018-057 Interconnection (TOIF) (EKC) | 156035 | Facilitate the interconnection of GEN-2018-057 | WERE | 24 | 744762
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Gordon Evans 138kV Substation Interconnection Expansion (DISIS-2018-001) | 156036 | Facilitate the interconnection of GEN-2018-057 | WERE | 24 | 1234682
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Stranger Creek 345kV GEN-2018-058 Interconnection (TOIF) (EKC) | 156235 | Facilitate the interconnection of GEN-2018-058 | WERE | 36 | 979960
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Stranger Creek 345kV Interconnection Expansion (DISIS-2018-001) | 156237 | Facilitate the interconnection of GEN-2018-058 and GEN-2018-059 | WERE | 36 | 771350
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Stranger Creek 345kV GEN-2018-059 Interconnection (TOIF) (EKC) | 156236 | Facilitate the interconnection of GEN-2018-059 | WERE | 36 | 979960
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Kelly 161kV Substation GEN-2018-061 Interconnection (TOIF) (EKC) | 156046 | Facilitate the interconnection of GEN-2018-061 | WERE | 24 | 842712
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Nearman 161kV Substation GEN-2018-062 Interconnection (TOIF) (KACY) | 156172 | Facilitate the interconnection of GEN-2018-062 | KACY | 36 | 510232
Interconnection | 03 - Central | DISIS-2018-001 P1 | ERIS | Nearman 161kV Substation Interconnection Expansion (DISIS-2018-001) | 156173 | Facilitate the interconnection of GEN-2018-062 | KACY | 36 | 2005192
Interconnection | 04 - Southeast | DISIS-2018-001 P1 | ERIS | North Boston-Bann 138kV GEN-2018-003 Interconnection (TOIF) (AEPW) | 156178 | Facilitate the interconnection of GEN-2018-003 | AEP | 36 | 1337068
Interconnection | 04 - Southeast | DISIS-2018-001 P1 | ERIS | North Boston-Bann 138kV Line Tap (DISIS-2018-001) | 156179 | Facilitate the interconnection of GEN-2018-003 | AEP | 36 | 8857127
Interconnection | 04 - Southeast | DISIS-2018-001 P1 | ERIS | Dover 138 kV Switching Station GEN-2018-011 Interconnection (TOIF) (WFEC) | 155903 | Facilitate the interconnection of GEN-2018-011 | WFEC | 36 | 1479500
Interconnection | 04 - Southeast | DISIS-2018-001 P1 | ERIS | Dover 138 kV Switching Station Interconnection Expansion (DISIS-2018-001) | 155904 | Facilitate the interconnection of GEN-2018-011 | WFEC | 0 | 0
Interconnection | 04 - Southeast | DISIS-2018-001 P1 | ERIS | Chisholm-Gracemont 345kV GEN-2018-021 Interconnection (TOIF) (AEP) | 155899 | Facilitate the interconnection of GEN-2018-021 | AEP | 36 | 733380
Interconnection | 04 - Southeast | DISIS-2018-001 P1 | ERIS | Chisholm-Gracemont 345kV Line Tap (DISIS-2018-001) | 155900 | Facilitate the interconnection of GEN-2018-021 | AEP | 36 | 50000
Interconnection | 04 - Southeast | DISIS-2018-001 P1 | ERIS | Canadian River-Muskogee and Muskogee-Seminole 345kV GEN-2018-024 Interconnection (TOIF) (OGE) | 155895 | Facilitate the interconnection of GEN-2018-024 | OGE | 24 | 1500000
Interconnection | 04 - Southeast | DISIS-2018-001 P1 | ERIS | Canadian River-Muskogee and Muskogee-Seminole 345kV Line Tap (DISIS-2018-001) | 155896 | Facilitate the interconnection of GEN-2018-024 | OGE | 24 | 2500000
Interconnection | 04 - Southeast | DISIS-2018-001 P1 | ERIS | Mustang 138kV Substation GEN-2018-026 Interconnection (TOIF) (OKGE) | 156170 | Facilitate the interconnection of GEN-2018-026 | OGE | 24 | 750000
Interconnection | 04 - Southeast | DISIS-2018-001 P1 | ERIS | Mustang 138kV Substation Interconnection Expansion (DISIS-2018-001) | 156171 | Facilitate the interconnection of GEN-2018-026 | OGE | 24 | 2000000
Interconnection | 04 - Southeast | DISIS-2018-001 P1 | ERIS | Tulsa Power Station 38kV Substation GEN-2018-027 Interconnection (TOIF) (AEP) | 156223 | Facilitate the interconnection of GEN-2018-027 | AEP | 36 | 1337068
Interconnection | 04 - Southeast | DISIS-2018-001 P1 | ERIS | Tulsa Power Station 38kV Substation Interconnection Expansion (DISIS-2018-001) | 156224 | Facilitate the interconnection of GEN-2018-027 | AEP | 36 | 9174000
Interconnection | 04 - Southeast | DISIS-2018-001 P1 | ERIS | Tulsa North 138kV Substation GEN-2018-028 Interconnection (TOIF) (AEP) | 156221 | Facilitate the interconnection of GEN-2018-028 | AEP | 36 | 1337068
Interconnection | 04 - Southeast | DISIS-2018-001 P1 | ERIS | Tulsa North 138kV Substation Interconnection Expansion (DISIS-2018-001) | 156222 | Facilitate the interconnection of GEN-2018-028 | AEP | 36 | 5324780
Interconnection | 04 - Southeast | DISIS-2018-001 P1 | ERIS | Horseshoe Lake 138kV Substation GEN-2018-029 Interconnection (TOIF) (OKGE) | 156041 | Facilitate the interconnection of GEN-2018-029 | OGE | 24 | 3500000
Interconnection | 04 - Southeast | DISIS-2018-001 P1 | ERIS | Horseshoe Lake 138kV Substation Interconnection Expansion (DISIS-2018-001) | 156042 | Facilitate the interconnection of GEN-2018-029 | OGE | 24 | 750000
Interconnection | 04 - Southeast | DISIS-2018-001 P1 | ERIS | Pecan Creek 345kV Substation GEN-2018-048 Interconnection (TOIF) (OGE) | 156180 | Facilitate the interconnection of GEN-2018-048 | OGE | 24 | 1500000
Interconnection | 04 - Southeast | DISIS-2018-001 P1 | ERIS | Pecan Creek 345kV Substation Interconnection Expansion (DISIS-2018-001) | 156182 | Facilitate the interconnection of GEN-2018-048 and GEN-2018-051 (Group 05) | OGE | 24 | 10000000
Interconnection | 04 - Southeast | DISIS-2018-001 P1 | ERIS | Longwood 345kV Substation GEN-2018-050 Interconnection (TOIF) (AEPW) | 156164 | Facilitate the interconnection of GEN-2018-050 | AEP | 36 | 1541013
Interconnection | 04 - Southeast | DISIS-2018-001 P1 | ERIS | Longwood 345kV Substation Interconnection Expansion (DISIS-2018-001) | 156165 | Facilitate the interconnection of GEN-2018-050 | AEP | 36 | 8130655
Interconnection | 04 - Southeast | DISIS-2018-001 P1 | ERIS | Terry Road 345kV Substation (TOIF) (AEP) | 156244 | Facilitate the interconnection of GEN-2018-055 | AEP | 36 | 733380
Interconnection | 04 - Southeast | DISIS-2018-001 P1 | ERIS | Terry Road 345kV Substation Interconnection Expansion | 156245 | Facilitate the interconnection of GEN-2018-055 | AEP | 36 | 50000
Interconnection | 05 - Southwest | DISIS-2018-001 P1 | ERIS | T14 Circuit 115kV GEN-2018-004 Interconnection (TOIF) | 156242 | Facilitate the interconnection of GEN-2018-004 | SPS | 32 | 1107176
Interconnection | 05 - Southwest | DISIS-2018-001 P1 | ERIS | T14 Circuit 115kV Line Tap (DISIS-2018-001) | 156243 | Facilitate the interconnection of GEN-2018-004 | SPS | 32 | 10430297
Interconnection | 05 - Southwest | DISIS-2018-001 P1 | ERIS | Tuco-Oklaunion 345kV GEN-2018-015 Interconnection (TOIF) (SWPS) | 156219 | Facilitate the interconnection of GEN-2018-015 | SPS | 32 | 1860250
Interconnection | 05 - Southwest | DISIS-2018-001 P1 | ERIS | Tuco-Oklaunion 345kV Line Tap (DISIS-2018-001) | 156220 | Facilitate the interconnection of GEN-2018-015 | SPS | 32 | 18641931
Interconnection | 05 - Southwest | DISIS-2018-001 P1 | ERIS | Pecan Creek 345kV Substation GEN-2018-051 Interconnection (TOIF) (OGE) | 156181 | Facilitate the interconnection of GEN-2018-051 | OGE | 24 | 1500000
Interconnection | 05 - Southwest | DISIS-2018-001 P1 | ERIS | Roadrunner 115kV Substation GEN-2018-052 Interconnection (TOIF) (SWPS) | 156183 | Facilitate the interconnection of GEN-2018-052 | SPS | 24 | 1128837
Interconnection | 05 - Southwest | DISIS-2018-001 P1 | ERIS | Roadrunner 115kV Substation Interconnection Expansion (DISIS-2018-001) | 156184 | Facilitate the interconnection of GEN-2018-052 | SPS | 24 | 1039552
9827302852.85

## All Thermal
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME
Non-Converge | 00NR | 0 | N/A | N/A | '' | None |  |  |  |  | None
Thermal | 00NR | 2 | 26SP | GEN-2018-043 | 'FROM -> TO' | 646209 S1209 5 161 646231 S1231 5 161 1 |  | 238 | 0.04405 | 106.21 | P12:161:OPPD:S1209-S1231 CKT 2:::HV:
Thermal | 00NR | 2 | 26SP | GEN-2018-043 | 'FROM -> TO' | 646209 S1209 5 161 646231 S1231 5 161 1 |  | 238 | 0.04405 | 106.21 | P21:161:OPPD:S1231-S1209 CKT2:LT::HV:
Thermal | 00NR | 2 | 26SP | GEN-2018-044 | 'FROM -> TO' | 646209 S1209 5 161 646231 S1231 5 161 1 |  | 238 | 0.05068 | 106.21 | P12:161:OPPD:S1209-S1231 CKT 2:::HV:
Thermal | 00NR | 2 | 26SP | GEN-2018-044 | 'FROM -> TO' | 646209 S1209 5 161 646231 S1231 5 161 1 |  | 238 | 0.05068 | 106.21 | P21:161:OPPD:S1231-S1209 CKT2:LT::HV:
Thermal | 00NR | 2 | 26SP | GEN-2018-015 | 'FROM -> TO' | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 |  | 426 | 0.04433 | 102.86 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 00NR | 2 | 23SP | GEN-2018-043 | 'FROM -> TO' | 646209 S1209 5 161 646231 S1231 5 161 1 |  | 238 | 0.04401 | 102.58 | P12:161:OPPD:S1209-S1231 CKT 2:::HV:
Thermal | 00NR | 2 | 23SP | GEN-2018-043 | 'FROM -> TO' | 646209 S1209 5 161 646231 S1231 5 161 1 |  | 238 | 0.04401 | 102.58 | P21:161:OPPD:S1231-S1209 CKT2:LT::HV:
Thermal | 00NR | 2 | 23SP | GEN-2018-044 | 'FROM -> TO' | 646209 S1209 5 161 646231 S1231 5 161 1 |  | 238 | 0.05063 | 102.58 | P12:161:OPPD:S1209-S1231 CKT 2:::HV:
Thermal | 00NR | 2 | 23SP | GEN-2018-044 | 'FROM -> TO' | 646209 S1209 5 161 646231 S1231 5 161 1 |  | 238 | 0.05063 | 102.58 | P21:161:OPPD:S1231-S1209 CKT2:LT::HV:
Thermal | 00NR | 2 | 23SP | GEN-2018-014 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.06677 | 115.66 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 2 | 23SP | GEN-2018-014 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.06677 | 115.66 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 00NR | 2 | 23SP | GEN-2018-014 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.06677 | 115.66 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 00NR | 2 | 26SP | GEN-2018-014 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.06677 | 104.98 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 00NR | 2 | 26SP | GEN-2018-014 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.06677 | 104.98 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 2 | 26SP | GEN-2018-014 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.06677 | 104.98 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 00NR | 2 | 26WP | GEN-2018-014 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 320 | 0.06677 | 104.27 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 00NR | 2 | 26WP | GEN-2018-014 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 320 | 0.06677 | 104.27 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 2 | 26WP | GEN-2018-014 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 320 | 0.06677 | 104.27 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 00NR | 2 | 23SP | GEN-2018-022 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.09659 | 115.66 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 2 | 23SP | GEN-2018-022 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.09659 | 115.66 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 00NR | 2 | 23SP | GEN-2018-022 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.09659 | 115.66 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 00NR | 2 | 26SP | GEN-2018-022 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.09659 | 104.98 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 00NR | 2 | 26SP | GEN-2018-022 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.09659 | 104.98 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 2 | 26SP | GEN-2018-022 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.09659 | 104.98 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 00NR | 2 | 26WP | GEN-2018-022 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 320 | 0.09659 | 104.27 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 00NR | 2 | 26WP | GEN-2018-022 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 320 | 0.09659 | 104.27 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 2 | 26WP | GEN-2018-022 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 320 | 0.09659 | 104.27 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 00NR | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.25468 | 115.66 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.25468 | 115.66 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 00NR | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.25468 | 115.66 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 00NR | 2 | 26SP | GEN-2018-038 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.25468 | 104.98 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 00NR | 2 | 26SP | GEN-2018-038 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.25468 | 104.98 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 2 | 26SP | GEN-2018-038 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.25468 | 104.98 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 00NR | 2 | 26WP | GEN-2018-038 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 320 | 0.25468 | 104.27 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 00NR | 2 | 26WP | GEN-2018-038 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 320 | 0.25468 | 104.27 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 2 | 26WP | GEN-2018-038 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 320 | 0.25468 | 104.27 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 00NR | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.25428 | 115.66 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.25428 | 115.66 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 00NR | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.25428 | 115.66 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 00NR | 2 | 26SP | GEN-2018-040 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.25428 | 104.98 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 00NR | 2 | 26SP | GEN-2018-040 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.25428 | 104.98 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 2 | 26SP | GEN-2018-040 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.25428 | 104.98 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 00NR | 2 | 26WP | GEN-2018-040 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 320 | 0.25428 | 104.27 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 00NR | 2 | 26WP | GEN-2018-040 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 320 | 0.25428 | 104.27 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 2 | 26WP | GEN-2018-040 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 320 | 0.25428 | 104.27 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 00NR | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.25428 | 115.66 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.25428 | 115.66 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 00NR | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.25428 | 115.66 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 00NR | 2 | 26SP | GEN-2018-041 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.25428 | 104.98 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 00NR | 2 | 26SP | GEN-2018-041 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.25428 | 104.98 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 2 | 26SP | GEN-2018-041 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.25428 | 104.98 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 00NR | 2 | 26WP | GEN-2018-041 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 320 | 0.25428 | 104.27 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 00NR | 2 | 26WP | GEN-2018-041 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 320 | 0.25428 | 104.27 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 2 | 26WP | GEN-2018-041 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 320 | 0.25428 | 104.27 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 00NR | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.25428 | 115.66 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.25428 | 115.66 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 00NR | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.25428 | 115.66 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 00NR | 2 | 26SP | GEN-2018-042 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.25428 | 104.98 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 00NR | 2 | 26SP | GEN-2018-042 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.25428 | 104.98 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 2 | 26SP | GEN-2018-042 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.25428 | 104.98 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 00NR | 2 | 26WP | GEN-2018-042 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 320 | 0.25428 | 104.27 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 00NR | 2 | 26WP | GEN-2018-042 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 320 | 0.25428 | 104.27 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 2 | 26WP | GEN-2018-042 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 320 | 0.25428 | 104.27 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 00NR | 2 | 23SP | GEN-2018-044 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.03027 | 115.66 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 2 | 23SP | GEN-2018-044 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.03027 | 115.66 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 00NR | 2 | 23SP | GEN-2018-044 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.03027 | 115.66 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 00NR | 2 | 26SP | GEN-2018-044 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.03027 | 104.98 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 00NR | 2 | 26SP | GEN-2018-044 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.03027 | 104.98 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 2 | 26SP | GEN-2018-044 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 281 | 0.03027 | 104.98 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 00NR | 2 | 26WP | GEN-2018-044 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 320 | 0.03027 | 104.27 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 00NR | 2 | 26WP | GEN-2018-044 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 320 | 0.03027 | 104.27 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 2 | 26WP | GEN-2018-044 | 'FROM -> TO' | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 |  | 320 | 0.03027 | 104.27 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Non-Converge | 01ALL | 0 | N/A | N/A | '' | None |  |  |  |  | None
Thermal | 01ALL | 2 | 23SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.57779 | 112.66 | 652455 ROBERTSCTY7 115 652522 SUMMIT-7 115 1
Thermal | 01ALL | 2 | 26SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.57764 | 112.34 | 652455 ROBERTSCTY7 115 652522 SUMMIT-7 115 1
Thermal | 01ALL | 2 | 23SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.46944 | 108.2 | P12:230:OTP:AUTO-SINGLE:HANKSON4:FORMAN4:1
Thermal | 01ALL | 2 | 23SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.46944 | 108.2 | P21:230:OTP:AUTO-SINGLE:HANKSON4:FORMAN4:1
Thermal | 01ALL | 2 | 26SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.46938 | 108.16 | P12:230:OTP:AUTO-SINGLE:HANKSON4:FORMAN4:1
Thermal | 01ALL | 2 | 26SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.46938 | 108.16 | P21:230:OTP:AUTO-SINGLE:HANKSON4:FORMAN4:1
Thermal | 01ALL | 2 | 26SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.45219 | 107.37 | 652529 WATERTN3 345 3WXFMR WT2 KU1A _1 1
Thermal | 01ALL | 2 | 26SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.46355 | 106.61 | 601031 BRKNGCO3 345 620483 ASTORIA 3 345 1
Thermal | 01ALL | 2 | 23SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.45225 | 106.53 | 652529 WATERTN3 345 3WXFMR WT2 KU1A _1 1
Thermal | 01ALL | 2 | 23SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.57779 | 106.49 | 652438 FORMAN 7 115 652455 ROBERTSCTY7 115 1
Thermal | 01ALL | 2 | 23SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.46362 | 106.42 | 601031 BRKNGCO3 345 620483 ASTORIA 3 345 1
Thermal | 01ALL | 2 | 23SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.46315 | 106.1 | 652529 WATERTN3 345 659165 CROCKER_-BE3 345 2
Thermal | 01ALL | 2 | 23SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.46315 | 106.1 | P12:345:UMZW:# 1681 #:: WT2 IN SD. WT2-GRT BRANCH FAULT:EHV:
Thermal | 01ALL | 2 | 26SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.57764 | 106.04 | 652438 FORMAN 7 115 652455 ROBERTSCTY7 115 1
Thermal | 01ALL | 2 | 26SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.46306 | 105.83 | 652529 WATERTN3 345 659165 CROCKER_-BE3 345 2
Thermal | 01ALL | 2 | 26SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.46306 | 105.83 | P12:345:UMZW:# 1681 #:: WT2 IN SD. WT2-GRT BRANCH FAULT:EHV:
Thermal | 01ALL | 2 | 26SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.45831 | 105.03 | 652537 WHITE 3 345 3WXFMR WHT KU1A _1 1
Thermal | 01ALL | 2 | 26SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.46553 | 104.77 | P12:230:OTP:AUTO-SINGLE:HANKSON4:WAHPETN4:1
Thermal | 01ALL | 2 | 26SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.46553 | 104.77 | P21:230:OTP:AUTO-SINGLE:HANKSON4:WAHPETN4:1
Thermal | 01ALL | 2 | 26SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.46334 | 104.72 | 620416 TWIN BRKS 3 345 620417 BSSOUTH3 345 1
Thermal | 01ALL | 2 | 26SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.46208 | 104.66 | P12:230:UMZW:# 1704 #: FB IN SD. FB-BIGSTONE LINE FAULT
Thermal | 01ALL | 2 | 26SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.46208 | 104.66 | P12:230:UMZW:# 1704 #:: FB IN SD. FB-BIGSTONE BRANCH FAULT:HV:
Thermal | 01ALL | 2 | 26SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.46352 | 104.65 | 620480 DEUEL CO 3 345 620483 ASTORIA 3 345 1
Thermal | 01ALL | 2 | 23SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.4656 | 104.53 | P12:230:OTP:AUTO-SINGLE:HANKSON4:WAHPETN4:1
Thermal | 01ALL | 2 | 23SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.4656 | 104.53 | P21:230:OTP:AUTO-SINGLE:HANKSON4:WAHPETN4:1
Thermal | 01ALL | 2 | 23SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.46339 | 104.51 | 620416 TWIN BRKS 3 345 620417 BSSOUTH3 345 1
Thermal | 01ALL | 2 | 26SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.45831 | 104.43 | P12:115:UMZW:# 127 #: BR IN SD. BR-WHT LINE FAULT
Thermal | 01ALL | 2 | 23SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.46359 | 104.42 | 620480 DEUEL CO 3 345 620483 ASTORIA 3 345 1
Thermal | 01ALL | 2 | 23SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.46215 | 104.24 | P12:230:UMZW:# 1704 #: FB IN SD. FB-BIGSTONE LINE FAULT
Thermal | 01ALL | 2 | 23SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.46215 | 104.24 | P12:230:UMZW:# 1704 #:: FB IN SD. FB-BIGSTONE BRANCH FAULT:HV:
Thermal | 01ALL | 2 | 23SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.45838 | 103.99 | 652537 WHITE 3 345 3WXFMR WHT KU1A _1 1
Thermal | 01ALL | 2 | 23SP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.46359 | 103.52 | 620417 BSSOUTH3 345 620480 DEUEL CO 3 345 1
Thermal | 01ALL | 2 | 26WP | GEN-2018-007 | 'FROM -> TO' | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 110 | 0.57735 | 103.37 | 652455 ROBERTSCTY7 115 652522 SUMMIT-7 115 1
Thermal | 01ALL | 2 | 26L | N/A | '' | None |  |  |  |  | None
Non-Converge | 01NR | 0 | N/A | N/A | '' | None |  |  |  |  | None
Thermal | 01NR | 2 | 26L | N/A | '' | None |  |  |  |  | None
Non-Converge | 02ALL | 0 | N/A | N/A | '' | None |  |  |  |  | None
Thermal | 02ALL | 2 | 23SP | GEN-2018-036 | 'FROM -> TO' | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.48602 | 117.11 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 02ALL | 2 | 23SP | GEN-2018-036 | 'FROM -> TO' | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.48602 | 117.07 | P12:345:UMZ:# 5863 #: PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 02ALL | 2 | 23SP | GEN-2018-036 | 'FROM -> TO' | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.48602 | 117 | 640252 KEYSTON3 345 659425 SD.LS-KS-MB3 345 1
Thermal | 02ALL | 2 | 26WP | GEN-2018-036 | 'FROM -> TO' | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.48575 | 115.75 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 02ALL | 2 | 26WP | GEN-2018-036 | 'FROM -> TO' | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.48575 | 115.67 | 640252 KEYSTON3 345 659425 SD.LS-KS-MB3 345 1
Thermal | 02ALL | 2 | 26WP | GEN-2018-036 | 'FROM -> TO' | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.48575 | 115.64 | P12:345:UMZ:# 5863 #: PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 02ALL | 2 | 26SP | GEN-2018-036 | 'FROM -> TO' | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.48769 | 113.22 | P12:345:UMZ:# 5863 #: PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 02ALL | 2 | 26SP | GEN-2018-036 | 'FROM -> TO' | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.48769 | 113.21 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 02ALL | 2 | 26SP | GEN-2018-036 | 'FROM -> TO' | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.48769 | 113.2 | 640252 KEYSTON3 345 659425 SD.LS-KS-MB3 345 1
Thermal | 02ALL | 2 | 26WP | GEN-2018-012 | 'FROM -> TO' | 640325 REDWILO3 345 762808 G18-045-TAP 345 1 |  | 956 | 0.07946 | 108.68 | 640252 KEYSTON3 345 640325 REDWILO3 345 1
Thermal | 02ALL | 2 | 26WP | GEN-2018-036 | 'FROM -> TO' | 640325 REDWILO3 345 762808 G18-045-TAP 345 1 |  | 956 | 0.22386 | 108.68 | 640252 KEYSTON3 345 640325 REDWILO3 345 1
Thermal | 02ALL | 2 | 26WP | GEN-2018-045 | 'FROM -> TO' | 640325 REDWILO3 345 762808 G18-045-TAP 345 1 |  | 956 | 0.40469 | 108.68 | 640252 KEYSTON3 345 640325 REDWILO3 345 1
Thermal | 02ALL | 2 | 26WP | GEN-2018-046 | 'FROM -> TO' | 640325 REDWILO3 345 762808 G18-045-TAP 345 1 |  | 956 | 0.40469 | 108.68 | 640252 KEYSTON3 345 640325 REDWILO3 345 1
Thermal | 02ALL | 2 | 26WP | GEN-2018-056 | 'FROM -> TO' | 640325 REDWILO3 345 762808 G18-045-TAP 345 1 |  | 956 | 0.09308 | 108.68 | 640252 KEYSTON3 345 640325 REDWILO3 345 1
Thermal | 02ALL | 2 | 23SP | GEN-2018-012 | 'FROM -> TO' | 640325 REDWILO3 345 762808 G18-045-TAP 345 1 |  | 956 | 0.06386 | 106.36 | 640252 KEYSTON3 345 640325 REDWILO3 345 1
Thermal | 02ALL | 2 | 23SP | GEN-2018-036 | 'FROM -> TO' | 640325 REDWILO3 345 762808 G18-045-TAP 345 1 |  | 956 | 0.24807 | 106.36 | 640252 KEYSTON3 345 640325 REDWILO3 345 1
Thermal | 02ALL | 2 | 23SP | GEN-2018-045 | 'FROM -> TO' | 640325 REDWILO3 345 762808 G18-045-TAP 345 1 |  | 956 | 0.435 | 106.36 | 640252 KEYSTON3 345 640325 REDWILO3 345 1
Thermal | 02ALL | 2 | 23SP | GEN-2018-046 | 'FROM -> TO' | 640325 REDWILO3 345 762808 G18-045-TAP 345 1 |  | 956 | 0.435 | 106.36 | 640252 KEYSTON3 345 640325 REDWILO3 345 1
Thermal | 02ALL | 2 | 23SP | GEN-2018-056 | 'FROM -> TO' | 640325 REDWILO3 345 762808 G18-045-TAP 345 1 |  | 956 | 0.07123 | 106.36 | 640252 KEYSTON3 345 640325 REDWILO3 345 1
Thermal | 02ALL | 2 | 23SP | GEN-2018-036 | 'FROM -> TO' | 659134 SIDNEY___TS4 230 659210 SIDNEY__-MB4 230 1 |  | 478 | 0.60749 | 100.62 | 640252 KEYSTON3 345 659425 SD.LS-KS-MB3 345 1
Thermal | 02ALL | 2 | 26L | N/A | '' | None |  |  |  |  | None
Non-Converge | 02NR | 0 | N/A | N/A | '' | None |  |  |  |  | None
Thermal | 02NR | 2 | 26L | N/A | '' | None |  |  |  |  | None
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-003 | '' | Non-Converge |  |  | 0.04335 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-003 | '' | Non-Converge |  |  | 0.04257 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-003 | '' | Non-Converge |  |  | 0.04785 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-003 | '' | Non-Converge |  |  | 0.04335 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-003 | '' | Non-Converge |  |  | 0.04257 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-003 | '' | Non-Converge |  |  | 0.04785 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-003 | '' | Non-Converge |  |  | 0.04335 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-003 | '' | Non-Converge |  |  | 0.04257 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-003 | '' | Non-Converge |  |  | 0.04785 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-003 | '' | Non-Converge |  |  | 0.04335 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-003 | '' | Non-Converge |  |  | 0.04257 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-003 | '' | Non-Converge |  |  | 0.04785 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-003 | '' | Non-Converge |  |  | 0.04335 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-003 | '' | Non-Converge |  |  | 0.04257 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-003 | '' | Non-Converge |  |  | 0.04785 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-003 | '' | Non-Converge |  |  | 0.04335 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-003 | '' | Non-Converge |  |  | 0.04257 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-003 | '' | Non-Converge |  |  | 0.04785 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-003 | '' | Non-Converge |  |  | 0.04335 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-003 | '' | Non-Converge |  |  | 0.04257 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-003 | '' | Non-Converge |  |  | 0.04785 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-006 | '' | Non-Converge |  |  | 0.04152 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-006 | '' | Non-Converge |  |  | 0.04071 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-006 | '' | Non-Converge |  |  | 0.04598 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-006 | '' | Non-Converge |  |  | 0.04152 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-006 | '' | Non-Converge |  |  | 0.04071 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-006 | '' | Non-Converge |  |  | 0.04598 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-006 | '' | Non-Converge |  |  | 0.04152 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-006 | '' | Non-Converge |  |  | 0.04071 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-006 | '' | Non-Converge |  |  | 0.04598 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-006 | '' | Non-Converge |  |  | 0.04152 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-006 | '' | Non-Converge |  |  | 0.04071 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-006 | '' | Non-Converge |  |  | 0.04598 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-006 | '' | Non-Converge |  |  | 0.04152 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-006 | '' | Non-Converge |  |  | 0.04071 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-006 | '' | Non-Converge |  |  | 0.04598 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-006 | '' | Non-Converge |  |  | 0.04152 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-006 | '' | Non-Converge |  |  | 0.04071 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-006 | '' | Non-Converge |  |  | 0.04598 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-006 | '' | Non-Converge |  |  | 0.04152 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-006 | '' | Non-Converge |  |  | 0.04071 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-006 | '' | Non-Converge |  |  | 0.04598 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-007 | '' | Non-Converge |  |  | 0.03248 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-007 | '' | Non-Converge |  |  | 0.03248 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-007 | '' | Non-Converge |  |  | 0.03248 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-007 | '' | Non-Converge |  |  | 0.03248 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-007 | '' | Non-Converge |  |  | 0.03248 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-007 | '' | Non-Converge |  |  | 0.03248 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-007 | '' | Non-Converge |  |  | 0.03248 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-010 | '' | Non-Converge |  |  | 0.04556 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-010 | '' | Non-Converge |  |  | 0.04476 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-010 | '' | Non-Converge |  |  | 0.05004 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-010 | '' | Non-Converge |  |  | 0.04556 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-010 | '' | Non-Converge |  |  | 0.04476 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-010 | '' | Non-Converge |  |  | 0.05004 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-010 | '' | Non-Converge |  |  | 0.04556 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-010 | '' | Non-Converge |  |  | 0.04476 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-010 | '' | Non-Converge |  |  | 0.05004 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-010 | '' | Non-Converge |  |  | 0.04556 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-010 | '' | Non-Converge |  |  | 0.04476 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-010 | '' | Non-Converge |  |  | 0.05004 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-010 | '' | Non-Converge |  |  | 0.04556 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-010 | '' | Non-Converge |  |  | 0.04476 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-010 | '' | Non-Converge |  |  | 0.05004 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-010 | '' | Non-Converge |  |  | 0.04556 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-010 | '' | Non-Converge |  |  | 0.04476 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-010 | '' | Non-Converge |  |  | 0.05004 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-010 | '' | Non-Converge |  |  | 0.04556 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-010 | '' | Non-Converge |  |  | 0.04476 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-010 | '' | Non-Converge |  |  | 0.05004 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-011 | '' | Non-Converge |  |  | 0.04581 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-011 | '' | Non-Converge |  |  | 0.045 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-011 | '' | Non-Converge |  |  | 0.05028 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-011 | '' | Non-Converge |  |  | 0.04581 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-011 | '' | Non-Converge |  |  | 0.045 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-011 | '' | Non-Converge |  |  | 0.05028 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-011 | '' | Non-Converge |  |  | 0.04581 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-011 | '' | Non-Converge |  |  | 0.045 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-011 | '' | Non-Converge |  |  | 0.05028 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-011 | '' | Non-Converge |  |  | 0.04581 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-011 | '' | Non-Converge |  |  | 0.045 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-011 | '' | Non-Converge |  |  | 0.05028 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-011 | '' | Non-Converge |  |  | 0.04581 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-011 | '' | Non-Converge |  |  | 0.045 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-011 | '' | Non-Converge |  |  | 0.05028 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-011 | '' | Non-Converge |  |  | 0.04581 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-011 | '' | Non-Converge |  |  | 0.045 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-011 | '' | Non-Converge |  |  | 0.05028 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-011 | '' | Non-Converge |  |  | 0.04581 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-011 | '' | Non-Converge |  |  | 0.045 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-011 | '' | Non-Converge |  |  | 0.05028 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-009 | '' | Non-Converge |  |  | 0.0471 |  | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-009 | '' | Non-Converge |  |  | 0.11684 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-009 | '' | Non-Converge |  |  | 0.11634 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-009 | '' | Non-Converge |  |  | 0.12515 |  | P23:345:SUNC:HLC_BRK188:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-009 | '' | Non-Converge |  |  | 0.11634 |  | P23:345:SUNC:HLC_BRK188:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-009 | '' | Non-Converge |  |  | 0.21256 |  | P23:345:SUNC:HLC_BRK282:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-009 | '' | Non-Converge |  |  | 0.21249 |  | P23:345:SUNC:HLC_BRK282:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-009 | '' | Non-Converge |  |  | 0.0471 |  | P42:345:SPS:HITCHLAND:1R15:SLG:EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-014 | '' | Non-Converge |  |  | 0.62733 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-014 | '' | Non-Converge |  |  | 0.63198 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-014 | '' | Non-Converge |  |  | 0.62695 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-014 | '' | Non-Converge |  |  | 0.63228 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-014 | '' | Non-Converge |  |  | 0.62733 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26L | GEN-2018-014 | '' | Non-Converge |  |  | 0.63198 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-014 | '' | Non-Converge |  |  | 0.62695 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-014 | '' | Non-Converge |  |  | 0.63228 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-014 | '' | Non-Converge |  |  | 0.62733 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-014 | '' | Non-Converge |  |  | 0.63198 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-014 | '' | Non-Converge |  |  | 0.62695 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-014 | '' | Non-Converge |  |  | 0.63228 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-014 | '' | Non-Converge |  |  | 0.62733 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-014 | '' | Non-Converge |  |  | 0.63198 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-014 | '' | Non-Converge |  |  | 0.62695 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-014 | '' | Non-Converge |  |  | 0.63228 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-014 | '' | Non-Converge |  |  | 0.62733 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-014 | '' | Non-Converge |  |  | 0.63198 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-014 | '' | Non-Converge |  |  | 0.62695 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-014 | '' | Non-Converge |  |  | 0.63228 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-014 | '' | Non-Converge |  |  | 0.62733 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-014 | '' | Non-Converge |  |  | 0.63198 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-014 | '' | Non-Converge |  |  | 0.62695 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-014 | '' | Non-Converge |  |  | 0.63228 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-014 | '' | Non-Converge |  |  | 0.62733 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-014 | '' | Non-Converge |  |  | 0.63198 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-014 | '' | Non-Converge |  |  | 0.62695 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-014 | '' | Non-Converge |  |  | 0.63228 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-022 | '' | Non-Converge |  |  | 0.54456 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-022 | '' | Non-Converge |  |  | 0.54413 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-022 | '' | Non-Converge |  |  | 0.54946 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-022 | '' | Non-Converge |  |  | 0.54456 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-022 | '' | Non-Converge |  |  | 0.54413 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-022 | '' | Non-Converge |  |  | 0.54946 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-022 | '' | Non-Converge |  |  | 0.54456 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-022 | '' | Non-Converge |  |  | 0.54413 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-022 | '' | Non-Converge |  |  | 0.54946 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-022 | '' | Non-Converge |  |  | 0.54456 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-022 | '' | Non-Converge |  |  | 0.54413 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-022 | '' | Non-Converge |  |  | 0.54946 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-022 | '' | Non-Converge |  |  | 0.54456 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-022 | '' | Non-Converge |  |  | 0.54413 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-022 | '' | Non-Converge |  |  | 0.54946 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-022 | '' | Non-Converge |  |  | 0.54456 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-022 | '' | Non-Converge |  |  | 0.54413 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-022 | '' | Non-Converge |  |  | 0.54946 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-022 | '' | Non-Converge |  |  | 0.54456 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-022 | '' | Non-Converge |  |  | 0.54413 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-022 | '' | Non-Converge |  |  | 0.54946 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-030 | '' | Non-Converge |  |  | 0.79137 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-030 | '' | Non-Converge |  |  | 0.79139 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-030 | '' | Non-Converge |  |  | 0.79137 |  | P23:345:SUNC:HLC_BRK188:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-030 | '' | Non-Converge |  |  | 0.79139 |  | P23:345:SUNC:HLC_BRK188:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-030 | '' | Non-Converge |  |  | 0.79137 |  | P23:345:SUNC:HLC_BRK282:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-030 | '' | Non-Converge |  |  | 0.79139 |  | P23:345:SUNC:HLC_BRK282:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-031 | '' | Non-Converge |  |  | 0.06116 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-031 | '' | Non-Converge |  |  | 0.06043 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-031 | '' | Non-Converge |  |  | 0.06575 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-031 | '' | Non-Converge |  |  | 0.06116 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-031 | '' | Non-Converge |  |  | 0.06043 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-031 | '' | Non-Converge |  |  | 0.06575 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-031 | '' | Non-Converge |  |  | 0.06116 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-031 | '' | Non-Converge |  |  | 0.06043 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-031 | '' | Non-Converge |  |  | 0.06575 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-031 | '' | Non-Converge |  |  | 0.06116 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-031 | '' | Non-Converge |  |  | 0.06043 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-031 | '' | Non-Converge |  |  | 0.06575 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-031 | '' | Non-Converge |  |  | 0.06116 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-031 | '' | Non-Converge |  |  | 0.06043 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-031 | '' | Non-Converge |  |  | 0.06575 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-031 | '' | Non-Converge |  |  | 0.06116 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-031 | '' | Non-Converge |  |  | 0.06043 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-031 | '' | Non-Converge |  |  | 0.06575 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-031 | '' | Non-Converge |  |  | 0.06116 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-031 | '' | Non-Converge |  |  | 0.06043 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-031 | '' | Non-Converge |  |  | 0.06575 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-032 | '' | Non-Converge |  |  | 0.03244 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-032 | '' | Non-Converge |  |  | 0.0324 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-032 | '' | Non-Converge |  |  | 0.03244 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-032 | '' | Non-Converge |  |  | 0.0324 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26L | GEN-2018-032 | '' | Non-Converge |  |  | 0.03244 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-032 | '' | Non-Converge |  |  | 0.0324 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-032 | '' | Non-Converge |  |  | 0.03244 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-032 | '' | Non-Converge |  |  | 0.0324 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-032 | '' | Non-Converge |  |  | 0.03244 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-032 | '' | Non-Converge |  |  | 0.0324 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-032 | '' | Non-Converge |  |  | 0.03244 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-032 | '' | Non-Converge |  |  | 0.0324 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-032 | '' | Non-Converge |  |  | 0.03244 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-032 | '' | Non-Converge |  |  | 0.0324 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-038 | '' | Non-Converge |  |  | 0.10571 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-038 | '' | Non-Converge |  |  | 0.10503 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-038 | '' | Non-Converge |  |  | 0.11033 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-038 | '' | Non-Converge |  |  | 0.10571 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-038 | '' | Non-Converge |  |  | 0.10503 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-038 | '' | Non-Converge |  |  | 0.11033 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-038 | '' | Non-Converge |  |  | 0.10571 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-038 | '' | Non-Converge |  |  | 0.10503 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-038 | '' | Non-Converge |  |  | 0.11033 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-038 | '' | Non-Converge |  |  | 0.10571 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-038 | '' | Non-Converge |  |  | 0.10503 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-038 | '' | Non-Converge |  |  | 0.11033 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-038 | '' | Non-Converge |  |  | 0.10571 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-038 | '' | Non-Converge |  |  | 0.10503 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-038 | '' | Non-Converge |  |  | 0.11033 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-038 | '' | Non-Converge |  |  | 0.10571 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-038 | '' | Non-Converge |  |  | 0.10503 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-038 | '' | Non-Converge |  |  | 0.11033 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-038 | '' | Non-Converge |  |  | 0.10571 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-038 | '' | Non-Converge |  |  | 0.10503 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-038 | '' | Non-Converge |  |  | 0.11033 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-040 | '' | Non-Converge |  |  | 0.10554 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-040 | '' | Non-Converge |  |  | 0.11018 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-040 | '' | Non-Converge |  |  | 0.10486 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-040 | '' | Non-Converge |  |  | 0.11016 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-040 | '' | Non-Converge |  |  | 0.10554 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26L | GEN-2018-040 | '' | Non-Converge |  |  | 0.11018 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-040 | '' | Non-Converge |  |  | 0.10486 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-040 | '' | Non-Converge |  |  | 0.11016 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-040 | '' | Non-Converge |  |  | 0.10554 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-040 | '' | Non-Converge |  |  | 0.11018 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-040 | '' | Non-Converge |  |  | 0.10486 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-040 | '' | Non-Converge |  |  | 0.11016 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-040 | '' | Non-Converge |  |  | 0.10554 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-040 | '' | Non-Converge |  |  | 0.11018 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-040 | '' | Non-Converge |  |  | 0.10486 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-040 | '' | Non-Converge |  |  | 0.11016 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-040 | '' | Non-Converge |  |  | 0.10554 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-040 | '' | Non-Converge |  |  | 0.11018 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-040 | '' | Non-Converge |  |  | 0.10486 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-040 | '' | Non-Converge |  |  | 0.11016 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-040 | '' | Non-Converge |  |  | 0.10554 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-040 | '' | Non-Converge |  |  | 0.11018 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-040 | '' | Non-Converge |  |  | 0.10486 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-040 | '' | Non-Converge |  |  | 0.11016 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-040 | '' | Non-Converge |  |  | 0.10554 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-040 | '' | Non-Converge |  |  | 0.11018 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-040 | '' | Non-Converge |  |  | 0.10486 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-040 | '' | Non-Converge |  |  | 0.11016 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-041 | '' | Non-Converge |  |  | 0.10554 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-041 | '' | Non-Converge |  |  | 0.11018 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-041 | '' | Non-Converge |  |  | 0.10486 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-041 | '' | Non-Converge |  |  | 0.11016 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-041 | '' | Non-Converge |  |  | 0.10554 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26L | GEN-2018-041 | '' | Non-Converge |  |  | 0.11018 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-041 | '' | Non-Converge |  |  | 0.10486 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-041 | '' | Non-Converge |  |  | 0.11016 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-041 | '' | Non-Converge |  |  | 0.10554 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-041 | '' | Non-Converge |  |  | 0.11018 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-041 | '' | Non-Converge |  |  | 0.10486 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-041 | '' | Non-Converge |  |  | 0.11016 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-041 | '' | Non-Converge |  |  | 0.10554 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-041 | '' | Non-Converge |  |  | 0.11018 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-041 | '' | Non-Converge |  |  | 0.10486 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-041 | '' | Non-Converge |  |  | 0.11016 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-041 | '' | Non-Converge |  |  | 0.10554 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-041 | '' | Non-Converge |  |  | 0.11018 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-041 | '' | Non-Converge |  |  | 0.10486 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-041 | '' | Non-Converge |  |  | 0.11016 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-041 | '' | Non-Converge |  |  | 0.10554 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-041 | '' | Non-Converge |  |  | 0.11018 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-041 | '' | Non-Converge |  |  | 0.10486 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-041 | '' | Non-Converge |  |  | 0.11016 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-041 | '' | Non-Converge |  |  | 0.10554 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-041 | '' | Non-Converge |  |  | 0.11018 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-041 | '' | Non-Converge |  |  | 0.10486 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-041 | '' | Non-Converge |  |  | 0.11016 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-042 | '' | Non-Converge |  |  | 0.10554 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-042 | '' | Non-Converge |  |  | 0.11018 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-042 | '' | Non-Converge |  |  | 0.10486 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-042 | '' | Non-Converge |  |  | 0.11016 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-042 | '' | Non-Converge |  |  | 0.10554 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26L | GEN-2018-042 | '' | Non-Converge |  |  | 0.11018 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-042 | '' | Non-Converge |  |  | 0.10486 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-042 | '' | Non-Converge |  |  | 0.11016 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-042 | '' | Non-Converge |  |  | 0.10554 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-042 | '' | Non-Converge |  |  | 0.11018 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-042 | '' | Non-Converge |  |  | 0.10486 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-042 | '' | Non-Converge |  |  | 0.11016 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-042 | '' | Non-Converge |  |  | 0.10554 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-042 | '' | Non-Converge |  |  | 0.11018 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-042 | '' | Non-Converge |  |  | 0.10486 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-042 | '' | Non-Converge |  |  | 0.11016 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-042 | '' | Non-Converge |  |  | 0.10554 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-042 | '' | Non-Converge |  |  | 0.11018 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-042 | '' | Non-Converge |  |  | 0.10486 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-042 | '' | Non-Converge |  |  | 0.11016 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-042 | '' | Non-Converge |  |  | 0.10554 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-042 | '' | Non-Converge |  |  | 0.11018 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-042 | '' | Non-Converge |  |  | 0.10486 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-042 | '' | Non-Converge |  |  | 0.11016 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-042 | '' | Non-Converge |  |  | 0.10554 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-042 | '' | Non-Converge |  |  | 0.11018 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-042 | '' | Non-Converge |  |  | 0.10486 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-042 | '' | Non-Converge |  |  | 0.11016 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-049 | '' | Non-Converge |  |  | 0.07523 |  | P23:345:SUNC:HLC_BRK188:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-049 | '' | Non-Converge |  |  | 0.05836 |  | P23:345:SUNC:HLC_BRK282:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-049 | '' | Non-Converge |  |  | 0.05734 |  | P23:345:SUNC:HLC_BRK282:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-054 | '' | Non-Converge |  |  | 0.06006 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-054 | '' | Non-Converge |  |  | 0.05932 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-054 | '' | Non-Converge |  |  | 0.06458 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-054 | '' | Non-Converge |  |  | 0.06006 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-054 | '' | Non-Converge |  |  | 0.05932 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-054 | '' | Non-Converge |  |  | 0.06458 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-054 | '' | Non-Converge |  |  | 0.06006 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-054 | '' | Non-Converge |  |  | 0.05932 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-054 | '' | Non-Converge |  |  | 0.06458 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-054 | '' | Non-Converge |  |  | 0.06006 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-054 | '' | Non-Converge |  |  | 0.05932 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-054 | '' | Non-Converge |  |  | 0.06458 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-054 | '' | Non-Converge |  |  | 0.06006 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-054 | '' | Non-Converge |  |  | 0.05932 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-054 | '' | Non-Converge |  |  | 0.06458 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-054 | '' | Non-Converge |  |  | 0.06006 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-054 | '' | Non-Converge |  |  | 0.05932 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-054 | '' | Non-Converge |  |  | 0.06458 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-054 | '' | Non-Converge |  |  | 0.06006 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-054 | '' | Non-Converge |  |  | 0.05932 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-054 | '' | Non-Converge |  |  | 0.06458 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-058 | '' | Non-Converge |  |  | 0.03054 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-058 | '' | Non-Converge |  |  | 0.0351 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-058 | '' | Non-Converge |  |  | 0.03054 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-058 | '' | Non-Converge |  |  | 0.0351 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-058 | '' | Non-Converge |  |  | 0.03054 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-058 | '' | Non-Converge |  |  | 0.0351 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-058 | '' | Non-Converge |  |  | 0.03054 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-058 | '' | Non-Converge |  |  | 0.0351 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-058 | '' | Non-Converge |  |  | 0.03054 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-058 | '' | Non-Converge |  |  | 0.0351 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-058 | '' | Non-Converge |  |  | 0.03054 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-058 | '' | Non-Converge |  |  | 0.0351 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-058 | '' | Non-Converge |  |  | 0.03054 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-058 | '' | Non-Converge |  |  | 0.0351 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-059 | '' | Non-Converge |  |  | 0.03054 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-059 | '' | Non-Converge |  |  | 0.0351 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-059 | '' | Non-Converge |  |  | 0.03054 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-059 | '' | Non-Converge |  |  | 0.0351 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-059 | '' | Non-Converge |  |  | 0.03054 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-059 | '' | Non-Converge |  |  | 0.0351 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-059 | '' | Non-Converge |  |  | 0.03054 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-059 | '' | Non-Converge |  |  | 0.0351 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-059 | '' | Non-Converge |  |  | 0.03054 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-059 | '' | Non-Converge |  |  | 0.0351 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-059 | '' | Non-Converge |  |  | 0.03054 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-059 | '' | Non-Converge |  |  | 0.0351 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-059 | '' | Non-Converge |  |  | 0.03054 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-059 | '' | Non-Converge |  |  | 0.0351 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-062 | '' | Non-Converge |  |  | 0.0506 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-062 | '' | Non-Converge |  |  | 0.05006 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-062 | '' | Non-Converge |  |  | 0.05536 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-062 | '' | Non-Converge |  |  | 0.0506 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-062 | '' | Non-Converge |  |  | 0.05006 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-062 | '' | Non-Converge |  |  | 0.05536 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-062 | '' | Non-Converge |  |  | 0.0506 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-062 | '' | Non-Converge |  |  | 0.05006 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-062 | '' | Non-Converge |  |  | 0.05536 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-062 | '' | Non-Converge |  |  | 0.0506 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-062 | '' | Non-Converge |  |  | 0.05006 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-062 | '' | Non-Converge |  |  | 0.05536 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-062 | '' | Non-Converge |  |  | 0.0506 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-062 | '' | Non-Converge |  |  | 0.05006 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-062 | '' | Non-Converge |  |  | 0.05536 |  | P22:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-062 | '' | Non-Converge |  |  | 0.0506 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-062 | '' | Non-Converge |  |  | 0.05006 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-062 | '' | Non-Converge |  |  | 0.05536 |  | P23:345:OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-062 | '' | Non-Converge |  |  | 0.0506 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-062 | '' | Non-Converge |  |  | 0.05006 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-062 | '' | Non-Converge |  |  | 0.05536 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-014 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.11268 | 147.41 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 23SP | GEN-2018-014 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.11268 | 147.41 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-014 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.11268 | 147.41 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.16234 | 147.41 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 23SP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.16234 | 147.41 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.16234 | 147.41 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42562 | 147.41 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42562 | 147.41 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42562 | 147.41 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42496 | 147.41 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42496 | 147.41 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42496 | 147.41 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42496 | 147.41 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42496 | 147.41 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42496 | 147.41 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42496 | 147.41 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42496 | 147.41 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42496 | 147.41 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-014 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.11268 | 143.36 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 23SP | GEN-2018-014 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.11268 | 143.36 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-014 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.11268 | 143.36 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-022 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.16234 | 143.36 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 23SP | GEN-2018-022 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.16234 | 143.36 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-022 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.16234 | 143.36 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.42562 | 143.36 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.42562 | 143.36 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.42562 | 143.36 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 143.36 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 143.36 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 143.36 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 143.36 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 143.36 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 143.36 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 143.36 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 143.36 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 143.36 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-014 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.10801 | 143.29 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26WP | GEN-2018-014 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.10801 | 143.29 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26WP | GEN-2018-014 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.10801 | 143.29 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.15768 | 143.29 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26WP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.15768 | 143.29 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26WP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.15768 | 143.29 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42104 | 143.29 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26WP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42104 | 143.29 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26WP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42104 | 143.29 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42037 | 143.29 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26WP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42037 | 143.29 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26WP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42037 | 143.29 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42037 | 143.29 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26WP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42037 | 143.29 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26WP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42037 | 143.29 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42037 | 143.29 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26WP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42037 | 143.29 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26WP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42037 | 143.29 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26SP | GEN-2018-014 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.11256 | 140.52 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26SP | GEN-2018-014 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.11256 | 140.52 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26SP | GEN-2018-014 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.11256 | 140.52 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26SP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.16224 | 140.52 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26SP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.16224 | 140.52 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26SP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.16224 | 140.52 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42563 | 140.52 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42563 | 140.52 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42563 | 140.52 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42496 | 140.52 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42496 | 140.52 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42496 | 140.52 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42496 | 140.52 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42496 | 140.52 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42496 | 140.52 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42496 | 140.52 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42496 | 140.52 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.42496 | 140.52 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-014 | 'FROM -> TO' | 541202 SIBLEY 5 161 997381 SIBLEY11 _1 161 11 |  | 440 | 0.11268 | 140.27 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 23SP | GEN-2018-014 | 'FROM -> TO' | 541202 SIBLEY 5 161 997381 SIBLEY11 _1 161 11 |  | 440 | 0.11268 | 140.27 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-014 | 'FROM -> TO' | 541202 SIBLEY 5 161 997381 SIBLEY11 _1 161 11 |  | 440 | 0.11268 | 140.27 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 997381 SIBLEY11 _1 161 11 |  | 440 | 0.16234 | 140.27 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 23SP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 997381 SIBLEY11 _1 161 11 |  | 440 | 0.16234 | 140.27 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 997381 SIBLEY11 _1 161 11 |  | 440 | 0.16234 | 140.27 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 997381 SIBLEY11 _1 161 11 |  | 440 | 0.42562 | 140.27 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 997381 SIBLEY11 _1 161 11 |  | 440 | 0.42562 | 140.27 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 997381 SIBLEY11 _1 161 11 |  | 440 | 0.42562 | 140.27 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 997381 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 140.27 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 997381 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 140.27 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 997381 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 140.27 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 997381 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 140.27 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 997381 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 140.27 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 997381 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 140.27 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 997381 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 140.27 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 997381 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 140.27 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 997381 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 140.27 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-014 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.10801 | 139.23 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26WP | GEN-2018-014 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.10801 | 139.23 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26WP | GEN-2018-014 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.10801 | 139.23 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-022 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.15768 | 139.23 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26WP | GEN-2018-022 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.15768 | 139.23 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26WP | GEN-2018-022 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.15768 | 139.23 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-038 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.42104 | 139.23 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26WP | GEN-2018-038 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.42104 | 139.23 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26WP | GEN-2018-038 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.42104 | 139.23 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-040 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.42037 | 139.23 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26WP | GEN-2018-040 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.42037 | 139.23 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26WP | GEN-2018-040 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.42037 | 139.23 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-041 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.42037 | 139.23 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26WP | GEN-2018-041 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.42037 | 139.23 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26WP | GEN-2018-041 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.42037 | 139.23 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-042 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.42037 | 139.23 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26WP | GEN-2018-042 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.42037 | 139.23 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26WP | GEN-2018-042 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.42037 | 139.23 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-014 | 'FROM -> TO' | 541202 SIBLEY 5 161 997377 SIBLEY11 _1 161 11 |  | 440 | 0.10801 | 137.23 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26WP | GEN-2018-014 | 'FROM -> TO' | 541202 SIBLEY 5 161 997377 SIBLEY11 _1 161 11 |  | 440 | 0.10801 | 137.23 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26WP | GEN-2018-014 | 'FROM -> TO' | 541202 SIBLEY 5 161 997377 SIBLEY11 _1 161 11 |  | 440 | 0.10801 | 137.23 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 997377 SIBLEY11 _1 161 11 |  | 440 | 0.15768 | 137.23 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26WP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 997377 SIBLEY11 _1 161 11 |  | 440 | 0.15768 | 137.23 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26WP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 997377 SIBLEY11 _1 161 11 |  | 440 | 0.15768 | 137.23 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 997377 SIBLEY11 _1 161 11 |  | 440 | 0.42104 | 137.23 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26WP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 997377 SIBLEY11 _1 161 11 |  | 440 | 0.42104 | 137.23 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26WP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 997377 SIBLEY11 _1 161 11 |  | 440 | 0.42104 | 137.23 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 997377 SIBLEY11 _1 161 11 |  | 440 | 0.42037 | 137.23 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26WP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 997377 SIBLEY11 _1 161 11 |  | 440 | 0.42037 | 137.23 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26WP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 997377 SIBLEY11 _1 161 11 |  | 440 | 0.42037 | 137.23 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 997377 SIBLEY11 _1 161 11 |  | 440 | 0.42037 | 137.23 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26WP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 997377 SIBLEY11 _1 161 11 |  | 440 | 0.42037 | 137.23 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26WP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 997377 SIBLEY11 _1 161 11 |  | 440 | 0.42037 | 137.23 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 997377 SIBLEY11 _1 161 11 |  | 440 | 0.42037 | 137.23 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26WP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 997377 SIBLEY11 _1 161 11 |  | 440 | 0.42037 | 137.23 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26WP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 997377 SIBLEY11 _1 161 11 |  | 440 | 0.42037 | 137.23 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26SP | GEN-2018-014 | 'FROM -> TO' | 541201 SIBLEY 7 345 997379 SIBLEY11 _1 161 11 |  | 440 | 0.11256 | 136.82 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26SP | GEN-2018-014 | 'FROM -> TO' | 541201 SIBLEY 7 345 997379 SIBLEY11 _1 161 11 |  | 440 | 0.11256 | 136.82 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26SP | GEN-2018-014 | 'FROM -> TO' | 541201 SIBLEY 7 345 997379 SIBLEY11 _1 161 11 |  | 440 | 0.11256 | 136.82 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26SP | GEN-2018-022 | 'FROM -> TO' | 541201 SIBLEY 7 345 997379 SIBLEY11 _1 161 11 |  | 440 | 0.16224 | 136.82 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26SP | GEN-2018-022 | 'FROM -> TO' | 541201 SIBLEY 7 345 997379 SIBLEY11 _1 161 11 |  | 440 | 0.16224 | 136.82 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26SP | GEN-2018-022 | 'FROM -> TO' | 541201 SIBLEY 7 345 997379 SIBLEY11 _1 161 11 |  | 440 | 0.16224 | 136.82 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26SP | GEN-2018-038 | 'FROM -> TO' | 541201 SIBLEY 7 345 997379 SIBLEY11 _1 161 11 |  | 440 | 0.42563 | 136.82 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26SP | GEN-2018-038 | 'FROM -> TO' | 541201 SIBLEY 7 345 997379 SIBLEY11 _1 161 11 |  | 440 | 0.42563 | 136.82 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26SP | GEN-2018-038 | 'FROM -> TO' | 541201 SIBLEY 7 345 997379 SIBLEY11 _1 161 11 |  | 440 | 0.42563 | 136.82 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26SP | GEN-2018-040 | 'FROM -> TO' | 541201 SIBLEY 7 345 997379 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 136.82 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26SP | GEN-2018-040 | 'FROM -> TO' | 541201 SIBLEY 7 345 997379 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 136.82 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26SP | GEN-2018-040 | 'FROM -> TO' | 541201 SIBLEY 7 345 997379 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 136.82 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26SP | GEN-2018-041 | 'FROM -> TO' | 541201 SIBLEY 7 345 997379 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 136.82 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26SP | GEN-2018-041 | 'FROM -> TO' | 541201 SIBLEY 7 345 997379 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 136.82 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26SP | GEN-2018-041 | 'FROM -> TO' | 541201 SIBLEY 7 345 997379 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 136.82 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26SP | GEN-2018-042 | 'FROM -> TO' | 541201 SIBLEY 7 345 997379 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 136.82 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26SP | GEN-2018-042 | 'FROM -> TO' | 541201 SIBLEY 7 345 997379 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 136.82 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26SP | GEN-2018-042 | 'FROM -> TO' | 541201 SIBLEY 7 345 997379 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 136.82 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26SP | GEN-2018-014 | 'FROM -> TO' | 541202 SIBLEY 5 161 997379 SIBLEY11 _1 161 11 |  | 440 | 0.11256 | 133.69 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26SP | GEN-2018-014 | 'FROM -> TO' | 541202 SIBLEY 5 161 997379 SIBLEY11 _1 161 11 |  | 440 | 0.11256 | 133.69 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26SP | GEN-2018-014 | 'FROM -> TO' | 541202 SIBLEY 5 161 997379 SIBLEY11 _1 161 11 |  | 440 | 0.11256 | 133.69 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26SP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 997379 SIBLEY11 _1 161 11 |  | 440 | 0.16224 | 133.69 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26SP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 997379 SIBLEY11 _1 161 11 |  | 440 | 0.16224 | 133.69 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26SP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 997379 SIBLEY11 _1 161 11 |  | 440 | 0.16224 | 133.69 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 997379 SIBLEY11 _1 161 11 |  | 440 | 0.42563 | 133.69 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 997379 SIBLEY11 _1 161 11 |  | 440 | 0.42563 | 133.69 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 997379 SIBLEY11 _1 161 11 |  | 440 | 0.42563 | 133.69 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 997379 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 133.69 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 997379 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 133.69 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 997379 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 133.69 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 997379 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 133.69 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 997379 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 133.69 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 997379 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 133.69 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 26SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 997379 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 133.69 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL
Thermal | 03ALL | 2 | 26SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 997379 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 133.69 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 03ALL | 2 | 26SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 997379 SIBLEY11 _1 161 11 |  | 440 | 0.42496 | 133.69 | P23:345:GMO-KCPL:SIBLEY-R8-10:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.0612 | 120.57 | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 2
Thermal | 03ALL | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.16522 | 120.57 | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 2
Thermal | 03ALL | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.16492 | 120.57 | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 2
Thermal | 03ALL | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.16492 | 120.57 | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 2
Thermal | 03ALL | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.16492 | 120.57 | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 2
Thermal | 03ALL | 2 | 26WP | GEN-2018-013 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 |  | 1195 | 0.09019 | 117.47 | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE
Thermal | 03ALL | 2 | 26WP | GEN-2018-013 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 |  | 1195 | 0.09019 | 117.47 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-053 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 |  | 1195 | 0.11148 | 117.47 | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE
Thermal | 03ALL | 2 | 26WP | GEN-2018-053 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 |  | 1195 | 0.11148 | 117.47 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-058 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 |  | 1195 | 0.44647 | 117.47 | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE
Thermal | 03ALL | 2 | 26WP | GEN-2018-058 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 |  | 1195 | 0.44647 | 117.47 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-059 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 |  | 1195 | 0.44647 | 117.47 | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE
Thermal | 03ALL | 2 | 26WP | GEN-2018-059 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 |  | 1195 | 0.44647 | 117.47 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-061 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 |  | 1195 | 0.11148 | 117.47 | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE
Thermal | 03ALL | 2 | 26WP | GEN-2018-061 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 |  | 1195 | 0.11148 | 117.47 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.05957 | 115.83 | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 2
Thermal | 03ALL | 2 | 26WP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.16361 | 115.83 | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 2
Thermal | 03ALL | 2 | 26WP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.16331 | 115.83 | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 2
Thermal | 03ALL | 2 | 26WP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.16331 | 115.83 | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 2
Thermal | 03ALL | 2 | 26WP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.16331 | 115.83 | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 2
Thermal | 03ALL | 2 | 26SP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.06123 | 115.69 | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 2
Thermal | 03ALL | 2 | 26SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.16529 | 115.69 | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 2
Thermal | 03ALL | 2 | 26SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.16499 | 115.69 | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 2
Thermal | 03ALL | 2 | 26SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.16499 | 115.69 | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 2
Thermal | 03ALL | 2 | 26SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.16499 | 115.69 | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 2
Thermal | 03ALL | 2 | 23SP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.07606 | 112.78 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.22569 | 112.78 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.22532 | 112.78 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.22532 | 112.78 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.22532 | 112.78 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-058 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 |  | 1329 | 0.46265 | 110.9 | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE
Thermal | 03ALL | 2 | 23SP | GEN-2018-058 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 |  | 1329 | 0.46265 | 110.9 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-059 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 |  | 1329 | 0.46265 | 110.9 | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE
Thermal | 03ALL | 2 | 23SP | GEN-2018-059 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 |  | 1329 | 0.46265 | 110.9 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 2 | 26SP | GEN-2018-058 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 |  | 1329 | 0.46235 | 110.68 | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE
Thermal | 03ALL | 2 | 26SP | GEN-2018-058 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 |  | 1329 | 0.46235 | 110.68 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 2 | 26SP | GEN-2018-059 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 |  | 1329 | 0.46235 | 110.68 | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE
Thermal | 03ALL | 2 | 26SP | GEN-2018-059 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 |  | 1329 | 0.46235 | 110.68 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.05719 | 110.47 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.15281 | 110.47 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.15281 | 110.47 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.15281 | 110.47 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.15281 | 110.47 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 26SP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.07616 | 110.22 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 26SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.22584 | 110.22 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 26SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.22547 | 110.22 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 26SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.22547 | 110.22 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 26SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.22547 | 110.22 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-022 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.07606 | 109.9 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.22569 | 109.9 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.22532 | 109.9 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.22532 | 109.9 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.22532 | 109.9 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 997381 SIBLEY11 _1 161 11 |  | 440 | 0.07606 | 107.53 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 997381 SIBLEY11 _1 161 11 |  | 440 | 0.22569 | 107.53 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 997381 SIBLEY11 _1 161 11 |  | 440 | 0.22532 | 107.53 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 997381 SIBLEY11 _1 161 11 |  | 440 | 0.22532 | 107.53 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 997381 SIBLEY11 _1 161 11 |  | 440 | 0.22532 | 107.53 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 26SP | GEN-2018-022 | 'FROM -> TO' | 541201 SIBLEY 7 345 997379 SIBLEY11 _1 161 11 |  | 440 | 0.07616 | 107.48 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 26SP | GEN-2018-038 | 'FROM -> TO' | 541201 SIBLEY 7 345 997379 SIBLEY11 _1 161 11 |  | 440 | 0.22584 | 107.48 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 26SP | GEN-2018-040 | 'FROM -> TO' | 541201 SIBLEY 7 345 997379 SIBLEY11 _1 161 11 |  | 440 | 0.22547 | 107.48 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 26SP | GEN-2018-041 | 'FROM -> TO' | 541201 SIBLEY 7 345 997379 SIBLEY11 _1 161 11 |  | 440 | 0.22547 | 107.48 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 26SP | GEN-2018-042 | 'FROM -> TO' | 541201 SIBLEY 7 345 997379 SIBLEY11 _1 161 11 |  | 440 | 0.22547 | 107.48 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-022 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.05719 | 107.28 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-038 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.15281 | 107.28 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-040 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.15281 | 107.28 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-041 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.15281 | 107.28 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-042 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.15281 | 107.28 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.05801 | 106.89 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.15362 | 106.89 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.15362 | 106.89 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.15362 | 106.89 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.15362 | 106.89 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 997377 SIBLEY11 _1 161 11 |  | 440 | 0.05705 | 106.56 | P22:345:AMMO::OVERTON:1
Thermal | 03ALL | 2 | 23SP | GEN-2018-013 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 |  | 1195 | 0.09037 | 106.24 | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE
Thermal | 03ALL | 2 | 23SP | GEN-2018-013 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 |  | 1195 | 0.09037 | 106.24 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-053 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 |  | 1195 | 0.11099 | 106.24 | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE
Thermal | 03ALL | 2 | 23SP | GEN-2018-053 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 |  | 1195 | 0.11099 | 106.24 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-058 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 |  | 1195 | 0.44654 | 106.24 | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE
Thermal | 03ALL | 2 | 23SP | GEN-2018-058 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 |  | 1195 | 0.44654 | 106.24 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-059 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 |  | 1195 | 0.44654 | 106.24 | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE
Thermal | 03ALL | 2 | 23SP | GEN-2018-059 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 |  | 1195 | 0.44654 | 106.24 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-061 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 |  | 1195 | 0.11099 | 106.24 | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE
Thermal | 03ALL | 2 | 23SP | GEN-2018-061 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 |  | 1195 | 0.11099 | 106.24 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 2 | 26SP | GEN-2018-013 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 |  | 1195 | 0.08982 | 105.79 | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE
Thermal | 03ALL | 2 | 26SP | GEN-2018-013 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 |  | 1195 | 0.08982 | 105.79 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 2 | 26SP | GEN-2018-053 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 |  | 1195 | 0.11107 | 105.79 | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE
Thermal | 03ALL | 2 | 26SP | GEN-2018-053 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 |  | 1195 | 0.11107 | 105.79 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 2 | 26SP | GEN-2018-058 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 |  | 1195 | 0.44608 | 105.79 | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE
Thermal | 03ALL | 2 | 26SP | GEN-2018-058 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 |  | 1195 | 0.44608 | 105.79 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 2 | 26SP | GEN-2018-059 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 |  | 1195 | 0.44608 | 105.79 | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE
Thermal | 03ALL | 2 | 26SP | GEN-2018-059 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 |  | 1195 | 0.44608 | 105.79 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 2 | 26SP | GEN-2018-061 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 |  | 1195 | 0.11107 | 105.79 | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE
Thermal | 03ALL | 2 | 26SP | GEN-2018-061 | 'FROM -> TO' | 532775 87TH 7 345 542977 CRAIG 7 345 1 |  | 1195 | 0.11107 | 105.79 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 997377 SIBLEY11 _1 161 11 |  | 440 | 0.05719 | 105.75 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 997377 SIBLEY11 _1 161 11 |  | 440 | 0.15281 | 105.75 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 997377 SIBLEY11 _1 161 11 |  | 440 | 0.15281 | 105.75 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 997377 SIBLEY11 _1 161 11 |  | 440 | 0.15281 | 105.75 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 997377 SIBLEY11 _1 161 11 |  | 440 | 0.15281 | 105.75 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-058 | 'FROM -> TO' | 533244 JARBALO3 115 533249 LEC U4 3 115 1 |  | 118 | 0.05313 | 105.72 | P23:345:WERE:STRA_345-100::
Thermal | 03ALL | 2 | 26WP | GEN-2018-058 | 'FROM -> TO' | 533244 JARBALO3 115 533249 LEC U4 3 115 1 |  | 118 | 0.05313 | 105.72 | P23:345:WERE:STRA-345-100:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-059 | 'FROM -> TO' | 533244 JARBALO3 115 533249 LEC U4 3 115 1 |  | 118 | 0.05313 | 105.72 | P23:345:WERE:STRA_345-100::
Thermal | 03ALL | 2 | 26WP | GEN-2018-059 | 'FROM -> TO' | 533244 JARBALO3 115 533249 LEC U4 3 115 1 |  | 118 | 0.05313 | 105.72 | P23:345:WERE:STRA-345-100:::EHV:
Thermal | 03ALL | 2 | 26SP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 997379 SIBLEY11 _1 161 11 |  | 440 | 0.07616 | 105.01 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 26SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 997379 SIBLEY11 _1 161 11 |  | 440 | 0.22584 | 105.01 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 26SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 997379 SIBLEY11 _1 161 11 |  | 440 | 0.22547 | 105.01 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 26SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 997379 SIBLEY11 _1 161 11 |  | 440 | 0.22547 | 105.01 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 26SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 997379 SIBLEY11 _1 161 11 |  | 440 | 0.22547 | 105.01 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-022 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.05801 | 103.59 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.15362 | 103.59 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.15362 | 103.59 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.15362 | 103.59 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.15362 | 103.59 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.07404 | 103.07 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.22402 | 103.07 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.22365 | 103.07 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.22365 | 103.07 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.22365 | 103.07 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.12064 | 103.05 | 541206 PRALEE 5 161 541211 BLSPS 5 161 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.12041 | 103.05 | 541206 PRALEE 5 161 541211 BLSPS 5 161 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.12041 | 103.05 | 541206 PRALEE 5 161 541211 BLSPS 5 161 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.12041 | 103.05 | 541206 PRALEE 5 161 541211 BLSPS 5 161 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-014 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.05526 | 102.94 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-014 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.05526 | 102.94 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON
Thermal | 03ALL | 2 | 26WP | GEN-2018-014 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.05526 | 102.94 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 03ALL | 2 | 26WP | GEN-2018-014 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.05526 | 102.94 | P23:345:GMO:SIBLEY-R3-8:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.07617 | 102.94 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.07617 | 102.94 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON
Thermal | 03ALL | 2 | 26WP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.07617 | 102.94 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 03ALL | 2 | 26WP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.07617 | 102.94 | P23:345:GMO:SIBLEY-R3-8:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18701 | 102.94 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18701 | 102.94 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON
Thermal | 03ALL | 2 | 26WP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18701 | 102.94 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 03ALL | 2 | 26WP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18701 | 102.94 | P23:345:GMO:SIBLEY-R3-8:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18669 | 102.94 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18669 | 102.94 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON
Thermal | 03ALL | 2 | 26WP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18669 | 102.94 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 03ALL | 2 | 26WP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18669 | 102.94 | P23:345:GMO:SIBLEY-R3-8:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18669 | 102.94 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18669 | 102.94 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON
Thermal | 03ALL | 2 | 26WP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18669 | 102.94 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 03ALL | 2 | 26WP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18669 | 102.94 | P23:345:GMO:SIBLEY-R3-8:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18669 | 102.94 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18669 | 102.94 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON
Thermal | 03ALL | 2 | 26WP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18669 | 102.94 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 03ALL | 2 | 26WP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18669 | 102.94 | P23:345:GMO:SIBLEY-R3-8:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-058 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 |  | 1515 | 0.46198 | 102.87 | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE
Thermal | 03ALL | 2 | 26WP | GEN-2018-058 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 |  | 1515 | 0.46198 | 102.87 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-059 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 |  | 1515 | 0.46198 | 102.87 | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE
Thermal | 03ALL | 2 | 26WP | GEN-2018-059 | 'FROM -> TO' | 532772 STRANGR7 345 532775 87TH 7 345 1 |  | 1515 | 0.46198 | 102.87 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.12064 | 102.15 | P12:161:GMO:PRAIRIELEE-BLUESPRINGSS-BLUESPRINGS:::HV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.12064 | 102.15 | P12:161:GMO:PRAIRIELEE-BLUESPRINGSS-BLUESPRINGSE
Thermal | 03ALL | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.12064 | 102.15 | P12:161:GMO:PRAIRIELEE-BLUESPRINGSS-BLUESPRINGSE_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.12041 | 102.15 | P12:161:GMO:PRAIRIELEE-BLUESPRINGSS-BLUESPRINGS:::HV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.12041 | 102.15 | P12:161:GMO:PRAIRIELEE-BLUESPRINGSS-BLUESPRINGSE
Thermal | 03ALL | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.12041 | 102.15 | P12:161:GMO:PRAIRIELEE-BLUESPRINGSS-BLUESPRINGSE_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.12041 | 102.15 | P12:161:GMO:PRAIRIELEE-BLUESPRINGSS-BLUESPRINGS:::HV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.12041 | 102.15 | P12:161:GMO:PRAIRIELEE-BLUESPRINGSS-BLUESPRINGSE
Thermal | 03ALL | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.12041 | 102.15 | P12:161:GMO:PRAIRIELEE-BLUESPRINGSS-BLUESPRINGSE_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.12041 | 102.15 | P12:161:GMO:PRAIRIELEE-BLUESPRINGSS-BLUESPRINGS:::HV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.12041 | 102.15 | P12:161:GMO:PRAIRIELEE-BLUESPRINGSS-BLUESPRINGSE
Thermal | 03ALL | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.12041 | 102.15 | P12:161:GMO:PRAIRIELEE-BLUESPRINGSS-BLUESPRINGSE_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.12064 | 102.13 | 541205 BLSPE 5 161 541211 BLSPS 5 161 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.12041 | 102.13 | 541205 BLSPE 5 161 541211 BLSPS 5 161 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.12041 | 102.13 | 541205 BLSPE 5 161 541211 BLSPS 5 161 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.12041 | 102.13 | 541205 BLSPE 5 161 541211 BLSPS 5 161 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-014 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.05741 | 102.02 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-014 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.05741 | 102.02 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON
Thermal | 03ALL | 2 | 23SP | GEN-2018-014 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.05741 | 102.02 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-014 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.05741 | 102.02 | P23:345:GMO:SIBLEY-R3-8:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.0783 | 102.02 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.0783 | 102.02 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON
Thermal | 03ALL | 2 | 23SP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.0783 | 102.02 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.0783 | 102.02 | P23:345:GMO:SIBLEY-R3-8:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18909 | 102.02 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18909 | 102.02 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON
Thermal | 03ALL | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18909 | 102.02 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18909 | 102.02 | P23:345:GMO:SIBLEY-R3-8:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18877 | 102.02 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18877 | 102.02 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON
Thermal | 03ALL | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18877 | 102.02 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18877 | 102.02 | P23:345:GMO:SIBLEY-R3-8:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18877 | 102.02 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18877 | 102.02 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON
Thermal | 03ALL | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18877 | 102.02 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18877 | 102.02 | P23:345:GMO:SIBLEY-R3-8:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18877 | 102.02 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18877 | 102.02 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON
Thermal | 03ALL | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18877 | 102.02 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.18877 | 102.02 | P23:345:GMO:SIBLEY-R3-8:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.1237 | 101.94 | 541218 GRNWD 5 161 541233 LEESUM 5 161 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.12348 | 101.94 | 541218 GRNWD 5 161 541233 LEESUM 5 161 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.12348 | 101.94 | 541218 GRNWD 5 161 541233 LEESUM 5 161 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.12348 | 101.94 | 541218 GRNWD 5 161 541233 LEESUM 5 161 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 997381 SIBLEY11 _1 161 11 |  | 440 | 0.05801 | 101.66 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 997381 SIBLEY11 _1 161 11 |  | 440 | 0.15362 | 101.66 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 997381 SIBLEY11 _1 161 11 |  | 440 | 0.15362 | 101.66 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 997381 SIBLEY11 _1 161 11 |  | 440 | 0.15362 | 101.66 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 997381 SIBLEY11 _1 161 11 |  | 440 | 0.15362 | 101.66 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.1171 | 101.54 | 541203 NASHUA 5 161 541247 LBRTYWT5 161 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.11688 | 101.54 | 541203 NASHUA 5 161 541247 LBRTYWT5 161 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.11688 | 101.54 | 541203 NASHUA 5 161 541247 LBRTYWT5 161 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.11688 | 101.54 | 541203 NASHUA 5 161 541247 LBRTYWT5 161 1
Thermal | 03ALL | 2 | 26SP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.05815 | 101.03 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 26SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.15379 | 101.03 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 26SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.15379 | 101.03 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 26SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.15379 | 101.03 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 26SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.15379 | 101.03 | 345408 7OVERTON 345 762751 GEN-2018-040 345 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.14324 | 100.75 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS
Thermal | 03ALL | 2 | 23SP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.14324 | 100.75 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-022 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.14324 | 100.75 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.14327 | 100.75 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS
Thermal | 03ALL | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.14327 | 100.75 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.14327 | 100.75 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.14301 | 100.75 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS
Thermal | 03ALL | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.14301 | 100.75 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.14301 | 100.75 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.14301 | 100.75 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS
Thermal | 03ALL | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.14301 | 100.75 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.14301 | 100.75 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 03ALL | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.14301 | 100.75 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS
Thermal | 03ALL | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.14301 | 100.75 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 |  | 418 | 0.14301 | 100.75 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1
Thermal | 03ALL | 2 | 26WP | GEN-2018-022 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.07404 | 100.46 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-038 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.22402 | 100.46 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-040 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.22365 | 100.46 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-041 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.22365 | 100.46 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-042 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.22365 | 100.46 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-014 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.05526 | 100.17 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-014 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.05526 | 100.17 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON
Thermal | 03ALL | 2 | 26WP | GEN-2018-014 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.05526 | 100.17 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 03ALL | 2 | 26WP | GEN-2018-014 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.05526 | 100.17 | P23:345:GMO:SIBLEY-R3-8:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-022 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.07617 | 100.17 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-022 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.07617 | 100.17 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON
Thermal | 03ALL | 2 | 26WP | GEN-2018-022 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.07617 | 100.17 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 03ALL | 2 | 26WP | GEN-2018-022 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.07617 | 100.17 | P23:345:GMO:SIBLEY-R3-8:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-038 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.18701 | 100.17 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-038 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.18701 | 100.17 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON
Thermal | 03ALL | 2 | 26WP | GEN-2018-038 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.18701 | 100.17 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 03ALL | 2 | 26WP | GEN-2018-038 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.18701 | 100.17 | P23:345:GMO:SIBLEY-R3-8:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-040 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.18669 | 100.17 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-040 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.18669 | 100.17 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON
Thermal | 03ALL | 2 | 26WP | GEN-2018-040 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.18669 | 100.17 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 03ALL | 2 | 26WP | GEN-2018-040 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.18669 | 100.17 | P23:345:GMO:SIBLEY-R3-8:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-041 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.18669 | 100.17 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-041 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.18669 | 100.17 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON
Thermal | 03ALL | 2 | 26WP | GEN-2018-041 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.18669 | 100.17 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 03ALL | 2 | 26WP | GEN-2018-041 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.18669 | 100.17 | P23:345:GMO:SIBLEY-R3-8:::EHV:
Thermal | 03ALL | 2 | 26WP | GEN-2018-042 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.18669 | 100.17 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 2 | 26WP | GEN-2018-042 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.18669 | 100.17 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON
Thermal | 03ALL | 2 | 26WP | GEN-2018-042 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.18669 | 100.17 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 03ALL | 2 | 26WP | GEN-2018-042 | 'FROM -> TO' | 541201 SIBLEY 7 345 997377 SIBLEY11 _1 161 11 |  | 440 | 0.18669 | 100.17 | P23:345:GMO:SIBLEY-R3-8:::EHV:
Thermal | 03ALL | 2 | 23SP | GEN-2018-038 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.12064 | 100.14 | 541206 PRALEE 5 161 541211 BLSPS 5 161 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-040 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.12041 | 100.14 | 541206 PRALEE 5 161 541211 BLSPS 5 161 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-041 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.12041 | 100.14 | 541206 PRALEE 5 161 541211 BLSPS 5 161 1
Thermal | 03ALL | 2 | 23SP | GEN-2018-042 | 'FROM -> TO' | 541201 SIBLEY 7 345 997381 SIBLEY11 _1 161 11 |  | 440 | 0.12041 | 100.14 | 541206 PRALEE 5 161 541211 BLSPS 5 161 1
Non-Converge | 03NR | 0 | N/A | N/A | '' | None |  |  |  |  | None
Thermal | 03NR | 2 | 26L | N/A | '' | None |  |  |  |  | None
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 122.58 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 122.58 | P42:345:AEPW:WELSHCB11990NBTB+FAULT
Thermal | 04ALL | 2 | 26SP0 | GEN-2018-027 | 'FROM -> TO' | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 |  | 116.29 | 509783 R.S.S.-4 138 509849 ORU ETP4 138 1
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-027 | 'FROM -> TO' | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 |  | 116.03 | 509783 R.S.S.-4 138 509849 ORU ETP4 138 1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 114.13 | 508054 BANN 4 138 508075 REDSPRG4 138 1
Thermal | 04ALL | 2 | 26SP0 | GEN-2018-027 | 'FROM -> TO' | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 |  | 113.03 | 509783 R.S.S.-4 138 509853 ORU-WTP4 138 1
Thermal | 04ALL | 2 | 26SP0 | GEN-2018-027 | 'FROM -> TO' | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 |  | 112.88 | 509849 ORU ETP4 138 509858 WARNTAP4 138 1
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-027 | 'FROM -> TO' | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 |  | 112.74 | 509783 R.S.S.-4 138 509853 ORU-WTP4 138 1
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-027 | 'FROM -> TO' | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 |  | 112.7 | 509849 ORU ETP4 138 509858 WARNTAP4 138 1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 112.36 | P12:138:AEPW:IPC-DOM4:BANN4
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 112.36 | P13:138-345:AEPW:WILKES4
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 112.08 | 508053 BANN 2 69.0 508063 LSORDTP2 69.0 1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 111.3 | 508057 HOOKS 2 69.0 508063 LSORDTP2 69.0 1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 111.17 | P12:138:AEPW:OKAY4:TURK4
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 111.17 | P12:HV:EES::OKAY4:TURK4%:1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 111.15 | 508060 IPC-DOM4 138 508075 REDSPRG4 138 1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 110.97 | 508059 IPC T 4 138 508060 IPC-DOM4 138 1
Thermal | 04ALL | 2 | 26SP0 | GEN-2018-027 | 'FROM -> TO' | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 |  | 110.44 | 509813 SHILETP4 138 509853 ORU-WTP4 138 1
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-027 | 'FROM -> TO' | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 |  | 110.18 | 509813 SHILETP4 138 509853 ORU-WTP4 138 1
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 109.71 | P13:138-345:AEPW:WILKES4
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 109.34 | 508057 HOOKS 2 69.0 508074 REDRVR-2 69.0 1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 109.21 | P12:138:AEPW:PATTERS4:NWTXARK4
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 109.21 | P12:HV:EES::PATTERS4!:NWTXARK4:1
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 109.06 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 109.06 | P42:345:AEPW:WELSHCB11990NBTB+FAULT
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 108.98 | 508072 NWTXARK7 345 508841 WILKES 7 345 1
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-021 | 'FROM -> TO' | 515802 GRACMNT4 138 997832 GRACMNT3 _1 138 1 |  | 478 |  | 108.6 | P42:345:OKGE:SB_CION7384::::
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-055 | 'FROM -> TO' | 515802 GRACMNT4 138 997832 GRACMNT3 _1 138 1 |  | 478 |  | 108.6 | P42:345:OKGE:SB_CION7384::::
Thermal | 04ALL | 2 | 26SP0 | GEN-2018-027 | 'FROM -> TO' | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 |  | 108.57 | P12:138:AEPW:R.S.S.-4:R:96YALE-4
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-027 | 'FROM -> TO' | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 |  | 108.48 | P12:138:AEPW:R.S.S.-4:R:96YALE-4
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-021 | 'FROM -> TO' | 515802 GRACMNT4 138 997832 GRACMNT3 _1 138 1 |  | 478 |  | 107.99 | P12:345:OKGE:BKRBKR24::::
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-055 | 'FROM -> TO' | 515802 GRACMNT4 138 997832 GRACMNT3 _1 138 1 |  | 478 |  | 107.99 | P12:345:OKGE:BKRBKR24::::
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 107.87 | 507402 ASHDWNR4 138 507428 OKAY 4 138 1
Thermal | 04ALL | 2 | 26SP0 | GEN-2018-027 | 'FROM -> TO' | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 |  | 107.48 | 509809 81YALTP4 138 509813 SHILETP4 138 1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 107.45 | P11:22:AEPW:WILKE2-1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 107.42 | P12:138:AEPW:PATTERS4:OKAY4
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 107.36 | P12:HV:EES::ASHDWNR4:PATTERS4!:1
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-027 | 'FROM -> TO' | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 |  | 107.28 | 509809 81YALTP4 138 509813 SHILETP4 138 1
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-021 | 'FROM -> TO' | 515800 GRACMNT7 345 997832 GRACMNT3 _1 138 1 |  | 478 |  | 107.27 | P42:345:OKGE:SB_CION7384::::
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-055 | 'FROM -> TO' | 515800 GRACMNT7 345 997832 GRACMNT3 _1 138 1 |  | 478 |  | 107.27 | P42:345:OKGE:SB_CION7384::::
Thermal | 04ALL | 2 | 26SP0 | GEN-2018-027 | 'FROM -> TO' | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 |  | 107.13 | 509847 96YALE-4 138 509858 WARNTAP4 138 1
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-027 | 'FROM -> TO' | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 |  | 107.07 | 509847 96YALE-4 138 509858 WARNTAP4 138 1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 106.69 | P12:345:AEPW:LYDIA7:WELSH7
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-021 | 'FROM -> TO' | 515800 GRACMNT7 345 997832 GRACMNT3 _1 138 1 |  | 478 |  | 106.67 | P12:345:OKGE:BKRBKR24::::
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-055 | 'FROM -> TO' | 515800 GRACMNT7 345 997832 GRACMNT3 _1 138 1 |  | 478 |  | 106.67 | P12:345:OKGE:BKRBKR24::::
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 106.52 | 508054 BANN 4 138 508075 REDSPRG4 138 1
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 106.28 | 508053 BANN 2 69.0 508063 LSORDTP2 69.0 1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 106.04 | 508059 IPC T 4 138 508106 CASSTP4 138 1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 105.71 | P12:138:AEPW:BANN4:NNBOSTN4
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 105.71 | 508054 BANN 4 138 508070 NWT-BNT4 138 1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 105.6 | 508106 CASSTP4 138 509668 ROACH 2 69.0 1
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 105.49 | 508057 HOOKS 2 69.0 508063 LSORDTP2 69.0 1
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 105.15 | P12:138:AEPW:IPC-DOM4:BANN4
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 105.11 | P12:345:AEPW:WELSH7:DIANA7_CKT1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 105.08 | P23:345:AEPW:DIANACB12000NBTB
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 105.08 | P42:345:AEPW:DIANACB12000NBTB+FAULT
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 105.03 | P12:345:AEPW:WELSH7:DIANA7_CKT2
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 104.84 | P12:69:AEPW:NEWBOST2:BANN2
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 104.58 | P23:345:AEPW:WELSHCB10610NBTB
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 104.58 | P42:345:AEPW:WELSHCB10610NBTB+FAULT
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 104.51 | P13:69-138:AEPW:SUGARHL2
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 104.44 | P11:20:AEPW:WILKE1-1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 104.41 | P11:24:AEPW:PIRKEY1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 104.41 | P11:HV:EES::PIRKEY0.0423611111111111
Thermal | 04ALL | 2 | 26SP0 | GEN-2018-027 | 'FROM -> TO' | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 |  | 104.36 | 509764 WRNMEDT4 138 509809 81YALTP4 138 1
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-021 | 'FROM -> TO' | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 349 |  | 104.29 | System Intact
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 104.23 | P23:345:AEPW:DIANACB11910NBTB
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 104.23 | P42:345:AEPW:DIANACB11910NBTB+FAULT
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-027 | 'FROM -> TO' | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 |  | 104.22 | 509764 WRNMEDT4 138 509809 81YALTP4 138 1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 104.2 | P12:HV:EES::PIRKEY0.167361111111111
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 104.2 | P13:138-24:AEPW:PIRKEY4
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 104.19 | P12:138:AEPW:OKAY4:TURK4
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 104.19 | P12:HV:EES::OKAY4:TURK4%:1
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 104.17 | 508060 IPC-DOM4 138 508075 REDSPRG4 138 1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 104.14 | P12:138:AEPW:PERDUE4:EXXONM4
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 104.06 | P13:69-138:AEPW:BANN2_#2
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 104.05 | P13:69-138:AEPW:BANN2_#1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 104.01 | 508067 NEWBOST2 69.0 508074 REDRVR-2 69.0 1
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 103.99 | 508059 IPC T 4 138 508060 IPC-DOM4 138 1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 103.98 | 520948 HUGO PP4 138 521079 VALLANT4 138 1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 103.95 | P12:345:AEPW:WELSH7:WILKES7
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 103.94 | 504124 ASHDWN_W 4 138 510890 CRAIGJT4 138 1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 103.93 | P12:138:AEPW:IDABEL-4:VALIANT4
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 103.8 | P11:HV:EES::1LEWIS_U3ST:1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 103.77 | P12:69:AEPW:SETEXAR2:TEXARK2
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 103.77 | P13:69-138:AEPW:SETEXAR2
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 103.76 | 520419 GARVIN4 138 521079 VALLANT4 138 1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 103.71 | P11:24:CLEC::G1DOLHIL:1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 103.71 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 103.64 | P11:345-24:CLEC::DOLHILL7:1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 103.64 | P13:345
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 103.64 | 520419 GARVIN4 138 520953 IDABEL 4 138 1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 103.62 | P12:138:AEPW:ARSHILL4:STLGENS4
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 103.6 | P12:HV:EES::ASHDWN_W4:PATTERS4!:1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 103.59 | P12:138:AEPW:CRAIGJT4:PATTERS4
Thermal | 04ALL | 2 | 26SP0 | GEN-2018-027 | 'FROM -> TO' | 509776 52DELTP4 138 509811 T.S.E.-4 138 1 |  | 278 |  | 103.55 | 509783 R.S.S.-4 138 509849 ORU ETP4 138 1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 103.49 | P12:138:AEPW:LSSOUTH4:DIANA4
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 103.48 | 510886 IDABEL-4 138 510888 B.BOWTP4 138 1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 103.35 | 520946 HOLYCRK4 138 520953 IDABEL 4 138 1
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-027 | 'FROM -> TO' | 509776 52DELTP4 138 509811 T.S.E.-4 138 1 |  | 278 |  | 103.15 | 509783 R.S.S.-4 138 509849 ORU ETP4 138 1
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-021 | 'FROM -> TO' | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 |  | 103.12 | System Intact
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 103.1 | 508057 HOOKS 2 69.0 508074 REDRVR-2 69.0 1
Thermal | 04ALL | 2 | 26SP0 | GEN-2018-027 | 'FROM -> TO' | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 |  | 103.04 | P12:138:AEPW:R.S.S.-4:S.HUD.-4
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-027 | 'FROM -> TO' | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 |  | 102.8 | P12:138:AEPW:R.S.S.-4:S.HUD.-4
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 102.33 | P12:HV:EES::TURK4%:1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 102.33 | P13:138-345:AEPW:TURK4
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 102.05 | System Intact
Thermal | 04ALL | 2 | 26SP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 101.9 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 04ALL | 2 | 26SP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 101.9 | P42:345:AEPW:WELSHCB11990NBTB+FAULT
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-021 | 'FROM -> TO' | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 |  | 101.76 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-027 | 'FROM -> TO' | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 |  | 101.62 | P23:345:AEPW:ONETACB3405ANBTB
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-027 | 'FROM -> TO' | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 |  | 101.62 | P42:345:AEPW:ONETACB3405ANBTB+FAULT
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 101.43 | 507402 ASHDWNR4 138 507428 OKAY 4 138 1
Thermal | 04ALL | 2 | 26SP0 | GEN-2018-027 | 'FROM -> TO' | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 |  | 101.16 | 509764 WRNMEDT4 138 509833 S.HUD.-4 138 1
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 101.07 | P12:138:AEPW:PATTERS4:OKAY4
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-027 | 'FROM -> TO' | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 |  | 101.06 | 509764 WRNMEDT4 138 509833 S.HUD.-4 138 1
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 101.02 | P12:HV:EES::ASHDWNR4:PATTERS4!:1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.9 | P23:345:AEPW:RIVERSIDECB3429ANBTB
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.9 | P42:345:AEPW:RIVERSIDECB3429ANBTB+FAULT
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.89 | P12:345:AEPW:R.S.S.-7:COGENT7
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-027 | 'FROM -> TO' | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 |  | 100.8 | 509766 77MEM-W4 138 509847 96YALE-4 138 1
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.78 | P12:138:AEPW:PATTERS4:NWTXARK4
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.78 | P12:HV:EES::PATTERS4!:NWTXARK4:1
Thermal | 04ALL | 2 | 26SP0 | GEN-2018-027 | 'FROM -> TO' | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 |  | 100.74 | 509766 77MEM-W4 138 509847 96YALE-4 138 1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.66 | P12:HV:EES::LOCKSBRG4:PATTERS4!:1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.63 | P12:138:ETEC:DOUGLASSVILLE-NLINDEN-ROACH:::HV:
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.62 | P12:138:AEPW:SETEXAR4:TURK4
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.54 | P12:HV:EES::TURK4%:1(1)
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.54 | P13:138-24:AEPW:TURK4
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.51 | 508078 SETEXAR4 138 508105 MANDEVILTP4 138 1
Thermal | 04ALL | 2 | 23SP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.5 | 508072 NWTXARK7 345 508841 WILKES 7 345 1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.45 | 588043 G16133_765R2 765 588044 G16133_765R3 765 1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.45 | 588041 G16133_765TN 765 588042 G16133_765R1 765 1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.45 | 509782 R.S.S.-7 345 588040 G16133G16146 345 1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.44 | 588044 G16133_765R3 765 588045 G16133_765CS 765 1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.44 | 588042 G16133_765R1 765 588043 G16133_765R2 765 1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.42 | P12:138:AEPW-EES-EAI:SNASHVL4:4MURFRE
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.42 | P12:HV:EES::4MURFBORO:SNASHVL4!:1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.38 | P12:115:EES-EAI:MURFSO:MURFET
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.38 | P12:HV:EES::3MURFBORO.S!:3HSEHV-W!:1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.38 | P12:HV:EES::3MURFBORO.S!:3MURFBORO.E#:1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.37 | 337672 4MURFBORO 138 3WXFMR 4MURFBORO 1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.34 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.34 | P24:115:EAI:LBF_HS.W_B~2
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.34 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.28 | P12:138:ETEC:DOUGLASSVILLE-BLALOCK-ALAMANCE:::HV:
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.21 | P12:138:AEPW:SDIERKS4:PATTERS4
Thermal | 04ALL | 2 | 26SP0 | GEN-2018-027 | 'FROM -> TO' | 509776 52DELTP4 138 509811 T.S.E.-4 138 1 |  | 278 |  | 100.2 | 509783 R.S.S.-4 138 509853 ORU-WTP4 138 1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.17 | P11:24:AEPW:TURKCOAL
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.17 | P11:345:WERE:WOLFU1_GEN::
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.17 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.17 | P11:HV:EES::TURKCOAL:1
Thermal | 04ALL | 2 | 26SP0 | GEN-2018-027 | 'FROM -> TO' | 509776 52DELTP4 138 509811 T.S.E.-4 138 1 |  | 278 |  | 100.13 | 509849 ORU ETP4 138 509858 WARNTAP4 138 1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.06 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.06 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.06 | 511568 TERRYRD7 345 511571 RUSHSPR7 345 1
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.05 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.05 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.02 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.02 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.02 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 04ALL | 2 | 26WP0 | GEN-2018-003 | 'FROM -> TO' | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 |  | 100.02 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 04ALL | 0 | N/A | N/A | '' | None |  |  |  |  | None
Thermal | 04ALL | 2 | 26L | N/A | '' | None |  |  |  |  | None
Non-Converge | 04NR | 0 | N/A | N/A | '' | None |  |  |  |  | None
Thermal | 04NR | 2 | 26L | N/A | '' | None |  |  |  |  | None
Non-Converge | 05ALL | 0 | N/A | N/A | '' | None |  |  |  |  | None
Thermal | 05ALL | 2 | 23SP | N/A | '' | None |  |  |  |  | None
Thermal | 05ALL | 2 | 26L | N/A | '' | None |  |  |  |  | None
Thermal | 05ALL | 2 | 26WP | N/A | '' | None |  |  |  |  | None
Thermal | 05ALL | 2 | 26SP | N/A | '' | None |  |  |  |  | None
Non-Converge | 05NR | 0 | N/A | N/A | '' | None |  |  |  |  | None
Thermal | 05NR | 2 | 26L | N/A | '' | None |  |  |  |  | None

## All Voltage
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME
Voltage | 00NR | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 01ALL | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 01NR | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 02ALL | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 02NR | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 03ALL | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 03NR | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 04ALL | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 04NR | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 05ALL | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 05NR | 3 | N/A | N/A | None | [7 empty] | None

## Short Circuit Ratio
Study Request | Current Cluster | Cluster Group | Transmission Owner | Capacity | Service Type | Generation Type | Point of Interconnection | GEN Bus # | Gen ID | POI Bus # | DIS1801TC01ALL-26L0.sav |  | DIS1801TC01ALL-26SP0.sav |  | DIS1801TC02ALL-26L0.sav |  | DIS1801TC02ALL-26SP0.sav |  | DIS1801TC03ALL-26L0.sav |  | DIS1801TC03ALL-26SP0.sav |  | DIS1801TC04ALL-26L0.sav |  | DIS1801TC04ALL-26SP0.sav |  | DIS1801TC05ALL-26L0.sav |  | DIS1801TC05ALL-26SP0.sav
[11 empty] | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio
ASGI-2017-013 | DIS-18-1 | 01 NORTH | WAPA | 40 | ER | Wind | Wolsey 69 kV Substation | 762353 | 1 | 655239 | 227.43 | 5.6857 | 227.95 | 5.6988 | 227.3 | 9.4708 | 227.86 | 28.4825 | 227.28 | 9.47 | 227.85 | 28.4812 | 227.28 | 9.47 | 227.85 | 28.4812 | 227.28 | 9.47 | 227.85 | 28.4812
ASGI-2018-003 | DIS-18-1 | 03 CENTRAL | KCPL | 20 | ER | Solar | AP City 69 kV Substation | 762364 | 1 | 541306 | 278.13 | N/A | 338.84 | 42.355 | 278.13 | N/A | 338.84 | 42.355 | 278.58 | N/A | 339.97 | 16.9985 | 278.15 | N/A | 338.84 | 42.355 | 278.13 | N/A | 338.84 | 42.355
ASGI-2018-006 | DIS-18-1 | 03 CENTRAL | KCPL | 20 | ER | Solar | Metz 69 kV Substation | 762375 | 1 | 541309 | 398.87 | N/A | 467.86 | 58.4825 | 398.88 | N/A | 467.86 | 58.4825 | 399.37 | N/A | 468.24 | 23.412 | 398.93 | N/A | 467.87 | 58.4838 | 398.87 | N/A | 467.86 | 58.4825
ASGI-2018-007 | DIS-18-1 | 03 CENTRAL | KCPL | 20 | ER | Solar | Salisbury 161 kV Substation | 762386 | 1 | 543062 | 2985.68 | N/A | 3253.39 | 406.6737 | 2985.85 | N/A | 3253.41 | 406.6762 | 3033.86 | N/A | 3284.95 | 164.2475 | 2985.92 | N/A | 3253.41 | 406.6762 | 2985.68 | N/A | 3253.39 | 406.6737
ASGI-2018-010 | DIS-18-1 | 03 CENTRAL | KCPL | 35 | ER | Solar | Pleasant Valley 161 kV Substation | 762408 | 1 | 543077 | 2301.14 | N/A | 2796.75 | 199.7679 | 2301.55 | N/A | 2796.77 | 199.7693 | 2332.28 | N/A | 2806.04 | 80.1726 | 2302.74 | N/A | 2796.86 | 199.7757 | 2301.19 | N/A | 2796.75 | 199.7679
ASGI-2018-011 | DIS-18-1 | 03 CENTRAL | KCPL | 35 | ER | Solar | South Ottawa 161 kV Substation | 762419 | 1 | 543066 | 1680.89 | N/A | 2053.96 | 146.7114 | 1681.08 | N/A | 2053.97 | 146.7121 | 1695.36 | N/A | 2057.94 | 58.7983 | 1681.75 | N/A | 2054.02 | 146.7157 | 1680.91 | N/A | 2053.96 | 146.7114
GEN-2018-003 | DIS-18-1 | 04 SOUTHEAST | AEPW | 150 | ER/NR | Solar | North Boston-Bann 138kV Line | 762430 | 1 | 762431 | 2492.46 | N/A | 2705.68 | 45.0947 | 2492.46 | N/A | 2705.68 | 45.0947 | 2492.65 | N/A | 2705.69 | 45.0948 | 2499.72 | N/A | 2709.78 | 18.0652 | 2492.64 | N/A | 2705.72 | 45.0953
GEN-2018-004 | DIS-18-1 | 05 SOUTHWEST | SPS | 74.99 | ER | Solar | T14 Circuit 115kV line | 762441 | 1 | 762442 | 3351.47 | N/A | 4175.22 | 139.1925 | 3351.48 | N/A | 4175.22 | 139.1925 | 3351.51 | N/A | 4175.23 | 139.1929 | 3352.05 | N/A | 4175.32 | 139.1959 | 3361 | N/A | 4216.64 | 56.2294
GEN-2018-007 | DIS-18-1 | 01 NORTH | WAPA | 150 | ER/NR | Solar | Summit 115kV Substation | 762452 | 1 | 652522 | 930.7 | N/A | 1031.07 | 6.8738 | 924.76 | N/A | 1027.04 | 17.1173 | 924.6 | N/A | 1027 | 17.1167 | 924.6 | N/A | 1027 | 17.1167 | 924.6 | N/A | 1027 | 17.1167
GEN-2018-008 | DIS-18-1 | 01 NORTH | WAPA | 124.32 | ER/NR | Wind | Groton-Leland Olds 345kV Line | 762540 | 1 | 762544 | 2539.04 | 20.4234 | 2597.75 | 20.8957 | 2503.77 | 33.5662 | 2573.6 | 103.5071 | 2502.72 | 33.5521 | 2573.18 | 103.4902 | 2502.7 | 33.5519 | 2573.18 | 103.4902 | 2502.7 | 33.5519 | 2573.18 | 103.4902
GEN-2018-008 | DIS-18-1 | 01 NORTH | WAPA | 127.68 | ER/NR | Wind | Groton-Leland Olds 345kV Line | 762543 | 1 | 762544 | 2539.04 | 19.886 | 2597.75 | 20.3458 | 2503.77 | 32.6829 | 2573.6 | 100.7832 | 2502.72 | 32.6692 | 2573.18 | 100.7668 | 2502.7 | 32.6689 | 2573.18 | 100.7668 | 2502.7 | 32.6689 | 2573.18 | 100.7668
GEN-2018-009 | DIS-18-1 | 03 CENTRAL | SUNC | 150 | ER/NR | Wind | Cimarron 115kV Substation | 762474 | 1 | 539654 | 1167.92 | 12.9769 | 1406.22 | 46.874 | 1168.5 | 12.9833 | 1406.45 | 46.8817 | 1171.38 | 7.8092 | 1408.61 | 9.3907 | 1169.22 | 12.9913 | 1407.06 | 46.902 | 1171.88 | 13.0209 | 1411.35 | 47.045
GEN-2018-010 | DIS-18-1 | 01 NORTH | WAPA | 74.1 | ER/NR | Battery | Neset 230kV Substation | 762485 | 1 | 659138 | 3740.65 | N/A | 4136.44 | 55.8224 | 3541.07 | N/A | 3895.6 | N/A | 3540.43 | N/A | 3895.36 | N/A | 3540.42 | N/A | 3895.36 | N/A | 3540.42 | N/A | 3895.36 | N/A
GEN-2018-011 | DIS-18-1 | 04 SOUTHEAST | WFEC | 74.1 | ER/NR | Battery | Dover 138 kV Switching Station | 762496 | 1 | 520882 | 2010.44 | N/A | 2070.43 | N/A | 2010.52 | N/A | 2070.45 | N/A | 2013.29 | N/A | 2071.47 | N/A | 2342.91 | N/A | 2470.63 | 33.3418 | 2011.21 | N/A | 2070.72 | N/A
GEN-2018-012 | DIS-18-1 | 02 NEBRASKA | NPPD | 74.1 | ER/NR | Wind | Antelope - Hoskins 345kV line | 762507 | 1 | 762508 | 5492.34 | 123.5344 | 5896.37 | 397.8658 | 5966.04 | 80.5134 | 6320.96 | 85.3031 | 5475.62 | 123.1583 | 5887.13 | 397.2423 | 5471.83 | 123.0731 | 5886.23 | 397.1815 | 5471.61 | 123.0682 | 5886.21 | 397.1802
GEN-2018-013 | DIS-18-1 | 03 CENTRAL | WERE | 74.1 | ER/NR | Wind | Abilene Energy Center-Northview 115kV Line | 762517 | 1 | 760000 | 1495.42 | 33.6352 | 1564.12 | 105.5412 | 1496.04 | 33.6491 | 1564.28 | 105.552 | 1686.64 | 22.7617 | 1746.23 | 23.5659 | 1496.77 | 33.6655 | 1564.42 | 105.5614 | 1495.52 | 33.6374 | 1564.14 | 105.5425
GEN-2018-014 | DIS-18-1 | 03 CENTRAL | KCPL | 74.1 | ER/NR | Wind | Holt County 345kV Substation | 762528 | 1 | 541510 | 5068.76 | 114.0072 | 5445.5 | 367.4427 | 5078.54 | 114.2272 | 5451.23 | 367.8293 | 5472.08 | 73.8472 | 5835.58 | 78.7528 | 5068.83 | 114.0088 | 5445.42 | 367.4373 | 5068.25 | 113.9957 | 5445.4 | 367.4359
GEN-2018-015 | DIS-18-1 | 05 SOUTHWEST | SPS | 126 | ER/NR | Solar | Tuco-Oklaunion 345kV Line | 762463 | 1 | 762467 | 2475.89 | N/A | 2879.07 | 57.1244 | 2475.92 | N/A | 2879.07 | 57.1244 | 2476.56 | N/A | 2879.19 | 57.1268 | 2506.32 | N/A | 2904.09 | 57.6208 | 2611.43 | N/A | 2992.92 | 23.7533
GEN-2018-015 | DIS-18-1 | 05 SOUTHWEST | SPS | 126 | ER/NR | Solar | Tuco-Oklaunion 345kV Line | 762466 | 1 | 762467 | 2475.89 | N/A | 2879.07 | 57.1244 | 2475.92 | N/A | 2879.07 | 57.1244 | 2476.56 | N/A | 2879.19 | 57.1268 | 2506.32 | N/A | 2904.09 | 57.6208 | 2611.43 | N/A | 2992.92 | 23.7533
GEN-2018-021 | DIS-18-1 | 04 SOUTHEAST | AEPW | 74.1 | ER/NR | Solar | Chisholm-Gracemont 345kV Line | 762573 | 1 | 560078 | 4872.69 | N/A | 5244 | 176.9231 | 4873.06 | N/A | 5244.09 | 176.9261 | 4880.29 | N/A | 5247.21 | 177.0314 | 5044.42 | N/A | 5371.42 | 72.4888 | 4900.86 | N/A | 5258.92 | 177.4265
GEN-2018-022 | DIS-18-1 | 03 CENTRAL | KCPL | 148.5 | ER/NR | Solar | Mullen Creek 345kV Substation | 762584 | 1 | 541197 | 4440.32 | N/A | 4833.92 | 81.3791 | 4446.45 | N/A | 4837.21 | 81.4345 | 4680.85 | N/A | 5055.93 | 34.0467 | 4440.64 | N/A | 4833.88 | 81.3784 | 4440.01 | N/A | 4833.85 | 81.3779
GEN-2018-022 | DIS-18-1 | 03 CENTRAL | KCPL | 148.5 | ER/NR | Solar | Mullen Creek 345kV Substation | 762587 | 1 | 541197 | 4440.32 | N/A | 4833.92 | 81.3791 | 4446.45 | N/A | 4837.21 | 81.4345 | 4680.85 | N/A | 5055.93 | 34.0467 | 4440.64 | N/A | 4833.88 | 81.3784 | 4440.01 | N/A | 4833.85 | 81.3779
GEN-2018-022 | DIS-18-1 | 03 CENTRAL | KCPL | 3 | ER/NR | Solar | Mullen Creek 345kV Substation | 762588 | 1 | 541197 | 4440.32 | N/A | 4833.92 | 4028.2665 | 4446.45 | N/A | 4837.21 | 4031.0082 | 4680.85 | N/A | 5055.93 | 1685.31 | 4440.64 | N/A | 4833.88 | 4028.2332 | 4440.01 | N/A | 4833.85 | 4028.2082
GEN-2018-024 | DIS-18-1 | 04 SOUTHEAST | OKGE | 100 | ER | Battery | Canadian River-Muskogee and Muskogee-Seminole 345kV | 762595 | 1 | 588838 | 8402.53 | N/A | 10860.33 | N/A | 8403.13 | N/A | 10860.38 | N/A | 8428.21 | N/A | 10864.58 | N/A | 8738.58 | N/A | 11417.27 | 114.1727 | 8407.96 | N/A | 10869.46 | N/A
GEN-2018-025 | DIS-18-1 | 02 NEBRASKA | OPPD | 200 | ER | Battery | Fort Calhoun 345kV Substation | 762606 | 1 | 645451 | 10131.95 | N/A | 11962.82 | N/A | 10245.96 | N/A | 12147.88 | 60.7394 | 10141.56 | N/A | 11967.61 | N/A | 10116.63 | N/A | 11957.29 | N/A | 10116.21 | N/A | 11957.28 | N/A
GEN-2018-026 | DIS-18-1 | 04 SOUTHEAST | OKGE | 100 | ER | Battery | Mustang 138kV Substation | 762617 | 1 | 514861 | 6850.37 | N/A | 9062.31 | N/A | 6850.87 | N/A | 9062.39 | N/A | 6872.15 | N/A | 9069.73 | N/A | 7121.23 | N/A | 9299.9 | 92.999 | 6859.42 | N/A | 9065.7 | N/A
GEN-2018-027 | DIS-18-1 | 04 SOUTHEAST | OKGE | 100 | ER | Battery | Tulsa Power Station 38kV Substation | 762628 | 1 | 762629 | 6460.55 | N/A | 9152.79 | N/A | 6461.08 | N/A | 9152.84 | N/A | 6486.22 | N/A | 9158.57 | N/A | 6742.9 | N/A | 9381.06 | 93.8106 | 6462.58 | N/A | 9154.53 | N/A
GEN-2018-028 | DIS-18-1 | 04 SOUTHEAST | OKGE | 200 | ER | Battery | Tulsa North 138kV Substation | 762639 | 1 | 509817 | 6722.57 | N/A | 8226.16 | N/A | 6723.21 | N/A | 8226.23 | N/A | 6755.81 | N/A | 8235.89 | N/A | 6887.05 | N/A | 8384.82 | 41.9241 | 6724.31 | N/A | 8226.93 | N/A
GEN-2018-029 | DIS-18-1 | 04 SOUTHEAST | OKGE | 100 | ER | Battery | Horseshoe Lake 138kV Substation | 762650 | 1 | 509788 | 6569.53 | N/A | 9392.54 | N/A | 6570.08 | N/A | 9392.59 | N/A | 6596.29 | N/A | 9398.75 | N/A | 6861.8 | N/A | 9629.67 | 96.2967 | 6571.65 | N/A | 9394.38 | N/A
GEN-2018-030 | DIS-18-1 | 03 CENTRAL | SPS | 200 | ER | Battery | Lamar-Finney 345kV Substation | 762661 | 1 | 762662 | 1718.91 | N/A | 1454.96 | N/A | 1722.5 | N/A | 1456.18 | N/A | 1820.26 | N/A | 1637.67 | 8.1883 | 1720.95 | N/A | 1455.7 | N/A | 1721.43 | N/A | 1456.23 | N/A
GEN-2018-031 | DIS-18-1 | 03 CENTRAL | KCPL | 50 | ER | Battery | Blue Valley 161kV Substation | 762672 | 1 | 543000 | 6594.82 | N/A | 10299.15 | N/A | 6599.36 | N/A | 10299.85 | N/A | 6814.62 | N/A | 10456.7 | 209.134 | 6601.82 | N/A | 10299.54 | N/A | 6594.91 | N/A | 10299.15 | N/A
GEN-2018-032 | DIS-18-1 | 03 CENTRAL | WERE | 155 | ER | Wind | Neosho 345kV Substation | 762683 | 1 | 532793 | 9869.74 | 106.1262 | 11307.59 | 364.761 | 9872.28 | 106.1535 | 11307.89 | 364.7706 | 10056.53 | 64.8808 | 11429.57 | 73.7392 | 9967.66 | 107.1791 | 11340.76 | 365.831 | 9871.62 | 106.1465 | 11308.06 | 364.7761
GEN-2018-032 | DIS-18-1 | 03 CENTRAL | WERE | 155 | ER | Wind | Neosho 345kV Substation | 762686 | 1 | 532793 | 9869.74 | 106.1262 | 11307.59 | 364.761 | 9872.28 | 106.1535 | 11307.89 | 364.7706 | 10056.53 | 64.8808 | 11429.57 | 73.7392 | 9967.66 | 107.1791 | 11340.76 | 365.831 | 9871.62 | 106.1465 | 11308.06 | 364.7761
GEN-2018-033 | DIS-18-1 | 02 NEBRASKA | OPPD | 200 | ER | Battery | Cass County 345kV Substation | 762694 | 1 | 645740 | 10917.16 | N/A | 12242.42 | N/A | 11019.3 | N/A | 12413.3 | 62.0665 | 10956.79 | N/A | 12263.65 | N/A | 10909.38 | N/A | 12239.95 | N/A | 10908.74 | N/A | 12239.92 | N/A
GEN-2018-036 | DIS-18-1 | 02 NEBRASKA | WAPA | 200 | ER | Battery | Stegall 230kV Substation | 762705 | 1 | 659135 | 2634.56 | N/A | 2780.8 | N/A | 2637.5 | N/A | 2862.91 | 14.3146 | 2629.59 | N/A | 2768.12 | N/A | 2628.43 | N/A | 2767.81 | N/A | 2628.34 | N/A | 2767.81 | N/A
GEN-2018-037 | DIS-18-1 | 02 NEBRASKA | OPPD | 100 | ER | Battery | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV | 762716 | 1 | 646211 | 7051.56 | N/A | 8935.19 | N/A | 7091.94 | N/A | 9051.15 | 90.5115 | 7059.07 | N/A | 8938.33 | N/A | 7046.62 | N/A | 8933.35 | N/A | 7046.42 | N/A | 8933.34 | N/A
GEN-2018-038 | DIS-18-1 | 03 CENTRAL | KCPL | 203.4 | ER/NR | Solar | Sibley 345kV Substation | 762727 | 1 | 541201 | 9447.44 | N/A | 12768.51 | 156.9384 | 9455.98 | N/A | 12770.41 | 156.9618 | 9896.73 | N/A | 13044.82 | 64.1338 | 9458.8 | N/A | 12769.24 | 156.9474 | 9447.5 | N/A | 12768.48 | 156.9381
GEN-2018-039 | DIS-18-1 | 01 NORTH | WAPA | 72 | ER/NR | Solar | Edgeley 115kV substation | 762738 | 1 | 652432 | 661.33 | N/A | 738.13 | 10.2518 | 653.65 | N/A | 731.11 | 25.3858 | 653.62 | N/A | 731.11 | 25.3858 | 653.62 | N/A | 731.11 | 25.3858 | 653.62 | N/A | 731.11 | 25.3858
GEN-2018-040 | DIS-18-1 | 03 CENTRAL | KCPL | 100 | ER/NR | Wind | Sibley - Overton 345kV Line Break | 762754 | 1 | 762751 | 9447.44 | 157.4573 | 12768.51 | 638.4255 | 9455.98 | 157.5997 | 12770.41 | 638.5205 | 9896.73 | 98.9673 | 13044.82 | 130.4482 | 9458.8 | 157.6467 | 12769.24 | 638.462 | 9447.5 | 157.4583 | 12768.48 | 638.424
GEN-2018-041 | DIS-18-1 | 03 CENTRAL | KCPL | 400 | ER/NR | Wind | Sibley - Overton 345kV Line Break | 762759 | 1 | 762751 | 9447.44 | 39.3643 | 12768.51 | 159.6064 | 9455.98 | 39.3999 | 12770.41 | 159.6301 | 9896.73 | 24.7418 | 13044.82 | 32.6121 | 9458.8 | 39.4117 | 12769.24 | 159.6155 | 9447.5 | 39.3646 | 12768.48 | 159.606
GEN-2018-042 | DIS-18-1 | 03 CENTRAL | KCPL | 300 | ER/NR | Wind | Sibley - Overton 345kV Line Break | 762770 | 1 | 762751 | 9447.44 | 52.4858 | 12768.51 | 212.8085 | 9455.98 | 52.5332 | 12770.41 | 212.8402 | 9896.73 | 32.9891 | 13044.82 | 43.4827 | 9458.8 | 52.5489 | 12769.24 | 212.8207 | 9447.5 | 52.4861 | 12768.48 | 212.808
GEN-2018-043 | DIS-18-1 | 02 NEBRASKA | OPPD | 167 | ER/NR | Solar | Ft. Calhoun - Raun 345 kV Line Break | 762783 | 1 | 762779 | 7578.61 | N/A | 8785.79 | 131.5238 | 7648.71 | N/A | 8865.98 | 53.0897 | 7576.07 | N/A | 8784.85 | 131.5097 | 7564.97 | N/A | 8780.91 | 131.4507 | 7564.76 | N/A | 8780.9 | 131.4506
GEN-2018-043 | DIS-18-1 | 02 NEBRASKA | OPPD | 167 | ER/NR | Solar | Ft. Calhoun - Raun 345 kV Line Break | 762786 | 1 | 762779 | 7578.61 | N/A | 8785.79 | 131.5238 | 7648.71 | N/A | 8865.98 | 53.0897 | 7576.07 | N/A | 8784.85 | 131.5097 | 7564.97 | N/A | 8780.91 | 131.4507 | 7564.76 | N/A | 8780.9 | 131.4506
GEN-2018-043 | DIS-18-1 | 02 NEBRASKA | OPPD | 166 | ER/NR | Solar | Ft. Calhoun - Raun 345 kV Line Break | 762789 | 1 | 762779 | 7578.61 | N/A | 8785.79 | 132.3161 | 7648.71 | N/A | 8865.98 | 53.4095 | 7576.07 | N/A | 8784.85 | 132.302 | 7564.97 | N/A | 8780.91 | 132.2426 | 7564.76 | N/A | 8780.9 | 132.2425
GEN-2018-044 | DIS-18-1 | 02 NEBRASKA | OPPD | 167 | ER/NR | Solar | Fort Calhoun 345kV Substation | 762793 | 1 | 645451 | 10131.95 | N/A | 11962.82 | 179.0841 | 10245.96 | N/A | 12147.88 | 72.7418 | 10141.56 | N/A | 11967.61 | 179.1558 | 10116.63 | N/A | 11957.29 | 179.0013 | 10116.21 | N/A | 11957.28 | 179.0012
GEN-2018-044 | DIS-18-1 | 02 NEBRASKA | OPPD | 167 | ER/NR | Solar | Fort Calhoun 345kV Substation | 762796 | 1 | 645451 | 10131.95 | N/A | 11962.82 | 179.0841 | 10245.96 | N/A | 12147.88 | 72.7418 | 10141.56 | N/A | 11967.61 | 179.1558 | 10116.63 | N/A | 11957.29 | 179.0013 | 10116.21 | N/A | 11957.28 | 179.0012
GEN-2018-044 | DIS-18-1 | 02 NEBRASKA | OPPD | 166 | ER/NR | Solar | Fort Calhoun 345kV Substation | 762799 | 1 | 645451 | 10131.95 | N/A | 11962.82 | 180.1629 | 10245.96 | N/A | 12147.88 | 73.18 | 10141.56 | N/A | 11967.61 | 180.2351 | 10116.63 | N/A | 11957.29 | 180.0797 | 10116.21 | N/A | 11957.28 | 180.0795
GEN-2018-045 | DIS-18-1 | 02 NEBRASKA | NPPD | 184 | ER/NR | Solar | Gentleman - Red Willow 345kV Line | 762804 | 1 | 762808 | 5491.52 | N/A | 8299.47 | 112.7645 | 5654.48 | N/A | 8400.83 | 45.6567 | 5512.27 | N/A | 8311.59 | 112.9292 | 5489.27 | N/A | 8297.91 | 112.7433 | 5487.54 | N/A | 8297.59 | 112.739
GEN-2018-045 | DIS-18-1 | 02 NEBRASKA | NPPD | 183 | ER/NR | Solar | Gentleman - Red Willow 345kV Line | 762807 | 1 | 762808 | 5491.52 | N/A | 8299.47 | 113.3807 | 5654.48 | N/A | 8400.83 | 45.9062 | 5512.27 | N/A | 8311.59 | 113.5463 | 5489.27 | N/A | 8297.91 | 113.3594 | 5487.54 | N/A | 8297.59 | 113.3551
GEN-2018-045 | DIS-18-1 | 02 NEBRASKA | NPPD | 183 | ER/NR | Solar | Gentleman - Red Willow 345kV Line | 762811 | 1 | 762808 | 5491.52 | N/A | 8299.47 | 113.3807 | 5654.48 | N/A | 8400.83 | 45.9062 | 5512.27 | N/A | 8311.59 | 113.5463 | 5489.27 | N/A | 8297.91 | 113.3594 | 5487.54 | N/A | 8297.59 | 113.3551
GEN-2018-046 | DIS-18-1 | 02 NEBRASKA | NPPD | 134 | ER/NR | Wind | Gentleman - Red Willow 345kV Line | 762815 | 1 | 762808 | 5491.52 | 68.3025 | 8299.47 | 309.6817 | 5654.48 | 42.1976 | 8400.83 | 62.6928 | 5512.27 | 68.5606 | 8311.59 | 310.1339 | 5489.27 | 68.2745 | 8297.91 | 309.6235 | 5487.54 | 68.253 | 8297.59 | 309.6116
GEN-2018-046 | DIS-18-1 | 02 NEBRASKA | NPPD | 133 | ER/NR | Wind | Gentleman - Red Willow 345kV Line | 762818 | 1 | 762808 | 5491.52 | 68.816 | 8299.47 | 312.0101 | 5654.48 | 42.5149 | 8400.83 | 63.1641 | 5512.27 | 69.0761 | 8311.59 | 312.4658 | 5489.27 | 68.7878 | 8297.91 | 311.9515 | 5487.54 | 68.7662 | 8297.59 | 311.9395
GEN-2018-046 | DIS-18-1 | 02 NEBRASKA | NPPD | 133 | ER/NR | Wind | Gentleman - Red Willow 345kV Line | 762821 | 1 | 762808 | 5491.52 | 68.816 | 8299.47 | 312.0101 | 5654.48 | 42.5149 | 8400.83 | 63.1641 | 5512.27 | 69.0761 | 8311.59 | 312.4658 | 5489.27 | 68.7878 | 8297.91 | 311.9515 | 5487.54 | 68.7662 | 8297.59 | 311.9395
GEN-2018-048 | DIS-18-1 | 04 SOUTHEAST | OKGE | 150 | ER/NR | Solar | Pecan Creek 345kV Substation | 762826 | 1 | 515235 | 9683.06 | N/A | 13730.47 | 228.8412 | 9683.98 | N/A | 13730.56 | 228.8427 | 9723.69 | N/A | 13738.94 | 228.9823 | 10193.24 | N/A | 14115.07 | 94.1005 | 9688.18 | N/A | 13794.34 | 229.9057
GEN-2018-048 | DIS-18-1 | 04 SOUTHEAST | OKGE | 150 | ER/NR | Solar | Pecan Creek 345kV Substation | 762829 | 1 | 515235 | 9683.06 | N/A | 13730.47 | 228.8412 | 9683.98 | N/A | 13730.56 | 228.8427 | 9723.69 | N/A | 13738.94 | 228.9823 | 10193.24 | N/A | 14115.07 | 94.1005 | 9688.18 | N/A | 13794.34 | 229.9057
GEN-2018-049 | DIS-18-1 | 03 CENTRAL | SUNC | 120 | ER/NR | Solar | Thistle 345kV Substation | 762837 | 1 | 539801 | 7599.87 | N/A | 8137.1 | 169.5229 | 7618.01 | N/A | 8145.96 | 169.7075 | 7933.56 | N/A | 8567.85 | 71.3987 | 7766.02 | N/A | 8264.28 | 172.1725 | 7639.82 | N/A | 8168.51 | 170.1773
GEN-2018-050 | DIS-18-1 | 04 SOUTHEAST | AEPW | 200 | ER/NR | Solar | Longwood 345kV Substation | 762848 | 1 | 508809 | 7402.72 | N/A | 9572.74 | 119.6593 | 7402.73 | N/A | 9572.74 | 119.6593 | 7403.33 | N/A | 9572.77 | 119.6596 | 7424.15 | N/A | 9607.09 | 48.0354 | 7403.27 | N/A | 9572.82 | 119.6603
GEN-2018-051 | DIS-18-1 | 05 SOUTHWEST | OKGE | 35 | ER/NR | Battery | Pecan Creek 345kV Substation | 762859 | 1 | 515235 | 9683.06 | N/A | 13730.47 | N/A | 9683.98 | N/A | 13730.56 | N/A | 9723.69 | N/A | 13738.94 | N/A | 10193.24 | N/A | 14115.07 | N/A | 9688.18 | N/A | 13794.34 | 394.124
GEN-2018-052 | DIS-18-1 | 05 SOUTHWEST | SPS | 70 | ER/NR | Battery | Roadrunner 115kV Substation | 762869 | 1 | 528025 | 1875.62 | N/A | 2039.8 | N/A | 1875.62 | N/A | 2039.8 | N/A | 1875.64 | N/A | 2039.8 | N/A | 1875.93 | N/A | 2039.86 | N/A | 1881.23 | N/A | 2213.85 | 31.6264
GEN-2018-053 | DIS-18-1 | 03 CENTRAL | WERE | 100 | ER/NR | Wind | Kelly 161kV Substation | 762881 | 1 | 532913 | 1846.86 | 30.781 | 1908.08 | 95.404 | 1848 | 30.8 | 1908.57 | 95.4285 | 1854.79 | 18.5479 | 1910.4 | 19.104 | 1847.23 | 30.7872 | 1908.11 | 95.4055 | 1846.85 | 30.7808 | 1908.08 | 95.404
GEN-2018-054 | DIS-18-1 | 03 CENTRAL | KCPL | 120 | ER/NR | Solar | KC South - N. Raymore 161kV Line | 762892 | 1 | 541231 | 1477.77 | N/A | 1670.34 | 34.7987 | 1477.95 | N/A | 1670.35 | 34.799 | 1488.19 | N/A | 1757.59 | 14.6466 | 1478.19 | N/A | 1670.36 | 34.7992 | 1477.78 | N/A | 1670.34 | 34.7987
GEN-2018-055 | DIS-18-1 | 04 SOUTHEAST | AEPW | 252 | ER/NR | Solar | Terry Road 345kV Station | 762903 | 1 | 511568 | 5108.96 | N/A | 5733.53 | 56.8803 | 5109.11 | N/A | 5733.54 | 56.8804 | 5113.68 | N/A | 5734.38 | 56.8887 | 5593.37 | N/A | 6330.62 | 25.1215 | 5155.8 | N/A | 5765.06 | 57.1931
GEN-2018-056 | DIS-18-1 | 02 NEBRASKA | WAPA | 102.6 | ER/NR | Solar | Fort Thompson-Grand Island (Grand Prairie) 345kV | 762914 | 1 | 762916 | 5144.87 | N/A | 5477.94 | 133.4781 | 5399.34 | N/A | 5715.61 | 55.7077 | 5095.5 | N/A | 5442.67 | 132.6187 | 5092.99 | N/A | 5442.04 | 132.6033 | 5092.81 | N/A | 5442.02 | 132.6028
GEN-2018-057 | DIS-18-1 | 03 CENTRAL | WERE | 203.4 | ER/NR | Solar | Gordon Evans 138kV | 762925 | 1 | 533040 | 6841.97 | N/A | 7978.02 | 98.0583 | 6848.28 | N/A | 7980.19 | 98.0849 | 7308.76 | N/A | 8627.39 | 42.4159 | 6941.27 | N/A | 8039.25 | 98.8108 | 6846.32 | N/A | 7980.06 | 98.0833
GEN-2018-058 | DIS-18-1 | 03 CENTRAL | WERE | 252 | ER/NR | Solar | Stranger Creek 345kV | 762936 | 1 | 532772 | 9390.32 | N/A | 15682.33 | 155.5787 | 9402.76 | N/A | 15685.17 | 155.6068 | 10237.77 | N/A | 16362.12 | 64.929 | 9409.83 | N/A | 15684.52 | 155.6004 | 9390.8 | N/A | 15682.36 | 155.579
GEN-2018-059 | DIS-18-1 | 03 CENTRAL | WERE | 252 | ER/NR | Solar | Stranger Creek 345kV | 762946 | 1 | 532772 | 9390.32 | N/A | 15682.33 | 155.5787 | 9402.76 | N/A | 15685.17 | 155.6068 | 10237.77 | N/A | 16362.12 | 64.929 | 9409.83 | N/A | 15684.52 | 155.6004 | 9390.8 | N/A | 15682.36 | 155.579
GEN-2018-060 | DIS-18-1 | 02 NEBRASKA | NPPD | 50 | ER/NR | Wind | Axtell-Post Rock 345 kV | 762957 | 1 | 560082 | 3936.43 | 131.2143 | 4191.97 | 419.197 | 4895.62 | 97.9124 | 5136.63 | 102.7326 | 3959.03 | 131.9677 | 4205.42 | 420.542 | 3937.61 | 131.2537 | 4192.39 | 419.239 | 3935.79 | 131.193 | 4191.9 | 419.19
GEN-2018-061 | DIS-18-1 | 03 CENTRAL | WERE | 50 | ER/NR | Wind | Kelly 161kV Substation | 762968 | 1 | 532913 | 1846.86 | 61.562 | 1908.08 | 190.808 | 1848 | 61.6 | 1908.57 | 190.857 | 1854.79 | 37.0958 | 1910.4 | 38.208 | 1847.23 | 61.5743 | 1908.11 | 190.811 | 1846.85 | 61.5617 | 1908.08 | 190.808
GEN-2018-062 | DIS-18-1 | 03 CENTRAL | KACY | 75.6 | ER/NR | Solar | Nearman 161kV substation | 762979 | 1 | 546653 | 3938.15 | N/A | 4981.9 | 164.7454 | 3939.7 | N/A | 4982.05 | 164.7503 | 4022.38 | N/A | 5009.89 | 66.2684 | 3941.25 | N/A | 4982.07 | 164.751 | 3938.22 | N/A | 4981.91 | 164.7457